## Slide 1
NFRC Telemetry update
TWG
4/24/2025
ERCOT Staff

## Slide 2: Retain NFRC Telemetry
RTCB improves the telemetry from Resources with Power Augmentation Capacity (offline when duct burners are not fired) by introducing new telemetry points.
  High limit of the Frequency Responsive Capacity (HFRL)
  Low Limit of the Frequency Responsive Capacity (LFRL)
  Frequency Responsive Capacity Factor (FRQF)
  Inactive Power Augmentation Capacity (PAUG)
ERCOT has identified the need to retain the current NFRC telemetry in RTCB to continue support the NERC BAL-001-TRE-2, unit governor response performance evaluation for Frequency Measurable Events. For this evaluation, only the unused/remaining duct capacity is excluded which is informed to ERCOT by the current NFRC telemetry.
PAUG telemetry in RTCB is expected to be static unfired Power Augmentation capacity when ducts are not fired and 0 when ducts are fired, while NFRC telemetry will gradually drop to 0 as the Resource dispatches into the duct capacity.
Without NFRC telemetry, ERCOT cannot derive the unused/remaining duct capacity which is needed for BAL-001-TRE-2 evaluation.

## Slide 3: Retain NFRC Telemetry
To resolve this, ERCOT is requesting Market Participants to retain the NFRC telemetry and any logic that is being used to calculate the NFRC telemetry and continue to use it as is in the RTCB.
ERCOT will reinstate the relevant protocol language related to NFRC in the future Nodal Protocol Revisions.
ICCP Handbook was updated.

## Slide 4: Questions?