## Slide 1
PDCWG Report to ROS
Chair: Chad Mulholland, NRG
Vice Chair: N/A
ROS
May 1st, 2025

## Slide 2: Report Overview & Notes
Report Overview
  Meeting Minutes
    Annual Inertia Presentation
    NPRR1278 - Establishing Advanced Grid Support Service as an Ancillary Service
    RTCB Telemetry for Resources with Power Augmentation Capacity
    NPRR1257/NOGRR271 - RRS Limits Update
    Status on BAL-001-TRE, SAR-13
  BAL-001-TRE-2 FMEs and IMFR
    1 FME in the month of March
  Frequency Control Report

## Slide 3: Frequency Measurable Events Performance

## Slide 4: Interconnection Minimum Frequency Response (IMFR) Performance
Frequency Response Obligation (FRO): 455 MW/0.1 Hz
IMFR Performance currently
1613.67 MW/0.1HZ

## Slide 5
Questions?

## Slide 6: Frequency Control Report
March 2025

## Slide 7: CPS1 Performance

## Slide 8: RMS1 Performance of ERCOT Frequency
Notes: 14.18 mHz on avg for March 2025

## Slide 9: Frequency Profile Analysis

## Slide 10: Time Error Corrections
Notes: Time error is negative throughout March. We saw significant accumulation in the first two weeks. ERCOT observed real-time telemetry and operational issues from wind and solar units which effected the ERCOT frequency control. ERCOT has been working with the Market Participants to address the operational issues. ERCOT tuned the GTBD ACE integral feedback to recover the time error.

## Slide 11: ERCOT Total Energy
Notes: 35,208,781 MWh

## Slide 12: ERCOT Total Energy from Wind Generation
Notes:   12,055,131 MWH

## Slide 13: ERCOT % Energy from Wind Generation
Notes: 34.24% of total energy was provided by wind generation

## Slide 14: ERCOT Total Energy from Solar Generation
Notes: 5,143,399 MWh

## Slide 15: ERCOT % Energy from Solar Generation
Notes: 14.61% of total energy was provided by solar generation

## Slide 16: ERCOT Daily Minimum System Inertia
Notes: Minimum Inertia in March 2025 = 118,032 MW*s on March 18th
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
March Data:
Mean: 154,700 MW*s
Max: 224,372 MW*s on March 24th
Min: 118, 032 MW*s on March 18th

## Slide 17: ERCOT Inertia Trend
Notes: Summary of ERCOT inertia for the previous 10 years. Lowest inertia this year was on March 18th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.