## Slide 1: Large Load Working Group
Presented to TAC
May 28, 2025
By Bob Wittmeyer

## Slide 2: Confirmation of Large Load Working Group Leadership
Chair
  Bob Wittmeyer – Longhorn Power
Vice Chair
  Patrick Gravois - ERCOT
Notes: Electing leadership is a crucial process in any organization or government. It involves selecting individuals who will guide and make decisions for the group. The process typically includes campaigning, debates, and voting. Effective leadership can drive success, inspire confidence, and ensure that the needs and wishes of the members are represented and acted upon.

## Slide 3: Voltage/Frequency Ride Through
Traditional – Protect the Load from Grid issues
    Maintaining Operation
      Voltage ride through enables electrical systems to sustain operation during short-term disturbances, preventing downtime of critical infrastructure.
    Advanced Power Management
      Effective voltage ride through strategies involve advanced power management systems that help prevent data loss and hardware damage during power fluctuations.
    Backup Systems
      Backup systems are crucial for voltage ride through, ensuring continued operation and mitigating risks associated with voltage disturbances.
Now – We need to Protect the Grid from Load Loss issues
Notes: Data center voltage ride through refers to the ability of electrical systems to maintain operation during short-term voltage disturbances. This ensures critical infrastructure remains operational, avoiding downtime. Effective voltage ride through strategies involve advanced power management and backup systems, aiding in the prevention of data loss and hardware damage during power fluctuations.

## Slide 4: Current Concerns
  3,055MW ERCOT approved capacity for operational LLs in WTX load zone
  Non-Coincident peak observed: ~2,200MW
Assuming a LL electric portion immediately trips if the voltage drops below 0.75pu, all the WTX LLs electronic portion will trip, leading to the total of loss of load of ~2,500MW
Assuming a LL electric portion can ride through 0.7pu for 20ms (ITIC curve), the total of loss of load is reduced to ~1,500MW
“Small” change can have a large impact
West Texas Today
West Texas Loads
Notes: Workshops are interactive sessions designed to enhance skills and knowledge on a particular subject. They provide hands-on experience and foster collaboration among participants. Whether focused on professional development, creative arts, or technical skills, workshops offer a valuable opportunity for learning and networking in an engaging environment.

## Slide 5: Workshop - July 11
Focus – Data Centers – Electronic Loads
Behind the Meter Solutions
  We will be interested in systems that can survive a short duration (sub second) of very low voltage without removing the load from the Grid.
  If you have such a system and would like to describe your solution, please contract the chair/vice chair.
Area/Regional Solutions
  We will be interested in solutions that could resolve Low Voltage issues on an area or wide area basis.
  If you have such a system and would like to describe your solution, please contract the chair/vice chair. (Batteries???)
Notes: Workshops are interactive sessions designed to enhance skills and knowledge on a particular subject. They provide hands-on experience and foster collaboration among participants. Whether focused on professional development, creative arts, or technical skills, workshops offer a valuable opportunity for learning and networking in an engaging environment.