## Slide 1
Combined Delaware Basin Stage 5 Project and Alternative
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
May 28, 2025

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Delaware Basin Stage 5 Project for Regional Planning Group (RPG) review in May 2024
Wind Energy Transmission Texas, LLC (WETT) submitted the Delaware Basin Stage 5 Project Alternative Project for Regional Planning Group (RPG) review in August 2024
    This Tier 1 Oncor proposed project submission was estimated to cost $744.6 million and will require a Certificate of Convenience and Necessity (CCN)
    This Tier 1 WETT proposed project submission was estimated to cost $305.5 million for WETT’s portion and will require a CCN
    Address reliability issues in Andrews, Borden, Culberson, Dawson, Gaines, Loving, Reeves, and Winkler Counties in the Far West Weather Zone
    Identified as Stage 5 from ERCOT’s 2019 Delaware Basin Load Integration Study

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT completed the Delaware Basin Load Integration Study (DBLIS) in December 2019 and recommended an import path option to reliably serve load once the peak demand level of the Delaware Basin area exceeds 5,422 MW, the 2023 RTP 2025 case exceeds this point
The 2024 Permian Basin Reliability Plan Study identified the need for the DBLIS upgrades in addition to significant new transmission upgrades in the Delaware Basin area

## Slide 5: Comparison of Project Options
Among the two options, Oncor’s Option addresses the reliability need to accommodate the significant and rapid load growth in the Delaware Basin area, is the least cost option, requires the least amount of CCN mileage and improves long-term load-serving capability.
ERCOT recommends Oncor’s Option as the preferred option
 | Oncor | WETT
Address the project needs | Yes | Yes
Meets ERCOT and NERC Reliability Criteria | Yes | Yes
Improves Long-Term Load-Serving Capability | Yes | Yes
Requires CCN (~miles) | 220 | 232
Expected ISD** (Month Year) | December 2029 | December 2029
Cost Estimate* (~$M) | 855.3 | 871.0
Feasible | Yes | Yes
* The cost estimates were provided by the TSPs
** The expected ISD is tentative and are subject to change based on requirements for various approvals, ROW acquisition, and/or construction progress

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Oncor’s Option and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Oncor’s Option did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse Oncor’s Option to address reliability issues in Andrews, Borden, Culberson, Dawson, Gaines, Loving, Reeves, and Winkler Counties in the Far West Weather Zone
TSPs expect to implement the upgrades by December 2029
Estimated Capital Cost: $855.30 million

## Slide 9: ERCOT Recommendation
Expand the existing Lamesa Switch, including a 13-breaker 138-kV breaker-and-a-half bus arrangement and a 9-breaker 345-kV breaker-and-a-half bus arrangement with two 600 MVA, 345/138-kV autotransformers. All terminal and associated equipment will meet or exceed 5,000 A for 345-kV and 3,200 A for 138-kV;
Construct a new Clearfork Switch to Lamesa Switch 345-kV double-circuit transmission line using a normal and emergency ratings of at least 2,988 MVA, which will require new right of way (ROW), approximately 77.0-mile;
Expand the existing Faraday 345-kV substation to accommodate the new Lamesa Switch to Faraday Switch 345-kV double-circuit transmission line and loop in the existing Long Draw to Scurry 345-kV transmission line;
Construct a new Lamesa Switch to Faraday Switch 345-kV double-circuit transmission line using a normal and emergency ratings of at least 2,988 MVA, which will require new ROW, approximately 38.0-mile;
Establish a new Pivot 138/69-kV Switch in the current Welch Tap location which will include;
  Relocating one of the existing Lamesa 138/69-kV autotransformers and three of the existing Lamesa 69-kV breakers to the new Pivot 138/69-kV Switch; and
  Rebuilding and converting the existing Lamesa Switch to Welch Tap 69-kV transmission line to 138-kV operation using a normal and emergency rating of at least 614 MVA, 2.0-mile;

## Slide 10: ERCOT Recommendation (Continued)
Rebuild the existing Clearfork 345-kV Switch by installing thirteen 5,000 A, 345-kV circuit breakers in a breaker-and-a-half bus arrangement;
Install two 5,000 A, 345-kV circuit breakers in a breaker-and-a-half bus arrangement at the planned Drill Hole 345-kV Switch; and
Construct a new Clearfork Switch to Drill Hole Switch 345-kV double-circuit transmission line using a normal and emergency ratings of at least 2,988 MVA, which will require new ROW, approximately 105.0-mile;

## Slide 11: ERCOT Recommendation