## Slide 1: Impact of Duration Constraints for NSPIN on SCED Awards
Presented to:
Technical Advisory Committee
Andrew Reimers, Ph.D.
Potomac Economics
May 28, 2025

## Slide 2: Summary and Recommendation
Imposing a four-hour duration constraint on NSPIN results in SCED awarding base points to ESRs, thus depleting rather than preserving SOC
This outcome runs counter to the stated objective of preserving reserve capacity through a prolonged reliability event
We recommend that ERCOT approve NPRR 1282 as amended by the IMM, which sets the duration requirement for NSPIN at one hour

## Slide 3: Higher Duration Constraints on NSPIN Lead to Greater Energy Awards for ESRs
The expressed intention of the higher duration constraint for NSPIN is to ensure that reserves are able to last longer through a reliability event such as prolonged forecast error
In practice, this constraint will lead to more base points being awarded to ESRs, which will then exhaust their SOC and make them unavailable to provide either energy or reserves as the event persists
  As SOC declines, SCED increasingly favors ESRs for energy instead of AS
  This dynamic does not depend on high-priced offers for AS
Lower duration requirements reduce the opportunity cost for ESRs to provide NSPN, thus preserving SOC until it is needed

## Slide 4: A Simplified SCED Simulation Tool Was Used to Demonstrate this Dynamic
No Transmission Constraints
Resources
  Thermal generator
    HSL = 40,000 MW
    AS Qty = 10,000
    Energy Offer = $29/MWh
  ESR
    HSL 10,000 MW
    AS Qty = 10,000 MW
    Energy Offer = $1000/MWh
    Max SOC = 10,000 MWh
  Both resources offer RegUp at $6 and all other AS at $0
Demand = 40,000 MW
AS Plan
  RegUp = 900MW
  RRS = 2300 MW
  ECRS = 2300 MW
  NSPIN = 4,000 MW
  Total = 9,500 MW

## Slide 5: Simplified Demand Curves Based on NPRR 1268
Chart: AS Demand Curves
| 0 | 810 | 810 | 832.5 | 832.5 | 855 | 855 | 877.5 | 877.5 | 900
REGUP | 9052 | 9052 | 3250 | 3250 | 2250 | 2250 | 1250 | 1250 | 250 | 250
RRS | 7051 | 7051 | 3100 | 3100 | 2100 | 2100 | 1100 | 1100 | 100 | 100
ECRS | 5050 | 5050 | 3040 | 3040 | 2030 | 2030 | 1020 | 1020 | 15 | 15
NSPIN | 5000 | 5000 | 1000 | 1000 | 100 | 100 | 55 | 55 | 15 | 15 | 0.1 | 0.1 | 0.01 | 0.01

## Slide 6: Impact of NSPIN Duration Requirement on Awards
Chart: 4-Hour NSPIN Duration
| 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
Energy | 0 | 0 | 0 | 99.5745 | 354.8936 | 610.2128 | 865.5319 | 10 | 964.0909 | 2733 | 0
NSPIN | 1643 | 1393.75 | 1143.75 | 907.9255 | 652.6064 | 397.2872 | 141.9681 | 0 | 0 | 0 | 0
Chart: 1-Hour NSPIN Duration
| 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
Energy | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 964.0909 | 2733 | 0
NSPIN | 4500 | 4500 | 4100 | 3100 | 2575 | 1575 | 651.25 | 10 | 0 | 0 | 0

## Slide 7: Impact of NSPIN Duration on Prices
Chart: 4-Hour NSPIN Duration
| 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
Energy | 1002.08 | 1002.08 | 1002.08 | 1020.6596 | 1020.6596 | 1020.6596 | 1020.6596 | 1085 | 1088.2727 | 1194.2 | 11053
REGUP | 18.5 | 18.5 | 18.5 | 129.9574 | 129.9574 | 129.9574 | 129.9574 | 516 | 535.6364 | 1171.2 | 9052
RRS | 12.5 | 12.5 | 12.5 | 123.9574 | 123.9574 | 123.9574 | 123.9574 | 510 | 529.6364 | 1165.2 | 7051
ECRS | 25 | 25 | 25 | 247.9149 | 247.9149 | 247.9149 | 247.9149 | 1020 | 1059.2727 | 1165.2 | 5050
NSPIN | 100 | 100 | 100 | 991.6596 | 991.6596 | 991.6596 | 991.6596 | 1056 | 1059.2727 | 1165.2 | 5000
Chart: 1-Hour NSPIN Duration
| 0 | 0.1 | 0.2 | 0.3 | 0.4 | 0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 1
Energy | 1000.01 | 1000.01 | 1000.01 | 1001.25 | 1004.58 | 1008.3 | 1083.3 | 1085 | 1088.2727 | 1194.2 | 11053
REGUP | 6.05 | 6.05 | 6.05 | 13.5 | 33.5 | 56 | 506 | 516 | 535.6364 | 1171.2 | 9052
RRS | 0.05 | 0.05 | 0.05 | 7.5 | 27.5 | 50 | 500 | 510 | 529.6364 | 1165.2 | 7051
ECRS | 0.1 | 0.1 | 0.1 | 15 | 55 | 100 | 1000 | 1020 | 1059.2727 | 1165.2 | 5050
NSPIN | 0.1 | 0.1 | 0.1 | 15 | 55 | 100 | 1000 | 1020 | 1059.2727 | 1165.2 | 5000

## Slide 8: Energy Offers and Forecast Error
These simulations assumed a $1000/MWh energy offer for ESRs
Higher energy offers (e.g., $2000/MWh) would have reduced or eliminated energy awards for ESRs. What if ESR operators just increase their EOC to preserve SOC?
One of the primary reliability risks under consideration is prolonged forecast error, i.e., net demand and corresponding prices are expected to decrease, but they remain elevated
If ESR operators perceive that net load and prices are set to decrease soon, they have less incentive to preserve SOC
Reducing the duration constraint on NSPIN decreases the opportunity cost of carrying reserves despite elevated energy prices

## Slide 9: Conclusions
Imposing a four-hour duration constraint on NSPIN results in SCED awarding base points to ESRs, thus depleting rather than preserving SOC
A four-hour duration constraint also increases the opportunity cost of carrying NSPIN relative to selling energy, i.e., there is a stronger incentive to sell energy rather than reserves while energy prices are elevated
In contrast to the expressed intention of the four-hour duration requirement, these tendencies lead to exhaustion of SOC such that ESRs cannot provide either energy or reserves as an event persists.
These outcomes would be avoided by approval of NPRR 1282 as amended by the IMM