## Slide 1
NPRR 1282 AS Duration Under RTC
May 26, 2025
TAC
Nitika Mago
Mgr Sr Balancing Operations Planning

## Slide 2: Introduction
Ancillary Services (AS) are an important mechanism for maintaining the reliability of the ERCOT Interconnection.
  The importance of AS has grown and continues to grow as variability and uncertainty of both supply resources and demands on the grid continue to increase.
AS are procured to satisfy two purposes:
  Meet certain supply and demand balancing related reliability objectives defined in NERC Reliability Standards, and
  Reduce operational risks associated with variability and uncertainty.
NPRR1282 specifies the duration requirements of AS that are procured in Real Time Market (RTM) based on reliability needs specially from the perspective of energy sufficiency to respond to typical events that have been experienced or may be experienced. ERCOT is recommending to,
  Increase Regulation and RRS duration to 30 minutes to reduce the risk of ERCOT violating ERCOT’s BAL-001 obligation in the event when SCED is not available due to unplanned events.
  Decrease ECRS duration to one-hour
  Retain the four-hour duration for Non-Spin
Under RTC during scarcity conditions, RTC-SCED is expected to prioritize serving load and not procure the full AS plan. Hence to assess the duration needs for Non-Spin, ERCOT’s analysis drew its conclusions specifically by looking at events which occurred on non-scarcity days. These would be days when offline capacity was available but due to the nature of events could not be committed in a timely manner.

## Slide 3: IMM’s Example: Valuing Energy over Non-Spin
The IMM shared analysis that demonstrated that because energy has a lower duration than Non-Spin, under specific system conditions with specific offers, it was possible for SCED to award ESRs energy over Non-Spin.
ERCOT notes that the example the IMM has laid out is a very extreme scenario.
ERCOT has conducted an analysis using the IMM’s assumptions and then extended the same. Specifically, ERCOT has analyzed the following 4 scenarios
  Example 1-1: Same as IMM’s posted on May 21 RTCTF meeting page.
  Example 1-2: ESR energy offer = $2,000/MW, rest same as Example 1-1.
  Example 2-1: AS plan from Aug 2025 HE 20, ESR energy offer = $1,000/MW, rest same as Example 1-1.
  Example 2-2: AS plan from Aug 2025 HE 20, ESR energy offer = $2,000/MW, rest same as Example 1-1.
ERCOT agrees that SCED optimization may award energy over longer duration AS. However, ERCOT notes that system conditions, the volume of AS being procured, and energy offers all play a role in the level of SOC depletion at which this may occur.
  With higher energy offers, ESRs are able to further protect SOC, if needed.
  With a more typical AS plan, SCED optimization may still award energy over Non-Spin or award Non-Spin to resources other than ESRs, but at relatively higher SOC depletion levels than what are in the IMM’s example.

## Slide 4: Extension to Analysis IMM Conducted
Example 1-1
No Transmission Constraints
Resources
  Thermal generator
    HSL = 40,000 MW
    AS Qty = 10,000
    Energy Offer = $29/MWh
  ESR
    HSL 10,000 MW
    AS Qty = 10,000 MW
    Energy Offer = $1000/MWh
    Max SOC = 10,000 MWh
  Both resources offer RegUp at $6 and all other AS at $0
Demand = 40,000 MW
AS Plan
  RegUp = 900 MW
  RRS = 2,300 MW
  ECRS = 2,300 MW
  NSPIN = 4,000 MW
  Total = 9,500 MW
Example 2-1
No Transmission Constraints
Resources, Demand, Energy and AS Offer same as Example 1-1
AS Plan from Aug HE20
  RegUp = 598 MW
  RRS = 2,300 MW
  ECRS = 1,451 MW
  NSPIN = 1,912 MW
  Total = 6,261 MW
Example 2-2
No Transmission Constraints
Resources, Demand, AS Offer same as Example 1-1
  Thermal generator
    Energy Offer = $29/MWh
  ESR
    Energy Offer = $2000/MWh
AS Plan from Example 2
Example 1-2
No Transmission Constraints
Resources, Demand, AS Offer same as Example 1-1
  Thermal generator
    Energy Offer = $29/MWh
  ESR
    Energy Offer = $2000/MWh
AS Plan from Example 1

## Slide 5: Energy Award Comparison
With an AS plan that matches the assumed load level, ESRs don’t get dispatched for energy till SOC depletion reaches 70% as compared to example 1-1 where ESRs were dispatched at 30% depletion level. Increasing ESR’s Energy Offer Curve further increases the SOC depletion level at which ESRs are dispatched for energy.

## Slide 6: Non-Spin Award Comparison
With an AS plan that matches the assumed load level, Non-Spin under procurement at most depletion levels is lower as compared to example 1-1. With more typical requirements, Non-Spin awards to GRs occur at higher SOC depletion than example 1-1. Change in Energy offer results in very low Non-Spin awards at extremely high SOC depletion levels.

## Slide 7: ECRS Award Comparison
With a AS plan that matches the assumed load level, ECRS is under procured at higher SOC depletion levels as compared to example 1-1. With more typical requirements, ECRS starts getting awarded to GRs at around 80% SOC depletion same as example 1-1 but lower volume of ECRS is awarded to GRs. With higher energy offer, GRs are awarded portion of ECRS in the 90% SOC depletion case only.

## Slide 8: PRC Comparison
With an AS plan that matches the assumed load level, at SOC depletion levels that are greater than 70%, PRC drops below 3,000 MW.

## Slide 9: Energy Price Comparison
Energy price outcomes are fairly similar and closely match the energy offer of the ESRs in each scenario.

## Slide 10: ECRS and Non-Spin Price Comparison
With a AS plan that matches the assumed load level, higher Non-Spin prices are experienced at higher level of SOC depletion compared to example 1-1.

## Slide 11: Summary
NPRR 1282 specifies the duration requirements for the AS that are procured in Real Tim Market (RTM) based on reliability needs.
RTC SCED optimization considers the value of SOC (MWh), apart from MW capacity when determining which products are cleared.
Further, ERCOT does not necessarily see a problem with SCED optimization awarding energy over longer duration AS to ESR during tight operating conditions, based on their energy offers.
  During scarcity conditions, it is appropriate for SCED to value energy over reserves and is expected to go short on procuring reserves.
  Further, if scarcity/higher prices were to occur earlier than the typical net peak hours (i.e. sunset) ESRs have the ability to change their energy offers and preserve SOC for the later hours.
ERCOT also recognizes and agrees that with the expected growth of ESR installed capacity, additional system changes are needed to better manage SOC requirements for the future hours. ERCOT will continue working on identifying these changes and will share its finding/progress with TAC and the appropriate stakeholder groups.
Lastly, ERCOT is open to revisiting duration analysis post RTC Go Live with actual market data both as a part of work it is conducting in response to the PUC’s AS Study and when Dispatchable Reliability Reserve Service is implemented. ERCOT will share its finding/progress with TAC and the appropriate stakeholder groups.

## Slide 12
Appendix

## Slide 13: Relevant NERC Rules
 | NERC Reliability Standard | Requirement Summary
Frequency Related | BAL-001-2 R1 | Maintain 12 month rolling average CPS1 score ≥ 100%
 | BAL-001-2 R2 | Average ACE does not exceed Balancing Authority ACE Limit (BAAL) for more than 30 minutes (including during EEA)
 | BAL-003-2 R1 | Balancing Authority (BA) must maintain its annual Frequency Response Measure above its Frequency Response Obligation
 | BAL-002-3 R1.1 | BA must recover frequency to pre-disturbance value within 15 minutes
Reserves Related | BAL-002-3 R2 | BA shall have a plan to maintain contingency reserves to cover the most severe single contingency (MSSC)
 | BAL-002-3 R3 | BA must restore its contingency reserve to at least its MSSC within 90 minutes
Operations Related | EOP-011 | Balancing Authority will declare EEA3 when a system’s operating reserves are less than its Most Severe Single Contingency (MSSC) and will immediately take actions (including manual load shed) adequate to mitigate this emergency.

## Slide 14: Duration at other ISOs
A majority of the ISOs in North America have set 60 minutes as the duration requirement for AS. Following are specific details
CAISO
  Duration requirement for Real Time energy: 5 minutes
  Duration requirement for Real Time AS procurement including Regulation: 30 minutes
  Duration requirement for DAM & RUC AS procurement: 60 minutes
  Notes (1) in CAISO ESRs are incented to have a duration of 4 hours due to resource adequacy related requirements; (2) duration requirements are designed to stay compliant with WECC rules; (3) CAISO ‘s ESR fleet is comparable to ERCOT
MISO, NYISO, NEISO
  Duration requirement for Real Time energy: 5 minutes
  Duration requirement for Real Time AS procurement including Regulation: 60 minutes
  Duration requirement for DAM & RUC AS procurement: 60 minutes
  NYISO & NEISO’s duration requirements are designed to stay compliant with NPCC rules.

## Slide 15: RRS Award Comparison
With a AS plan that matches the assumed load level, RRS is under procured at higher SOC depletion levels as compared to example 1-1. Energy offer change does not seem to impact RRS procurement. At 90% SOC depletion, GRs are awarded portion of RRS.

## Slide 16: Regulation Award Comparison
With a AS plan that matches the assumed load level, Regulation Up is under procured at slightly higher SOC depletion levels as compared to example 1-1. Change in ESR Energy Offer Curve does not change the outcome. 100% from ESRs.

## Slide 17: Reg Up and RRS Price Comparison
Reg Up and RRS price outcomes are fairly similar in all scenarios.