## Slide 1
Lesson Learned
Loss of Monitoring and Control due to a Communication Failure between Control Centers
Wei Qiu
ERCOT TWG Conference Call
May 29, 2025

## Slide 2: Remote Operation

## Slide 3: Case 1
Planned maintenance on UPS at control B
Unintended consequence
  A momentary loss of power
  Stand-by backup firewall not recover properly
  ARP routine Issue
  Data was prevented from routing correctly through the firewall
Correction Actions
  Operators transitioned from control center A to control B
  Informed RC

## Slide 4: Case 2
Problem
  VPN tunnel collapsed (with unknown reasons)
  Both sites became “Primary” by design due to loss of communications between control centers
  After connecting both sites, a split-brain scenario was formed
  The system struggled to determine which COM was primary, which delayed the restoration process
  The databases out of sync
Corrective Actions
  A patch from EMS vendor

## Slide 5: Case 3
Problem
  Periodically operating from the alternate control center
  An issue with Ethernet Virtual Private Line (EVPL) connection
  Two-direction communication downgraded to one-direction
Corrective Actions
  the web-based read-only version of the EMS and communicated instructions

## Slide 6: Lessons Learned
Utilizing EMS servers located in the same area as the operation personnel, especially during nights, weekends, and holidays
Keeping/deploying a small number of operators work from the backup center during planned maintenance activities
Configuring workstations within the data center where the EMS server are hosted – avoid a need for VPN tunnels
Additional VPN tunnels across different geographical areas
And more

## Slide 7
Questions and Answers
Contact Information:
wei.qiu@nerc.net