## Info
Header Information
TDSP | Operator of the Major Transmission Element.
Major Transmission Element (MTE) | Transmission Element which was, or scheduled to be, on outage and has been associated with one or more high congestion(s).
Equip. Type | Equipment Type of the MTE.
kV | Voltage Level of the MTE. High-side voltage for transformers
Congestion Year/Month | Year and Month the associated congestion occurred.
Contingency | Contingency associated with the MTE.
Overload | Overload associated with the MTE.
Source | Source of the information: RT = Based on historical Real-Time congestion, ST = Based on Outage Coordination Studies. ADD = Addition Requests (both Private and Public)
Outage Type | Outage Type is categorized to be either Planned (PL) and Forced (FR, FE, UE, M1, M2, M3)
Cancel | Outage(s) for the specific MTE was Cancelled, Rejected, or Withdrawn.
Removal Requestor | Stakeholder who is requesting to remove the MTE from the list (Organization)
Addition Requestor | Stakeholder who is requesting to add the MTE from the list (Organization)
Reason for Addition | Justification for adding the MTE to the list. Details of the specific scenarios that the MTE may cause high congestion, including but not limited to: 1. ERCOT Load Level: Peak, Off-Peak (or 35GW, 70GW, etc). 2. Any specific regional load condition: High Houston Load, etc. 3. Wind Generation Level: High, Mid, Low, or N/A. 4. Solar Geneartion Level: High, Mid, Low, or N/A. 5. Any specific abnormal transmission equipment status: i.e. 345 kV line from A to B out-of-service, etc. 6. For Private Submissions, any specific generator output level: i.e. Resource A at 300 MW or above, etc. 7. (Optional) PSSE or PowerWorld case if available.
Reason for Removal | Justification for removing the MTE from the list. Usually entails a Transmission Upgrade Project.
OCITF Consensus | Consensus after OCITF meetings.
Decision | Final (TAC) Decision of the Addition/Removal Request for Non-Consensus items.
Discussion Items | Any other information that stakeholder(s) want to discuss during the OCITF meetings.

## MTE(2025)
TDSP | Major Transmission Element (MTE) | Equip. Type | kV | Congestion Year/Month | Contingency | Overload | Source | Outage Type | Cancel | Removal Requestor | Reason for Removal | OCITF Consensus | Decision | Discussion Items | From Acronym | To Acronym | ERCOT Equip Name | ERCOT Contingency ID
AEP | Abilene Elmcreek - Abilene Northwest | LN | 138 | 25/2 | Sweetwater East Switch -…- Perigee 345kV | Abilene Northwest Series Device 1 | RT | Planned | ELMCRK | ABNTHWST | ABNTHW_ELMCRK1 |  |  |  | ELMCRK | ABNTHWST | ABNTHW_ELMCRK1 | SABEABN8
AEP | Abilene Mulberry Creek - Abilene Northwest | LN | 138 | 25/3 | Foxtail To Oklaunion Lin 1 345kV | Abilene Elmcreek - Abilene Industrial Park 138kV | RT | Planned | MULBERRY | ABNTHWST | ABNTHW_MULBER1 |  |  |  | MULBERRY | ABNTHWST | ABNTHW_MULBER1 | SABNABM8
AEP | Abilene Mulberry Creek - Bluff Creek | LN | 345 | 25/3, 25/4 | Sweetwater East Switch To Long Creek Lin _a 345kV, DCKT Riley - Bowman Switch 345kV | Abilene Mulberry Creek - Long Creek 345kV, Fisher Road Switch - Riley 345kV | RT | Planned | [6 empty] | BLUF_CRK | MULBERRY | BLUF_C_MULBER1 | SABMBLU5
CNPE | Addicks - TH Wharton | LN | 345 | 22/4 | Roans Prairie - Singleton 345 kV & Singleton - Tomball 345 kV | TH Wharton - Zenith 345 kV | RT | Planned | [6 empty] | THW | ADK | ADKTHW71A | SADKTHW5
CNPE | Addicks - White Oak | LN | 345 | 23/1 | DCKT Obrien-WAP (OB-WAP98 & OB-WAP99) 345 kV | Jeanetta - Westwood 138 kV | RT | Planned | [6 empty] | WO | ADK | ADKWO_71 | SWOADK5
AEP | Agave - Whitepoint | LN | 138 | 23/3, 22/12 | DCKT White Point - Nueces Bay & Portland & Gibbs 138kV, Whitepoint Auto 345_1 345/138 kV, Lon Hill - Whitepoint 345 kV, Weil Tract - Lon Hill 138 kV | Lon_Hill - Calallan Waterworks Tap 69 kV, Lon_ Hill - Koch_ Hearns Ferry 138 kV | RT | Planned | [6 empty] | PELICAN | WHITE_PT | PELICA_WHITE_1 | SPELWHI8
CNPE | Airpro - Boggy | LN | 138 | 23/1 | Jefferson - College 138 kV | Conial - Philip 138 kV | RT | Planned | [6 empty] | AZ | BOG | AZ_BOG85A | SAZBOG8
AEP | Ajo - Cebolla | LN | 345 | 25/4 | Lon Hill To Nelson Sharpe Lin 1 345kV | Celanese Bishop - Nelson Sharpe 138kV | RT | Forced | [6 empty] | CEBOLLA | AJO | AJO_CEBOLL1 | SAJ2CEB5
TNMP | Alvin TNP - Mainland TNP | LN | 138 | 21/11 | Meadow - Ph Robinson 345 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned | [6 empty] | MAINLAND | ALVIN | 138_ALV_MNL | SALVMAI8
TNMP | Alvin Tnp - North Alvin Tnp | LN | 138 | 23/5 | Meadow - PH Robinson 345 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned | [6 empty] | ALVIN | TNNALVIN | 138_ALV_NAL | SALVTNN8
LCRA | Amos Creek - Brown Switch | LN | 345 | 24/5 | Big Hill - Kendal 345kv | Orient - Tennyson 138kV | RT | Forced | [6 empty] | BWNSW | AMOSCR | 710T710 | SAMOBWN5
AEP, CNPE | Angstrom - South Texas Project | LN | 345 | 25/2 | DCKT South Texas Project - Elmcreek 345kV | Blessing Auto 1382 345/138kV | RT | Planned | [6 empty] | STP | ANGSTROM | ANGSTR_STP1 | MANGNAI5
AEP | Angstrom - Whitepoint | LN | 345 | 23/12 | DCKT Fowlrton - San Miguel 345 kV | Asherton - … - Piloncillo 138 kV | RT | Planned | [6 empty] | ANGSTROM | WIHTE_PT | ANGSTR_WHITE_1 | SANGWHI5
ONCOR | Anna Switch - Cedar Elm Switch | LN | 345 | 22/3 | Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned | [6 empty] | CDESW | ANASW | 38025_A | SCDEANA5
ONCOR | Anna Switch - Krum West Switch | LN | 345 | 22/3, 21/12 | Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned | [6 empty] | KRWSW | ANASW | 38010_A | SANAKR15
LCRA | Antler - Highway 46 | LN | 138 | 23/7 | DCKT Bergheim - Kendall 345 kV & Kendall - Welfare 138 kV | Cranes Mill - Sattler 138 kV, Hunter - Purgatoy Road 138 kV | RT | Forced | [6 empty] | ANTLER | HIGH46 | 610T610 | SANTRIV8
AEP | Armstrong Aep - Yturria Sub | LN | 138 | 25/2, 23/7 | Lon Hill To Nelson Sharpe Lin 1 345kV, Ajo - Nelson Sharpe 345 kV | Celane Bishop - Nelson Sharpe 138kV, Falfurias - Premont 69 kV | RT | Planned, Forced | [6 empty] | LOYOLA | ARMSTRON | ARMSTR_LOYOLA1 | SARMRA38
AEP | Arroz - … - Lane City | LN | 138 | 23/10 | Esperanza - STP Switch 138 kV | Blessing - Lavlov 138 kV | RT | Planned | [6 empty] | ARROZ | LAN)CTY | ARROZ_LANCTY1 | SLANARR8
AEN | Austrop - Lost Pines Aen | LN | 345 | 24/10 | Holman Aen -…- Lytton Springs 345kV | Paige - Winchester 345 kV | RT | Planned | [6 empty] | AUSTRO | LOSTPINE | CKT_3120 | SLOSAUS5
LCRA, ONCOR | Austrop - Sandow Switch (440) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV (1661_A), Gilleland Creek - Mcneil 138 kV | RT | Planned | [6 empty] | SNDSW | AUSTRO | 440 | SSNDAU15
LCRA, ONCOR | Austrop - Sandow Switch (450) | LN | 345 | 22/4 | Hutto Switch - Zorn 345 kV & Hutto Switch - Gilleland Creek 345 kV, AEN Gilleland Creek - Techridge 138 kV | Round Rock - Round Rock Northeast 138 kV (1661_A), Gilleland Creek - Mcneil 138 kV | RT | Planned | [6 empty] | SNDSW | AUSTRO | 450 | SSNDAUS5
LCRA, STEC | Bakersfield - Cedar Canyon (BAKRFLD_CEDCA2) | LN | 345 | 24/10, 24/9 | Meteor Switch to Wolf Switching Station Lin_A, Meteor Switch to Moss Switch Lin_B | Odessa Ehv Switch - Yarbrough Sub 138kV, Penwell Pod - Wolf Switching Station 138kV | RT | Planned | [6 empty] | CEDACA | BAKESW | BAKRFLD_CEDCA2 | SBAKCED5
LCRA, STEC | Bakersfield - Cedar Canyon (BAKRFLD_CEDCAN) | LN | 345 | 22/4 | Midessa South Sw - Odessa EHV Switch 345 kV & Morgan Creek Ses -…- Quail Switch 345 kV, DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 Kv | Midessa South SW AXFMR1 345/138 kV, Dewey Lake Tap - Polecat Creek Switch 138 kV, Falcon Seaboard - Morgan Creek Ses 345 kV, Odessa - Odessa North 138 kV | RT | Planned | [6 empty] | CEDACA | BAKESW | BAKRFLD_CEDCAN | SBAKSCH5
GAR, LCRA | Bakersfield - Nevill Road Switch | LN | 345 | 22/4 | Moss Switch - Odessa EHV Switch 345 kV & Odessa EHV Switch - Wolf Switching Station 345 kV | Odessa - Odessa North 138 kV | RT | Planned | [6 empty] | NEVILLSW | BAKESW | NEVILL_BAKESW1 | SBAKNOR5
LCRA | Bandera - Rio Lago | LN | 138 | 24/11 | Cagnon-kendal 345 &cico-mengcr 138 | Medina Lake - Pipe Creek 138kV | RT | Planned | [6 empty] | RIOLAG | BANDER | 790T790 | SRIOBAN8
ONCOR | Barber Lake Switch - Morgan Creek Ses | LN | 138 | 24/5 | Wett_long_draw To Vealmoor 345kV | Morgan Creek SES - Moser Canyon Pod 138kV | RT | Planned | BRBSW | MGSES | 14035_A | SBRBMG38 |  |  | BRBSW | MGSES | 14035_A | SBRBMG38
AEP | Barney Davis -...- Nelson Sharpe | LN | 138 | 25/3 | Lon Hill To Nelson Sharpe Lin 1 345kV | Celanese Bishop - Nelson Sharpe 138kV | RT | Planned | [6 empty] | B_DAVIS | ALAZAN | ALAZAN_B_DAVI1 | SALAN_28
CNPE | Bayou Cogen - Big Bay | LN | 138 | 24/11 | Twr (138) Arm-ft35 & Ft-phr35 | Drouet - Garden Villas 138kV | RT | Forced | [6 empty] | BYU | BBP | BBPBYU79 | SBBPBYU8
ONCOR | Bell County - Temple Switch | LN | 138 | 25/4 | DCKT Chief Brady -…- Spanish Oak 138kv, Round Rock To Hutto Switch Lin 138kV | Round Rock - Round Rock Westinghouse 138kV | RT | Planned | [6 empty] | BELCNTY | TMPSW | 1715_A | SBELTMP8
BRAZOS | Bell County -…- Gabriel & Bartlett | LN | 69 | 25/2, 25/1 | DCKT Georgetown East -…- Bell County 345kV, DCKT Salado Switch - Knob Creek Switch 345 And Temple Switch - Bell County | Bell Country Auto XFMR 138/69 kV | RT | Planned | [6 empty] | BELCNTY | BARTLTSW | BEL_BART | SBARGAB9
ONCOR | Bell County East Switch - Sandow Switch | LN | 345 | 24/6, 24/8, 24/7, 24/6, 24/8, 24/7 | DCKT Salado Switch - Hutto Switch 345 Dblckt | Sandow Switch - Bell County East Switch Lin 421 345kV | RT | Planned | [6 empty] | SNDSW | BCESW | 421 | SBCESN35
CNPE | Bellaire - Kirby | LN | 138 | 21/10 | Eastside - Polk 138 kV | Downtown - Polk 138 kV | RT | Planned | [6 empty] | BI | KB | BI_KB_37A | SKBBI8
CNPE | Bellaire - Smithers | LN | 345 | 24/10, 24/9 | Twr (345) Jn-wap64 & Jn-wap72 | Bellaire - Wa Parish 345kV | RT | Forced | [6 empty] | BI | SMITHERS | BI_SMR98 | SBISMI5
ONCOR | Belton - … - Killeen Switch (641) | LN | 138 | 24/4 | DCKT Killeen Switch - Salado Switch 345 kV | Killeen Switch - Harker Heights South 138 kV | RT | Planned | [6 empty] | KLELM | KLNTF | 641_B | SHKHKLN8
ONCOR | Belton - Temple South | LN | 138 | 24/9 | DCKT Gabriel - Bell County & Gabriel- Knob Creek Switch 345/138kV | Scott and White POI - Temple South 138kV | RT | Planned | [6 empty] | TMSTH | BLTON | 610_A | SSANTM28
ONCOR | Benbrook -...- Wedgewood Switch (6120_J) | LN | 138 | 25/4 | Mdbsw To Rkcrk 345 And Tvwsw To Bnbsw 345 Dblckt | Hemphil - Mistletoe Heights 138kV | RT | Planned | [6 empty] | BNBRK | BRIRV | 6120_J | SBNBBNB8
ONCOR | Benbrook -…- Wedgewood Switch (6115_J) | LN | 138 | 25/4 | Mdbsw To Rkcrk 345 And Tvwsw To Bnbsw 345 Dblckt | Hemphil - Mistletoe Heights 138kV | RT | Planned | [6 empty] | BNBRK | BRIRV | 6115_J | SBNBBN28
ONCOR | Benbrook Switch - Parker Switch (6005_A) | LN | 345 | 21/10 | Comanche Peak Ses - Mitchell Bend Switch 345 kV & Comanche Peak Ses - Wolf Hollow 345 Switch 345 kV, DBCKT Comanche Peak Ses - Parker Switch 345 kV | Benbrook Switch - Parker Switch 345 kV (6042_A) | RT | Planned | [6 empty] | BNBSW | PKRSW | 6005_A | SBNBPKR5
ONCOR | Benbrook Switch - Parker Switch (6042_A) | LN | 345 | 25/3, 25/3, 21/10 | DCKT Comanche Peak Ses - Wolf Hollow Switch 345kV, DCKT Carmichael Bend Switch - Rocky Creek 345kV, DCKT Comanche Peak Ses - Parker Switch 345 kV | Benbrook Switch - Parker Switch 345kV (6005), Benbrook Switch - Parker Switch 345 kV (6042_A) | RT | Planned | [6 empty] | PKRSW | BNBSW | 6042_A | SBNBPK25
ONCOR | Benbrook Swith - … - Timberview Switch | LN | 345 | 20/10, 19/11, 17/3, 17/2 | DCKT Wedgewood Sw - Benbrook Switch 138 kV, DCKT Timberview Switch - Comanche Peak SES & Carmichael Bend Switch 345 KV | Hemphill - Mistletoe Heights 138 kV | RT | Planned, Forced | N | [5 empty] | BNBSW | SYCRK | 6000_A | SSYCEV25
LCRA | Benedum - Midkiff Switch | LN | 138 | 22/9 | SKYWEST to SPRABERRY SWITCH LIN 1 | Smidla Midland - Ctfld Sub 138 kV | RT | Planned | [6 empty] | BENEDU | MDKSW | 631T631 | SBENUPT8
LCRA | Bergheim - Hays Energy | LN | 345 | 23/3, 23/2, 22/8, 22/7, 21/10, | Cagnon - Kendall 345 kV & Cico - Menger Creek 138 kV, Cagnon - Kendall 345 kV & Cico - Comfort 138 kV, DCKT Cagnon-Kendall 345 kV&Txresch-Tally_Rd 138 kV | Medina Lake - Pipe Creek 138 kV, Bergeim - Kendall 345 kV, Bergheim Auto AT1 345/138kV, Helotes - Ranchtwn 138 kV, Medila Lake - Pipec Creek 138 kV | RT | Forced | [6 empty] | BERGHE | HAYSEN | 398T3891 | SHAYBER5
LCRA | Bergheim - Kendall | LN | 345 | 25/4, 20/12 | DCKT Cagnon-Kendall 345 kV & Cico-Comfort 138 kV, Zorn - Haysen 345KV, Cagnon-kendal 345 &cico-mengcr 138 | Mason Creek - Bandera 138 kV, Bergheim Auto, Txresrch - Tally_rd 138kV | RT | Planned, Forced | N | [5 empty] | BERGHE | KENDAL | 656T6561 | SKENBER5
STEC | Bevo Auto BEVO 138/69 kV | XF | 138 | 15/6 | Bevo Sub to Asherton 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned | [6 empty] | BEVO |  | BEVO | XBEV89
ONCOR | Big Spring Switch -…- Natural Dam | LN | 138 | 21/11, 21/10 | Grady - Expanse Switch 138 kV, DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses | Big Spring West - Stanton East 138 kV, Expanse Switch - Grady 138kV | RT | Planned | [6 empty] | BSPSW | BEALS | 6315_A | SSTABS18, SNATBEA8
ONCOR | Bird Dog Switch - Jacksboro Switching (37010) | LN | 345 | 23/5 | Hicks Switch - Roanoke Switch 345 kV | Alliance - Hicks Switch 345 kV | RT | Planned | [6 empty] | JCKSW | KRWSW | 37010 | SJCKBDG5
AEP | Blessing - Lolita | LN | 69 | 24/7 | DCKT Nelson Sharpe -…- South Texas Project 345kV, DCKT Whitepoint -…- Holman Aen 345kV | Carancahua - Palacios 69kV | RT | Planned | [6 empty] | BLESSING | LOLITA | BLESSI_LOLITA1 | SLOLBLE8
ONCOR | Bluff Creek Switch -…- Dermott Switch | LN | 138 | 25/4 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Deep Creek Sub - Sacroc 138kV | RT | Planned | [6 empty] | KNAPP | SCRCV | 6437_F | SKNADM48
CNPE | Boggy - Pair | LN | 138 | 22/10 | DCKT Exxon - Baytown & SR Bertron - Texas 138 kV, DCKT SR Bertron - Quanab & Dowlap 138 kV | Jefferson - Sc Channel 138 kV | RT | Forced, Planned | [6 empty] | BCV | PSA | BCVPSA | SBCVPSA8
AEP, ONCOR | Bowman Switch - Riley (34570) | LN | 345 | 21/3 | DCKT Clear Crossing-Coulomb & Clear Crossing-Pendulo 345 kV | Fisher Road Switch - Riley 345 kV | RT | Planned | N | [5 empty] | RILEY | BOMSW | 34570_A | SBOMRI25
AEP, ONCOR | Bowman Switch -…- Riley (34560) | LN | 345 | 21/3 | DCKT Clear Crossing-Coulomb & Clear Crossing-Pendulo 345 kV | Fisher Road Switch - Riley 345 kV | RT | Planned | N,Y | [5 empty] | RILEY | BOMSW | 34560_A | SBOMRI15
CPS | Braunig - Cagnon | LN | 345 | 24/12 | Skyline-calavers 345kv | Calaveras - Pawnee Switching Station 345kV | RT | Planned | [6 empty] | BRAUNIG | CAGNON | R5_U3 | SBRACAG5
CPS | Braunig - Calaveras | LN | 345 | 21/1 | DCKT Skyline-Calaveras 345 kV | Cagnon - Calaveras 345 kV | RT | Planned | N | [5 empty] | CALAVERS | BRAUNIG | N5_U31 | SBRACAL5
CPS | Brooks - Southton | LN | 138 | 22/12 | DCKT Calavers - Kirby & Beck Rd 138kV | Harlanda - Southsan 138 kV, Stockdale - Sutherland Springs 138 kV | RT | Planned | [6 empty] | V2 | Z5 | V2_Z5 | SV2Z58
ONCOR | Brown Switch - Buckhorn Switch | LN | 345 | 22/12, 22/9, 21/6, 20/12 | Comanche Sw (Oncor)-Comanche Peak 345 kV, DCKT Bighil-Kendall 345kV | Comanche Tap - Comanche Switch (oncor) 138 kV, Yellow Jacket - Treadwell 138 kV | RT | Planned, Forced | N | [5 empty] | BUCSW | BWNSW | 35095 | SBWNBUC5
AEP | Bruni - Crestonio | LN | 138 | 15/6, 15/5 | Laquinta to Lobo 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y, N | [5 empty] | BRUNI4 | CRESTONI | BRUNI4_CRESTO1 | SCREBRU8
TMPA | Btu_Jack_Creek - Gibbons Creek | LN | 345 | 17/4, 16/1 | DCKT Jewett to Singleton 345 kV | Gibbons Creek - Twin Oak Sw 345 kV, BTU_Jack_Creek Auto XF1 345/138 kV | RT, ST | Planned | Y | [5 empty] | GIBCRK | JK_CK | GC_JK | SJK_GIB5
ONCOR | Buckhorn Switch - Killeen Switch (35092) | LN | 345 | 22/12 | Comanche Sw (Oncor)-Comanche Peak 345 kV | Comanche Tap - Comanche Switch (oncor) 138 kV | RT | Planned | [6 empty] | KLNSW | BUCSW | 35092 | SBUCKLN5
PEC | Buda - Turnersville | LN | 138 | 24/6, 24/6, 23/8 | DCKT Henne-…-Zorn 138kV | Crosswinds - Goforth 138kV, Crosswinds - Turnersville 138 kV | RT | Planned | [6 empty] | TURNER | BUDA | 258T380 | SBUDTUR8
CNPE | Bunker - H O Clarke | LN | 138 | 21/9 | Meadow - Oasis 345 kV | Blodgett - Garrott 138 kV | RT | Planned | [6 empty] | BUN | HOC | BUNHOC08 | SBUNHO28
ONCOR | Burwick Switching Station - Graham SES | LN | 345 | 21/10 | DBCKT Graham Ses - Parker Switch 345 kV | Barton Chapel Wind Farm - Graham Switch 138 kV, Barton Chapel Wind Farm - Oran Sub 138 kV | RT | Planned | [6 empty] | BURSW | GRSES | 36030_A | SGRSJC25
CPS | Cagnon - Howard | LN | 138 | 23/3 | DCKT Calavers-Kirby&Beck_Rd 138kV | Merida - Wstside 138 kV | RT | Planned | [6 empty] | CAGNON | S1 | R4_S1 | SS1CAG8
CPS, STEC | Calaveras - Pawnee Switching Station | LN | 345 | 25/2, 24/3 | DCKT Elmcreek - San Miguel Gen 345 Kv | Coy City Tap - Pleasanton 138kV, Blessing - Lolita 138 kV | RT | Forced, Planned | [6 empty] | PAWNEE | CALAVERS | PAWNEE_SPRUCE | SPAWCAL5
CPS | Calaveras - Skyline (N5_P4_1) | LN | 345 | 22/5, 22/4, 22/3, 17/12, 17/5 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV, HILL COUNTRY to CAGNON 345 kV | Skyline - Calaveras 345 kV, Pawnee Switching Station - Calaveras 345 kV, Skyline - Elmcreek 345 kV, Coleto Creek - Rosata Tap 138 kV, Cagnon - Calaveras 345 kV, Pawnee Swithing Station Auto XF1 345/138 kV, Cagnon Auto XFMR4L-H 345/138 kV | RT | Planned, Forced | [6 empty] | CALAVERS | SKYLINE | N5_P4_1 | SSKYCA25
CPS | Calaveras - Skyline (N5_P4_2) | LN | 345 | 22/5, 22/4, 22/3, 17/12 | DCKT Cagnon to Braunig & Calaveras to Cagnon 345 kV, DCKT Hill Country to Marion 345 kV, HILL COUNTRY to CAGNON 345 kV, CAGNON to BRAUNIG 345 kV | Pawnee Switching Station - Calaveras 345 kV, Pawnee Switching Station Auto XF1 345/138 kV, Skyline - Elmcreek 345 kV, Coleto Creek - Rosata Tap 138 kV, Cagnon - Calaveras 345 kV, Cagnon Auto XFMR4L-H 345/138 kV | RT | Planned | [6 empty] | CALAVERS | SKYLINE | N5_P4_2 | SSKYCAL5
AEP | Campwood - … - Rock Springs | LN | 69 | 24/1, 21/9 | Bandera Auto AT3 138/69 kV , DBCKT Big Hill - Kendall 345 kV | Bandera Auto AT2 138/69 kV, Friess Ranch - Rocksprings 69 kV | RT | Forced, Planned | [6 empty] | NEWBARKS | CAMPWOOD | CAMPWO_NEWBAR1 | SCAMROC9
ONCOR | Carmichael Bend Switch - Mitchell Bend Switch | LN | 345 | 23/3 | Benbrook Switch - Parker Switch (6042) 345 kV | Benbrook Switch - Parker Switch (6005) 345 kV | RT | Planned | [6 empty] | MBDSW | CMBSW | 6017 | SMBDCMB5
AEP | Carrizo Springs - Crystal City | LN | 69 | 20/10 | Asherton-Bevo 138 kV | Bevo - Brundage Sub 69 kV | RT | Planned | Y, N | [5 empty] | CARRIZO | CRYSTAL | CARRIZ_CRYSTA11 | SCARCRY9
ONCOR, TNMP | Carrollton Northwest - Lakepointe Tnp | LN | 138 | 23/4, 22/12 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | South Tnp - Ti TNP 138 kV | RT | Planned | [6 empty] | CRLNW | LKPNT | 591_A | SLKPCRL8
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (105_A) | LN | 345 | 2018 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | ADD | [7 empty] | CRLNW | LWSSW | 105_A | SLWSCRL5
BRAZOS, ONCOR | Carrollton Northwest - Lewisville Switch (83) | LN | 345 | 17/3 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | CRLNW | LWSSW | 83 | SKRWCR25
AEP | Carver - Live Oak Aep | LN | 138 | 23/2 | DCKT Twin Buttes-DivideSwitchyard 345 kV | Hargrove - Twin Buttes 138 kV | RT | Forced | [6 empty] | LVOK | CARVER | CARVER_LVOK1 | SCARLVO8
ONCOR | Cash Switch - Sulphur Springs Switch | LN | 345 | 25/4 | DCKT Farmersville Switch - Cyclone Switch & Farmersville Switch - Saltillo Switch 345kV | Sulfur Spring Switch - Liberty Pod 138kV | RT | Planned | [6 empty] | SSPSW | CSHSW | 214_A | MSSPSDY5
AEP | Cassava - … - San Angelo Mathis Field | LN | 69 | 24/12, 23/12, 23/10 | Carver - Friend Ranch 138 kV, Bakersfield - Cedar Canyon 345 kV, Twin Buttes - Hargrove 138kV | Atlantic Sonora - Sonora 69 kV, San Angelo Concho - San Angelo Lake Nasworthy 69 kV, Lake Nasworthy - San Angelo Mathis Field 69kV | RT | Forced | [6 empty] | CASSAVA | MERR | CASSAV_MERR1 | SPHBBGL9
LCRA | Castell - Pitsburg | LN | 138 | 25/2 | Big Hill - Kendal 345kv | Yellow Jacket - Fort Mason 138kV | RT | Planned | [6 empty] | PITSBU | CASTEL | 44T2681 | SCASPIT8
LCRA | Castle Mountain - Crane Lcra | LN | 138 | 22/7, 22/5 | DCKT LCRA Crane - King Mountain West Tap & AND Castillo 138 kV, LCRA Crane - Castiollo 138 kV | Rio Pecos - LCRA crane Lcra 138 kV | RT | Planned | [6 empty] | LCRANE | CASTMO | 716T716 | SLC2CAS8
CNPE | Cedar Bayou Plant - … - Quanum | LN | 138 | 24/3 | DCKT Boggy - Derick & South Channel 138 kV | Baytown - Miller 138 kV | RT | Planned | [6 empty] | CBY | WKR | CBYWKR85 | SQNMCB28
CNPE | Cedar Bayou Plant - Center | LN | 345 | 25/2, 22/3, 24/12 | Jordan - King & Jordan - North Belt 345 kV, North Belt - Th Wharton 345 kV, DCKT North Belt - Jorr & Jorr - King, Wa Parish To Obrien OB_WAP99 345kV | Jefferson - South Channel 138 kV, Highlands - Power Systems Arco Cogen 138kV, Wa Parish - Obrien 345kV | RT | Planned | [6 empty] | CTR | CBY | CBYCTR97A | SCBYCTR5
ONCOR | Cedar Crest Switch - ... - Mountain Creek Ses (3150) | LN | 138 | 23/9 | DCKT Cedar Hill Switch - Mountain Creek Ses 345 kV | Cedar Crest Switch - Oak Cliff South 138 kV | RT | Forced | [6 empty] | PLKTM | HMTRD | 3150_D | SPLKMCS8
ONCOR | Cedar Crest Switch - … - Industrial Blvd | LN | 138 | 19/3, 18/5 | DCKT Westmoreland - Cedar Hill Switch 138 kV & Mountain Creek Ses - Fish Creek Switch 69 kV | Saint Augustine Tap 2 - Sargent Road 138 kV | RT | Planned | [6 empty] | CMPST | CDCSW | 3130_A | SCMPIND8
ONCOR | Cedar Elm Switch - Krum West Switch | LN | 345 | 22/4 | Krum West Switch - Lewisville Switch 345 kV & Lewisville Switch - Roanoke Switch 345 kV | Argyle - Highlands Tnp 138 kV | RT | Planned | [6 empty] | KRWSW | CDESW | 38020 | SANAKR25
ONCOR | Cedar Hill Switch - … - Timberview Switch (6020) | LN | 345 | 23/8 | DCKT Liggett Switch - Venus Switch 345 kV | Cedar Hill Switch - Webb Sub 345 kV | RT | Planned | [6 empty] | CRTLD | TVWSW | 6020_B | STVWCRT5
ONCOR | Cedar Hill Switch - Courtland | LN | 345 | 19/10, 18/9, 18/5 | DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV | Cedar Hill Switch - Fish Crek Switch (3180) 138 kV | RT | Planned, Forced | [6 empty] | CRTLD | CDHSW | 6020_A | STVWCRT5
AEP | Celanese Bay City - Wadsworth | LN | 138 | 21/1 | DCKT Jones Creek-South Texas Project & Refuge 345 kV | Blessing - Pavlov 138 kV | RT | Planned | N | [5 empty] | CELANEBC | WADSWORT | CELANE_WADSWO11 | SCELWAD8
AEP | Celanese Bishop - Kleberg AEP | LN | 138 | 25/1, 24/1, 23/11 | DCKT Lon Hill - Bunsen & Wil Tract 138 kV, Lon Hill - Nelson Sharpe 345 Kv, Lon Hill - Robstown Tap 69kV | Calallen Sub - Lon Hill 69 kV, Nelson Sharpe Auto XF1 345/138 kV | RT | Planned | [6 empty] | CELANEBI | KLEBERG | CELANE_KLEBER1 | SCELKLE8
CNPE | Center - PH Robinson | LN | 345 | 23/12, 23/11 | DCKT Cedar Bayou Plant - Jordan & Chambers - Jordan 345 kV | Cedar Bayou Plant Auto AT3 345/138 kV | RT | Forced | [6 empty] | CTR | PHR | CTRPHR97 | SPHRCTR5
ONCOR | Centerville Road Switch - … - Judd Court & Kirkland Park | LN | 138 | 19/9, 19/3 | DCKT Centerville Road Switch to Parkdale Switch 138 kV | Prairie Creek - Scyene Road 138 kV | RT | Planned | [6 empty] | CNRSW | GRLRD | 3250_A, 3250_I | SLKHCNR8
ONCOR | Centerville Road Switch - Forney Switch | LN | 345 | 2017 | DCKT Forney Switch - Royse Switch 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [7 empty] | CNRSW | FORSW | 110 | SCNRFOR5
ONCOR | Centerville Road Switch - Lake Hubbard Ses (3681) | LN | 138 | 23/11 | DCKT Lake Hubbard Ses - … - Prairie Creek Switch 138 kV | Centerville Road Switch - Lake Hubbard Ses 138 kV (3671) | RT | Forced | [6 empty] | CNRSW | LHSES | 3681 | SLHSCNR8
CNPE | Chanel - Deepwater | LN | 138 | 21/11 | Eastside - Gable Stree 138 kV | Downtown - Polk 138 kV | RT | Planned | [6 empty] | DPW | CHL | CHLDPW70A | SCHLDPW8
LCRA | Chief Brady - Georgetown | LN | 138 | 25/2 | Georgetown South -…- Georgetown East 138kV, Hutto Switch -…- Georgetown Switch 138kV, Bell County - Temple Switch 138kV, DCKT Temple Switch - Knob Creek Switch 345 kV & Temple Switch - Bell County 138kV | Bell County - Salado Switch 138kV, Salado South - Salado Switch 138kV, Georgetown South - Midnight Sub 138kV | RT | Planned | [6 empty] | CHIEBR | GEORGE | 221T355 | SCHIGEO8
LCRA | Chief Brady - Round Rock | LN | 138 | 24/6 | Bell County - Temple Switch 138kV, DCKT Temple Switch - Knob Creek Switch 345 kV & Temple Switch - Bell County 138kV, DCKT Round Rock -...- Georgetown South 138kV, DCKT Salado Switch To Knob Creek Switch 345kV And Temple Switch To Bell County 138kV | Georgetown South - Round Rock Westinghouse 138kV, Bell County - Salado Switch 138kV | RT | Forced | [6 empty] | RNDRK | CHIEBR | 213T378 | SCHIRND8
ONCOR | China Grove Switch - Snyder | LN | 138 | 24/9, 19/5 | DCKT Dermott Switch - Bluff Creek Switch & Ennis Creek Switch 138 kV, | Morgan Creek SES - Sun Switch 138 kV, Snyder Auto FMR1 138/69 kV | RT | Planned | [6 empty] | CGRSW | SNYDR | 6235 | SSNYCGR8
STEC | Choate_station - Four Corners Sub | LN | 138 | 24/12 | Manual Stp To Hlj & Anstrom345 Kv Double | Blessing Auto 1382 345/138kV | RT | Planned | [6 empty] | FORCRNS | CHOATE | CHOATE_FORCRNS | SFORPAW8
AEP, ONCOR | Clear Crossing - ... - Willow Creek Switch | LN | 345 | 21/11 | DBCKT Edith Clarke - Riley 345 kV, Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Long Creek 345 kV, Abilene Mulberry Creek - Bluff Creek 345 kV | RT | Planned | [6 empty] | CLEARCRO | TOMSW | 35150 | SCLEWC25
AEP, ONCOR | Clear Crossing - … - Dermott Switch (CLEARC_KIRCHH1) | LN | 345 | 18/12, 18/11, 18/9, 18/8, 18/7, 18/6, 18/5, 18/4 | DCKT Dermott Sw to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH1 | SKIRDMT5
AEP, ONCOR | Clear Crossing - … - Dermott Switch (CLEARC_KIRCHH2) | LN | 345 | 18/5, 18/4 | DCKT Dermott Switch to Scurry County South Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | KIRCHHOF | CLEARC_KIRCHH2 | SKIRDM35
AEP | Clear Crossing - … - Edith Clarke (CLEARC_GAUSS2) | LN | 345 | 17/9, 17/8, 17/7 | Basecase | Panhandle GTC | RT | Planned | [6 empty] | CLEARCRO | GAUSS | CLEARC_GAUSS2 | SGAUED35
AEP | Clear Crossing - West Shackelford (CLEARC_WSHACK1) | LN | 345 | 21/9, 19/3, 19/2, 19/1 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | WSHACK | CLEARC_WSHACK1 | SCLEWS15
AEP | Clear Crossing - West Shackelford (CLEARC_WSHACK2) | LN | 345 | 19/3, 19/2, 19/1 | DCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | CLEARCRO | WSHACK | CLEARC_WSHACK2 | SCLEWS25
AEP | Coleto - Lon Hill | LN | 345 | 20/3, 17/3, 16/12, 16/1, 15/3 | DCKT Whitepoint to Hecker & Dupont Sw Ingleside 138 kV, Coleto Creek to Pawnee Sw 345 kV, Pawnee Sw to Lon Hill 345 kV, Goddard to Pawnee Switching Station 345 kV | Whitepoint - Rincon 138 kV, Kenedy Sw - Coleto Creek 138 kV, Magruder - Victoria 138 kV, Kenedy Sub - Kenedy Sw 69 kV, Callicoatte - Lon Hill 138 kV | RT, ST | Planned, Forced | Y, N | [5 empty] | COLETO | LON_HILL | COLETO_LON_HI1 | SCOLLON5
AEP | Coleto Creek - Raptor | LN | 345 | 24/11 | Tango To Pawnee Switching Station 345kV, DCKT Whitepoint -…- Holman Aen 345kV | Victoria 138 kV - Warburton Road Switching Station, Melon Creek - Sea Drift Coke 138kV | RT | Planned | RT | Planned | RT | Planned | RT | Planned | COLETO | RAPTOR | COLETO_RAPTOR1 | SRAPCOL5
AEP | Coleto Creek - Victoria (COLETO_VICTOR2) | LN | 138 | 22/10, 22/3, 21/11 | Coleto Creek - Pawnee Switching Station 345 kV, DCKT White Point to Angstrom & Lon Hill 345KV | Coleto Creek - Victoria 138 kV | ADD | Planned | [6 empty] | COLETO | VICTORIA | COLETO_VICTOR2 | SVICCOL8
ONCOR | Comanche Peak Ses - Comanche Switch | LN | 345 | 22/4, 21/4, 18/11 | DCKT Killeen Switch - Buckhorn Switch & Russell Gap Switch 345 kV | Comanche Tap - Comanche Switch 138 kV | RT | Planned, Forced | [6 empty] | CMNSW | CPSES | 662 | SCMNCPS5
ONCOR | Comanche Peak Ses - Mitchell Bend Switch | LN | 345 | 20/3 | DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV | Comanche Peak SES - Wolf Hollow 345 Switch 345 kV, Mitchell Bend Switch - Wolf Hollow 345 Switch 345 kV | RT | Planned | [6 empty] | CPSES | MBDSW | 6033 | SDCSCPS5
ONCOR | Consavvy Switch - Morgan Creek Ses | LN | 345 | 25/3, 24/11, 24/6 | Wett_long_draw To Volta Lin 1, DCKT Bakersfield - Cedar Canyon 345kV, | Longshore Switch - Consavvy Switch 345kV | RT | Planned | [6 empty] | MGSES | CONSW | 6053 | SCONMGS5
LPL | Coop Substatoin - Slaton Sub | LN | 138 | 23/10, 23/9 | Double Mountain Switch - Fiddlewood Switch 345 kV | Dunbar Sub - Holly Sub 138 kV | RT | Planned | [6 empty] | LPLCO | LPLSL | LPLCO_LPLSL | SL11LPL0
AEP | Cotula Sub - Dilley Switch Aep | LN | 138 | 24/9 | Dilley Switch Aep Auto 69_1 138/69 | Dilley Switch Auto 69_1 138/69kV | RT | Planned | [6 empty] | DILLEYSW | JARDIN | DILLEY_JARDIN1 | SJARDIL8
STEC | Cotulla Sub - … - Freer Sub | LN | 69 | 22/1 | Fowlerton - Lobo 345 kV | Bruni Sub Auto 138/69 kV | RT | Planned | [6 empty] | COTULAS | HOLANDS | COT_HOLA | SFREBRU9
LCRA | Crane Lcra - King Mountain West Tap | LN | 138 | 22/5 | Crane LCRA - Castillo 138 kV | Rio Pecos - LCRA Crane 138 kV | RT | Planned | [6 empty] | LCRANE | KINGMO | 664T664 | SLCRKIN8
AEP | Crestonio - Falfurrias | LN | 138 | 24/5 | North Edinburg to Pomelo NEDIN_POMELO1 345kV | Freer - Lobo 69kV | RT | Planned | [6 empty] | FALFUR | CRESTONI | CRESTO_FALFUR1 | SCREFAL8
LCRA | Crosswinds - Turnersville | LN | 138 | 22/7 | DCKT McCarty Lane - Hunter & Hilltop 138kV | Turnersville - Buda 138 kV | RT | Planned | [6 empty] | CROSSWI | TURNER | 261T272 | STURCRO8
CNPE | Crown -Jefferson | LN | 138 | 23/3 | PAIR to BOGGY 138 kV | Conial - Philip 138 kV | RT | Planned | [6 empty] | JFS | CRN | CRNJFS94 | SCRNJFS8
LCRA | Cypress Creek - Raymond F Barker | LN | 138 | 25/4 | Cagnon - Kendall 345kV & Cico - Comfort 138kV | Raymond F Barker - Comfort 138kV | RT | Planned | [6 empty] | RAYBAR | CYPRCR | 662T662 | SCYPCOM8
AEP | Del Mar - Laredo Plant | LN | 138 | 19/10 | North Edinburg - Pomelo 345 kV | Laredo VFT North - Las Cruces 138 kV | RT | Planned | [6 empty] | DEL_MAR | LAREDO | DEL_MA_LAREDO1 | SDELLAR8
AEP | Dermott Switch - … - Figaro | LN | 345 | 21/10 | DBCKT Dermott Switch - Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | [6 empty] | DMTSW | FIGARO | DMTSW_FIGARO1 | SFIGDMT5
ONCOR, WETT | Dermott Switch - Mhos (T-301) | LN | 345 | 22/10, 22/9, 22/5 | Double Mountain Switch - Fiddlewood Switch 345 kV, Blackwater Draw Switch - Double Mountain Switch 345 kV | Holly Substation - Dunbar Substation 115 kV, MacKenzie Substation - Northeastern Substation 115 kV | RT | Forced | [6 empty] | MHOS | DMTSW | T-301 | SDMTW_15
ONCOR, WETT | Dermott Switch - Mhos (T-302) | LN | 345 | 22/10, 22/9, 22/5 | Double Mountain Switch - Fiddlewood Switch 345 kV, Blackwater Draw Switch - Double Mountain Switch 345 kV | Holly Substation - Dunbar Substation 115 kV, MacKenzie Substation - Northeastern Substation 115 kV | RT | Forced | [6 empty] | MHOS | DMTSW | T-302 | SDMTW_25
ONCOR | Dermott Switch - Scurry County South Switch (34540) | LN | 345 | 20/11 | DCKT Clear Crossing-…-Figaro & Clear Crossing-…-Dermott Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | N | [5 empty] | DMTSW | SCOSW | 34540_A | SDMTSC15
ONCOR | Dermott Switch - Scurry County South Switch (34550) | LN | 345 | 20/11 | DCKT Clear Crossing-…-Figaro & Clear Crossing-…-Dermott Sw 345 kV | Knapp - Scurry Chevron 138 kV | RT | Planned | N | [5 empty] | DMTSW | SCOSW | 34550_A | SDMTSC25
BRAZOS, ONCOR | Desoto Switch -…- Sterrett | LN | 138 | 22/12 | JOHNSON SWITCH (ONCOR) to CONCORD 345 kV, ENNIS WEST SWITCH - ENNIS TRACTEBEL 138 kV, DCKT Kemp Ranch Switch - Sardis & Soap Creek Switch -Cedar Hill Tu 138 kV | Midlothian Txi -…- Midlothian South 138 kV, Wilmer Auto FMR1 138/69 Kv | RT | Planned | [6 empty] | DESSW | GLNHT | 945_A | SGLNDES8
TNMP | Dickinson Tnp - Freeway Park Tnp | LN | 138 | 23/5 | Hastings Tnp - North Alvin Tnp 138 kV | Dickinson Tnp - Freeway Park Tnp 138 kV | RT | Planned | [6 empty] | DICKNSON | FRWYPARK | G138_14 | SDICFR28
TNMP | Dickinson Tnp - League City Tnp | LN | 138 | 24/10, 20/10 | North Alvin TNP-Hastings Tnp 138 kV | League City Tnp - Hidden Lakes Tnp 138 kV | RT | Planned | N | [5 empty] | DICKNSON | LEAGCITY | G138_091 | SLEADIC8
GEUS, TMPA | Diesel - Greenville Steam | LN | 69 | 15/7 | Shelby Auto BT1 138/69 kV | Greenville Steam Auto XT1 138/69 kV | ST | Planned | [6 empty] | DIESEL | GN_S_I | DIE_GNS | SDIEGN_9
AEP | Dolan Tap - Whiting | LN | 138 | 21/10 | Odlaw Switch -…- Uvalde AEP 138 kV | Hamilton Road - Maverick 138 kV | RT | Planned | [6 empty] | DOLAN | WHITING | DOLAN_WHITIN1 | SCT2CAR8
ONCOR | Double Mountain Switch - Fiddlewood Switch | LN | 345 | 24/5 | Dunbar Substation - Wadsworth Susbsation 115kV | Dunbar Substation - Holly Substation 115kV | RT | Planned | [6 empty] | FIDSW | DBMSW | ONCFW_ONCDM | SDBMFID5
CNPE | Dow Chemical - Oasis (DOWOAS18) | LN | 345 | 25/4, 24/9, 24/5, 24/6, 25/4, 24/9, 24/5, 24/6, 22/4, 21/4, 22/9 | DCKT Jones Creek-South Texas Project & Refuge 345 kV, Wa Parish - Waley & Wa Parish - Wolf 345kV | South Texas Project - WA Parish 345 kV, Bay City Sub - Sargent Sub 69 kV, Oasis - Dow Chemical 345kV | RT | Planned, Forced | N | [5 empty] | OAS | DOW | DOWOAS18A | SOASDO25
AEP, STEC | Downie Switching Station - … - Uvalde AEP | LN | 138 | 19/5 | Asphalt Mines to Odlaw Switchyard 138 kV | Hamilton - Maverick 138 kV | RT | Planned | [6 empty] | UVALDE | READING | READIN_UVALDE1 | SREAUVA8
STEC | Driscoll Sub - … - Loyola Sub | LN | 69 | 20/4 | Ajo-Nelson Sharpe 138 kV | Falfurrias - Premont 69 kV | RT | Planned | N | [5 empty] | DRSCOLS | RICRDOS | DRS_RICR | SRICLOY9
ONCOR | Dublin - Stephenville (oncor) | LN | 138 | 25/4 | Comanche Switch - Comanche Peak Ses 345kV | Scott and White POI - Temple South 138kV | RT | Planned | [6 empty] | STNVL | DUBLN | 651_E | MDUBFUL8
LPL | Dunbar Sub - Holly Sub | LN | 115 | 24/2 | Double Mountain Switch - Fiddlewood Switch 345 kV | Dunbar Sub - Wadsworth Sub 115 kV | RT | Planned | [6 empty] | LPLDB | LPLHY | LPLHY_LPLDB | SL13LPL0
AEP | Dupont Switch Ingleside - Dupont PP1 Ingleside (I_DUPP_I_DUPS2) | LN | 138 | 24/1 | Ingleside Cogen Switch Gen CTG1 | Dupont Switch Ingleside - Dupont PP1 Ingleside (I_DUPP_I_DUPS1) | RT | Forced | [6 empty] | I_DUPP1 | I_DUPSW | I_DUPP_I_DUPS2 | SI_DI_38
AEP | Edith Clarke - Riley (Edithc_Riley1) | LN | 345 | 18/3, 18/2, 18/1, 17/12, 17/11, 17/10 | Basecase | Panhandle GTC | RT | Planned | [6 empty] | EDITHCLA | RILEY | EDITHC_RILEY1 | SRILED15
AEP | Edith Clarke - Riley (Edithc_Riley2) | LN | 345 | 18/3, 18/2, 18/1, 17/12, 17/11, 17/10 | Basecase | Panhandle GTC | RT | Planned | [6 empty] | EDITHCLA | RILEY | EDITHC_RILEY2 | SRILED25
AEP, WETT | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC3) | LN | 345 | 17/6, 17/5, 17/4, 17/3, 17/2, 17/1, 16/12, 16/11 | Basecase | Panhandle GTC | RT, ST | Planned, Forced | [6 empty] | EDITHCLA | W_CW_345 | COTTON_EDITHC3 | SW_CED55
AEP, WETT | Edith Clarke - Wett_Cottonwood (COTTON_EDITHC4) | LN | 345 | 17/6, 17/5, 17/4, 17/3, 17/2, 17/1, 16/12, 16/11 | Basecase | Panhandle GTC | RT, ST | Planned, Forced | [6 empty] | EDITHCLA | W_CW_345 | COTTON_EDITHC4 | SW_CED45
AEP, LCRA | El Campo - Ricebird | LN | 138 | 23/3 | DCKT Vanderbilt Switching Station - Energy Transfer Partners 138kV & EL Toro Switching Station - Edna Substation 69kV | Danevang Switching Station Auto 138_69 138/69 kV | RT | Planned | [6 empty] | RICEBI | EL_CAMPO | 589T589 | SRICEL_8
ONCOR | Elkins Road Pod - Midland East | LN | 138 | 21/11 | Grady - Expanse Switch 138 kV | Big Spring West - Stanton East 138 kV | RT | Planned | [6 empty] | ERPOD | MDLNE | 6146_A | SSTAMDL8
ONCOR | Elkton - Martin Lake Ses | LN | 345 | 2017 | Martin Lake - Styker and - Enterprise DCKT | Martin Lake - Shamburger | ADD | [7 empty] | ELKTN | MLSES | 180 | SELKMLS5
ONCOR | Elkton - Tri Corner | LN | 345 | 18/12, 18/11, 2017, 17/11 | DCKT Trinidad Ses- Mt Enterprise & Stryker Creek Ses, DCKT Martin Lake Ses - Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3, Lufkin Switch - Nacogdoches South Tap 138 kV | ADD, RT | Planned | [6 empty] | ELKTN | TRCNR | 170 | SELKFOR5
CNPE, CPS | Elmcreek - South Texas Project | LN | 345 | 22/4 | Elmcreek - South Texas Project 345 kV & South Texas Project - WA Parish 345 kV | Hillje - South Texas Project 345 kV | RT | Planned | [6 empty] | STP | ELMCREEK | STPELM271 | SELMSTP5
GAR | Elmgrove - Wylie Switch | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | ELMGROVE | WYLIESW | WYL_ELMG | SWYLELM8
LCRA | Engle -…- Schulenburg | LN | 138 | 22/5 | Joslin - Formasa 138 kV | Lolita - Victoria 138 kV | RT | Planned | [6 empty] | ENGLE | FLATON | 145T112 | SENGFLA8
ONCOR | ENNIS WEST SWITCH -...- SHANKLE SWITCH (941) | LN | 138 | 19/6 | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | Ennis West Switch- Wahaxhachie - Sterrett | ADD | Planned | [6 empty] | ENWSW | SHKSW | 943 | SENWSHK8
ONCOR | Ennis West Switch -…- Sterrett (940) | LN | 138 | 18/11 | ENNIS WEST SWITCH -...- SHANKLE SWITCH 138 kV (941) | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | ADD | Planned | [6 empty] | ENWSW | ENSSO | 941_C | SENSENW8
ONCOR | Ennis West Switch -Ennis South (941_C) | LN | 138 | 19/4 | WXHCH-WXOCF_69kV & ENWSW-STERT_138kV | ENNIS WEST SWITCH - SHANKLE SWITCH 138 kV (943) | ADD | Planned | [6 empty] | ENWSW | ENSSO | 941_C | SENSENW8
AEP | Escondido - Ganso | LN | 138 | 25/4 | Brackettville To Pinto Creek 138kV | Ganso - Maverick 138kV | RT | Planned | [6 empty] | ESCONDID | GANSO | ESCOND_GANSO1 | SESCGAN8
AEP | Escondido -…- Rosita Creek | LN | 138 | 25/1 | Brackettville To Pinto Creek 138kV, Hamilton Road To Pinto Creek 138kV | HAMILTON 138 - MAVERICK | RT | Planned | [6 empty] | ROSICR | ESCONDID | 627T627 | SROSSUN8
ONCOR | Eskota Switch - … - Morgan Creek Ses (6285) | LN | 345 | 23/11 | McElmurray - … - Moore 138 kV | Capella - Merkel 69 kV, Eskota Switch - Trent 69 kV | RT | Planned | [6 empty] | LSPOI | MGSES | 6285_B | SSWDMGS8
AEP | Esperanza - Stp Switch | LN | 138 | 24/1 | Arroz - El Campo 138 kV | Blessing - Pavlov 138 kV | RT | Planned | [6 empty] | ESPERANZ | STPSW | ESPERA_STPSW1 | SSTPESP8
ONCOR | Everman Switch - Oakhill Tap 1 | LN | 138 | 22/2, 21/12 | Davis -…-Everman Switch 138 kV, DBCKT Deen Switch -…- Hicks Switch 138 kV | Hemphill - Mistletoe Heights 138 kV | RT | Planned, Forced | [6 empty] | EVRSW | OAKT1 | 6310_A | SOAKEVR8
ONCOR | Exchange Switch - Roanoke Switch | LN | 345 | 24/10, 24/11, 24/10, 24/11 | Krwsw To Wdent 345 And Krwsw To Lwssw 345 Dblckt, Krum West Switch To Bird Dog Switch Lin _a, Krwsw To Wdent 345 And Krwsw To Lwssw 345 Dblckt, Krum West Switch To Bird Dog Switch Lin _a | RNKSW 345 - EXCSW | RT | Planned | [6 empty] | RNKSW | EXCSW | 109 | SRNKEXC5
ONCOR | Falcon Seaboard - Midland East | LN | 345 | 20/10 | DCKT Odessa EHV Sw-Moss Sw & Wolf Switching Station 345 kV | Odessa North - Odessa 138 kV | RT | Planned | N | [5 empty] | FLCNS | MDLNE | 6045_A | SFLCMDL5
ONCOR | Falcon Seaboard - Ranger Camp Switch | LN | 345 | 25/2, 25/1 | Consavvy Switch To Morgan Creek Ses 345kV, DCKT Morgan Creek Ses -…-Longshore Switch 345kV | Morgan Creek Ses 345/138 kV Auto MR1H, Morgan Creek Ses - Ranger Camp Switch 345kV, Longshore Switch - Consavvy Switch 345kV | RT | Planned | [6 empty] | FLCNS | MGSES | 6046_A | MRGRFLC5, MRGRMGS5
ONCOR, WETT | Farmland - Wett_long_draw | LN | 345 | 24/8 | Blackwater Draw Switch - Double Mountain Switch 345kV | MacKenzie Substation - Northeast Substation 115 kV | RT | Planned | [6 empty] | FARMLAND | W_LD_345 | FARMLAND_LONGD | SW_LFAR5
LCRA | Fayette Plant 3 - Lytton Springs | LN | 345 | 23/2 | DCKT Fayette Plant 1 and 2 - Lostpine & Winches 345kV | Fayetteville Auto AT2H 345/138 kV | RT | Planned | [6 empty] | FPPYD2 | LYTTON_S | 355T255 | SFPPLYT5
ONCOR | Forney Switch - Royse Switch (200) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [7 empty] | FORSW | RYSSW | 200 | SFORRYS5
ONCOR | Forney Switch - Royse Switch (210) | LN | 345 | 2017 | Forney Sw - Centerville Road Sw 345 kV | Forney Switch 345/138 kV Auto MR3 | ADD | [7 empty] | FORSW | RYSSW | 210 | SFORRY25
AEP | Fort Mason - Mason AEP | LN | 138 | 19/5 | DCKT Ferguson to Granite Mountain 138 kV and Starcke to Wirtz 138 kV | Flat Rock LCRA - Wirtz 138 kV | RT | Planned | [6 empty] | MASN | FORTMA | FORTMA_MASN1 | SMA2FOR8
AEP | Fort Mason - Yellow Jacket | LN | 138 | 22/11 | DCKT Bighill -Kendall 345kV | Yello Jacket - Hext LCRA 138 kV | RT | Forced | [6 empty] | YELWJCKT | FORTMA | FORTMA_YELWJC1 | SFORYEL8
AEP, STEC | Fowlerton - Lobo | LN | 345 | 25/2, 24/11 | DCKT Lobo - San Miguel Gen & Lobo - Torrecillas 345 Kv | North Laredo Switch - Mines Road 138kV, Catarina - Piloncillo 138kV | RT | Planned, Forced | [6 empty] | LOBO | FOWLRTON | LOBO_FOWLRTN1 | SFOWLOB5
STEC | Fowlerton - San Miguel Gen (FOWRTN_SMIGL) | LN | 345 | 25/3, 24/2, 21/2 | DCKT North Edinburg - Pomelo 345 kV, DCKT Dilley Switch - San Miguel Switch & Dilley Switch - Cotulla Sub 138 kV, DCKT Fowlerton To Avanzada & Lobo To Fowlerton 345kV | Freer - Lobo 69 kV, Dilley Switch Aep - Cotulla Sub 69 Kv, Laredo Vft North - Las Cruces 138kV, North Laredo Switch - Mines Road 138kV | RT | Planned, Forced | [6 empty] | FOWLRTON | SANMIGL | FOWRTN_SMIGL | SSANFOW5
TNMP | Freeway Park Tnp - Mainland Tnp | LN | 138 | 22/4, 22/3, 21/2 | Meadow - Ph Robinson 345 kV, PH Robinson-Gaf Tnp 138 kV | Magnolia Tnp - Seminole Tnp 138 kV, Freeway Park Tnp - Dickinson Tnp 138 kV | RT | Planned | N | [5 empty] | MAINLAND | FRWYPARK | 138_FWP_MNL1 | SFRWMAI8
LCRA | Friend Ranch - Fort Lancaster | LN | 138 | 24/9 | DCKT Bakersfield - Cedar Canyon 345kv | Crossover - Palouse 138kV | RT | Planned | [6 empty] | FRIEND_R | FTLN | 438T438 | SFRIFTL8
TNMP | Friendswood TNP - Seminole Tnp | LN | 138 | 23/10 | Meadow - PH Robinson 345 kV | Alvin Tnp - North Alvin Tnp 138 kV | RT | Planned | [6 empty] | FRDSWOOD | SEMINOLE | G138_10C | SFRDSEM8
ONCOR | Garland - Rowlett Tap | LN | 138 | 24/8 | Walnut - Naaman 138kV | College - Jupiter 138kV | RT | Planned | [6 empty] | RWLTP | GRLND | 1630_H | SFSTRYS8
CNPE | Garrott - Kirby | LN | 138 | 21/11 | Eastside - Gable Stree 138 kV | Downtown - Polk 138 kV | RT | Planned | [6 empty] | GT | KB | GT_KB_37A | SGTKB8
AEP | Gateway and Wormser Road to North Laredo Switch | LN | 138 | 22/4 | Fowlerton - Lobo 345 kV | Gateway West Tnp - Wormser Road 138 kV | RT | Forced | [6 empty] | GATE_WAY | GATEWTP | GATEWT_GATE_W1 | SNLAGAT8
CNPE, CROSS, GAR, TMPA | Gibbons Creek - Limestone Plant (GIB_LIME181) | LN | 345 | 23/5, 21/3 | DCKT Twin Oak Switch - Gibbons Creek & Jack Creek 345 kV, DCKT Jewett-Singleton 345 kV | Jewett - Singleton 345 kV, Gibbons Creek - Twin Oak Switch 345 kV | RT | Planned | N | [5 empty] | GIBCRK | LEG | GIB_LIME181 | SLE2GIB5
CNPE, CROSS, GAR, TMPA | Gibbons Creek - Limestone Plant (GIB_LIME501) | LN | 345 | 25/3, 23/5, 21/3 | DCKT Twin Oak Switch - Gibbons Creek & Jack Creek 345 kV, DCKT Jewett-Singleton 345 kV | Jewett - Singleton 345 kV, Gibbons Creek - Twin Oak Switch 345 kV | RT | Planned | N | [5 empty] | GIBCRK | LEG | GIB_LIME501 | SLEGGIB5
TMPA | Gibbons Creek - Twin Oak Switch | LN | 345 | 20/11, 20/5 | DCKT GibbonsCreek-Limestone 345 kV, DCKT Jewett-Singleton 345 kV | Jewett - Singleton 345 kV | RT | Planned | N | [5 empty] | GIBCRK | TOKSW | 256_A1 | SGIBTOK5
AEP | Gila -…- Whitepoint | LN | 138 | 23/2 | Whitepoint Auto 345_1 345/138 | Nueces_Bay - White Pt 138 kV | RT | Forced | [6 empty] | MAYO | GILA | GILA_MAYO1 | SMAYWHI8
AEP, STEC | Goddard - Tango | LN | 345 | 22/2, 22/1, 21/11 | Fowlerton - San Miguel Gen 345 kV, Grissom - Lon Hill 345 kV, Coleto Creek - Grissom 345 kV & Fannin Sub - Goliad 69 kV | George West Switch Station - Sigmor 138 kV, Choke Canyon Aep - San Miguel Gen 138 kV, North Carbide - Sea Drift Coke 138 kV | RT | Forced, Planned | [6 empty] | GODDARD | PAWNEE | GODDAR_TANGO1 | SGODTAN5
ONCOR | Golden Switch - Sun Switch | LN | 138 | 20/3 | DCKT Dermott Switch to Scurry County South Switch 345 kV | Knapp - Scurry Chevron 138 kV | RT | Forced | [6 empty] | GLDSW | SUNSW | 6438 | SGLDSUN8
ONCOR | Graham SES - Rice Switch | LN | 138 | 22/4 | Windthorst Switch -…- Wichita Falls South Switch 138 kV | Cottonwood Road Switch - Olney Pod 69 kV | RT | Planned | [6 empty] | GRSES | RICSW | 6560_A | SRICGRS8
ONCOR | Graham SES - Tonkawa Switch | LN | 345 | 21/11 | Abilene Mulberry Creek - Sweetwater East Switch 345 kV & Long Creek - Sweetwater East Switch 345 kV | Abilene Mulberry Creek - Bluff Creek 345 kV | RT | Planned | [6 empty] | GRSES | TKWSW | 6035_A | STKWGRS5
CROSS | Gray - Railhead | LN | 345 | 16/5, 16/3 | Basecase, DCKT Alibates to Tule Canyon 345 kV | Panhandle GTC, Low Voltage in Panhandle area | RT, ST | Planned | Y | [5 empty] | RAILHEAD | CTT_GRAY | RAILHD_GRAY | SRAICTT5
AEP, CROSS | Gray - Tesla (GRAY_TESLA_1) | LN | 345 | 17/1 | Basecase | Panhandle GTC | RT | Forced | [6 empty] | CTT_GRAY | TESLA | GRAY_TESLA_1 | SCTTTES5
CROSS | Gray South Bus (CB GY_BKR_G130, etc.) | BUS | 345 | 16/5 | DCKT Alibates to Tule Canyon 345 kV | Low Voltage in Panhandle area | ST | Planned | Y | [5 empty] | GTT_GRAY |  | 1002 | N/A
ONCOR | Gresham Road Switch - … - Nacogdoches Se | LN | 138 | 19/1, 18/12, 18/10, 18/8, 18/7, 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Nacogdoches Se - Redland Switch 138 kV, Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned | [6 empty] | CSHNG | GRDSW | 1450_F | SNCDCMI8
ONCOR | Gresham Road Switch - Stryker Creek Ses | LN | 138 | 18/6 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Nacogdoches Se - Redland Switch 138 kV | RT | Planned | [6 empty] | SCSES | GRDSW | 11010 | SGRDSCS8
AEP | Grissom - Lon Hill | LN | 345 | 24/9 | Coleto Creek - Pawnee Switching Station 345kV | Coleto Creek - Victoria 138kV | RT | Planned | [6 empty] | GRISSOM | LON_HILL | GRISSO_LON_HI1 | SGRILON5
AEP | Grissom - Raptor (GRISSO_RAPTOR1) | LN | 345 | 24/11 | Tango To Pawnee Switching Station Lin 1 | Victoria 138 kV - Warburton Road Switching Station | RT | Planned | [6 empty] | GRISSOM | RAPTOR | GRISSO_RAPTOR1 | SGRIRAP5
AEP | Grissom - Raptor (GRISSO_RAPTOR2) | LN | 345 | 24/11 | Manual Stp To Hlj & Anstrom345 Kv Double | Melon Creek - Sea Drift Coke 138kV | RT | Planned | [6 empty] | GRISSOM | RAPTOR | GRISSO_RAPTOR2 | SGRIRAP5
AEP | Haine Drive - La Palma | LN | 138 | 17/4 | DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | HAINE_DR | LA_PALMA | HAINE__LA_PAL1 | SHAILA_8
LCRA | Hamilton Road - Pinto Creek | LN | 138 | 23/4, 23/3 | DCKT Bighill-Kendall 345kV | Hamilton Road - Maverick 138 kV, Escondido - Ganso 138 kV | RT | Planned | [6 empty] | PINTCR | HAMILTON | 464T464 | SBRAHAM8
ONCOR | Harker Heights -...- Nolanville | LN | 138 | 25/2, 25/3, 25/2, 25/3 | DCKT Salado Switch - Killeen Switch 345kV | Belton - Belton Southwest 138kV | RT | Planned | [6 empty] | NLNVL | HKHTS | 640_N | SNLNHKH8
AEP | Harlingen Switch - Raymondville 2 | LN | 138 | 21/2 | DCKT North Edinburg-Lon Hill & North Edinburg -…-El Trueno WInd 345 kV, DCKT South Santa Rosa-Rio Hondo 138 kV | Haine Drive - La Palma 138 kV | RT | Planned | N | [5 empty] | HARLNSW | RAYMOND1 | HARLNS_RAYMON11 | SRAYHAR8
LCRA | Harlingen Switch - Weslaco Switch | LN | 138 | 21/1, 20/11 | North Eninburg TRX 1382345/138 kV, DCKT North Edinburg-Lon Hill & North Edinburg -…-El Trueno WInd 345 kV, DCKT South Santa Rosa-Rio Hondo 138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | N | [5 empty] | WESLACO | NWESLACO | 207T4801 | SNWEWES8
ONCOR | Hawk Hollow Switch - … - Rivercrest Ses (1561) | LN | 138 | 23/8 | DCKT Hawk Hollow Switch - Paris Switch 138 kV | Tenaska (TXU) - Toco Switch 138 kV | RT | Planned | [6 empty] | DRPEA | HWKSW | 1561_C | SHWKDPR8
ONCOR | Hawk Hollow Switch - … - Tenaska (TXU) (1560) | LN | 138 | 23/8 | DCKT Hawk Hollow Switch - Paris Switch 138 kV | Deport REA - Rivercrest Ses 138 kV | RT | Planned | [6 empty] | PREST | RENTP | 1560_A | SHWLBL8
LCRA | Hays Energy Center - Zorn (388T3881) | LN | 345 | 2021 | DCKT Cagnon - Kendal 345kV & Cico - Comfor 138kV | Hays Energy Center - Zorn 345 kV (6T227) | ADD | [7 empty] | HAYSEN | ZORN | 388T3881 | SHAYZO25
LCRA | Hays Energy Center - Zorn (6T227) | LN | 345 | 2021 | DCKT Cagnon - Kendal 345kV & Cico - Comfor 138kV | Hays Energy Center - Zorn 345 kV (388T3881) | ADD | [7 empty] | HAYSEN | ZORN | 6T227 | SHAYZOR5
AEP | Hicks Switch - Roanoke Switch | LN | 345 | 24/9 | DCKT Krum West Switch - West Denton & Krum West Switch - Lewisville Switch 345kV | Alliance - Roanoke Switch 345kV | RT | Planned | [6 empty] | RNKSW | HCKSW | 107 | SHCKEXC5
AEP | Hidalgo Energy Center - North Edinburg | LN | 138 | 25/4 | Mccoll Road - North Edinburg & North Edinburg - North Mcallen 138kV | North Edinburg - Hidalgo Energy Center 138kV | RT | Forced | [6 empty] | NEDIN | HEC | HEC_NEDIN1 | SDUKNED8
TNMP, ONCOR | Highlands Tnp - Lewisville Switch | LN | 138 | 21/12, 20/12, 20/1, 20/3, 20/2 | Carrollton Northwest-Lakepoint Tnp 138 kV, DCKT Carrollton Northwest to Lewisville Switch 345 kV | South Tnp - Carrollton Northwest, Argyle - Highlands Tap 138 kV, TI Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | LWSSW | LWSVH | 593 | SLWSLWS8
LCRA | Hill Country - Marion | LN | 345 | 23/2, 19/2 | DCKT Elmcreek - Skyline 345 kV | Hill Country - Marion 345 kV | RT | Planned | [6 empty] | MARION | HILLCTRY | HILL_MAR_1 | SMARHI25
ONCOR | Hillsboro - Whitney | LN | 138 | 24/10 | Bale Switch To Jewett Lin _b | Haney Bepc - Navarro 138kV | RT | Forced | [6 empty] | HLSBR | WHTNY | 1200 | SHLSWH28
CPS | Holbrook - Kirby | LN | 138 | 24/10 | Braunig-coliseum&highland 138kv | Kirby - St_hedwg 138kV | RT | Planned | [6 empty] | Y1 | C4 | C4_Y1 | SY1C148
LCRA | Hollmig - Kendall | LN | 138 | 24/10 | Kendall To Comfort Lin 1 | Kerrville Stadium - Kendal 138kV | RT | Forced | [6 empty] | FREDER | HOLLMI | 73T120 | SCOMKEN8
AEP | Holly - Westside Aep | LN | 138 | 22/05, 18/11 | Airline Aep - … - Westside Aep 138 kV | Arcadia - Southside 138 kV | RT | Planned, Forced | [6 empty] | HOLLY4 | WESTSIDE | HOLLY4_WESTSI1 | SHOLWES8
LPL | Holly Sub - Southeast Sub | LN | 115 | 23/11 | Double Mountain Switch - Fiddlewood Switch 345 kV | Slaton Sub - Southeast Sub 115 kV | RT | Planned | [6 empty] | LPLHY | LPLSE | LPLSE_LPLHY | SL17LPL0
CNPE | Holmes - Plaza | LN | 138 | 21/10 | Eastside - Polk 138 kV | Downtown - Polk 138 kV | RT | Planned | [6 empty] | PZ | HM | HM_PZ_06A | SHMG1V8
CPS | Howard - Somerset | LN | 138 | 24/5, 23/9, 18/1, 17/12 | DCKT Cagnon - Rafter & Rafter - Txresrch 138 kV, DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 kV, Medina Lake - Pipe Creek 138kV | RT | Planned | [6 empty] | HOWARD | E3 | E3_S1 | SE3S18
ONCOR, TMPA | Jack_Creek - Twin Oak Switch | LN | 345 | 20/11 | DCKT GibbonsCreek-Limestone 345 kV | Jewett - Singleton 345 kV (260_A) | RT | Planned | N | [5 empty] | JK_CK | TOKSW | JK_TOKSW1 | SJK_TOK5
BRAZOS | Jaybird - Rw Miller | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | MIL | JAYBIRD | JYBRD_MIL | SSTVMIL8
BRAZOS | Jaybird - Stephenville Bepc | LN | 138 | 16/11 | Mineral Wells to Mineral Wells West 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | JAYBIRD | STV | JYBRD_STV | SJAYSTV8
CNPE | Jeanetta - WA Parish | LN | 345 | 21/12 | Meadow - Ph Robinson 345 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned | [6 empty] | WAP | JN | JN_WAP72A | SJNWA1P5
CNPE | Jeanetta - Westchase | LN | 138 | 23/2 | DCKT Bellaire -H O Clarke 138 kV | Jeanetta - Westwood 138 kV | RT | Planned | [6 empty] | JN | WZ | JN_WZ_05 | SWZJN8
CNPE | Jeanetta - White Oak | LN | 345 | 24/7 | Wa Parish To Obrien Lin OB_WAP99 | Wa Parish - Obrien Lin OB_WAP98 | RT | Forced | [6 empty] | WO | JN | JN_WO_72 | SWOJN5
ONCOR | Jewett - Singleton (260_A) | LN | 345 | 2018 | DCKT Gibbons Creek to Singleton 345 kV | Jewett - Singleton 345 kV (240) | ADD | [7 empty] | JEWET | SNG | 260_A | SSNGJE25
AEP | Jim Treece - Riley | LN | 345 | 16/11 | Basecase | Panhandle GTC | ST | Planned | [6 empty] | JIMTREEC | RILEY | JIMTRE_RILEY2 | SJIMRI25
AEP | Jim Treece - Tesla | LN | 345 | 17/2, 16/11 | Basecase | Panhandle GTC | ST | Planned | Y, N | [5 empty] | JIMTREEC | TESLA | JIMTRE_TESLA2 | SJIMTE25
DME, TMPA | Jimchristal - West Denton | LN | 138 | 23/10 | Fort Worth Sub - Teasley Sub 138 kV | Rd Wells Interchange - West Denton 138 kV | RT | Planned | [6 empty] | JCHRSTL | W_DENT | AIR_W_DE | SJMCW_D8
ONCOR | Johnson Switch - Venus Switch | LN | 345 | 19/11, 19/10 | DCKT Venus Switch to Timberview Switch & Everman Switch 345 KV, Concord Auto CRD1 345/138 kV | Cedar Hill Switch - Fish Creek Switch 138 kV (3180), Concord Auto CRD2 345/138 kV | RT | Planned | [6 empty] | JONSW | VENSW | 141 | SJONVEN5
CNPE | Jones Creek - Refuge | LN | 345 | 24/12 | Twr (345) Blu-bly72 & Hlj-wlf64 | South Texas Project - Jones Creek 345kV | RT | Planned | [6 empty] | JCK | REF | JCKREF27 | SREFJCK5
CNPE | Jones Creek - South Texas Project | LN | 345 | 22/6, 22/4 | Elmcreek - South Texas Project 345 kV & South Texas Project - WA Parish 345 kV, DCKT BLUE-Bailey & Hillje - Wolf 345 kV | Hillje - South Texas Project 345 kV, Jones Creek - Refuge 345 kV | RT | Planned, Forced | [6 empty] | JCK | STP | JCKSTP18A | SJCKSTP5
TNMP | Jones Street Tnp - Lakepointe Tnp | LN | 138 | 20/3, 20/2, 20/1,19/3, 17/12, 17/11 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | Ti Tnp - West Tnp 138 kV, Carrollton Northwest - Lakepointe Tnp 138kV, Argyle - Hihglands Tnp 138 kV | RT | Planned | [6 empty] | LWVJS | LKPNT | 590_B | SLWVLKP8
BRAZOS, TNMP | Jones Street Tnp - Lewisville Switch | LN | 138 | 20/3 | DCKT Carrollton Northwest to Lewisville Switch 345 kV | TI Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | LWSSW | LWVJS | 590_A | SLWVLWS8
CNPE | Jordan - King | LN | 345 | 22/11, 21/11 | Jordan - King 345 kV & Jordan - North Belt 345 kV, DCKT Crown - Tanker 138 kV & Davson - ... - Greens Bayou 138 kV | Lychem - Power Systems Arco Cogen 138 kV | RT | Planned | [6 empty] | KG | JOR | JORKG_97 | SKGJOR5
AEP | Joslin - Sand Crab | LN | 138 | 21/11 | Formosa G3 | Formosa - Lolita 138 kV | RT | Planned | [6 empty] | JOSLIN | SANDCRAB | JOSLIN_SANDCR1 | SJOSSAN8
LCRA | Kendall - Kerrville Stadium | LN | 138 | 24/5 | Comfort To Cypress Creek 138kV | Raymond F Barker - Comfort 138kV | RT | Planned | [6 empty] | KERRST | KENDAL | 115T123 | SKERKEN8
LCRA | Kendall CTEC - Maenius Road | LN | 138 | 22/4 | Comfort - Kendall 138 kV | Hollmig - Kendall 138 kV | RT | Planned | [6 empty] | KENDCT | MAENRO | 22T342 | SMAEKEN8
ONCOR | Killeen Switch - Salado Switch (271) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | KLNSW | SALSW | 271 | SKLNSA25
ONCOR | Killeen Switch - Salado Switch (272) | LN | 345 | 18/12 | Killeen Switch TRX KLNSW_3_2 345/138 | Killen Switch TRX MR1H 345/138 kV | RT | Planned | [6 empty] | KLNSW | SALSW | 272 | SKLNSAL5
ONCOR | Killeen Switch Auto AXFMR1 345/138 kV | XF | 345 | 22/5, 22/4, 22/3, 22/2, 22/1 | DBCKT Salado Switch - Killeen Switch 345 kV | Killeen Switch Auto AXFMR2 345/138 kV | ADD | Planned | [6 empty] | KLNSW |  | AXFMR1 | XKLN58
ONCOR | Killeen Switch Auto AXFMR2 345/138 kV | XF | 345 | 2022 | DBCKT Salado Switch - Killeen Switch 345 kV | Killeen Switch Auto AXFMR1 345/138 kV | ADD | Planned | [6 empty] | KLNSW |  | AXFMR2 | XKLN358
ONCOR | Knob Creek Switch - Salado Switch | LN | 345 | 19/9 | DCKT Temple Elm Creek to Belton 138 kV | Temple Southeast - Temple Switch 138 kV | RT | Planned | [6 empty] | SALSW | KNBSW | 36040 | SKNBSAL5
ONCOR | Krum West Switch - Lewisville Switch | LN | 345 | 25/3 | DCKT Anna Switch - Cedar Elm Switch & Anna Switch -Krum West Switch 345kV | Argyle - Corinth 138kV | RT | Planned | [6 empty] | LWSSW | KRWSW | 35010 | SKRWLW25
AEP, ONCOR | Krum West Switch - Riley | LN | 345 | 24/11 | Riley-bomsw 345&byrsw-bomsw 345_dblckt, Jacksboro Switching To Cobb Switching Station Lin _a, Riley-bomsw 345&byrsw-bomsw 345_dblckt, Jacksboro Switching To Cobb Switching Station Lin _a | FSHSW 345 - RILEY, BOMSW 345 - GRVSW, FSHSW 345 - RILEY, BOMSW 345 - GRVSW | RT | Planned | [6 empty] | RILEY | KRWSW | 37020 | SKRWRI15
AEP | La Palma - Villa Cavazos | LN | 138 | 23/5, 23/3, 22/6 | STILLMAN - LOMA ALTA SUBSTATION 138 kV, WATERPORT SUBSTATION - LOMA ALTA SUBSTATION 138 kV | Titan_ Substation - Scarbi Carbide 138 kV, Paloa Alto Substation - Titan_ Substation 138 kV | RT | Planned, Forced | [6 empty] | LA_PALMA | VCAVAZOS | LA_PAL_VCAVAZ1 | SVCALA_8
AEP | La Palma -...- Military Highway Aep | LN | 138 | 24/6, 24/10 | Stillman To Loma Alta Substation 138kV | Titan Substation - South Carbide 138kV | RT | Planned | [6 empty] | VCAVAZOS | MILITARY | MILITA_VCAVAZ1 | SVCAMIL8
AEP | La Palma 138 kV bus #1 (CB 55, etc.) | BUS | 138 | 18/5 | DCKT Rio Hondo - North Edinburg 345 kV & Harlingen Switch 138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | LA_PALMA |  | 0BB1 | N/A
AEP | La Palma 138 kV bus #2 (CB 2015, etc.) | BUS | 138 | 18/5, 17/2 | DCKT Rio Hondo - North Edinburg 345 kV & Harlingen Switch 138 kV, North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | LA_PALMA |  | 8BB2 | N/A
AEP | Laquinta - Lobo | LN | 138 | 15/5 | Crestonio to Falfurrias 138 kV | Bruni Auto 69_1 138/69 kV | ST | Planned | Y | [5 empty] | LOBO | LAQUINTA | LAQUIN_LOBO1 | SLAQLOB8
AEP | Laredo Vft North - … - Mines Road | LN | 138 | 18/4 | Molina to Wormser Road 138 kV, Lobo to Molina 138 kV | Del_Mar - Laredo Plant 138 kV | RT | Planned | [6 empty] | LARDVNTH | LASCRUCE | LARDVN_LASCRU1 | MNLALAR8
AEP | Laredo Vft North - Lobo (LARDVN_LOBO1) | LN | 138 | 21/4 | Fowlerton-Lobo 345 kV | North Laredo Switch - Piloncillo 138 kV | RT | Planned | N | [5 empty] | LOBO | LARDVNTH | LARDVN_LOBO11 | SLARLO28
AEP | Laredo VFT North - Lobo (LARDVN_LOBO2) | LN | 138 | 21/5 | Laredo Vft North - Lobo 138 kV | Molina - Sierra Vista 138 kV | RT | Planned | [6 empty] | LOBO | LARDVNTH | LARDVN_LOBO2 | SLARLOB8
AEP | Laredo Vft North - Milo | LN | 138 | 24/6 | University Aep To Del Mar 138kV | Catarina - Piloncillo 138kV | RT | Planned | [6 empty] | LASCRUCE | MILO | LASCRU_MILO1 | SLARLAS8
AEP | Laredo VFT North -…- North Laredo Switch | LN | 138 | 24/6, 24/2, 23/4, 22/5, 22/4 | Fowlertron Auto 7TR 345/138 kV, Molina -…- Wormser Road 138 kV, Fowlerton - Lobo 345 kV, DCKT Lobo -…- Fowlerton 345kV | Del Mar - Laredo Plant 138 kV, Bruni Sub Auto1 138/69 kV, Wormser Road - Gateway West Tap 138 kV, Lardvnt Vft North - Las Cruces 138 Kv, Catarina - Piloncillo 138kV | RT | Planned, Forced | [6 empty] | MILO | MINES_RD | MILO_MINES_1 | SMINNLA8
AEP | Las Pulgas - Raymondville 2 | LN | 138 | 21/12, 21/11, 21/10, 21/9, 17/4, 16/12 | Lon Hill - North Edinburg - Bonilla - El Trueno Wind Farm 345 kV & Primera-…- Rio Hondo 138 kV, Loyola Sub to Kleberg Aep 138 kV, DCKT Rio Hondo to North Endinburg 345 kV & Harlingen Sw | Haine Drive - La Palma 138 kV, Loyola Sub Auto 69_1 138/69 kV, Burns Sub - Rio Hondo 138 kV | RT | Planned | [6 empty] | RAYMND2 | LASPULGA | LASPUL_RAYMND1 | SRAYRI38
AEP | Las Pulgas - Rio Hondo | LN | 138 | 17/4, 16/12 | Loyola Sub to Kleberg Aep 138 kV | Loyola Sub Auto 69_1 138/69 kV | ST | Planned | [6 empty] | LASPULGA | RIOHONDO | LASPUL_RIOHON1 | SRAYRI28
PEC | Leander - Seward Junction | LN | 138 | 25/2 | Bertram To Andice 138kV, Bertram To Burnet 138kV, Burnet -...- Naruna & Bertram 138kv, DCKT Georgetown South -…- Hutto Switch138kV | Georgetown South - Round Rock Westinghouse 138kV, Georgetown South - Midnight Sub 138kV, Bell County - Salado Switch 138kV | RT | Planned | [6 empty] | SEWAJU | LEANDE | 353T353 | SSEWLEA8
ONCOR | Lewisville Switch - Roanoke Switch | LN | 345 | 25/3, 19/4, 19/3 | DCKT Carrollton Northwest - Lewisville Switch 345 kV, Argyle - … - Lewisville Switch 138 kV, DCKT Hicks Switch -…- Roanoke Switch 138kV, Timberview Switch -…- Venus Switch 345kV | Argyle - Highlands Tap 138 kV, Roanoke Switch Auto MR1L 345/138kV, Liggett Switch - Norwood Switch 345kV | RT | Planned, Forced | [6 empty] | LWSSW | RNKSW | 105_B | SLWSRNK5
BRAZOS | Lewisville Switch Auto FMR2 345/138 kV | XF | 345 | 17/4 | Jones Street Tnp to Lewisville Sw 138 kV | Ti Tnp - West Tnp 138 kV | RT | Planned | [6 empty] | LWSSW |  | FMR2 | XLWS158
BPUB, ONCOR | Loma Alta Substation - Stillman | LN | 138 | 23/3 | Millitary Highway Aep - Villa Cavazos 138 kV, DCKT La Palma - Villa Cavazos 138 kV & Rangerville 69 kV | Titan_ Substation - Scarbi Carbide 138 kV | RT | Forced | [6 empty] | LOMA_ALT | STILLMAN | STLLMN_LOMA | SSTILOM8
BPUB | Loma Alta Substation - Waterport Substation | LN | 138 | 18/1, 16/5 | Loma Alta Sub Auto T1 138/69 kV, La Palma to East Harrison 69 kV | La Palma - Villa Cavazos 138 kV, Haine Drive - La Palma 138 kV | RT | Planned, Forced | [6 empty] | WATERPRT | LOMA_ALT | WP_LA | SWATLO28
AEP | Lon Hill - … - Mathis | LN | 69 | 24/1 | George West Switching Station Auto 138_69_1 138/69 kV | Orange Grove Switching Station Auto 138_69_1 138/69 kV | RT | Planned | [6 empty] | EDROY | SMITH | EDROY_SMITH1 | SSTELO29
STEC | Loop 463 Sub - Victoria | LN | 138 | 22/4 | Coleto Creek - Victoria 138 kV (COLETO_VICTOR1) | Coleto Creek - Victoria 138 kV (COLETO_VICTOR2) | RT | Planned | [6 empty] | L_463S | VICTORIA | LOOP_VICTORIA | SL_4VIC8
ONCOR | Lufkin Switch - … - Nacogdoches Se | LN | 138 | 17/12 | DCKT Martin Lake Ses to Stryker Creek Ses & Trinidad Ses to Mt Enterprise 345 kV | Nacogdoches Se - Redland Switch 138 kV | RT | Planned | [6 empty] | LFKSW | NCSTP | 1350_E | SNCDNCD8
ONCOR | Martin Lake Ses - Mt Enterprise | LN | 345 | 2017 | Martin Lake - Elktion and Tyler Grande DCKT | Martin Lake - Shamburger | ADD | [7 empty] | MLSES | ENTPR | 360 | SENTMLS5
ONCOR | Martin Lake Ses - Styker Creek Ses | LN | 345 | 2017 | DCKT Martin Lake Ses to Elkton & Tyler Grande 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [7 empty] | MLSES | SCSES | 370 | SMLSSCS5
ONCOR | Martin Lake Ses - Tyler Grande | LN | 345 | 2017 | DCKT Martin Lake Ses to Styker Creek Ses & Mt Enterprise 345 kV | Martin Lake Ses - Shamburger Sw 345 kV | ADD | [7 empty] | MLSES | TYGND | 340 | STYGMLS5
LCRA | Mccarty Lane - Zorn (201T201) | LN | 138 | 25/2 | Henne -…-Zorn 138kv | Bergheim - Devils Hill 138kV | RT | Planned | [6 empty] | BEBACK | ZORN | 201T201 | SMCCZOR8
LCRA | Mccarty Lane - Zorn (97T202) | LN | 138 | 24/10 | Mccala-henne & Zorn 138kv | Crosswinds - Turnersville 138kV | RT | Planned | [6 empty] | MCCALA | ZORN | 97T202 | SMCCZO28
LCRA | Mccarty Lane - Zorn (97T205) | LN | 138 | 24/9 | Henne - Comal Lin 88T234 138kV, Ranch Road 12 -…- Hunter 138kV | Beback - Zorn 138kV, Crosswinds - Turnersville 138kV | RT | Planned | [6 empty] | MCCALA | ZORN | 97T205 | SMCCZO38
GAR | Mccree - Shiloh | LN | 138 | 24/5 | Ben Davis - Brand 138kV | Miller - Newman 138kV | RT | Planned | [6 empty] | SHILOH | MCCREE | SHIL_MCC | SSHIMCC8
LPL | Mcdonald Substation - Northwest Substation | LN | 115 | 23/4, 23/2 | Blackwater Draw Switch - Double Mountain Switch 345 kV | MacKenzie Substation - Northeastern Substation 115 kV | RT | Planned | [6 empty] | LPLNW | LPLMD | LPLNW_LPLMD | SL18LPL0
LCRA | Mcneil - Wells Branch | LN | 138 | 23/11, 23/9, 22/6 | DCKT Techridge - Ashton Woods AEN & Howard Lane AEN, DCKT Hutto Switch - Round Rock & Georgetown South 138 kV | Hutto Switch - Round Rock Northeast 138 kV, Howard Lane - Wells Branch 138 kV | RT | Planned | [6 empty] | WELLBR | MCNEIL_ | 96T136 | SWELMCN8
CNPE | Meadow - Ph Robinson | LN | 345 | 22/11 | DCKT Gable Street -…- Greens Bayou 138 kV, NORTH ALVIN TNP - ALVIN TNP 138 kV , DCKT Davidson - ..-Greens Bayou BY21 & Crown - Tanker 138 kV | Magnolia Tnp - Seminole Tnp 138 kV | RT | Planned | [6 empty] | MDO | PHR | MDOPHR99 | SMDOPHR5
STEC | Merett Sub - Palmhurst Sub | LN | 138 | 22/10 | DCKT North Edinburg -..- North Pharr & North McAllen 138 kV | Hec Energy Center - Azteca Sub 138 kV | RT | Planned | [6 empty] | MV_PALM4 | MERETT | MERETT_PLMHRST | SMERMV_8
ONCOR | Meyers Draw Pod - Stephenson Lake Pod | LN | 138 | 24/7 | DCKT Consavvy Switch - Morgan Creek Ses and Consavvy Switch - Longshore Switch 345kV | Polecat Creek Switch - Wrage Ranch Pod 138kV | RT | Planned | [6 empty] | SLKPD | MDPOD | 14040_D | MCRMSB48
ONCOR | Midkiff Switch - Catclaw Switch | LN | 138 | 24/5 | Skywest - Driver 138kV | Rocky Road - Stiles 138kV | RT | Planned | [6 empty] | MDKSW | CCLSW | 16010 | SMDKCCL8
AEP | Miles - … - San Angelo Concho | LN | 69 | 23/10 | San Angelo Red Creek - … - Weiss 138 kV | Steamboat - Winters 69 kV | RT | Forced | [6 empty] | HARI | MILES | HARI_MILES1 | SHARSAC9
CNPE | Miller -…- Rohmas | LN | 138 | 23/1 | Jefferson - College 138 kV | Conial - Philip 138 kV | RT | Forced | [6 empty] | BNS | MLR | BNSMLR88 | SRHMLR8
AEP | Mines Road - North Laredo Switch | LN | 138 | 24/12, 24/11, 24/12, 24/11 | Manual Double Lobo To Fowlerton 1&2 345 | DEL_MAR 138 - LAREDO | RT | Planned | [6 empty] | NLARSW | MINES_RD | MINES__NLARSW1 | MINNLA8
ONCOR | Mitchell Bend Switch - Rocky Creek | LN | 345 | 22/12, 19/11, 19/10 | DCKT Comanche Peak SES - Timberview Switch & Johnson Switch 345 kV, DCKT Timberview Switch - Comanche Peak SES & Carmichael Bend Switch 345 kV | Carmichael Bend Switch - Mitchell Bend Switch 345 kV, Benbrook SW - Sycamore Creek 345 kV | RT | Planned, Forced | [6 empty] | RKCRK | MBDSW | 152_A | SRKCMB35
ONCOR | Mitchell Bend Switch - Wolf Hollow 345 Switch | LN | 345 | 23/3, 22/3 | Comanche Peak Ses - Johnson Switch (Oncor) 345 kV & Comanche Peak Ses - Timberview Switch 345 kV | Comanche Peak Ses - Mitchell Bend Switch 345 kV | RT | Forced | [6 empty] | WOFHO | MBDSW | 6034_A | SRKCMB25
ONCOR | Montfort Switch -...- Shankle Switch | LN | 138 | 24/6 | Pebble Creek Switch -…- Shankle Switch 138kV | Ennis West Switch - Templeton 138kV | RT | Forced | [6 empty] | ENPTP | TLC | 920_D | SSHKCRI8
ONCOR | Monticello Ses - … -Paris Switch | LN | 345 | 2017 | Paris Switch to Valley South 345 kV & Pacific Switch to Valley SES 345 Kv | Paris Sw 345/138 kV Auto MR1 | ADD | [7 empty] | PRSSW | WDDSW | 390 | SMNSPRS5
ONCOR | Morgan Creek Ses - Sun Switch | LN | 138 | 25/3 | DCKT Dermott Switch - Scurry County South Switch 345 | Morgan Creek Ses - Sun Switch 138kV | RT | Planned | [6 empty] | SUNSW | MGSES | 6474_A | MRGRSUN8
ONCOR | Moss Switch - …- Odessa Ehv Switch | LN | 138 | 24/9 | DCKT Moss Switch -…- Wolf Switching Station 345kV | Odessa North - Odessa 138 kV | RT | Forced | [6 empty] | BTHOT | ODEHV | 6500_B | SBTHOD58
ONCOR | Moss Switch -…- Yucca Drive Switch | LN | 138 | 25/2, 25/1, 24/12 | Wolf Switching Station -…- Red Lakes Switch 138kV, Moss Switch -…- Red Lakes Switch 138kV, DCKT Moss Switch -…- Wolf Switching Station 345kV | Odessa Ehv Switch - Yarbrough Sub 138kV, Wolf Switching Station - Sandhills Tap 138kV | RT | Forced | [6 empty] | MOSSW | METSW | 34630 | SMOSYUC8
ONCOR | Mt Enterprise - Trinidad Ses | LN | 345 | 2017 | DCKT Tri Corner - Elkton & Tyler Grande 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | ENTPR | TRSES | 361 | SENTTR25
LCRA | Muldoon - Plum | LN | 138 | 25/2 | Weimar To Glidden 138kV | Luling Auto AT1 138/69kV | RT | Planned | [6 empty] | PLUM | MULDOO | 146T1331 | SPLUMUL8
BRAZOS | Myra -…- Spring | LN | 138 | 25/2, 25/1 | DCKT Lewisville Switch -…- West Denton 345kV | Bennett Road Switch - Decatur 138kV, Allison - Krum Switch 138kV | RT | Planned | [6 empty] | MYRA | VALYVIEW | MYRA_VAL | SMYRSPR8
ONCOR | Nacogdoches Se - Redland Switch | LN | 138 | 18/12 | DCKT Mt Enterprise - Trinidad Ses & Martin Lake Ses - Stryker Creek Ses | Lufkin Switch - Nacogdoches South Tap 138 kV | RT | Planned | [6 empty] | NCDSE | REDSW | 1170 | SNCDRED8
AEP | Nelson Sharpe Auto 345_138_AUTO 345/138 kV | XF | 345 | 23/3 | Barney Davis - Alazan 138 kV | Celanebi Bishop - Kleberg Aep 138 kV | RT | Forced | [6 empty] | N_SHARPE | N_SHARPE | 345_138_AUTO | XN_S58
CNPE | New Gulf - South Lane City | LN | 138 | 22/5 | STP SWITCH -…- STP Facilites HLP & Esperanza & Blessing 138 kV | Blessing - Pavlov 138 kV | RT | Forced | [6 empty] | LC | NEW | LC_NEW60 | SNEWGLF8
AEP | North Carbide - Sand Crab | LN | 138 | 24/5 | DCKT Fowlerton - San Miguel Gen 345kV, DCKT San Miguel Gen -…- Cenizo & Torrecillas 345kV | Big Tree - Victoria Dupont Switch 138kV | RT | Planned | [6 empty] | NCARBIDE | SANDCRAB | NCARBI_SANDCR1 | MJOSNCA8
AEP | North Edinburg - Lon Hill | LN | 345 | 17/3, 16/3, 15/3 | Nelson Sharpe to Ajo 345 kV, Nelso Sharpe to Ajo 345 kV, DCKT Rio Hondo to North Edinburg 345 kV & Harlingen Sw 138 kV, Basecase | Raymondville 2 - Yturria Sub 138 kV, Celanese Bishop - Nelson Sharpe 138 kV, Burns Sub - Rio Hondo 138 kV, Valley GTC | RT, ST | Planned, Forced | [6 empty] | NEDIN | LON_HILL | LON_HI_NEDIN1 | SNEDLON5
AEP, STEC | North Edinburg - West Ednburg Sub (NEDIN_MVWED_1A) | LN | 138 | 23/10 | DCKT North Edinburg - North McAllen & McColl Road 138 kV | Azteca Sub - Hidalgo Energy Center 138 kV | RT | Planned | [6 empty] | NEDIN | MV_WEDN4 | NEDIN_MVWED_1A | SALTMV_8
AEP, STEC | North Edinburg - West Ednburg Sub (NEDNBRG_WEDNBG) | LN | 138 | 23/10 | DCKT North Edinburg - North McAllen & McColl Road 138 kV | Azteca Sub - Hidalgo Energy Center 138 kV | RT | Planned | [6 empty] | NEDIN | MV_WEDN4 | NEDNBRG_WEDNBG | SMV2NED8
AEP | North Edinburg Auto 138 345/138 kV | XF | 345 | 19/4, 17/2 | North Edinburg Auto 1382 345/138 kV | Burns Sub - Rio Hondo 138 kV, Haine Drive - La Palma 138 kV | RT | Planned, Forced | [6 empty] | NEDIN |  | 138H | XNED358
AEP | North Edinburg Auto 345_1382 345/138 | XF | 345 | 20/5 | DCKT Loss of North Edinburg Train 345 kV | North Edinburt Auto 345_138 345/138 kV | RT | Planned | Y, N | [5 empty] | NEDIN | NEDIN | 345_1382 | XNED258
AEP | North Laredo Switch - Piloncillo | LN | 138 | 25/1, 25/1, 21/10 | DCKT San Miguel Gen -…- Cenizo & Torrecillas 345kV, Fowlerton - Lobo 345 kV | Catarina - Piloncillo 138kV, Laredo Vft North - Las Cruces 138 kV | RT | Planned | [6 empty] | NLARSW | PILONCIL | NLARSW_PILONC1 | SPILNLA8
LCRA, ONCOR | North McCamey - … - Odessa Ehv Switch | LN | 345 | 2018 | Basecase | McCamey GTC | ADD | [7 empty] | NORTMC | ODEHV | MCCAMEY_ODESSA | SNORODE5
STEC | Oaks Sub - Poteet Sub | LN | 69 | 18/1, 17/12 | DCKT Castrvll to Razorbac & Txresrch 138kV | Hondo Creek Switching Station - Moore Switching Station 138 Kv | RT | Planned | [6 empty] | POTEETS | OAKS9 | POT_OAKS | SPOTOAK9
ONCOR | Oates - … - Royse Switch 138 Kv (1391) | LN | 138 | 23/9 | Centerville - Oates 138 kV | Buckner Home - Mesquite Forney Road 138 kV | RT | Planned | [6 empty] | RYSSW | FATES | 1391_E | SDALRY28
CNPE | Obrien - Wa Parish (OB_WAP98) | LN | 345 | 23/9, 22/8 | DCKT Wa Parish-Jeanetta 345 kV | Wa Parish - Obrien 345 kV (OB_WAP99) | RT | Planned | [6 empty] | WAP | OB | OB_WAP98 | SOBWA2P5
CNPE | Obrien - Wa Parish (OB_WAP99) | LN | 345 | 22/8, 20/8 | DCKT Wa Parish-Jeanetta 345 kV | Wa Parish - Obrien 345 kV (OB_WAP98) | RT | Forced, Planned | [6 empty] | WAP | OB | OB_WAP99A | SOBWAP5
ONCOR, WETT | Odessa EHV Switch - Wett_Grelton | LN | 345 | 22/4, 22/3 | DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Scurry County South Switch - Wett_Long_draw 345 kV & Wett_Faraday - Wett_Long_Draw 345 kV, DCKT Scurry County South Switch - Tonkawa Switch 345 kV | Gail Sub - Willow Valley Switch 138 kV, Dewey Lake Tap - Polecat Creek Switch 138 kV, Kocht Tap - Vealmoor 138 kV | RT | Planned | [6 empty] | W_GT_345 | ODEHV | T-306 | SW_GODE5
LCRA | Odlaw Switch - … - Uvalde Aep | LN | 138 | 22/12, 22/11, 19/2 | Bighill - Kendal 345 kV, Big Hill - Twin Buttes 345 kV | Hamilton Road - Maverick 138kV, Ganso - Maverick 138 kV | RT | Planned, Forced | [6 empty] | BLEWET | ASPHALT | 222T570 | SBRAUVA8
GAR | Olinger - Wylie Switch (WYL_OLI1) | LN | 138 | 16/4 | Greenville Steam to Shelby 138 kV | Shelby Auto BT1 138/69 kV | ST | Forced | [6 empty] | WYLIESW | OLINGR | WYL_OLI1 | SFIRWY18
GAR | Olinger - Wylie Switch (WYL_OLI2) | LN | 138 | 16/9, 15/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | WYLIESW | OLINGR | WYL_OLI2 | SOLIWY18
GAR | Olinger - Wylie Switch (WYL_OLI3) | LN | 138 | 16/9 | Pruitt to Swindell 138 kV | Ben Davis - Olinger 138 kV | ST | Planned | [6 empty] | WYLIESW | OLINGR | WYL_OLI3 | SOLIEL28
AEP | Olmito - Palo Alto Substation | LN | 138 | 25/3 | Stillman To Loma Alta Substation 138kV | Villa Cavazos - Military Highway Aep 138kV | RT | Forced | [6 empty] | OLMITO | PALOALTO | OLMITO_PALOAL1 | SPALMIL8
AEP | Owls - Santa Rita | LN | 138 | 25/1 | DCKT Big Hill - Schneenman Draw 345kV | Lake Nasworthy - San Angelo Mathis Field 69kV | RT | Forced | [6 empty] | SANTARIT | OWLS | OWLS_SANTAR1 | SSANOWL8
AEP | Paint Creek Bus #1 (CB 4135, etc.) | BUS | 138 | 17/1, 16/6, 16/5 | Scurry Sw to Sun Sw 138 kV, Salt Creek Bepc to Salt Creek Reactor 138 kV | Eskota Sw - Longworth 69 kV, Aspermont Auto 69T1 138/69 kV | ST | Planned | [6 empty] | PAINTCRE |  | 8BB1 | N/A
LCRA | Paleface - Starcke | LN | 138 | 25/4 | Turnersville - Buda 138kV, DCKT Zorn - Austrop & Zorn - Lytton Springs | Marshall Ford - Paleface 138kV | RT | Planned | [6 empty] | STARCK | PALEFA | 83T196 | SPALSTA8
AEP, BPUB | Palo Alto Sub - Titan Sub | LN | 138 | 16/5 | Loma Alta Sub T1 138/69 kV | La Palma - Villa Cavazos 138 kV | RT | Planned | [6 empty] | PALOALTO | TITAN_SU | PALOAL_TITAN_1 | SPALSCA8
ONCOR | Paris Switch - Valley Ses | LN | 345 | 22/11 | Woodward Switch - Monitcello Ses 345 kV | Paris Switch AXFMR1H 345/138 kV | RT | Forced | [6 empty] | PRSSW | VLSES | 391_A | SPRSVLS5
ONCOR | Paris Switch - Valley South | LN | 345 | 22/11 | Woodward Switch - Monitcello Ses 345 kV | Paris Switch AXFMR1H 345/138 kV | RT | Forced | [6 empty] | PRSSW | VLYSO | 403_A | SVLYPRS5
ONCOR | Paris Switch CB_8635 | CB | 345 | 2017 | Paris Switch to Pacific Switch & Valley South 345 kV | Paris Sw 345/138 kV Auto MR1 | ADD | [7 empty] | PRSSW |  | 8635 | N/A
STEC | Pawnee Switching Station - San Miguel Gen | LN | 138 | 25/4 | DCKT Skyline - Calaveras 345kv | Pawnee Switching Station - San Miguel Gen 345kV | RT | Forced | [6 empty] | PAWNEE | SANMIGL | PAWNE_SANMI_1A1 | SPAWSAN5
AEP, STEC | Pawnee Switching Station - Tango | LN | 345 | 22/2, 22/1, 21/11 | Coleto Creek - Grissom 345 kV & Fannin Sub - Goliad 69 kV, Grissom - Lon Hill 345 kV, Fowlerton - San Miguel Gen 345 kV | North Carbide - Sea Drift Coke 138 kV, Choke Canyon Aep - San Miguel Gen 138 kV, George West Switch Station - Sigmor 138 kV | RT | Forced, Planned | [6 empty] | PAWNEE | TANGO | PAWNEE_TANGO1 | STANPAW5
AEP | Primera - Rio Hondo | LN | 138 | 20/7 | La Palma-Rangerville (MVEC) 138 kV | Haine Drive - La Palma 138 kV | RT | Forced | [6 empty] | S_SNROSA | PRIMERA | PRIMER_S_SNRO11 | SS_SPRI8
ONCOR | Red Lakes Switch -…- Wolf Switching Station | LN | 138 | 24/8 | DCKT Meteor Switch -…- Odessa Ehv Switch 345kV, Meteor Switch - Moss Switch 345kV | Yarbrough Sub - Odessa Ehv Switch 138kV | RT | Forced | [6 empty] | WLFSW | PWPOD | 6485_A | SWLFECT8
LCRA | Redwood - San Marcos | LN | 138 | 25/2 | Turnersville - Buda 138kV | Crosswinds - Goforth 138kV | RT | Planned | [6 empty] | REDWOO | SANMAR | 106T2001 | SREDSAN8
CNPE | Refuge - South Texas Project | LN | 345 | 24/3 | DCKT Bailey - Blue 345 kV & Hillje - Wolf 345 kV | Jones Creek - South Texas Project | RT | Planned | [6 empty] | REF | STPSW | REFSTP27 | SSTPREF5
AEP | Riley - Tesla | LN | 345 | 21/11 | DBCKT Edith Clarke - Riley 345 kV | Abilene Mulberry Creek - Long Creek 345 kV | RT | Planned | [6 empty] | RILEY | TESLA | RILEY_TESLA1 | STESRI15
AEP | Rio Hondo - South Santa Rosa | LN | 138 | 24/8 | Las Pulgas - Raymondville 2 138kV | Haine Drive - La Palma 138kV | RT | Forced | [6 empty] | S_SNROSA | RIOHONDO | RIOHON_S_SNRO1 | MPRIRIO8
LCRA | Rio Lago - Verde Creek | LN | 138 | 24/11 | Cagnon - Kendal 345kV & Cico - Menger Creek 138kV | Medina Lake - Pipe Creek 138kV | RT | Planned | [6 empty] | RIOLAG | VERDCR | 67T280 | SRIOVER8
ONCOR | Rivercrest Ses - Talco West Tap | LN | 138 | 24/9 | DCKT Valley Ses - Pacific Switch & Paris Switch - Valley South 345kV | Monticello Tap - Talco West Tap 138kV | RT | Forced | [6 empty] | TALTP | RCSES | 1650_G | STALTAL8
ONCOR, TMPA | Roanoke Switch - West Denton | LN | 345 | 25/4 | Krum West Switch - Lewisville Switch 345kV, DCKT Lewisville Switch - Roanoke Switch & Lewisville Switch - Krum West Switch 345kV | Argyle - Highlands TNP 138kV, Denton Creek Switch - Decatur 138kV | RT | Planned | [6 empty] | RNKSW | W_DENT | 165 | SW_DRNK5
ONCOR | Round Rock - Round Rock Westinghouse | LN | 138 | 24/7 | Bell County - Temple Switch 138kV | Chief Brady - Georgetown 138kV | RT | Forced | [6 empty] | RNDRK | RRWES | 1680_B | SGEOHU48
ONCOR | Russell Gap Switch - Killeen Switch (35091) | LN | 345 | 22/9 | Comanche Switch (Oncor) to Comanche Peak SES 345 kV, DCKT Bighil-Kendal 345 kV | Comanche Tap - Comanche Switch (Oncor) 138 kV, Yellow Jacket - Treadwell 138 kV | RT | Forced | [6 empty] | RGPSW | KLNSW | 35091 | SRGPKLN5
AEP, BRAZOS | Salt Creek SS - … - Spur | LN | 138 | 19/5 | DCKT Dermott Switch to Bluff Creek Switch & Golden Switch 138 kV | Morgan Creek SES - Sun Switch 138 kV | RT | Planned | [6 empty] | SLTCRKSS | SCKR | SCKR_SCK | SSPUSLT8
STEC | Sam Rayburn Switch - Vanderbilt Switch | LN | 138 | 15/10 | Loop 463 to Sam Rayburn 138 kV | Sam Rayurn Swithcing Station Auto 69_2 138/69 kV | ST | Planned | [6 empty] | RAYBURN | VANBLTSS | RAY_VANB | SVANRAY8
LSTR, ONCOR | Sam Switch - Venus Switch | LN | 345 | 25/1 | DCKT Navarro - Limestone Plant & Limestone Plant - Outlaw Sitch 345kV | DCKT Big Brown Ses 345 - Jewett 345kV | RT | Planned | [6 empty] | SAMSW | VENSW | 35055 | STHSVE65
AEP | San Angelo College Hills - … - San Angelo Power Station | LN | 138 | 19/9 | San Angelo Paulann to San Angelo Red Creek 138 kV | San Angelo Concho - San Angelo Emerson Street 69 kV | RT | Planned | [6 empty] | SAPOWER | SOUTHLAN | SAPOWE_SOUTHL1 | SSASSA28
AEP | San Angelo Power Station - … - SA Highland Street | LN | 138 | 19/9 | San Angelo Coke Street to San Angelo Red Creek 138 kV | San Angelo Power Station - San Angelo South 69 kV | RT | Planned | [6 empty] | SAPOWER | SAST | SAPOWE_SAST1 | SSASRED8
AEP | San Angelo Red Creek - … - San Angelo North | LN | 138 | 24/4 | San Angelo College Hills - … - San Angelo Power Station 138 kV | San Angelo Power Station Auto T1 138/69 kV | RT | Forced | [6 empty] | PAULANN | REDCREEK | PAULAN_REDCRE1 | SPAUSAR8
AEP | San Angelo Red Creek Auto T2 345/138 kV | XF | 345 | 16/10 | San Angelo Red Creek Auto T1 345/138 kV | Nicole - Orient 138 kV | RT | Planned | [6 empty] | REDCREEK |  | T2H | XSA3R58
AEP | Santa Rita - Wolfcamp | LN | 138 | 24/11 | Twin Buttes To Hargrove Lin 1 | SAMATHIS 69 - TANK | RT | Forced | [6 empty] | SANTARIT | WOLFCAMP | SANTAR_WOLFCA1 | SWOLPAL8
ONCOR, WETT | Scurry County South Switch - Wett_Long_Draw (T-304) | LN | 345 | 24/4, 22/5, 22/4 | Blackwater Draw Switch - Double Mountain Switch 345 kV, DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses | MacKenzie Substation - Northeast Substation 115 kV, Falcon Seaboard - Morgan Creek Ses 345 Kv | RT | Planned | [6 empty] | W_LD_345 | SCOSW | T-304 | SW_LSCO5
AEP, BRAZOS | Scurry Switch - … - Spur | LN | 138 | 16/10, 16/3 | Aspermont Aep to Spur 138 kV | Spur Auto 69_1 138/69 kV | ST | Planned | Y, N | [5 empty] | SCURRYSW | SCK | SLTCRK_SCRYSW | SSPUMW18
AEP | Silver - Sterling City & Spade Ranch | LN | 69 | 24/12 | DCKT Noelke - Cedar Canyon 345kV | Sterling City - Sterling County 69kV | RT | Forced | [6 empty] | ANGORA | STER | ANGORA_STER1 | SSPACED9
BPUB | Sixth Street Substation - South Plant Substation | LN | 138 | 18/4, 18/3 | DCKT San Miguel Gen to Elmcreek 345 kV, Kendall to Cagnon 345 kV; | Pawnee Switching Station - Calaveras 345 kV, CICO - Comfort 138 kV | RT | Planned | [6 empty] | SOUTH_PL | SIXTH_ST | 6ST_SP | SSIXSOU8
ONCOR | Snyder - … - Sun Switch (6240) | LN | 138 | 21/4 | DCKT Dermott Sw-…- Bluff Creek Sw & Ennis Creek Sw 138 kV | Morgan Creek Ses - Sun Switch 138 kV | RT | Planned | N | [5 empty] | SNYDR | DPCRK | 6240_A | SSACSUN8
AEP | South Carbide - Titan Sub 138 kV | LN | 138 | 24/3 | Loma Alta Sub - Stillman 138 kV | La Palma - Villa Cavazos 138 kV | RT | Planned | [6 empty] | TITAN_SU | SCARBIDE | SCARBI_TITAN_1 | STITSCA8
CNPE | South Texas Project - WA Parish | LN | 345 | 23/2, 22/3, 22/2, 21/12, 21/9 | Jones Creek - Refuge 345 kV & Jones Creek - South Texas Project 345 kV, Jones Creek - South Texas Project 345 kV & Refuge - South Texas Project 345 kV, Hillje - Wolf 345 kV | Hillje - South Texas Project 345 kV, Blessing - Pavlov 138 kV, Jones Creek - South Texas Project 345 kV | RT | Planned | [6 empty] | STP | WAP | STPWAP39 | STPWAP39
BPUB, STEC | Southmost Sub - Waterport Sub | LN | 138 | 18/1 | Lon Hill to Coleto Creek 345 kV, La Palma to East Harrison 69 kV, DCKT Jewett to Singleton 345 kV | Warburton Road Switching Station - Victoria 138 kV, Btu Jack Creek - Twin Oak Sw 345 kV | RT | Forced | [6 empty] | WATERPRT | SOUTHMOS | WP_SM | SSOUWAT8
BRAZOS | Stephenville Bepc Auto FMR1 138/69 kV | XF | 138 | 15/3 | Oran Sub to Mineral Wells & RW Miller 138 kV | Bunker - RW Miller 138 kV | ST | Planned | [6 empty] | STV |  | FMR1 | XSTV289
ONCOR | Stryker Creek Ses - Trinidad Ses | LN | 345 | 2017 | DCKT Elkton to Tri Corner & Tyler Grande to Tri Corner 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | SCSES | TRSES | 480 | STRSSCS5
ONCOR | Tall City - Telephone Road | LN | 138 | 23/4 | NATURAL DAM to BEALS CREEK 138 kV | Big Spring West - Stanton East 138 kV | RT | Planned | [6 empty] | TALLCITY | TELPH_RD | TALLCITY_TELPR | STALTEL8
ONCOR | Temple Elm Creek - Temple North | LN | 138 | 24/10 | Salsw To Knbsw 345 And Tmpsw To Belcnty 138 Dblckt, Salsw To Knbsw 345 And Salsw To Belcnty 138 Dblckt, Salsw To Klnsw 345 Dblckt, Salsw To Knbsw 345 And Tmpsw To Belcnty 138 Dblckt, Salsw To Knbsw 345 And Salsw To Belcnty 138 Dblckt, Salsw To Klnsw 345 Dblckt | SANDW 138 - TMSTH | RT | Planned | [6 empty] | TMECR | TMNTH | 625_C | MDPPCBN8
ONCOR | Temple Elm Creek - Temple Pecan Creek | LN | 138 | 25/4 | DCKT Temple Switch - Temple Pecan Creek Lin 315 & Temple Switch - Belfalls Switch 345kV | Temple Switch - Temple Pecan Creek Lin 300_A 345kV | RT | Planned | [6 empty] | TMECR | TMPCR | 1425 | STMETM48
CNPE | Th Wharton - Zenith (THWZEN71) | LN | 345 | 22/12 | DCKT Singleton to Tomball 345 kV and Kuykendahl to Roans Prairie 345 kV and Kuykendahl to Rothwood 345 kV | Thw Wharton - Zenith (THWZEN98) 345 kV | RT | Planned | [6 empty] | THW | ZEN | THWZEN71 | SZENTHW5
TNMP | TI TNP - West TNP | LN | 138 | 21/10 | DBCKT Carrollton Northwest - Lewisville Switch 345 kV | Jones Street Tnp - Lewisville Switch 138 kV | RT | Planned | [6 empty] | LWVTI | LWSVW | 588_A | SLWSLW48
TNMP | Tnp One Plant - Twin Oak Switch | LN | 345 | 25/3, 25/4, 25/3, 25/4 | DCKT Hillje -…- Wolf 345kV, Fort Smith Switch - Venus Switch 345kV | Twin Oak Switch -…- TNP One Plant Lin 261_A 345kV, Sam Switch - Venus Switch 345kV | RT | Planned | [6 empty] | TOKSW | TNP_ONE | 262_A | STNPTOK5
ONCOR | Tri Corner - Tyler Grande | LN | 345 | 2017 | DCKT Trinidad Ses to Stryker Creek Ses & Mt Enterprise 345 kV | Elkton 345/138 kV Auto MR3 | ADD | [7 empty] | TRCNR | TYGND | 341 | STYGTRC5
ONCOR | Tri Corner - Watermill Switch (215) | LN | 345 | 20/2, 19/10, 19/9 | DCKT Centerville Road Switch to Parkdale Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV | Prairie Creek - Scyene Road 138 kV, Kleberg Tap - Seagoville 138 kV | RT | Planned | [6 empty] | TRCNR | WTRML | 215 | STRCWTR5
ONCOR | Tri Corner - Watermill Switch (515) | LN | 345 | 24/12, 20/2, 19/10, 19/9 | DCKT Parkdale Switch - Centerville Road Switch 138 kV, DCKT Big Brown SES to Richland Chambers 345 kV, Tri Corner To Seagoville Switch Lin _b | Prairie Creek - Scyene Road 138 kV, Kleberg Tap - Seagoville 138 kV, FORSW 345 - TRCNR | RT | Planned | [6 empty] | TRCNR | WTRML | 515 | STRSWTR5, MDWRTR25
TBREC | Trumbull Auto TRF2 138kV/69kV | XF | 138 | 25/1 | Desoto Switch -…- Pebble Creek Switch 138kV | Trumbull Auto TRF1 138/69kV | RT | Planned | [6 empty] | TRU | TRU | TRF1 | XTRU89
ONCOR | Venus Switch - Fort Smith Switch | LN | 345 | 25/3, 25/1 | DCKT Tradinghouse Ses -...- Sam Switch 345kV, DCKT Limestone Plant -…- Outlaw Switch 345kV | Jewett - Big Brown Mine 2 345kV, Tradinghouse - Four Brothers Switch 345kV | RT | Planned, Forced | [6 empty] | VENSW | FTSSW | 35050 | SVENFTS5
WETT | Volta - Wett_grelton | LN | 345 | 24/6, 24/5 | DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Wett Faraday -…- Scurry County South Switch 345kV, Odessa Ehv Switch To Wett_grelton 345kV | Alkali Lake - Jim Payne Poi 138kV, Koch Tap - Vealmoor 138kV | RT | Planned | [6 empty] | W_GT_345 | VLTA | T-312 | SW_GVLT5
WETT | Volta - Wett_long_draw | LN | 345 | 24/6, 24/5 | DCKT Consavvy Switch - Longshore Switch & Morgan Creek Ses, Wett Faraday -…- Scurry County South Switch 345kV, Odessa Ehv Switch To Wett_grelton 345kV | Alkali Lake - Jim Payne Poi 138kV, Koch Tap - Vealmoor 138kV | RT | Planned | [6 empty] | VLTA | W_LD_345 | T-305 | SW_LVLT5
STEC | Warburton Road Switching Station - Warburton Road Switching Station | CB | 69 | 24/7 | Victoria -…- Peregrine Substation 345kV, Grissom - Raptor 345kV | Warburton Road Switching Station - Victoria 138 kV | RT | Forced | [6 empty] | WARBURTN | WARBURTN | 464 | XWAR89