## Slide 1
ERCOT Frequency Events
May 2025
ERCOT
Operations Planning
PDCWG | June 20, 2025

## Slide 2: 5/6/2025 10:44:22 (Non-FME)
Notes: The unit tripped offline while carrying ~570 MW
Starting Frequency: 59.981 Hz
Minimum Frequency: 59.933 Hz
A-C Time : 3 seconds
Recovery Time(back to deadband): 3 minutes 44 seconds
ECRS Released: 0 MW
Trip Reason: Unknown at this time
Reason for no selection: Frequency is outside low deadband and C point is 59.933
Contextual Information: A total of 165 MW of regulation Up was deployed during the event.

## Slide 3: 5/15/2025 16:59:38 (Non-FME)
Notes: The unit tripped offline while carrying ~ 682 MW
Starting Frequency: 60.017 Hz
Minimum Frequency: 59.940 Hz
A-C Time : 4 seconds
Recovery Time(back to deadband): 4 minutes 10 seconds
ECRS Released: 0 MW
Trip Reason: Breaker room issue
Reason for no selection: C point is 59.940

## Slide 4: 5/29/2025 23:47:55 (Non-FME)
Notes: A unit tripped for loss of ~626 MW
Starting Frequency: 59.996 Hz
Minimum Frequency: 59.935 Hz
A-C Time : 4 seconds
Recovery Time(back to deadband): 6 minutes 41 seconds
ECRS Released: 0 MW
Trip Reason: Unknown at this time
Reason for no selection: The C point is 59.935

## Slide 5: Questions?
Thank you!