## Slide 1: Data Center Modeling for Transmission Planning Studies
Parag Mitra
Principal Technical Leader

## Slide 2: Data Center Electrical Distribution
About 90% of the total load is electronically driven (Switched Mode Power Supplies and Electronic Drives)
The main electrical equipment that interfaces with the grid are:
Uninterruptible power supply
Single phase power supply units (*)
Variable speed drives/direct connected motors
Lighting (LED)
Battery Energy Storage/Power Conditioning Equipment (*)

## Slide 3: Main Electrical Components – Double Conversion UPS
Sun, Jingjing, "Data Center Power System Emulation and GaN-Based High-Efficiency Rectifier with Reactive Power Regulation. " PhD diss., University of Tennessee, 2022. https://trace.tennessee.edu/utk_graddiss/7200
UPS operation mode | Conditions
Eco | Normal
Double conversion | Degraded
Double conversion | Always
Important to understand the operation mode of the UPS
Not critical for PSS®E assessment
Important for small signal assessment when such analysis is needed.
If in ECO mode, the controls of the single-phase power supply unit would matter
All transfers happen using static switches (4-5 ms)

## Slide 4: Main Electrical Components – Double Conversion UPS
Front end of the UPS controls the voltage at the dc bus and maintains power factor
  Id command generated to follow Vdref
  Iq generally set to 0 to maintain unity PF
  Conventional dq control
Back end of the UPS would operate in constant V and F-droop mode- similar to GFM
Battery is always connected to the dc bus, floating and charging using the dc-dc converter in buck mode. Operates in constant I or V mode
As grid voltage drops, dc bus voltage drops as well. If dc bus voltage drops below a Vset (90%-70%), rectifier is shut off and dc-dc converter starts to control dc bus voltage in boost mode
As rectifier shuts off, data center disconnects from the grid
  Control system model useful only for voltages above 70% as of now.
As voltage recovers, UPS may switch the load back and total load for some time is data center load + batt charging
Utility
Data Center
Front - Rec
Back - Inv
Dc-bus

## Slide 5: Single Phase Power Supply Unit
L
R
C
idc
vdc
vac
iac
gate
PI
PLL
H-band
control
S/R
x
-
gate
Vdcref
f
ϴ
Load power is transmitted as a voltage setpoint to the PFC controller.
DC current is regulated by an H-band controller, where the IGBT gate is activated when the minimum/maximum hysteresis band limits are reached.
Vphase 1
H-band current controller
Vac and Iac PFC output

## Slide 6: Behavior during Transient and Steady State
This behavior is only applicable for V dip up to 0.7 pu as the load moves to the battery below that threshold
Constant P
Transient dip

## Slide 7: Modeling for Transmission Planning Studies
Slower Dynamics and Ride-Through
Sub-synchronous Oscillations
Ferroresonance
Flicker
Fast controller interactions
Harmonics and switching transients
0.1 Hz
10 -15 Hz
kHz range
Phasor simulators
EMT simulators
Lack of information
Lack of models and information

## Slide 8: EMT vs Phasor Model – What are the needs?
 | EMT | Phasor
Generic | Develop understanding of device at hand, Screen for possible risks, Possibly use as starting point of OEM models. Not suitable for issue resolution | Long-term assessments, Bulk system reliability risks. Not suitable for equipment specific dynamics that might be of interest.
Vendor Specific | Actual risk screening, solution for issues arising at facilities. Not suitable for developing understanding of device at hand (generally) | Actual risk screening, solution for issues arising at facilities not represented by generic models. Not very suitable for long term assessments

## Slide 9: Positive Sequence Model for Data Center Load
Dynamics due to process controls (Inverter Control)
Ability to model multiple protection behavior
Modeling current limits of the device
Protection logic
Available as dll in PSS®E V34, V35
Original created in PSLF by EPRI

## Slide 10: Parameterizing PSS/E data center model (Undervoltage disconnection)
1.
LVTA
4. LVRA
2. LVDTA
3. LVDRA
5. RAMPUA
Voltage (pu)
Active Power (MW)
Time (s)
 | Parameter description | Parameter name
1 | UNDERVOLTAGE TRIP SETTING | LVTA
2 | UNDERVOLTAGE TIME TO TRIP SETTING | LVDTA
3 | UNDERVOLTAGE DELAY TIME TO RECONNECT SETTING | LVDRA
4 | UNDERVOLTAGE RECONNECTION SETTING | LVRA
5 | RAMP AFTER UNDERVOLTAGE DELAY TIME | RAMPUA
PSS/E model parameters
Mapping

## Slide 11: High Load (FIDVR)

## Slide 12: Low load

## Slide 13: Other Modeling Questions

## Slide 14: AI Training and Pulsing Load Shape
Example AI training load
Steam turbine torsional model
Conventional generators have torsional modes of oscillations in the 5-55 Hz range (oscillations between different turbine sections and the generator)
AI training creates pulsating loads which can excite these torsional modes
Over an extended period, this can cause fatigue and even damage the turbine shaft

## Slide 15: How these Facilities Need to be Modeled?
Tesla proposed using GFM Megapack to address both the pulsing load problem and ride-through issue (Tesla presentation at NERC LLTF 2025)
Utility metered data
Compute load
BESS used to smoothen pulsing load
BESS used to mimic load ride-through
Siemens proposed using E-STATCOM (STATCOM with super capacitor or flywheel) to address both the pulsing load problem and ride-through issue (Siemens Energy Presentation at ESIG Spring Large Load Workshop 2025)
E-STATCOM used to smoothen pulsing load
E-STATCOM used to ride-through disturbance