## Slide 1
ERCOT Frequency Control Report
June 2025
ERCOT
Operations Planning
PDCWG | July 22nd , 2025

## Slide 2: Summary of June 2025
CPS1: 173.75%
Current CPS1 12-Month Rolling Average: 176.07%
0 BAAL Exceedance(s)
1 hourly CPS1 score below 100%
BAAL-003 Events have updated through 2023
2023 BAAL-003 FRM Performance: -1130.21
2025 RMS1 Statistics
  Mean: 15.31 mHz
  Min: 13.39 mHz
  Max 17.11 mHz
Energy Statistics
  Total Energy: 45,650,658 MWh
  Wind Energy: 10,604,250 MWh
  Percent Energy from Wind: 23.23%
  Solar Energy: 6,948,383 MWh
  Percent Energy from Solar: 15.22%
Minimum System Inertia
  Mean: 266,883 MW*s
  Max: 300,140 MW*s on June 30th
  Min: 209,684 MW*s on June 17th

## Slide 3: Frequency Control
CPS1, BAAL, & RMS1

## Slide 4: Hourly CPS1 by Day
Jun-25 CPS1 (%): 173.75
Notes: CPS1 Score is 173.75%
One outlier under 100% on June 2nd:
Score was 98.35% @ 1600
IRR Down Ramp: Solar Gen Ramp down by ~2000MW during this hour..
Regulation: Reg-Up was exhausted during this hour (~508MW).
SCED Offsets: 2 manual GTBD SCED offsets were applied during this period, one @ 1605 and another at 1657. Both deployments for 200MW.

## Slide 5: BAAL Exceedances & Violations
There were 0 BAAL exceedance(s) in June.

## Slide 6: 15-Minute Average CPS1%
Jun-25 CPS1 (%): 173.75
Notes: CPS1 score is above 160% for all 15-minute intervals.

## Slide 7: 12-Month Rolling Average CPS1
Current 12-Month Rolling Average: 176.07%
Notes: 12 month rolling average CPS1 score is 176.07% which is in line with expectations

## Slide 8: Daily RMS1 of ERCOT Frequency by Year
Notes:   Daily RMS1 frequency by year is lower compared to 2024.
  2025 Stats:
  Mean: 14.73 mHz
  Min: 11.86 mHz
  Max 18.33 mHz

## Slide 9: Daily RMS1 of ERCOT Frequency by Month
Notes: A More granular look at last 15 years of RMS1 by Month
15.50 mHz on avg for June 2025

## Slide 10: Daily RMS1 of ERCOT Frequency by Month
Notes: Same data with 10 years shown instead of 15

## Slide 11: Frequency Profile Comparison

## Slide 12: Frequency Profile Comparison
Notes: Comparison of frequency profile between May 2024 and May 2025. Compared to last year, there are slightly less instances of frequency hovering around the lower dead bands.

## Slide 13: Frequency Profile Comparison
Notes: Comparison of frequency profile between May 2023 and May 2025. Similar to the previous slide, compared to 2023, there are less instances of frequency hovering around the dead bands.

## Slide 14: Time Error Correction

## Slide 15: ERCOT Daily Time Error
Notes: We did not make time error corrections in the month of June.

## Slide 16: Time Error Corrections Log Summary
There have been no time error corrections since December 2016

## Slide 17: BAL-003 Performance

## Slide 18: Op. Year 2024 BAL-003 Selected Events – Update
Notes: BAL-003

## Slide 19: Op. Year 2023 BAL-003 FRM Performance - Update
Notes: OP2018: FRO = -381.0, FRM_median = -843.17, FRM_average = -959.7
OP2019: FRO = -381.0, FRM_median = -811.14, FRM_average = -892.5
OP2020: FRO = -425.0, FRM median = -789.34, FRM average = -879.0
OP2021: FRO = -471.0, FRM median = -913.56, FRM average = -992.
OP2022: FRO = -412.0, FRM median = -1060.40, FRM average = -1153.4
OP2023: FRO = -463.0, FRM median = -1130.21, FRM average = -1302.7
OP2024: FRO = -395.0, FRM median = -1127.76, FRM average = -1264.3
OP2025: FRO = -455.0,

## Slide 20: ERCOT Energy Statistics

## Slide 21: Total Energy
Notes: 45,650,658 MWh – Increase in total energy compared to last month

## Slide 22: Total Energy from Wind Generation
Notes:   10,604,250 MWH – Increase in total energy from wind compared to last month

## Slide 23: % Energy from Wind Generation
Notes: 23.23% of total energy was provided by wind generation

## Slide 24: Total Energy From Solar Generation
Notes: 6,948,383 MWh – Increase in total energy from Solar

## Slide 25: % Energy from Solar Generation
Notes: 15.22% of total energy was provided by solar generation

## Slide 26: ERCOT System Inertia

## Slide 27: Daily Minimum System Inertia
Notes: Minimum Inertia in June 2025 = 209,684 MW*s on June 17th
Historical Overall Minimum was 109,029 MW*s on 3/22/2021
May Data:
Mean: 266,883 MW*s
Max: 300,140 MW*s on June 30th
Min: 209,684 MW*s on June 17th

## Slide 28: ERCOT Inertia 2015-2025
Date and Time | 2015 11/25 2:00 AM | 2016 4/10 2:00 AM | 2017 10/27 4:00 AM | 2018 11/03 3:30 AM | 2019 3/27 1:00 AM | 2020 05/01 2:00 AM | 2021 03/22 00:00 AM | 2022 03/21 01:00 AM | 2023 04/18 02:00 AM | 2024 03/29 03:00 AM | 2024 03/29 03:00 AM | 2025 03/18 12:00 AM
Min synch. Inertia (GW*s) | 152 | 143 | 130 | 128.8 | 134.5 | 131.1 | 109 | 115 | 124 | 130 | 130 | 118.3
System load at minimum synch. Inertia (MW) | 27,190 | 27,831 | 28,425 | 28,397 | 29,883 | 30,679 | 32,599 | 33,365 | 35,799 | 37,297 | 37,297 | 48,973
Non-synch. Gen. in % of System Load | 42 | 47 | 54 | 53 | 50 | 57 | 65 | 66 | 61 | 68 | 68 | 74
Notes: Summary of ERCOT inertia for the previous 10 years. Lowest inertia this year was on March 18th.
For each box, the central mark (red line) is the median, the edges of the box (in blue) are the 25th and 75th percentiles, the whiskers correspond to +/- 2.7 sigma (i.e., represent 99.3% coverage, assuming the data are normally distributed. The corresponding lowest inertia in each year is given in the table.
The circle on each boxplot is showing inertia during time when highest portion of load was served by wind/solar generation in that year.

## Slide 29: Questions?
Thank you!