## Slide 1: Large Load Working Group Update
Bob Wittmeyer
Chair LLWG
bob@longhornpwr.com
512 762 8895

## Slide 2: June Workshop & July LLWG Meeting
The June workshop focused on problem statement related to large electronic loads (LEL) riding through momentary low voltage events
July meeting focused on possible solutions for LEL with UPS systems
  AI Data Centers and Hyperscalers typically have UPS system to protect the load from loss of system power.
    These systems have historically been designed to protect the Load from loss of Grid power.
    ERCOT needs these system to now protect the grid from loss of load when there is a momentary voltage loss.
  Crypto Data Centers typically do NOT have a UPS

## Slide 3: Disclaimer
ERCOT has proposed Voltage Ride Through Requirements intended to initiate discussions with LEL owners/operators and Original Equipment Manufacturers and help define what ERCOT considers acceptable ride-through of LELs.
ERCOT is not requiring existing Large Loads to meet proposed voltage ride-through requirements to remain operational or receive Approval to Energize.
  Final requirements will be used to determine if LELs can ride-through common system disturbances and if they will be included in mitigation plans to maintain potential System Operating Limits for grid reliability.
Future LELs will need to meet voltage ride-through requirements.

## Slide 4: Draft - Proposed LEL Voltage Ride-Through
Fault ride through (9 cycles, 0.15 sec, similar to IBRs)
Reduced voltage ride through (e.g. delayed clearing events)
Sustained power breakpoint (some electronic loads can do 0.7 pu or lower, but might hinder grid voltage recovery)
Percent of Nominal Voltage at POI
1
2
3

## Slide 5: LL LVRT RTO Comparison

## Slide 6: Next Steps
Developing process flow for Large Load Interconnections
Next Meeting – Aug 14 – Webex and in person
  Seeking additional solutions to VRT issues
Stakeholder list of FAQ
  Posted under Key Documents of LLWG page
  Please review – if you have additional questions, please email bob@longhornpwr.com and Patrick.Gravois@ercot.com