## Slide 1
Proposed 2026 Ancillary Service Methodology
Luis Hinojosa
Ancillary Services & Operations Analytics
WMS
August 06, 2025

## Slide 2: Introduction
ERCOT has reviewed the methodology to determine minimum Ancillary Service (AS) requirements.
ERCOT is proposing the following changes for 2026.
  Change to a probabilistic methodology to compute ERCOT Contingency Reserve Service (ECRS) and Non-Spinning Reserve Service (Non-Spin) requirements.
  Change methodology for Regulation Service to remove the FRRS component as it will retire with the implementation of RTC.
ERCOT is not proposing any changes in the methodologies used to compute Responsive Reserve Service.
  NERC’s preliminary BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2026 assessment for ERCOT shows a change in ERCOT’s IFRO. In order to align with ERCOT’s new IFRO, the minimum RRS-PFR limit for 2026 will change to 1,377 MW.
A redline document of the AS Methodology document will be available prior to the TAC meeting.
The following slides share the preliminary quantities for each AS based on the proposed methodologies.
  As requested by Market Participants we have included values for all quantities for 2026, but please note that 2025 data has not been included yet for months after July and will change once that data is included.
2026 Methodology Review Timeline
April 23, 2025 – TAC Kickoff
May 19, 2025 – Workshop #1
June 20, 2025 – PDCWG
June 30, 2025 – Workshop #2
July 07, 2025 – WMWG (Proposed)
July 15, 2025 – OWG (Proposed)
July 22, 2025 – PDCWG (Proposed)
August 04, 2025 – Workshop #3
August 06, 2025 – WMS
August 07, 2025 – ROS
August 28, 2025 – TAC
September 23, 2025 – BoD
Oct, Nov, Dec 2025 – PUC

## Slide 3: Hourly Average Regulation Comparison
Reg-Up 2026:
On avg. 80 MW increase from prev. year
Largest increase is in Jun by 124 MW
Reg-Down 2026:
On avg. 39 MW increase from prev. year
Largest increase is in May by 70 MW

## Slide 4: Hourly Average RRS Comparison
2026 RRS:
On avg. 15 MW decrease from prev. year
Largest increase is in Jun by 80 MW
Largest decrease is in Jan by 203 MW

## Slide 5: Summary of PUC’s Findings Related To AS Methodology
Topic | Finding | Next Steps
PROVIDING ADEQUATE INCENTIVES FOR DISPATCHABLE GENERATION | The reliability standard rule (16 TAC § 25.508) has defined a process for assessing and ensuring resource adequacy. | The first holistic reliability standard assessment in 2026 will include an assessment of whether incentives are adequate to support a sustainable level of dispatchable generation, and ERCOT should incorporate the impact of new market features such as Texas Energy Fund, DRRS, and real-time co-optimization plus batteries (RTC+B) into this assessment.
APPROPRIATE CRITERION FOR AS PROCUREMENT QUANTITIES | ERCOT's current posture of maintaining AS quantities that minimize the chance of Entering the pre-emergency operational condition of an Operational Watch should be maintained in order to balance system improvements made since Winter Storm Uri until additional data is available to support further Commission evaluation of this operating posture. | ERCOT should develop the capability to provide current estimates of costs and probabilities of experiencing a Watch, Emergency Alert, and Load Shed for several potential alternative target reserve levels as soon as practicable and no later than to support the Commission setting an objective, data-based procurement criteria for the 2027 AS Methodology.
PROBABALISTIC MODELING TO DETERMINE AS QUANTITIES | ERCOT's current practice to determine AS quantities relies on a statistical analysis using historical operating conditions and outcomes. This methodology is no longer sufficient as myriad changes to the wholesale markets and operating conditions continue to impact reasonable forecasting needs. Changes such as incorporation of an unknown amount of TEF-supported capacity, how new large loads are integrated into grid operations, or the impact of new market designs present uncertainty for forecasting tools based exclusively on historical data. | ERCOT should develop a suitable probabilistic, forward-looking modeling capability, provide regular updates to TAC, and present options that can be incorporated no later than the 2027 AS Methodology.
DYNAMIC DETERMINATION OF AS QUANTITIES | Tradeoffs exist between the certainty provided to market participants by calculating AS quantities primarily on an annual basis (as is done currently) and the efficiency of calculating some portion of AS quantities closer to the operating day. | ERCOT should work with stakeholders to explore a dynamic AS methodology that best Balances these trade-offs.
PUCT's 2024 Ancillary Services Study

## Slide 6: Probabilistic Methodology Approach for ECRS and NSRS
+Convergence Criteria = 𝐸𝐶𝑅𝑆+𝑁𝑆𝑅𝑆<𝑁𝑒𝑡𝑅𝑖𝑠𝑘+𝑀𝑎𝑥(𝑅𝑒𝑔+𝑅𝑅𝑆,ZZ) with probability of 1 in XX year.

## Slide 7: Risk and Risk Credits Details
Risk
  Net Load Forecast Error (NLFE) (2022-2025)
    X hour ahead
    30 min ahead
    Account for Solar Capacity Growth
  Forced Outages (2022-2025)
    Rolling X hour ahead forced outage of conventional resources
Risk Credits
  Online Headroom Capacity that is Sustainable for 4 hours
    Conventional unit headroom that is available to SCED, but excluding Ancillary Service Capacity is included (2022-2025)
    System Hourly ESR Capability is calculated using historical Real-Time telemetered hourly average ESR data is included (SOC, MNOS, AS Responsibility). (2023-2025)
    Reliability Unit Commitment (RUC) Capacity is excluded
  Offline Capacity (2022-2025)
    Conventional unit capacity that can be started within 30 minutes excluding any capacity reserved for Ancillary Services
Net Risk = Risk – Risk Credit*Y where the variable is configurable
Notes: Data excludes Weather Events such as Elliot, Beryl, and URI

## Slide 8: Probabilistic Methodology Input & Criteria Recommendations
ERCOT Recommends the following Parameters:
  Risk: X = 6 Hour ahead NLFE and 6 hour ahead rolling forced outage of conventional resources.*
  Risk Credit: Y = 60% for each risk credit from historic availability in night hours (HE23-HE5) and Y = 25% in day hours (HE6-HE22) as capacity that is available to cover the risk for which these products are designed.
  Convergence Criteria: ZZ = Max(Reg+RRS, 3000) indicating the ECRS and Non-Spin quantities will be setup such that there is a 1 in XX=10 year probability of operational reserves dropping below 3,000 MW (Emergency Condition) due to uncertainty in load and resource and should be sufficient to restore procured regulation and responsive reserves.
Additional details provided on the following slides.
*the method is also aware and analyzing the 30 min ahead NLFE

## Slide 9: Distribution of Startup Hours of RUCs Jan 1, 2018, through Jun 28, 2025
Between 2018-2025, based on the data analyzed,
  As can be expected most RUCs are to solve issues during seasonal peak hours.
  9% of RUCs (for capacity) had a startup time of 2 hours or less
  45% of RUCs (for capacity) had a startup time of 4.95 hours or less
  53% of RUCs (for capacity) had a startup time greater than 4.95 hours
  51% of RUCs (for capacity) during low PRC days had a startup time greater than 4.95 hours.
  *The following approach was used to identify low PRC days
    Between Jan 1, 2018, and Oct 13, 2021, Operating Days with minimum PRC value below 3,500 MW.
    Beginning Oct 14, 2021, Operating Days with minimum PRC value below 5,000 MW.
The startup times of Reliability Unit Commitments (RUCs) between Jan 1, 2018, and Jun 28, 2025, were analyzed.
RUC Extensions and RUCs for Congestion were excluded.
Key Takeaway: At least 50% of units RUC’ed to solve capacity issues have a startup time of 4.95 hours or more. Further the RUC process also typically takes another 20-30 minutes to complete. Based on this, 6-hour lead time is recommended to be used in the analysis of net load forecast risk for Non-Spin.

## Slide 10: Capacity Trends by Season: Offline and Online
With implementation of RTC, ERCOT accepts that the magnitude of headroom available may change compared to history. ERCOT expects there will be consistent amounts of offline and online capacity available through night hours compared to daytime hours. As a result, we recommend taking a higher credit for around 60% for night hours and a moderate credit of around 25% for day hours.
*shaded area identifying night hours

## Slide 11: Impacts of differing Risk Credits on ECRS+NSRS

## Slide 12: 1 in (10 Vs 5 VS 1) - Impact to the ECRS+NSRS Quantities
We ran additional probability sensitivities while maintaining avoiding Watch threshold and identified that 1 in 10 Years will produce the highest reserve quantity but there is not a large change overall amongst the sensitivities.

## Slide 13: Watch vs EEA1 or EEA3 Impact to the ECRS+NSRS Quantities
When looking at additional sensitivities around the Threshold (Watch, EE1, or EEA3) on convergence criteria we see there is negligible difference in the ECRS+NSRS requirements for the 7 months that are calculated.

## Slide 14: ERCOT Recommendations for Parameters in Probabilistic Framework
Parameter | Value | Reason
Risk: X | 6 Hours 30 Minutes | At least 50% of units RUC’ed to solve capacity issues have a startup time of 4.95 hours or more. Further the RUC process also typically takes another 20-30 minutes to complete. Hence 6-hour lead time is recommended to be used in the analysis of net load forecast risk for Non-Spin. 30 minute ahead for ECRS as the next unit that can start is 30 mins away in NSRS.
Risk Credit: Y | 60% in night hours (HE23-HE5) 25% in day hours (HE6-HE22) | ERCOT agrees that historical available (online + offline) headroom capacity may not materialize in future and is not comfortable on relying heavily historical behavior in this analysis. That said, ERCOT expects the trend of having higher headroom capacity during night hours will continue. Due to this the net risk for ECRS and Non-Spin in night hours is expected to be lower than day hours. As a result, ERCOT recommends taking a higher credit for around 60% for night hours and a moderate credit of around 25% for day hours.
Convergence Criteria: ZZ, XX | Max(Reg+RRS,3000) 1in 10 | There is minimal difference in outcomes when XX = 1, 5 or 10. 3,000 MW (“Watch”) is appropriate to operate the system more conservatively.

## Slide 15: Hourly Average ECRS Comparison

## Slide 16: Hourly Average NSRS Comparison

## Slide 17: Summary
Below is a summary of the proposed changes to the methodology used for computing minimum AS quantities for 2026,
ERCOT is proposing the following changes:
  Change to a probabilistic methodology to compute ERCOT Contingency Reserve Service (ECRS) and Non-Spinning Reserve Service (Non-Spin) requirements.
  Change methodology for Regulation Service to remove the FRRS component as it will retire with the implementation of RTC.
ERCOT is not proposing any changes in the methodology used to compute Responsive Reserve Service.
A Spreadsheet that contains the preliminary quantities from Jan to Dec 2026 have been posted to the meeting page. Please note months after July do not include 2025 data yet and will change as that data is included.
A redline document of the AS Methodology document will be available prior to the TAC meeting.
ERCOT is seeking endorsement on ERCOT’s proposed methodology for computing minimum AS quantities for 2026.

## Slide 18: Questions
?

## Slide 19: Appendix

## Slide 20: Overall impact of probabilistic method
Probabilistic Methodology allows for the ability to tailor quantities to highest risk times while achieving similar average quantities.

## Slide 21: Cost Analysis of AS Requirements
Using Historical Market Clearing Price for Capacity (MCPC) we can see impacts of sensitivities in Risk Credits and Threshold based on 7 months of quantities calculated.
Case: Watch for 1 in 10 Years | ECRS Total Cost | NSRS Total Cost
A - 100% Credit | $737,801 | $1,458,435
B - ERCOT Recommended | $869,367 | $1,957,046
C - 0% Credit | $939,276 | $2,257,735
Case: EEA1 for 1 in 10 Years | ECRS Total Cost | NSRS Total Cost
B - ERCOT Recommended | $862,249 | $1,939,558
Delta - Watch to Load Shed | -$7,118 | -$17,488
Case: Load Shed for 1 in 10 Years | ECRS Total Cost | NSRS Total Cost
B - ERCOT Recommended | $862,249 | $1,939,558
Delta - Watch to Load Shed | -$7,118 | -$17,488

## Slide 22: Managing Uncertainty
On days when there is a sustained under-forecast in net load and there is some available capacity (assess these are not scarcity days) the typical approach used is,
The 10-minute reserve ECRS, is relied upon first to respond to the additional energy need created by the under-forecast in net load.
The 30-minute reserve Non-Spin, is relied upon next to relieve/restore the deployed ECRS.
The deployed Non-Spin is relied upon till offline unit(s) can turn on to relieve/restore the deployed AS.
As a result of the above when considering duration needs, it is important to assess
The historical uncertainty in consistently under-forecasting net load
  in 30 minute Ahead timeframe.
  in post RUC timeframe
Duration of historic ECRS and offline Non-Spin deployment events
Setup: Consider operating on a day with moderate forecasted load during shoulder months with a portion of the generation fleet on outage. A fast-moving weather front causes a large net-load under-forecast error (ex. load picks up significantly, wind drops). Then a large thermal unit gets forced out.
Use Non-Spin till offline unit turns on and supplements the capacity needs
Use ECRS till Non-Spin supplements the deployed ECRS capacity.

## Slide 23: Why 6 Hour is still appropriate for NSRS based on RUCs