## Slide 1
Weekly
RTC+B Market Trials Update
ERCOT Staff
August 18, 2025

## Slide 2: Outline
Antitrust Admonition
Reminder of Key Document Postings
Expectations of QSEs for the Week
Scorecards for in-flight Activities
RTC Market Trials outcomes
Communicate any known Issues within On-going Trial
Support any Technical and/or Business Questions
Appendix- Supporting Materials:
  New RTC Pricing reports location
  NPRR1290 market submission validation change
  Links to Handbooks
  Prior Scorecards
  FAQ Updated 8/8/2025
  Connectivity and Configuration (digital certs)

## Slide 3
WebEx Meeting reminders (same as other ERCOT forums):
Please keep line muted
If you have a question, please use the chat feature to either:
  Type in your question, or
  Type in “Question” and wait to be recognized to state question

## Slide 4
Sequence and Dates for Market Trials to Go-Live
#1 RTC QSE Submission Testing
(Submit COP, RT AS Offers,
DAM Virtual AS, Outages for ESRs)
#3 Open-loop RTC SCED
(QSE offers, SCED non-binding award/dispatch)
#5 Ongoing Open-Loop
& Periodic Closed-loop SCED/LFC
(QSE RTC offers and telemetry to support closed-loop frequency control test 2-3 tests of 2-4 hour durations)
#2 RTC QSE Telemetry Checkout (QSEs add/verify new telemetry points for UDSP, New ramp rates, ESR telemetry)
#6 Day-Ahead Market
(Non-binding DAM using QSE offers for at least 2 tests)
Transition to Go-Live
Upon completion of testing, confirmation of ERCOT and market readiness for Go-Live.
May 2025
June 2025
July 2025
Aug 2025
Sep 2025
Oct 2025
Nov 2025
Dec 2025
#4 QSE Telemetry Tests
(Individual QSE to follow UDSP and support new ramp rate and ESR telemetry)
QSE Scorecards & Exit Criteria for each Trial Phase
Start
5/5/25
Start
7/7/25
30-day Market Notice
11/5/25
Start
9/2/25
Go-Live
12/5/25*
* Go-Live date reflects 12/5/2025 as first Operating Day
where 12/4/2025 is planned software migration.
March/April
2025
QSE/Vendor Submission Sandbox and Telemetry Points added Prod EMS model.
Market trials are a progression of activities to mitigate the risk for Go-Live on new systems and processes for both the Market Participants & ERCOT.

## Slide 5: Resources for July/Aug Market Trials
Everything needed for current market trials is on RTCBTF home page
Note- TAC Approved the Market Trials Plan in October 2024
May/June complete
July/Aug in flight

## Slide 6
HB#3: QSE will support “parallel production” 2days/week by entering $bids/offers for non-binding RTC energy and A/S awards and dispatch (Open-loop test)
Scorecard to demonstrate successful submissions and telemetry reflective of production, and mitigation plans in place for any outliers.
HB#4: Coordination of individual QSE tests on subset of resources to ensure resources can follow new UDSP telemetry point from ERCOT.
Scorecard goal for QSEs to successfully demonstrate, and mitigation plans in place to address in next trial phase.
July & August:
Initial Real-Time Market execution and verify QSE ability to follow ERCOT frequency signals during individual QSE test

## Slide 7: July/August Market Trials Summary
Handbook #3 - Dual “production-like” data Tue/Thu 9am-5pm
  Market Trials ERCOT/QSE support required for:
    Submissions (TPO/COP/ASOffer etc.) – No outage submissions required
    Telemetry (current and new telemetry points)
    To assist RUC studies, please submit COP, 3PSO, ASOffer through end of OD (midnight)
    Systems will be running 7x24, so submissions encouraged but not required on all days.
Scoring for QSE submissions & telemetry as 2 scorecards for Handbook #3
  All QSEs for all Resources on Monitored Operating Days July 22– Aug 28 every Tue/Thu 9-5
  Green is > 95%
  Yellow is 85% - 95%
  Red is < 85%
  Also an “ERCOT-wide score”
12 OpDays scored in 3a
for market submissions
12 OpDays scored in 3b
for accurate telemetry

## Slide 8: July/August Market Trials Summary
Handbook #4 - Coordinated Individual QSE Tests to follow UDSP
  ERCOT will schedule meetings with QSEs
    Meeting and test not required for “NCLR-only” QSEs
  Please contact ERCOT if you are ready to test in the trials window
  Single successful test for QSE to complete.
    Green is successfully tested
    Yellow is scheduled but not complete
    Red is not scheduled for test
  Also tracking an “ERCOT-wide score” to achieve 98% testing completed by end of August

## Slide 9: Scorecard 3A for Handbook 3- Market submissions:
Scores for QSEs with Resources – Appropriate submissions made for each owned resources.
COP – ALL
TPO – Gen, ESR, CLR
ASO – AS Qualified Resources
Last 3 weeks have progressed
System Wide from
Week 1- 65%
Week 2- 74%
Week 3- 85%
Last Week- 95%
Scoring:

## Slide 10: Scorecard 3B for Handbook 3- Acceptable Telemetry point values received by ERCOT for active resources.
8/18 Scores for QSE with Resources – Accurate telemetry data sent to ERCOT
Scoring:

## Slide 11: Scorecard 3B for Handbook 3 Acceptable Telemetry Point values received by ERCOT for active resources.
Key points for Telemetry scorecard check
  Device types checked - Units, CLRs, NCLRs, ESRs for each QSE
  RTCB Telemetry status should be “Good” quality
  RTCB Units / CLRs / NCLRs Telemetry values should be within “Expected Range” or an expected value. Details are provided in next few slides.
  Expected values are derived from equivalent analogs in current production, based on defined criteria.
  RTCB ESR telemetry values are checked against corresponding combo model Battery Unit / CLR counterparts in production.
Scoring:

## Slide 12: RTC+B Telemetry points validation

## Slide 13: Scorecard 4 for Handbook 4- QSEs demonstrate ability to follow UDSP in coordinated test with ERCOT
8/18 UDSP following tests
All QSEs Scheduled!
Scoring:

## Slide 14: Summary of SCED functionality
What is RTC SCED using to solve in trials?
  Production Network model from NMMS
  QSE submitted offers (energy and A/S)
  QSE production telemetry
    ERCOT performs some overrides for stale data from QSE sites- improving each week
  Outages in prod telemetry would be outage in RTC SCED
  July 31 improvements:
    NPRR1268/1269 ASDC and Proxies logic implemented
    AS Plan improved and now same as Prod
  Aug 4 improvements:
    IRR Forecast synchronization has been manual, but now automated
  Upcoming: Aug 18 improvements (today):
    Active constraints flag being manually copied (automation planned for Aug 18)
    Load Forecasts being fed into RTC, but ERCOT manually aligns which forecast is being used based on operator selection in Prod (automation planned for Aug 18)

## Slide 15: Market Trials OD Summary 08-12-2025 (9am – 5pm)

## Slide 16: System Lambda (plus Adders)

## Slide 17: Ancillary Service Prices

## Slide 18: AS Awards* Summary by Resource Type
* Pre-RTC (RTM AS Schedule)

## Slide 19: AS Awards* Summary by Resource Type

## Slide 20: SPP by Hub and Competitive Load Zone

## Slide 21: Ancillary Service Demand Curves

## Slide 22: Market Trials OD Summary 08-14-2025 (9am – 5pm)

## Slide 23: System Lambda (plus Adders)

## Slide 24: Ancillary Service Prices

## Slide 25: AS Awards* by Resource Type
* Pre-RTC (RTM AS Schedule)

## Slide 26: AS Awards* by Resource Type
* Pre-RTC (RTM AS Schedule)

## Slide 27: SPP by Hub and Competitive Load Zone

## Slide 28: Ancillary Service Demand Curves

## Slide 29: Market Trials known issues/updates
Current issues/updates:
  Issues:
    COP submission rejects/incorrect validation error when ECRS capability is equal than HSL – LSL (planned fix Aug 27)
  Automation:
    Active constraints flag being manually copied (automation today/Aug 18)
    Load Forecasts being fed into RTC, but ERCOT manually aligns which forecast is based on operator selection in Prod (automation today/Aug 18)
  September/October Reports are now being posted, but data is not yet accurate:
    Example: RTD Indicative Awards and Price Adders reports postings
Optional- Day-Ahead submission for Monitored Op Day window
  Submissions will be closed from 10AM-11AM on the day prior to OD test windows.
  Day-ahead Submissions window (normally 7AM-10AM) for OD 8/20 will remain open on 8/19 until 6pm for those wanting to test their Day Ahead submissions validation. Not required.

## Slide 30: Market Trials Calendar
We are here….

## Slide 31: Wrap-Up and Questions
Friday emails:
Email to all AR, BAR, RTC+B AE-
  Highlight Sept that is less than 4 weeks away. On Thursday, September 11, 2025 ERCOT and QSE control rooms and operators plan to switchover to the RTC+B production systems for two hours between 10am-1pm.
Email to all AR, BAR, RTC+B AE as heads-up of ERCOT staff reaching out on telemetry issues (hope to resolve this week)
Remainder of meeting for questions
Can always email the RTC+B Program mailbox: RTCB@ercot.com
Tomorrow/Aug 19
RTCBTF 9:30-11:30am
LFC Workshop 1-3pm: Additional Closed-Loop LFC Workshop August
  Another joint RTCBTF/TWG workshop to walk-through September test

## Slide 32: APPENDIX- Supporting Materials
New RTC Pricing Reports location
NPRR1290 Validation Changes
Links to Handbooks
Prior Scorecards
FAQ Updated 8/8/2025
Connectivity and Configuration (digital certs)

## Slide 33: RTC+B New Reports Posted to the ERCOT Website
Links to the available RTC+B versions of Real-Time reports posted on Real-Time Market Information page.

## Slide 34: Submission validation update - PROD vs RTC+B
NPRR1290 :
  cleaned up protocol language around submitting offer curves and bid curves
  disallows having more than 2 price/quantity points in a flat/vertical segment of the curve.
Impacts to QSEs during dual-submission – some submissions accepted in Production will be rejected in Market Trials environment:
RTM Energy bids – protocol requiring “increasing quantities” now enforced.
  Reverted this change to validation. Further discussion highlighted protocol should be brought in line to long-standing practice, not validation.
  Example: Bid with Q1=0mw, Q2=10mw, Q3=10mw will be rejected as Q3 does not increase from Q2.
TPO & RTM Bid – more than 2 price/quantity pairs with same price or quantity will be rejected
Market Submission Validation
Rules document updated.

## Slide 35: Submission validation update - PROD vs RTC+B
TPO – EB/OC - EOC
RTM EB
RTM EB

## Slide 36: Market Trials Framework:
TAC Approved the Market Trials Plan in October 2024
Discussions with RTC+B Task Force have shaped the Handbooks
Handbook #1- QSE Submission Testing
Handbook #2- QSE Telemetry Tests
Handbook #3- Open Loop SCED
Handbook #4- QSE Telemetry Tests
Handbook #5- Close-Loop LFC Tests
Handbook #6- Day-Ahead Market Tests
All are posted on the
RTCBTF Homepage
under Market Trials banner

## Slide 37: Market Trials Technical Details
Detailed discussions with TWG have provided technical content details
Digital Certificate details
Connectivity/URL details to User Interfaces and APIs
Reminder of how to submit new ICCP requests
RTC and Production Telemetry connectivity
Network Model Load Schedule
All are posted on the
RTCBTF Homepage
under Technical Details banner

## Slide 38: Scorecard 1 for Handbook 1- Market submissions:
7/3 Scores for QSEs with Resources – successful submissions for resource types specified in Handbook 1
Scoring: Complete
Complete

## Slide 39: Scorecard 2A for Handbook 2- 100% of ICCP Telemetry points added by QSE:
7/21 Scores for QSE with Resources - ICCP Telemetry points added in current model.
99.5% of 26k points complete
Last points are identified and are being worked on.
Scoring:

## Slide 40: Scorecard 2B for Handbook 2- Telemetry checkout meetings completed with ERCOT staff for sample of live data transfer capability
7/3 Scores for QSEs with Resources – Scheduling Check-out and Check-out complete
Scoring: Complete
Complete

## Slide 41: Reminder of RTC+B FAQ (updated 7/28/2025)
Worksheets for categories
Posted on RTCBTF Home Page under Key Documents
Common questions/responses in Excel Workbook (target weekly updates)
Search workbook for Key Words

## Slide 42
RTC+B Market Submissions - Systems configurations
RTC QSE
Submission Testing
Open-loop
RTC SCED
Ongoing Open-Loop
& Periodic Closed-loop SCED/LFC
May 2025
June 2025
July 2025
Aug 2025
Sep 2025
Oct 2025
Nov 2025
Dec 2025
Start
03/2025
Start
05/2025
Start
09/2025
Go-Live
12/5/25*
Apr 2025
Mar 2025
Feb 2025
Optional: RTC QSE/Vendor Developer
Submission Testing
Start
07/2025
Certificate: Current MOTE
Env: ERCOT RTC Market Trial
URL: RTC MIS MOTE URL
Certificate: Current Production
Env: ERCOT RTC Market Trial
URL: RTC MIS Market Trial
Cert: Production
Env: Prod
URL: MIS Prod
QSE/Vendor developer can use MOTE certificates & RTC MIS MOTE API URL to test the submissions until end of submission testing phase (end of June) as needed. At the start of the Open Loop testing, RTC MOTE MIS URLs will be disabled.
URL links: RTC MOTE and Market Trial URL links to be used for MMSUI, OSUI and API submissions. Actual links are provided in next slide.
For notifications/responses to MPs from RTC Market Trials environment, MP will need to provide the listener URL to ERCOT

## Slide 43: RTC+B Market Submissions - Systems configurations (Updated with URLs)
RTC+B Market Trials and Go-live
RTC Phase | Digital Certificate | MMSUI / OSUI URL | API / WAN URL
Vendor/QSE Submissions Testing | Current MOTE | RTC MOTE MIS URLs https://testmarkettrials.ercot.com/mmsui/mmsui/displayTradesLanding.action https://testmarkettrials.ercot.com/osrui/osrui/Summary.action | RTC MOTE API/WAN URL https://testmarkettrialsapi.ercot.com/NodalAPI/EWS/ https://testmarkettrialsapi.wan.ercot.com/NodalAPI/EWS/
Open Loop and Closed Loop Testing | Current Production | RTC Market Trial URL https://markettrials.ercot.com/mmsui/mmsui/displayTradesLanding.action https://markettrials.ercot.com/osrui/osrui/Summary.action | RTC Market Trial API/WAN URL https://markettrialsapi.ercot.com/NodalAPI/EWS/ https://markettrialsapi.wan.ercot.com/NodalAPI/EWS/
From RTC Go-live onwards | Current Production | Current Prod MIS URL mis.ercot.com/mmsui mis.ercot.com/osui | New Production API/WAN URL

## Slide 44: RTC+B Market Submissions - Systems configurations Public Key Update for WAN/API submissions
For API/WAN submissions into Market Trials environments, need to download public keys and place into the keystore location in system being used for RTC+B submissions.
No change to digital user certificates – continue to use existing MOTE and Production Certificates
Market Trial API Public key location: https://www.ercot.com/services/mdt/webservices