## Slide 1
Proposed 2026 Ancillary Service Methodology and Preliminary Quantities
TAC
August 27, 2025
Luis Hinojosa
Manager, Ancillary Services & Operations Analytics
ERCOT

## Slide 2: Background
ERCOT has been actively reviewing the methodology to determine minimum Ancillary Service (AS) requirements for 2026 (2026 AS Methodology). As a part of this review, ERCOT has incorporated two recommendations related to the AS Methodology from PUC’s 2024 Ancillary Services Study.
Topic | Finding | Next Steps
PROVIDING ADEQUATE INCENTIVES FOR DISPATCHABLE GENERATION | The reliability standard rule (16 TAC § 25.508) has defined a process for assessing and ensuring resource adequacy. | The first holistic reliability standard assessment in 2026 will include an assessment of whether incentives are adequate to support a sustainable level of dispatchable generation, and ERCOT should incorporate the impact of new market features such as Texas Energy Fund, DRRS, and real-time co-optimization plus batteries (RTC+B) into this assessment.
APPROPRIATE CRITERION FOR AS PROCUREMENT QUANTITIES | ERCOT's current posture of maintaining AS quantities that minimize the chance of Entering the pre-emergency operational condition of an Operational Watch should be maintained in order to balance system improvements made since Winter Storm Uri until additional data is available to support further Commission evaluation of this operating posture. | ERCOT should develop the capability to provide current estimates of costs and probabilities of experiencing a Watch, Emergency Alert, and Load Shed for several potential alternative target reserve levels as soon as practicable and no later than to support the Commission setting an objective, data-based procurement criteria for the 2027 AS Methodology.
PROBABALISTIC MODELING TO DETERMINE AS QUANTITIES | ERCOT's current practice to determine AS quantities relies on a statistical analysis using historical operating conditions and outcomes. This methodology is no longer sufficient as myriad changes to the wholesale markets and operating conditions continue to impact reasonable forecasting needs. Changes such as incorporation of an unknown amount of TEF-supported capacity, how new large loads are integrated into grid operations, or the impact of new market designs present uncertainty for forecasting tools based exclusively on historical data. | ERCOT should develop a suitable probabilistic, forward-looking modeling capability, provide regular updates to TAC, and present options that can be incorporated no later than the 2027 AS Methodology.
DYNAMIC DETERMINATION OF AS QUANTITIES | Tradeoffs exist between the certainty provided to market participants by calculating AS quantities primarily on an annual basis (as is done currently) and the efficiency of calculating some portion of AS quantities closer to the operating day. | ERCOT should work with stakeholders to explore a dynamic AS methodology that best Balances these trade-offs.
Included in 2026

## Slide 3: Introduction
Following is a summary of the proposed the 2026 AS Methodology
  Regulation Service (Reg Up, Reg Down): Continue using the methodology approved in December 2024 with one modification that removes feedback from Fast Responding Regulation Service (FRRS). FRRS will retire with the implementation of Real Time Co-optimization plus Batteries (RTC+B) project.
  Responsive Reserve Service (RRS): Continue using the methodology approved in December 2024. Update minimum RRS from Primary Frequency Response (PFR) to 1,377 MW to align with NERC’s BAL-003 Interconnection Frequency Response Obligation (IFRO) for Operating Year (OY) 2026.
  ERCOT Contingency Reserve Service (ECRS) and Non-Spinning Reserve Service (Non-Spin): Use a probabilistic model that uses last four years of 6 hours ahead risk (net load forecast error and cumulative forced outages of conventional resources) and 30 minute ahead net load forecast error to determine quantities such that there is a 1-in-10 year probability of operational reserves dropping below the sum of Reg Up plus RRS or Watch threshold, whichever is higher, due to uncertainty in net load forecast and conventional resource availability. A moderate amount of credit in the net risk derived using historic online headroom & offline capacity is also recommended.
Proposed Timeline
April 23, 2025 – TAC Kickoff
May 19, 2025 – Workshop #1
June 20, 2025 – PDCWG
June 30, 2025 – Workshop #2
July 07, 2025 – WMWG (Proposed)
July 15, 2025 – OWG (Proposed)
July 22, 2025 – PDCWG (Proposed)
August 04, 2025 – Workshop #3
August 06, 2025 – WMS
August 07, 2025 – ROS
August 27, 2025 – TAC
September 23, 2025 – BoD
Oct, Nov, Dec 2025 – PUC
A redline document for 2026 AS Methodology and preliminary quantities have been posted. Note that 2025 data has not been included yet for months after July.

## Slide 4: Proposed Probabilistic Framework for ECRS and Non-Spin
  ERCOT recommends using a probabilistic model to establish quantities of ECRS and Non-Spin in 2026. This model is designed to establish sufficient ECRS plus Non-Spin reserves quantities for non-scarcity days when sufficient capacity is available but may not otherwise be online or available in time to cover risks to react to uncertainties in load, wind, solar forecasts and availability of dispatchable resources.
Recommended Values: X = 6 Hours, Y = 60% for HE23 to HE5 and 25% HE6 to HE22, XX = 10 years ZZ = 3,000 MW
+Convergence Criteria = 𝐸𝐶𝑅𝑆+𝑁𝑆𝑅𝑆<𝑁𝑒𝑡𝑅𝑖𝑠𝑘+𝑀𝑎𝑥(𝑅𝑒𝑔+𝑅𝑅𝑆,ZZ) with probability of 1 in XX year.

## Slide 5: Benefit of probabilistic framework
Key Takeaway: Probabilistic approach allows for the ability to tailor quantities to highest risk times while achieving similar average quantities.

## Slide 6: Parameters in Probabilistic Framework – Issues
Issue | ERCOT’s Recommendation and Summary of Stakeholder Feedback | ERCOT’s Perspective
How far ahead to look at forecast error and forced outages of conventional resources? Parameter X (in hours) | 6 Hours (ERCOT) OR 3 Hours (IMM and Consumers) | ERCOT’s recommendation of 6 hours is informed by policy guidance from Summer 2021 to operate to a higher reliability threshold (i.e. operate the system more conservatively with limited RUCs) and is based on historic availability of offline resources during RUC timeframe. (See this slide in appendix for details). ERCOT believes that this parameter can be reduced upon implementation of Dispatchable Reliability Reserve Service (DRRS), which is expected to have a 2 hour start time. With DRRS, ERCOT expects DRRS quantities would be setup to cover the uncertainties Non-Spin won’t, hence the look ahead for Non-Spin can be reduced. Absent DRRS’ implementation, ERCOT cautions that reducing the outlook could result in reliance on RUCs to cover such risks. As noted in past, this approach would setup an operational policy that is counter to the guidance from policymakers and stakeholders. Implications of such a policy change should be carefully considered.

## Slide 7: Parameters in Probabilistic Framework – Issues, Contd.
Issue | ERCOT’s Recommendation and Summary of Stakeholder Feedback | ERCOT’s Perspective
What is the level of risk ERCOT should try to avoid by procuring AS to cover forecast error? Parameter ZZ (in MW) | 3,000 i.e. Watch (ERCOT) OR 1,500 i.e. Load Shed (IMM) | ERCOT has noticed minimal difference in outcomes between ZZ = 3,000, 2,500 and 1,500 MW since quantities for most hours are a function of the amount of Reg Up plus RRS that these reserves have to replace. (See this slide in appendix for details) ERCOT’s recommendation of using XX=10 and ZZ=3,000 is based on policymakers’ desire for ERCOT to operate to a higher reliability threshold and operate the system more conservatively. Lastly, ERCOT opposes eliminating replacement of Reg Up and RRS from the convergence criteria.
How much should we discount the AS quantities for a particular time period based on the “extra” headroom from resources that were historically committed by market in that time period? Parameter Y (in %) | 60% in Night and 25% in Day (ERCOT) OR 50% (Consumers) OR 100% (IMM*) | ERCOT agrees with the perspective that with RTC+B available (online + offline) headroom capacity may not materialize and is not comfortable on relying heavily on historical behavior. Post RTC+B, ERCOT expects the trend of having higher available (online + offline) headroom capacity during night hours to continue (See this slide in appendix for details). ERCOT is open to taking a moderate credit based on historical available (online + offline) headroom capacity as this aligns with approach the past AS Methodologies have taken and has recommended a higher credit of 60% for night hours and a lower credit of 25% for day hours.
*The IMM also recommends using a 1-hour duration for ESR headroom as opposed to 4-hour approved under NPRR1282.

## Slide 8: ECRS preliminary 2026 Quantities

## Slide 9: Non-Spin preliminary 2026 Quantities

## Slide 10: Cost Analysis of AS Requirements
Using historical ECRS and NSRS Market Clearing Price for Capacity (MCPC) by hour for the first 7 months of 2025 we can see impacts of sensitivities in Risk Credits and Threshold for the 7 months of quantities calculated.

## Slide 11: Regulation Quantities 2025 vs. preliminary 2026
Reg-Up 2026:
On avg. 80 MW increase from prev. year
Largest increase is in Jun by 124 MW
Reg-Down 2026:
On avg. 39 MW increase from prev. year
Largest increase is in May by 70 MW

## Slide 12: RRS Comparison 2025 vs. preliminary 2026
2026 RRS:
On avg. 15 MW decrease from prev. year
Largest increase is in Jun by 80 MW
Largest decrease is in Jan by 203 MW

## Slide 13: Summary
ERCOT notes again, focus of AS methodology is not scarcity days/hours. Its purpose is to ensure sufficient AS is procured on all other days/hours when sufficient capacity is available but may not otherwise be online or available in time to cover risks.
Below is a summary of the proposed changes to the methodology used for computing minimum AS quantities for 2026,
  One change in the methodology used to compute Regulation Service;
  No change in the methodology for RRS;
  Minimum RRS-PFR limit changes to 1,377 MW; and
  Use a probabilistic model to establish quantities of ECRS and Non-Spin, with X (in hours) = 6; Y = 60% for HE23 through HE5 and Y = 25% for HE6 through HE22; XX (in years) = 10 and ZZ (in MW) = 3,000
A redline document for 2026 AS Methodology and preliminary quantities have been posted. Note that 2025 data has not been included yet for months after July.
ERCOT is seeking stakeholder feedback and endorsement on the proposed methodology for computing minimum AS quantities for 2026.

## Slide 14
Appendix

## Slide 15: Managing Uncertainty
On days when there is a sustained under-forecast in net load and there is some offline available capacity (i.e. these are not scarcity days) the typical approach used is,
The 10-minute reserve ECRS, is relied upon first to respond to the additional energy need created by the under-forecast in net load.
The 30-minute reserve Non-Spin, is relied upon next to relieve/restore the deployed ECRS.
The deployed Non-Spin is relied upon till offline unit(s) can turn on to relieve/restore the deployed AS.
Setup: Consider operating on a day with moderate forecasted load during shoulder months with a portion of the generation fleet on outage. A fast-moving weather front causes a large net-load under-forecast error (ex. load picks up significantly, wind drops). Then a large thermal unit gets forced out.
Use Non-Spin till offline unit turns on and supplements the capacity needs
Use ECRS till Non-Spin supplements the deployed ECRS capacity.

## Slide 16: Distribution of Startup Hours of RUCs Jan 1, 2018, through Jun 28, 2025
Between 2018-2025, based on the data analyzed,
  As can be expected most RUCs are to solve issues during seasonal peak hours.
  9% of RUCs (for capacity) had a startup time of 2 hours or less
  45% of RUCs (for capacity) had a startup time of 4.95 hours or less
  53% of RUCs (for capacity) had a startup time greater than 4.95 hours
  51% of RUCs (for capacity) during low PRC days had a startup time greater than 4.95 hours.
  *The following approach was used to identify low PRC days
    Between Jan 1, 2018, and Oct 13, 2021, Operating Days with minimum PRC value below 3,500 MW.
    Beginning Oct 14, 2021, Operating Days with minimum PRC value below 5,000 MW.
The startup times of Reliability Unit Commitments (RUCs) between Jan 1, 2018, and Jun 28, 2025, were analyzed.
RUC Extensions and RUCs for Congestion were excluded.
Key Takeaway: At least 50% of units RUC’ed to solve capacity issues have a startup time of 4.95 hours or more. Further the RUC process also typically takes another 20-30 minutes to complete. Based on this, 6-hour lead time is recommended to be used in the analysis of net load forecast risk for Non-Spin.

## Slide 17: Available Headroom Capacity Trends: Offline and Online
Online Headroom Capacity that is Sustainable for 4 hours
  Conventional unit headroom that is available to SCED, but excluding Ancillary Service Capacity (2022-2025)
  System wide hourly ESR capability is calculated using historical Real-Time telemetered hourly average ESR data (like SOC, MNOS and AS responsibility). (2023-2025)
  Reliability Unit Commitment (RUC) Capacity is excluded
Offline Capacity (2022-2025)
  Conventional unit capacity that can be started within 30 minutes excluding any capacity reserved for AS
*shaded area identifying night hours

## Slide 18: Impact of changing Probability to the ECRS+NSRS Quantities
ERCOT tested a variety of probability sensitivities (1-in-10, 1-in-5 and 1-in1) while maintaining avoiding Watch threshold and noted that there is not a large change overall amongst the sensitivities.

## Slide 19: Watch vs. EEA1 or EEA3 Impact on ECRS+NSRS Quantities
When looking at additional sensitivities around the Threshold (Watch, EEA1, or EEA3) on convergence criteria we see there is negligible difference in the ECRS+NSRS requirements for the 7 months that are calculated.