## Instructions
Instructions for PMU Data Entry Template:
1. Enter the exact Station Code and the exact names of your Unit(s) and MPT(s) as they appear in the ERCOT Network Operations Model. Make sure they are the exact spelling, in all CAPS, and no spaces.
2. Overwrite the MPT and UNIT labels with the exact names of your MPT(s) and Unit(s) as they appear in the ERCOT Network Operations Model. Make sure they are the exact spelling, in all CAPS, and no spaces.
3. It is best to provide MPT high side data for any resource configuration. However, it is preferred to also provide PMU data for individual units when there are mixed technologies behind a single MPT.
4. Provide the following data for each MPT and UNIT(if applicable):
- Voltage Magnitudes and Angles: Va, Vb, Vc and ∠Va, ∠Vb, ∠Vc (Volts, Degrees)
- Current Magnitudes and Angles: Ia, Ib, Ic and ∠Ia, ∠Ib, ∠Ic (Amps, Degrees)
- Real and Reactive Power: MW, MVAR (This is not a requirement but can be helpful in identifying possible incongruencies between the PMU and Telemetered MW/MVAR flows prior to submitting to ERCOT)
5. Only provide UTC timestamps under the UTC timestamp column
6. If you already have CPT time, you can simply paste it into the CPT column to overwrite the existing formula.
7. Leave all unused data fields blank (do not delete any columns or fields)
8. You may hide MPT sections or UNIT sections that are not used
9. Please do not include any extra data. Only include required data.
10. If you have more than 6 MPTs please use an additional copy of this PMU data template as the sections are limited to 6 MPTs
11. (Mixed Tech Tab) If you have more than four units behind an MPT with available low-side data, please use an additional copy of this PMU data template, as each template is limited to four units per MPT.

## Single Tech(High Side)
STATION CODE (EXACT): | XXXX_SUB | Instructions: In cell B1 put the exact Station Code that is in the ERCOT Network Operations Model. Make sure it is the exact spelling and in all CAPS and no spaces.
PMU Data Submission Guide and Template
Protocol/Operating Guide References | [5 empty] | IRR and IBR PMU Submission Process: | [10 empty] | Conventional and C.C. PMU Submission Process:
•NOG 6.1.4 •NOG 6.1.4.3 •NOG 6.1.3.2 Phasor Measurement Unit Reqs •NERC PRC 028 | [5 empty] | • Make sure all units are generating at least 5-10 MW and MVARs • Submit at least 5 minutes of PMU data recorded with a GPS based clock, or ercot approved alternative • Submit a minimum output recording rate of 60 samples per second (each sample including the timestamp should be distinct). • Ensure all data is fluid, not stale. • The frequency and voltage (if expressed in kV) should have at least 4 decimal places of precision • Provide 3 (a-b-c) voltage magnitude signals and 3 (a-b-c) voltage phase angle signals • Provide 3 (a-b-c) current magnitude signals and 3 (a-b-c) current phase angle signals • Provide Frequency (Hz). Should be in the vicinity of 60 Hz • Provide Rate of Change of Frequency (ROCOF) signal • Phase angles should have approximately 120 degree angle difference between each phase depending on balance of phase. For a phase angle of θ in phase A, the angles for the remaining two phases should be approximately θ - 120˚ and θ + 120˚. • The phase angle measurements will typically swing between -180˚ and +180˚ (this is a reflection of varying system frequency) • If an MPT has units of different technologies (mixed-tech), it is preferred to provide lowside data for each unit and highside MPT data. This is to provide clarity in fault/event and VRT analysis. • Please compare the calculated MW and MVAR flows with the telemetered MW and MVAR flows before submitting. | [10 empty] | • Make sure all units are generating at least 5-10 MW and MVARs • Submit at least 5 minutes of PMU data recorded with a GPS based clock, or ercot approved alternative • Submit a minimum output recording rate of 30 samples per second (each sample including the timestamp should be distinct). • Ensure all data is fluid, not stale. • The frequency and voltage (if expressed in kV) should have at least 4 decimal places of precision • Provide 3 (a-b-c) voltage magnitude signals and 3 (a-b-c) voltage phase angle signals • Provide 3 (a-b-c) current magnitude signals and 3 (a-b-c) current phase angle signals • Provide Frequency (Hz). Should be in the vicinity of 60 Hz • Provide Rate of Change of Frequency (ROCOF) signal • Phase angles should have approximately 120 degree angle difference between each phase depending on balance of phase. For a phase angle of θ in phase A, the angles for the remaining two phases should be approximately θ - 120˚ and θ + 120˚. • The phase angle measurements will typically swing between -180˚ and +180˚ (this is a reflection of varying system frequency) • If an MPT has units of different technologies (mixed-tech), it is preferred to provide lowside data for each unit and highside MPT data. This is to provide clarity in fault/event and VRT analysis. • Please compare the calculated MW and MVAR flows with the telemetered MW and MVAR flows before submitting.
Timestamp(mm-dd-yyyy hh:mm:ss.000) |  | MPT-01 (Highside)**Replace with exact MPT name as seen on the production model in all CAPS** | [15 empty] | MPT-02 (Highside) | [17 empty] | MPT-03 (Highside) | [13 empty] | MPT-04 (Highside) | [17 empty] | MPT-05 (High) | [15 empty] | MPT-06 (High)
UTC | CPT (auto-converted) | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR
2025-08-21 11:54 | 2025-08-21 06:54 | 60.0152 | 0.02089 | 202517.5 | 9.0218 | 202864.6 | -110.95 | 203026.7 | 128.9575 | 413.9817 | -8.232 | 413.9793 | -8.4188 | 415.0392 | -127.9514 | 240.5518 | 74.6556
Note on B7: If you already have CPT time, you can simply paste it into this column to overwrite the existing formula.
Note on A8: The data in row 8 is example data. Please overwrite with real data

## Mixed Tech(Low Side)
STATION CODE (EXACT): | XXXX_SUB
PMU Data Submission Guide and Template
Protocol/Operating Guide References | [5 empty] | IRR and IBR PMU Submission Process: | [10 empty] | Conventional and C.C. PMU Submission Process:
•NOG 6.1.4 •NOG 6.1.4.3 •NOG 6.1.3.2 Phasor Measurement Unit Reqs •NERC PRC 028 | [5 empty] | • Make sure all units are generating at least 5-10 MW and MVARs • Submit at least 5 minutes of PMU data recorded with a GPS based clock, or ercot approved alternative • Submit a minimum output recording rate of 60 samples per second (each sample including the timestamp should be distinct). • Ensure all data is fluid, not stale. • The frequency and voltage (if expressed in kV) should have at least 4 decimal places of precision • Provide 3 (a-b-c) voltage magnitude signals and 3 (a-b-c) voltage phase angle signals • Provide 3 (a-b-c) current magnitude signals and 3 (a-b-c) current phase angle signals • Provide Frequency (Hz). Should be in the vicinity of 60 Hz • Provide Rate of Change of Frequency (ROCOF) signal • Phase angles should have approximately 120 degree angle difference between each phase depending on balance of phase. For a phase angle of θ in phase A, the angles for the remaining two phases should be approximately θ - 120˚ and θ + 120˚. • The phase angle measurements will typically swing between -180˚ and +180˚ (this is a reflection of varying system frequency) • If an MPT has units of different technologies (mixed-tech), it is preferred to provide lowside data for each unit and highside MPT data. This is to provide clarity in fault/event and VRT analysis. • Please compare the calculated MW and MVAR flows with the telemetered MW and MVAR flows before submitting. | [10 empty] | • Make sure all units are generating at least 5-10 MW and MVARs • Submit at least 5 minutes of PMU data recorded with a GPS based clock, or ercot approved alternative • Submit a minimum output recording rate of 30 samples per second (each sample including the timestamp should be distinct). • Ensure all data is fluid, not stale. • The frequency and voltage (if expressed in kV) should have at least 4 decimal places of precision • Provide 3 (a-b-c) voltage magnitude signals and 3 (a-b-c) voltage phase angle signals • Provide 3 (a-b-c) current magnitude signals and 3 (a-b-c) current phase angle signals • Provide Frequency (Hz). Should be in the vicinity of 60 Hz • Provide Rate of Change of Frequency (ROCOF) signal • Phase angles should have approximately 120 degree angle difference between each phase depending on balance of phase. For a phase angle of θ in phase A, the angles for the remaining two phases should be approximately θ - 120˚ and θ + 120˚. • The phase angle measurements will typically swing between -180˚ and +180˚ (this is a reflection of varying system frequency) • If an MPT has units of different technologies (mixed-tech), it is preferred to provide lowside data for each unit and highside MPT data. This is to provide clarity in fault/event and VRT analysis. • Please compare the calculated MW and MVAR flows with the telemetered MW and MVAR flows before submitting.
Timestamp(mm-dd-yyyy hh:mm:ss.000) |  | MPT-01(Low Side)**Replace with exact MPT name as seen on the production model in all CAPS** | [63 empty] | MPT-02(Low Side) | [63 empty] | MPT-03(Low Side) | [63 empty] | MPT-04(Low Side) | [63 empty] | MPT-05(Low Side) | [63 empty] | MPT-06(Low Side)
|  | UNIT-A**Replace with exact unit name as seen on the production model in all CAPS** | [15 empty] | UNIT-B | [15 empty] | UNIT-C | [15 empty] | UNIT-D | [15 empty] | UNIT-E | [15 empty] | UNIT-F | [15 empty] | UNIT-G | [15 empty] | UNIT-H | [15 empty] | UNIT-I | [15 empty] | UNIT-J | [15 empty] | UNIT-K | [15 empty] | UNIT-L | [15 empty] | UNIT-M | [15 empty] | UNIT-N | [15 empty] | UNIT-O | [15 empty] | UNIT-P | [15 empty] | UNIT-Q | [15 empty] | UNIT-R | [15 empty] | UNIT-S | [15 empty] | UNIT-T | [15 empty] | UNIT-U | [15 empty] | UNIT-V | [15 empty] | UNIT-W | [15 empty] | UNIT-X
UTC | CPT(auto-converted) | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR | Frequency (Hz) | df/dt | Va (V) | ∠Va (°) | Vb (V) | ∠Vb (°) | Vc (V) | ∠Vc (°) | Ia (A) | ∠Ia (°) | Ib (A) | ∠Ib (°) | Ic (A) | ∠Ic (°) | MW | MVAR
Note on C1: This cell is prefilled with an example. Please overwrite and Include ONLY upper case letters and must be between 2 and 8 characters long. The only special characters allowed are underscores and dashes.