## Cutover-Cutback Plan - QSEs
RTC+B - Live Production Closed Loop Testing - Cutover and Cutback Plan ( QSEs/External) - 09/11/2025 09:00 - 13:00
Step | Start Time | End Time | Tasks / Steps | Responsible Entity/Resources | Status | Notes
RTC+B Pre Cutover Steps
1 | 2025-09-04 | 2025-09-10 | QSEs to verify that their RTC+B EMS AGC/SCADA Calcs/Scripts and Market/COP Interfaces are setup and ready for Closed Loop Testing. | QSEs
2 | 2025-09-04 | 2025-09-10 | QSEs to verify that RTC+B ICCP/EMS and Market systems are updated with latest model. | QSEs
3 | 2025-09-04 | 2025-09-10 | QSEs to verify all their resources RTC+B Resource Status (RSTR) telemetry point in their ICCP/SCADA is setup correctly and sending good quality RSTR telemetry to ERCOT ICCP. | QSEs
4 | 2025-09-04 | 2025-09-10 | QSEs to verify all their resources UDSP telemetry point in their ICCP/SCADA is setup correctly and receiving good quality UDSP signal from ERCOT ICCP. | QSEs
5 | 2025-09-04 | 2025-09-11 | QSEs to continue to submit production quality real-time market submissions (COP, TPO, AS Offers, ESR Bids/Offers, Output Schedules etc.) utilizing their parallel RTC+B Market Systems. | QSEs
Communication
6 | 2025-09-11 09:00 | 2025-09-11 13:00 | Webex Conference Call will be open for QSEs IT/OT staff | ERCOT |  | ERCOT will send Closed Loop Testing Webex conference call details to QSEs AR on 09/08/2025.
7 | 2025-09-11 09:00 | 2025-09-11 09:15 | QSEs IT/OT staff to join the Webex Conference Call | QSEs IT/OT Staff |  | One representative of each QSE is required to be on the call to execute and coordinate the Cutover/Cutback plan with ERCOT and provide status updates during entire time of Closed Loop Testing
8 | 2025-09-11 09:00 | 2025-09-11 13:00 | QSE IT/OT staff shall provide their system cutover and cutback status in Webex chat by sending the message in the following format: QSE Name - Status (Example: ABC - Cutover Complete, XYZ - Cutover ran into issues, ABC - Cutback complete, XYZ-Cutback ran into issues). If QSE runs into critical issues during cutover and cutback that can not be resolved within 5 minutes, QSE shall notify ERCOT by sending the message in Webex chat with nature of the issue, resolution status and confirming that their resources are holding at their current generation. | QSEs IT/OT Staff
RTC+B Cutover Steps
9 | 2025-09-11 10:00 | 2025-09-11 10:15 | ERCOT Control Room to make hotline call to QSEs/TOs to notify on Cutover to RTC+B at 10:35 AM | ERCOT Control Room
10 | 2025-09-11 10:35 | 2025-09-11 10:35 | a. Perform Taylor QSE ICCP systems fail over to cutover to RTC+B EMS. b. Verify all QSE ICCP links and ISD links are up and get the telemetry | ERCOT
11 | 2025-09-11 10:35 | 2025-09-11 10:37 | ****QSEs to wait until ERCOT gives instructions through Webex Call on this step**** a. QSEs to Cutover to their EMS AGC/SCADA Calcs/Scripts etc. to RTC+B and start following UDSP. ***QSEs cutover should complete within 30-60 seconds***. b. QSEs to report the cutover status to ERCOT through Webex chat | QSEs |  | QSEs should not automate the Cutover based on UDBP or another telemetry points data quality. QSEs IT/OT staff should wait for ERCOT instructions through Webex call to perform their systems Cutover.
12 | 2025-09-11 10:36 | 2025-09-11 10:37 | a. Perform Bastrop QSE ICCP systems fail over to cutover to RTC+B EMS. B. Verify all QSE ICCP links and ISD links are up and get the telemetry | ERCOT
13 | 2025-09-11 10:37 | 2025-09-11 10:37 | Verify that following outbound telemetry points common to both current and RTC+B systems are getting updated from the RTC+B EMS. Similarly, verify that all existing system level telemetry points are getting updated from RTC+B EMS. BP/LMP/SBBH/SCCT/NDPL/RDPL/MMEC/KVM/KVT | ERCOT
14 | 2025-09-11 10:37 | 2025-09-11 10:40 | ERCOT to verify QSEs are following RTC+B UDSP and report any issues to QSEs through Webex chat. | ERCOT |  | Wind and Solar Resources do not follow UDBP unless they are curtailed.
15 | 2025-09-11 10:37 | 2025-09-11 10:40 | QSEs to verify their resources are following RTC+B UDSP and report any issues to ERCOT through Webex chat. | QSEs
16 | 2025-09-11 10:37 | 2025-09-11 10:40 | QSEs to provide their systems cutover status through Webex chat (created for communicating to designated ERCOT contacts Only) in the format mentioned above | QSEs |  | QSE IT/OT staff shall provide their system cutover status in Webex chat by sending the message in the following format: QSE Name - Status (Example: ABC - Cutover Complete, XYZ - Cutover ran into issues). If QSE runs into critical issues during cutover that can not be resolved within 5 minutes, QSE shall notify ERCOT by sending the message in Webex chat with nature of the issue, resolution status and confirming that their resources are holding at their current generation.
17 | 2025-09-11 10:39 | 2025-09-11 10:40 | Disable current Production UDBP, Regulation and other non-RTC+B outbound telemetry points in ERCOT Bastrop and Taylor ICCP Systems. ***This means these telemetry points value will be stale with suspect quality for duration of test with a UDBP value approximately from 10:39:30 AM*** | ERCOT |  | QSEs should not automate the Cutover/Cutback based on UDBP or another telemetry points quality. QSEs IT/OT staff should wait for ERCOT instructions through Webex call to perform their systems Cutover/Cutback.
18 | 2025-09-11 10:40 | 2025-09-11 10:45 | After all QSEs cutover to RTC+B from current production is completed, Control Room makes hotline call to QSEs/TOs announcing ERCOT is operating on RTC+B and also posts a message on the MIS for ALL QSEs as well. | ERCOT Control Room
QSEs Cutover to RTC+B is completed and following RTC+B UDSP Signal
19 | 2025-09-11 10:40 | 2025-09-11 12:35 | QSEs to update the RTC+B telemetry and COPs (and bids/offers) to reflect the real-time conditions as they do normally during normal operations and also continue to update current production telemetry and COPs etc. (example: Unit Trips etc.) | QSEs
20 | 2025-09-11 10:40 | 2025-09-11 12:35 | QSEs control room operators shall perform the dual entry of operator actions (Example: Telemetry manual overrides etc.) based on grid conditions and communicate to ERCOT control room directly on any operational updates as they do normally during normal operations. | QSEs
RTC+B Cutback Steps
21 | 2025-09-11 12:15 | 2025-09-11 12:25 | Get final confirmation from ERCOT Control Room to start the cutback activities at 12:34:30 PM | ERCOT
22 | 2025-09-11 12:20 | 2025-09-11 12:25 | Enable ERCOT current Production UDBP, Regulation and other non-RTC+B outbound telemetry points in ERCOT Bastrop and Taylor ICCP Systems. ***This means these telemetry points values will show latest values with good quality *** ***QSE resources should continue to follow RTC+B UDSP signal until cutback is completed*** | ERCOT |  | This step ensures smooth cutback to current production. QSEs should not automate the Cutback based on UDBP or another telemetry points data quality. QSEs IT/OT staff should wait for ERCOT instructions through Webex call to perform their systems Cutback.
23 | 2025-09-11 12:25 | 2025-09-11 12:30 | ERCOT Control Room to make hot line call to QSEs/TOs and inform that cutback will happen around 12:35 PM. | ERCOT Control Room
24 | 2025-09-11 12:34 | 2025-09-11 12:35 | Perform Taylor QSE ICCP systems fail over to cutback to Current Production EMS from RTC+B EMS. Verify all QSE ICCP links and ISD links are up and get the telemetry | ERCOT
25 | 2025-09-11 12:36 | 2025-09-11 12:36 | ****QSEs to wait until ERCOT gives instructions through Webex Call on this step**** a. QSEs to Cutback to their EMS AGC/SCADA Calcs/Scripts etc. to Current Production and start following current production UDBP and Regulation Instructions. ***QSEs cutback should complete within 30-60 seconds***. b. QSEs to report the cutback status to ERCOT through Webex chat. | QSEs
26 | 2025-09-11 12:36 | 2025-09-11 12:36 | Perform Bastrop QSE ICCP systems fail over to cutback to Current Production EMS from RTC+B EMS. Verify all QSE ICCP links and ISD links are up and get the telemetry. | ERCOT
27 | 2025-09-11 12:36 | 2025-09-11 12:37 | Verify that following outbound telemetry points common to both current and RTC+B systems are getting updated from the Current Production EMS. Similarly, verify that all existing system level telemetry points are getting updated from Current Production EMS. BP/LMP/SBBH/SCCT/NDPL/RDPL/MMEC/KVM/KVT | ERCOT
28 | 2025-09-11 12:36 | 2025-09-11 12:50 | ERCOT to verify QSEs are following Current Production UDBP & Regulation Instructions and report any issues to QSEs through Webex chat. | ERCOT
29 | 2025-09-11 12:36 | 2025-09-11 12:50 | QSEs to verify that their resources are following Current Production UDBP & Regulation Instructions and report any issues to QSEs through Webex chat. | QSEs
30 | 2025-09-11 12:36 | 2025-09-11 12:45 | QSEs to provide their systems cutback status through Webex chat | QSEs |  | QSE IT/OT staff shall provide their system cutback status in Webex chat by sending the message in the following format: QSE Name - Status (Example: ABC - Cutback Complete, XYZ - Cutback ran into issues). If QSE runs into critical issues during cutback that can not be resolved within 5 minutes, QSE shall notify ERCOT by sending the message in Webex chat with nature of the issue, resolution status and confirming that their resources are holding at their current generation.
31 | 2025-09-11 12:45 | 2025-09-11 12:50 | After all QSEs cutback to current Production from RTC+B is completed, Control Room makes hotline call to QSEs/TOs announcing ERCOT is back to normal operations and also posts a message on the MIS for ALL QSEs as well. | ERCOT Control Room
QSEs Cutback to Current Production is completed and following UDBP and Regulation Signals
32 | 2025-09-11 12:55 | 2025-09-11 13:00 | Communicate to QSEs (through Webex Conference Call) confirming the end of closed loop testing and close the webex Conference call | ERCOT