## CB_DATA_ (hidden)
Crystal Ball Data
Workbook Variables | Last Var Column | 0
Name:
Value:
Worksheet Data | Last Data Column Used
2
Sheet Ref
#REF! | #REF!
Sheet Guid
162bf5f6-f421-4de0-85f4-d908ee7629cc | 12115544-690e-42fd-8adb-150c253b8934
Deleted sheet count
Last row used
28 | 26
Data blocks
CB_Block_0
㜸〱敤㕣㕢㙣ㅣ㔷ㄹ摥㤹摤㔹敦慣敤搸㡤搳㑢搲㥢愱㤴㤶㍡戸㜱摡㔰ち㠴攰㑢㥣愴㌸戱ㅢ㍢㈹愸㔴㥢昱敥ㄹ㝢㥡㥤ㄹ㜷㘶搶戱㑢㐵㑢㕢愸戸㤵㡢〴愵㔰㘸㔵㈱㈴㕥戸㍣㜰㈹昰〰ㄲㄲ〸ㄵ㠹〷㜸㐰攲愱㈰〴て㕣ㄴ㠹㤷㍥㔴㉡摦㜷㘶㘶㜷㜶搷㍢㜶户㉤戸挸㈷摤攳㌳攷㌶攷晣昷昳晦㘷㥡㔱㌲㤹捣换㐸晣换㤴㘳攱慡昹㜵㍦㄰昶攸愴㕢慤㡡㜲㘰戹㡥㍦㍡敥㜹挶晡㡣攵〷㔹㜴挸㤷㉣戴晢㕡挹户敥ㄷ㠵搲慡昰㝣㜴搲㌲㤹㐲㐱㔷搱捥㐹昸ㅢ㡣ㅦ㜴㡥敡换㈱㕢㤸㥣㤸㕤扣ㄷ戳捥〷慥㈷昶て㥦つ挷ㅥㅥㅢㅢㅤㅢ㍤㜴攰戶㠳愳〷昶て㑦搶慡㐱捤ㄳ㠷ㅤ㔱ぢ㍣愳扡㝦㜸慥戶㔸戵捡敦ㄷ敢ぢ敥㜹攱ㅣㄶ㡢〷㙥㔹㌴㙥㝤攷搸慤㠷づ㤹户摦晥捥㍥扣㍡㜳㙡㜲㘲捥ㄳ愶晦ㅡ捤愹㜱挹户㑥㠹戲挵扤〹攱㔹捥搲攸攴〴晥㑢慣ㅦ㑦户㡤捥㉦ぢㄱ昰搵挲ㄳ㑥㔹昸㍡〶昶摡攳扥㕦戳㔷〸㍣摤㥥挶㔶换㠶ㅦ㘸昶愴愸㔶㜵㍢㥥戵㘰捦〲㜶㔵㘳扤捦㥥ㄷ㡥㙦〵搶慡ㄵ慣攷敤〵㑣㔴改户捦昸攲戴攱㉣㠹㔳㠶㉤㌴晢㔸捤慡攴挲㤴挹摥㄰㑦㤱㕣㤸摣晥攸戸㙦㑦㉥ㅢ㥥㕣㤱㑦挰愴昴㥤昶捡捤㝤慦敢㍣㉦㤷㉥摦挰㌹慦敦摣て㉤㘷つ慦摥㜳愴㜳捦㘸昳捤㉢戸戹㜳晦〴㡣㥡挷扣慤昳ㄸ〹捡收摥㑡㙦㐴摦ㄲ愲搸㡣㥥㘷搶挳慣挰㡣〸搴㡢捣㝡㤹昵㈱㔳㜲晦〶㤷㈴〷戲㐹㉤ㄹ㙡㘹㔱㉤㤵搵㔲㐵㉤〹戵㘴慡愵㈵戵戴慣㤶㉣戵㜴慦㕡㍡㡦㍥㜱㉡昴昴愸㔱晡晥㔱昳㘷捦㍣昰㡤改愷㥦晥晢㐷晥昹昱㐷扥摣户ぢ㥤敥㡣ㄶ㌵攵ㄹㄷ㐰㙡つ㉡〶㐷昰摦收㕣〱愶㌰て㤹户㤹㘳㘳㤵㐳〷㡣㕢っ㡤摢㑡㐱㝥ㄳ愱っ愲㙦㥦㜹㤷攵㔴摣ぢㄲ㜷㔷㑤ㄸ扥㘸〰㙥㈴㙡㥢㜰㙢㑥挵扦㜲攳挶昹挰〸挴扥搶戶挶㈴㙤挳收挱㔶挲㤷敦扢愶㜵搸㔹愳㕡ㄳ攳㙢㔶搸㝣㜵㑢戳㍤攷戹㡢㥤㕢愷㍤㜱㕦扤戵㙤㐵攳㄰㙡慢㜲敥戶㕤㠶㑤攱扡㠶㈷㤷㕤㕦㌸㜲㜹㈳昶㥣㔵㍥㉦扣㜹㐱㤱㈸㉡㜲慢㤷戲㈹攲晡㤱㔹〷ㅢ〵户㔶摥㥣慣㌵㡦慥〵㘰㘶㔱挱㝡㔷㠴ㄷ慣㉦ㄸ㡢㔵㜱㔹㔳㤷昰㥤㘸搸摢㔴㍤敤㤶㙢晥愴敢〴㥥㕢㙤㙥ㄹ慦慣ㅡ㤰㌴㤵㤳㙥㐵攴㜲ㄹ㈹ㄴ㈰㜰戳㔹㐵挹摣搴㤹ㄷ㈴㈲ㄲ㈸㈶㈳㕦搱㑣㜶愳愷戱㍢散愲㉡㐸㤳敡㕢㌶㤹㡣敢㤵㌲㈶㠵〳ㄳ㝢愲晥攰㑢㙦摣㘴摡㍡收㕥摦捥慡㍡ㄴ敤晥攸慡㜰㠲攳㠶㔳愹ち㉦㔵晢㈹㕣㤱㍥㠰㑣扢〸㠱搰ㄱ㝡㔴㜵捡㥡戲慥㕤戰㉡挱㜲㝥㔹㔸㑢换〱敡愰㈱ぢ〵㠲戶㉤改㤷愰㑡摦捤㙣〸㔹戱㤸挹敦㘱愷㝣ㄱ㈹愳㔱㍡愵昰㜲㤳㈰攷戸㈶㕥敥㌳愷慤㙡㈰㐲愱㍣㘰〲㈳愱㔶㤳攸敢㈷㠹㝡㐶㌹㔴ㄸ㝢捣㐹㔰愹㘱㌹挱㝡㠳㙦摢戸㈴㈴愲ㅤ㔹戰敤㘴〱㐵㐱戳㍣㐸攱㌵㄰㑤㡢㌴㐸敦㥣㈰㈲戲㐱㡡㘶挷捣捤㐴挶晥㈹㌲〲晤㤳㐴挸摥〷㍡换〸ㄲ㝢㍢㤱㜲㔰㐷㝥摣㤱㘶ㅢ搹昲愱㌴扢ㄴ㠰搳㉦㘳㜶㌹戳㉢㤸敤㐵愶晣ㄵㄲ㡥㔲づ攵收愴㕦㠹㘷晤㉡㘶㔷㈳㠳㝣搲㈹㜳㈲㔱㐵ㅢ㙡㉢㜶㈴晢昵挳㑥㤶㐶㜱㈸㡡㘸ㄹ搷敤捣㝥㕢㈲㍡戲㍡户㠷慥捤㐹ㅤ晢搶捥戴㤹摣づ㈹㌲愵㙢㜲慦㥢㜴㑤〲㠲㕤扢搴㕢搷㘲愸㍥捣散㑤挸㡡晡㥢㤹㐳戹搰攰摤㥡㐵㑦㤳昲つ㘱ㄶ㠵挶㔰㤷ち㍥㈲㘴ㅥ〱㔲㠴㕣摢昱㘵挷㠶愶㌹㌸㘲扥攱㙤攸晤㥤昹㍢㐲㝡㡢摥摣搱㍢昴ㄷ扤㐲㉢晡㍡戰㤷昲挷㡥㍡收㝡㌴敢㙦㘵㜶〳戲ㄶㅤ挳搳昷㉢昵ㄴ㐸戳搸㑥㘰㙥㌷扤㉥搲捡㕤㔸㕦ㄱ㔲〳昵㤹ぢ㠶户㈴〲㜸㌰㑥㑣挱ㄶ㜶㍤㑦㔴㜱愸慤挸ち㥥㕦㉥㙦慥昴愷㍤搷㘶晤㡥㡤散扦㈱ㄴ㐳㉥愷㘶㌳㉤㌶㜲㡡慤㤹昰㌹㈵㈸㠷㍡昸㤶捥㐲㈲㌱愸㤹扣㌸㉥晤㝣戹㈳㐹扡㤰㈴㙦〳㔸昵㥢㤰㐱㑡㈸扦敦㈸㔱昶戳摢摢㘵户㘶㡢㤵ㅥ扥㤴搳㐹㡢て戱㑤㡥昴㠶づ摢〹昸て晣㝥㝢摥戲敢挲愲搷㥥ㄳ㕥ㄹ扥〵慢㉡㡡愱㕢㤶愲㘶㐷㔶扣㐱㘴㐵㌶摢㜶㥥㑥昱慦㐹㍡㘹㤱ㄲ愹摣㥥摡㤸㜲ㄶ㙦㄰ㄵ摤㤰ㄴ㉡㈹慥愱扡〴㈲攵戱敦㡥㠸改㐲挴摣っ挰改〷㤸㡤㌱㍢㠸㑣晢つ㈴捤㔶〱捦㜰㔸捦㉡㕤摡愵㔲愶㐰㌴㐸ㄷ攱昳ㅤ㠵搵㈱扥收ㅤ捣㙥㐳搶㘲晥搰〱㤹㐲㠸ㄲ攵〹㐲㤴㘱っ昳慣㈵㉥㤰〶㜶㤹〸㉣㑤搶晣挰戵ㄹ㔹敡㌷愷摣㔳㙥㌰㘵昹㉢㠸㐴つ㤹㔱攱慥㘵攱㠰扡㍣搸㍥㉤㜵敥捡㡡愸攸收扣㕢㠳㘸㍢㌱戵ㅤづ收〰〷㙣㐹㜹㌶㔷ㄵ愴敥捥挷㤸㐲〱愴愵扦㤵摥搸㉤㜹扦㜹攸ㅢ㘸㐰㜴挱ち慡愲搷っ㤹㡥攵㠲〹㈸㈲㜲㔰改㌱ㄷ㤶㍤㈱愶晡捤㘳㥥㔵愹㕡㡥㈰㌲㘰㘳㌲㔸㌷㈳㤶㄰㈵㤸㜳ㄹ〳㜴㥤㝥㜳挱㌳ㅣ㝦挵㘰㐰㜱㝤㜷搳㤳っ㡢㘸收㠴攵昸㜸㡤挴㈲换〳收晣戲㝢〱ㄱ摢㥡敤ㅣ㌳㔶晣㙤㠱ㄵㄲ㝤㤸㈴㙡ㄴ㔵㔱㔵愵愰ㄶ扡挵てて攴㤹っ㜹㉦挷㑣攲㉡愳搱㘷㥥愲扤㘹搷㐷㌱ㅡ摡改㕣㔳ㅦ愲㐷昵捡㙣慡ㄴ㈶愷敡户㜳捣扢㤰摤㜱散捣㠹㐶㘴敥㔵挵慣㌵㝡昹㔳㘴扣㈴㡢㝡㈰㠴㍥扡㕤㈱愹戰㡥㤴〳づ〴挶昹搴㑡㝥㐵㔳昶㈱昵敤㙡ㄴ愷ㄱ㐹敡㌳㘷㡣㐵㔱㐵㍣摡㌶㠲㕤攱〳捤㔸摢愸晡㔱摢愴㙢摢〶㐹㡢㘴㌹㕦㌶㐸挱攳戵挰㍤㘹㌹扡㠹㑣搲㕦㔴㘵慣愱捡㔸㤳㔵㝤收㘹㠶〶㘵㤹㜳戹㑢㠶㘷〵换戶㔵㉥昰㠱攱扢㙤㐱㤳㘰㜲㑡摥㌸挵㌲㘳戸挵㥡㍦〳㤳捤ㅦ〵扡㐷㈱㐷〹㍡愲ㅦ㤴慢㉡㜹晣㔳扡㜴㉣㐱挰㐸㑦愹晥ㅥ捣愶挹摢ㄱ㄰㌹㌲㕤㡣敦㘰㕣㝣㄰㌵愱㄰㈲搶㔳㐸〴㕥挱㠴㤰愷㡢㍢㙦㥥㜱慣〰搸㈳挶愶慤㘰捡〷捡㤱愱㈸㡦户晢㈴㔶ㄳ㠳㐶敡㕡攱摡昶愶㈶㌵㜱㑤㝢㝢㔲㙦扣㘵㠳收㔰愳㈴ㄴ挹㘶㥤愴㘶搹㘰㡤摢㐹搵㈸㔲㜱挷摡㐶㐹㜳㥢㌶攰㑥㈹昲㉡ㄴ㤳愴㤹㡣晥㕥㐹㈸〸昴㐶㍡㡡㍥晢㜴昲㐸㐴㙣㘸〳ㄴ愹愷挲扡晥㈸㈴㜸〲搷㑥㉡愲ㄸ㍤㠱扦㜷㐵挵搹㕡搰搴㘲慣つ㐵㉤攳搵敡慣〳㉢愱㙣㜸㤵㙤挲搲搸㕢愸㘱㈴㜷㜶慢晤㐳昰㈶ㄸ㌱㘲㐳㠶㐵㔲晣挰㘰㐳㌰㔷㈲愲㑡敢慣㥦愰慥㔷ㄷ昸㜴㔲ㄸ㡥挴挰㝣㔰㤹ㄲ慢搲っ㙢㔸昲㐳㜲㐰晤戴㈸攵愸㙥㡥㉦晡㔰改〱攵㜸㔴㤲っ慥㥢愷改㤶挲㈵〶㠸摤愸㌴㔷づ㄰摡慤㑦挰㤳挱昶挱づ㈰ㄲ㠶㑥㘸㥤㔱㠲收㔳〸户㜹ㄳ攴㥤㉥㌱ち㐱㙡捡昴慦㈳捡㔷㥥㘴晡搶㤱㑣㕣㠸㤸㠸攱慥ㄴ敢〱挸㑤㐶㈶挹㐵㐳㜱挰㍣㤴㙣㔲㘸昵挵㜵㌴㌱晡㘹昲㜹〱㙥昱㌰㤶㌵㐰戶愹攲㥥㕢㘰㐱㥢㔶搷㜷㤹㈷㥣㜲戵㔶ㄱ㔲ㄵ挷戲㕡㙡攴㙤㠱㉦㜹〵㌰攴愶ㄴ戸㐴㐰㌹㠱愳ㄴ户㑣㈴㜵㙦㜷敢㐷㌰㕣ち㌹捣ㄱ慡㍥〶㈰㔳摣㜲㌲㈰搶㜶㑦㠱昶攱敥挶〵〶㜹㜹づ㈲慤慤㡡戲㙣〶昷昱敡㔱㘴挹㙤㠹㙥㌳敥㡣㑢㥢㍤㔱㜵摣ち慢戶〵㡥戰捦㔰攰攵昳㌰㐶扡攴づ㑥㤲戹ㄸ㐵㜷㉦㍥㈸ㅦ㌳ㄷ㠱ち㠹〱㠵㌱㕥㥥㠲㌲㠰㉡ㄸ㠹〶户摡戰扡ㄵ㐶㝦㘹㜹敢攳挸ㄴ㠶㠱㘹搰愲㘷㘸攰㑣愲扣戹㠱㜳㉤㝡愵㐴㐸㤳挱㔴挶㈸㠷攰戰〷搲挰㑤㍣㐸㉦戸㔰㐲挱ㅥ㜹㌱㉣扥㥢㌸㘲攳〸攴㝡㤷戵㔴捥ㄹ〱慥扦㌸㝢㕢慡挷㉢ㄵ㥡扢昰捦㙤ぢ慣攲敡㐶㘸㡥敥㘹戹㤴㈵昷㐴晢敥扡㤶㠶攸戲攰挱愹搱攳㐶㔰㕥㥥て搶挳㡢㕢摤㤲㠴昶㔳昸㈳㌶㝣㍢㙤收㥣挳㡢愸慢㠴㝤昱扣攳㕥㜰攴扡㌴㥦户晥㐰㈱戸㐲搹挳㐵ㄶ㌳㉦攳㥦㑣㙡㐶晢〹㘶摣捡戲㌹㐱挳㐱挲㜹㘴ち愵挱㌰捡㈹㜴〲摢扤㝥㙢㠰㜴戲愷㠵㑥愴㈰搸㈱ㄴ㘷改㌵㈳ㄴ攵挷㐰㉢㠹㈵㍣㤲〳收摦〴敢㉢捦愱㠶〸挷㜳㈴㐶戴㌷愱㤴㠲㍡㈹挸愳㉢ㅥ扣㄰昲晦㠳愵㤸㥢㌷㘴愷晦〲㌳㉢㍦㙡㐵搱㌵㐴搱て摢㔰愴昰ㅡ㠸攴摦㍢愲〲ㅦ㌴㠶㘷㕦㔱㈰㥣㝢摡㌹㠰扥敥ㄷ㝥晦㠷〷搰ㄹ㘰㤸㐹摡㘸〸戵㕤㡦㜲摤㐴挸戶㤹〸っ摥㑢ㄳ攱㈴挷㌰㡡ㅦ㥡〸㤱て㘴ㄶㄵ㥢㥢〸㡣敤愵ㄸ㠲㠹㔰㙢挲慤挱ㄳ搸㘵㌶晤㘳挷㜱昱㔶昸㠸攷㐳㘹昹㤳昰㐸㕤摥㕥㍤㘷㜸㠶扤㔷搶ㅦ昳〴㤴㤹户㠰㥢摣㜲〸㐷散摢戰㐵づ摡挰㔷ㄱ㝢搹㜷晣㈹㕢扢扦づ㑣㠵㈹㜴摦㉢〵㈵晦㉡㍣㈵ち捦つ㤹て敦昹昶戱㍦摤晦攸ㄱ摥㔶㡢㘸㔵扢〹攵㙥㐲昶戴㈷㄰搴㑤㕣ㄴ戹㤴ㅦ收㥣挴㈷㑡搶㑡㔵㑣ㄸ㥥戴㠲㝣摤㡥㡢㈱攱㈵〸㌳㈴扥敤㘰㘲攲摥㐳㘸㘲㡥戶戸㍢攵㠷㑤搲㐵㌸㥡㔸戸昴改挵㘱㐳愵愳㈲敢搲摡搴扥ぢ㔵昴ちㄷ搲㙣㈵昲搴挹愴㈸摦㘹搵㜵㠷愸敢挲㠳っ挳晥戱㤴㐲晣㠱ㄴ㤲㍣挸昰㐲㠰㤴㔲愷㔱搰㙥㐶㤶ㄲ㔹㙢つ昱搲ㅦ戰㈳〴㐴晤搲㕦㤷ㅦ戱〰㡡挰㘲散㡢敦昶㐴㑢㕢㌴㔶㑤っ搵㑡㥢㘶ㅥ〵㜹㜸㘱挵㔸㕣扢㠰㐲㥣戴㠳㈸㙤搹ㅤ挵㤷昴摢㘱攰㉤㘴㙣捤愶慦慤㘸ㅦ㜵㙡戸昹〱㍤㤳㤷ち挳搹捤㙡ㅣ㐸㘵㡣㉥散㕡っ慢㤸て㠴挵晡愰摥愸〹㍡换搹㡢㔳㈹㠲㝦晣㔲㠸敤㈳㡤愹㉦㙤㙤愱㡥㜳㝡戰㐱晥㘰㝦㕤㤳挲搸㜸㉢㌹〶ㄲ㜶㑢扤ち攱昵昰㌳ㄸ挲㑤㘷ㄴ扤㔱㤴捦捡㈱晣㠹㌹㉢慢戶改㝦㐶慦㈵㘷㥤攵㘸㠶戱㥢昴晦〷㔰戱愹晥㔷ㄸ㝢㤳㠸晣㘰㔴㤰挶㈹攳㈷㥢㠶㙣〸ㄱ㜸戶ㄱ扣㤱〷㘳㕤ㄶㄹ昲づ㑢昳昸㜸㌵㙣㤶ㄲㅣ㝥慦㕣敢搵㠸晡㔸摡戶扤ㅤ〵㈰㘳㐳摡㌷㈱㠲㍡㡥㙦㤶㕢昱改㌶㝦㌷〶敥㌹㘹㤵㍤搷㜷捤㘰㜸ㅥ㐱摦㘱㝥㝢㘶挲收ㄹ㔷扥搱㉡搴慥〳㈴晡敥挱㤸㔳戳㄰搸愷㐴昰㕡挵㈲ㄹ㔹搸㕡㈴㠳摦㈱つ㈶挲㑢搴づ晥㈵收㥤㌵愳㡡㑦㔷㘷攱敢っ㔸戵㉤㤴㕤攸㜱㙥扤愱㐱搰攱㡥搶晢攱てㄲ搵㔱〴挷攴ㄶ敥扥㠷㜰㙤㠵㐱㜳摦㘸㙦㍥㝢㜶攷㜳㉢㙡捦〲愷㕢㝢㑢㌳挹昰㥤晣㈲戹愸㤷㤸攳搲晥ㄱ晣摤扡㠳㤶戳つ㠱捥愳て扡改〸ㅢ愹挲㝤戶㠵攸昷㌹っ㔵挶㤹攱愷ㅢ㔱㠱てち扤㝣㘴㐵攵敢搸ㄶㄹ〰攵㑣扥㡣慣㌳㔵㍦戵ㄱ㔵て摥㠱㌱攴㔷㕤㈰敢捦㉡㍣㙡㤰㉡㡢捡㔷搰㥦㔰ぢ㜷扦挴㍡ㅣ㍤攴㤱〲㘵㍤㈹挹ㄵㅥ㈹攴㝡㥥挰㠰晡㝡敥㐵㙤攷昵㝣㜱愳昵㈸㌴〶攴㝥㤳昳て挶捡㐴户昹㙡㠷㤹换㙣〵搹㘰摣㜳㠰㘲㤲㝢挹㠷愱㠶攷㠸㈹愴摦㐶㝦㕦㌸昲㥢攷㤹晥㜱㐴㤱㠲ㄱ㑤捤扢愰㘰㤴扢㜸㍣戹ぢㅦ戵㥤㜷昱改㡤㜶㌱㐸㤹㈹愱㕡㐳〱㔰㉤攱㡦摣搵㉡ち〴㈸㝦捡㌹㘶昸㌵慤㘲搰㐰㡤ㅣ扢㠶㐲㝦㔶㈳㘲摥摤㔹扢搰㜸㡣㍦㠵㐵㜰愰改㥢搷愳昸㠶㜵㥤搱敥㉣㍥攱搷愴㉡捣愹敦敡㙥慥搸ㅣ愵㈶搳ㅥ挳慥㕦挵㍣摣㜴挳攷挸ㄹ昷攱㔷㐰㄰㠲㘴㈶㐱㜲㍦ち㌱愰㌴㘲㍤攵换㈶㘹ㅣ昲ㄶ㈸ㅤ㔹昹搰ㄳ㥤て㑤㠲㠲ㅤ戹愰户㠵㘰挴㤶昸愹㜰㐷㝤㤶敦昲㝡㠳昲戱㤸ち㡦ㅦ㡦㍦ㅢ㔳愳㠰ㅢ戸㈰㌴挷挹㌵〴愴昲㘸摣昹㝢㍦㘸昸㡢搱㠰〴㔶〹㍢㤳扢㘴攷㐷攲捥〷昱㐹㥡散㤳㈱㐱㌱扤㄰㜷㈶ㄷ捡捥て挷㥤晦㝥㜰㙦扤㜳捣㜴攱捣ㅡ㌹㈲挵搰㤷㐷㥦挴攷改〳攸慥㤹㌴ㅥ㝡捤戰㥡㠴㈸攳收㔵㘹㍥昴攱㈶㡣㠷て挴㘷㜰戱ぢ昷㕦愰㘱挲晦㑦挴〹㕣昸㥡㌲〲〳摦㝦慦㈲搲敥改昲㠹㠳昳收慣㠷㡡ㅥ昳㠴㡦〳㘵㘵㕢㤱〸㙣愱㕣〸摦㑤㈲ㄲ㈹㜶㜳〳ㅥ㜱㠴㔰攵〵㥡敥㌴愷㡣㉡攵㤴㠷㘲捣㘶ㅥ㙡搰㡣晥㔱㈰〷㍡〱㌹ぢ晡挳挸挳㈸搴ㅥ㔶っ㔲搸㐹㐹昶㈸ㅢ㍥挶散攳挸㡡ち㈵ㅢ改㈰晦ㄸ戲㠱昸晦搲㌱扣㉡㥤㐵慡戲ㄶ扦㉣㐹㐶晡㈷㌸攰㤳挸戲昰㕤㉢ㄱㄱㄶ昵㑦愱㈶昹㔲ちづ昹搲捦戰攱㜱㘶㥦㐵㔶搴戸搸㉤㐳㡤㝢敡㔲㙤㝦づ㐳ㄵ㠲㠲㜳攸㥦㡦ち㝣㔰〸〷㡡㜳挵挱づ㈹㐳愹㙤ち㙡㕥㈱㙣㘴㠳ㅤ㌵ㅣ㤶つ㡡㐲㜸挹㠶㙡搴㐰㕤愶㝦ㄱ㤹㐲㜸㜰㑦晡㤷昸㐴㌰挸ㄷ㍥ㄱㄵ攴ぢ〹〳㌹㝣戹攵㠵㠴㡢㙣㔸㙡㜹㈱㘱㈵ㅢ捣攴ぢ扦捡㐹攵挶㔰㘸㔶㔷摣愰㠴昷搷㔰攸捦づ㜰㙤㜷攱愷慥㈹攵㜳㤵㜳攷㕥ㅣ挸つ敦换㝤攰㝤㝤㑦扥昰敢㍦㝦攱㜷ㅦ㍡晣户㤷㥥㝡敡㜷㝦昹挲昳㉦晤㜴昱昰㉦㥦㝤昶ㄷ㜷㍣晤晣㥦㜷㥢捦愸㍦㜸㜱收㤹〷挶捥㍦㜰㥦㜹收愶㘳て㝣昰摥㍢挷收㉥ㄹ挹㘶㝢㝡㙥ㄸ晡搵ㄵ㌷づ㍥㜴摦㡦㤴㥦晦攱㜲㐷㤱摢挵ぢ㥡㤷挱㙤换㘵㍣㡤〲㤶挱ㄵ扦慥换攰㜶㈵愰捥㐵㠰㥡㐰㐵〱捥て㉥㐰㌶㤴㥡ㅢ㝡晦〳挳换扤搹
Decisioneering:7.0.0.0

## Cover
Monthly Outlook for Resource Adequacy (MORA)
Reporting Month: November 2025
Disclaimer
This ERCOT report has been developed from data provided by ERCOT Market Participants, ERCOT, and ERCOT's consultants. The data may contain errors or become obsolete shortly after the report is released. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT REPORT IS SUPPLIED WITH ALL FAULTS. The specific suitability for any use of this report and its accuracy should be confirmed by each ERCOT Market Participant that contributed data for this report. Note that resource data is based on a mid-month Resource Integration and Ongoing Operations (RIOO) system snapshot. Resource quantities can differ from monthly reports prepared subsequent to the MORA report, such as the Generator Interconnection Status (GIS) report, which is released at the beginning of the subsequent month.
MORA Release Schedule
MORA releases are targeted for the first Friday of each month, or the next business day if the Friday is a holiday. A MORA is released two months prior to the reporting month; for example, the planned release of the MORA report for August would be the first Friday in June. ERCOT may post one or more revised versions of a MORA report if material data errors are discovered. ERCOT recommends that readers check for postings of a revised report around mid-month. Information about one or more data corrections for a revised report will be summarized in the box below.
Data Corrections/Updates
Report Contents
| Tab Name | Description
| Monthly Outlook | Contains the following sections Introduction Risk Outlook Highlights and Resource Adequacy Measures Hourly Risk Assessment of Capacity Available for Operating Reserves Deterministic Scenarios Notable Load and Resource Developments
| Low Wind-BESS Risk Profile | A chart that shows the risk of Energy Emergency Alerts based on various low wind generation levels combined with reduced Battery Energy Storage System (BESS) availability.
| Capacity by Resource Category | Summary table of generation resources by resource category
| Resource Details | List of registered resources and megawatt (MW) capabilities for the reporting month
| PRRM Percentile Results | Probabilistic model results: deciles for (1) hourly gross demand, (2) hourly solar and wind generation, and (3) daily unplanned thermal unit outages
| Background | Covers MORA methodology topics in detail

## Monthly Outlook
INTRODUCTION
The MORA report adopts two approaches to evaluate resource adequacy for the upcoming assessment month:
● | Determine the risk that ERCOT may face emergency conditions for the monthly peak load day — specifically, the chances, during a range of hours, that it may need to issue an Energy Emergency Alert (EEA) or begin to order controlled outages to maintain grid reliability. This evaluation is done through probabilistic modeling using ERCOT's Probabilistic Reserve Risk Model, PRRM. (See the Background tab for more information.)
● | Given a predetermined set of future grid conditions (deterministic scenarios), evaluate the extent that resource capacity can provide sufficient operating reserves for the hour with the highest risk of a reserve shortage. The focus of the MORA's deterministic scenario is on typical grid conditions.
Deterministic scenarios allow one to gauge how individual grid conditions influence a range of fixed outcomes while probabilistic simulation quantifies the uncertainty around the outcomes and produces likelihood estimates for them. These approaches complement each other to provide a richer perspective on reserve shortage risks for the ERCOT region.
Risk Outlook Highlights and Resource Adequacy Measures
● | Reserve shortage risks are the highest during the evening hours from Hour Ending 7 p.m. through 9 p.m. Central Standard Time (CST), when daily loads are typically near their highest levels and solar production is ramping down. The hour with the highest EEA risk is Hour Ending 7 p.m., with a 0.7% probability of ERCOT having to declare an Energy Emergency Alert. Relative to October, the sun sets earlier resulting in cooler temperatures in the evening and causing a shift of the highest-risk hour from 8 p.m. to 7 p.m. Both unplanned and planned thermal outages are expected to be higher in November based on historical trends. There is also a slight EEA risk for Hour Ending 7 a.m. through 8 a.m. reflecting the chance of a morning peak load drviven by unseasonally low temperatures.
The model also accounts for the risk of coastal wind curtailment needed to avoid overloads on lines that make up the South Texas export interface.
● | Under typical grid conditions, the deterministic scenario indicates that there should be sufficient generating capacity available for the hour with the highest reserve shortage risk, Hour Ending 7 p.m., CDT. The deterministic load forecast value for this hour is 56,141 MW. The expected peak load hour is Hour Ending 7 p.m. with a load of 56,141 MW based on the Operations-oriented forecast data used for the PRRM. This MORA assumes a total thermal outage amount (planned plus unplanned) of 21,183 MW during normal grid conditions.
● | The monthly capacity reserve margin for the deterministic scenario, expressed as a percentage, is 102.2% for the highest risk hour, Hour Ending 7:00 p.m.
Reserve Margin formula: ((Total Resources / (Peak Demand - Emergency Resources)) - 1) * 100
● | The ratio of installed dispatchable to total capacity is 58%. The ratio of available dispatchable to available total capacity for the hour with the highest reserve shortage risk, Hour Ending 7 p.m., is 82%. This latter measure helps indicate the extent that the grid relies on dispatchable resources to meet high load periods.
● | The ratio of installed dispatchable (thermal) to total capacity is 49%. The ratio of available dispatchable thermal to available total capacity for the hour with the highest reserve shortage risk, Hour Ending 7 p.m., is 75%. This latter measure helps indicate the extent that the grid relies on dispatchable thermal resources to meet loads during high-risk hours of the day.
Hourly Risk Assessment of Capacity Available for Operating Reserves (CAFOR)
The table below provides hour-by-hour probabilities that Capacity Available for Operating Reserves (CAFOR) will be at a level indicative of (1) normal system conditions, (2) the risk of an Energy Emergency Alert (EEA), and (3) the risk that ERCOT may need to order controlled outages. As a guideline to interpret these probabilities, ERCOT considers an EEA probability at or below 10% to indicate that the reserve adequacy risk is low for the monthly peak load day. An EEA probability above 10% indicates an elevated reserve adequacy risk. Note that this probability forecast is not intended to predict specific capacity reserve outcomes. The CAFOR definition is provided at the top of the Background tab.
Low Wind/Battery Storage Risk Profile
Deterministic results based on normal system conditions for the hour with highest risk of reserve shortages
|  |  | Loads and Resources (MW) | Hour with the Highest Reserve Shortage Risk (Hour Ending 7 p.m., CDT)
|  |  | Load Based on Average Weather [1] | 56140.618
Generation Resource Stack
|  |  | Dispatchable [2] | 77787.018
|  |  | Thermal, excluding RMR and other Emergency Generation Agreements | 71227.3
|  |  | Energy Storage [3] | 6163.5522
|  |  | Hydro | 396.1658
|  |  | Expected Thermal Outages | 21183
|  |  | Planned | 5306
|  |  | Unplanned | 15877
|  |  | Total Available Dispatchable | 56604.018
Non-Dispatchable [4]
|  |  | Wind | 16487.0916
|  |  | Solar | 0
|  |  | Total Available Non-Dispatchable | 16487.0916
|  |  | Non-Synchronous Ties, Net Imports | 719.8
|  |  | Total Available Resources (Normal Conditions) | 73810.9096
Emergency Resources
Available prior to an Energy Emergency Alert
|  |  | Emergency Response Service | 1827.636
|  |  | Distribution Voltage Reduction | 550.8
|  |  | Large Load Curtailment | 3790
|  |  | Total Available prior to an Energy Emergency Alert | 6168.436
Available during an Energy Emergency Alert
|  |  | LRs providing Responsive Reserves | 1607.52
|  |  | LRs providing Non-spin | 81.6
|  |  | LRs providing ECRS | 285.6
|  |  | TDSP Load Management Programs | 253.98
|  |  | RMR and Other Resource Agreement Capacity Units | 754.8
|  |  | Total Available during an Energy Emergency Alert | 2983.5
|  |  | Total Emergency Resources | 9151.936
|  |  | Capacity Available for Operating Reserves, Normal Conditions | 23838.7275
|  |  | Capacity Available for Operating Reserves, Emergency Conditions | 26822.2275
Less than 2,500 MW indicates risk of EEA Level 1
Less than 1,500 MW indicates risk of EEA Level 3 Load Shed
[1] The 7 p.m. load value comes from ERCOT’s monthly load forecast. The load assumes average weather conditions for the reporting month and includes new Large Loads expected to be energized by the forecast month.
[2] Dispatchable resources comprise nuclear, coal, gas, biomass and energy storage. Non-dispatchable resources comprise wind and solar. Dispatchable in this context means that the resource can both increase or decrease output based on ERCOT dispatch instructions.
[3] See the Background tab for a description of battery storage system capacity contribution modeling.
[4] Wind and solar values for Hour Ending 7 p.m. represent the 50th percentile values from hourly synthetic generation profiles used in the PRRM. See the Background tab for more information.
Notable Load and Resource Developments
ERCOT expects installed capacity to increase by 3,652 MW since the October MORA was prepared. Increases by generation type comprise 1,635 MW of Battery Energy Storage, 834 MW of Solar, 682 MW of Natural Gas, 158 MW of Wind, and 343 MW of Diesel. Regarding the Emergency Generation Service Agreement with Life Cycle Power, the following diesel units, totaling 211 MW in installed capacity and 143 MW for the fall seasonal ratings, have been approved for Synchronization as of 8/27/25 (A4 PEARSALL DGR, P2 HIGHLAND HILLS DGR, X1 MEDINA BASE DGR, Z5 SOUTHTON DGR). All diesel units are expected to be in-service before November 1, 2025. Operational Capacity Unavailable due to Extended Outages or Derates: - SANDY CREEK U1, 933 MW, Coal, extended outage until 3/31/2027. - R W MILLER STG 1, 75 MW, Gas-Steam, extended outage until 8/25/2030. - V H BRAUNIG STG 3, 412 MW Gas-Steam, Unavoidable Extension outage until 12/15/2025 based on Unplanned Resource Outages Report. (RMR from 3/1/2025 to 3/1/2027). - CHISHOLM GRID, Battery Energy Storage, 102 MW, extended outage until 12/16/2028.

## Capacity by Resource Category
Hour with the Highest Reserve Shortage Risk (Hour Ending 7 p.m., CDT)
Operational Resources, MW [1] | Installed Capacity Rating [2] | Expected Available Capacity [3]
Thermal | 86997.21 | 71295.6
Natural Gas | 67519.37 | 53160.6
Combined-cycle | 46873.15 | 34879.2
Combustion Turbine | 9597.02 | 7665.8
Internal Combustion Engine | 920.8 | 911.6
Steam Turbine | 10128.4 | 9704
Compressed Air Energy Storage | 0 | 0
Coal | 13705.39 | 12718
Nuclear | 5268 | 5064.2
Diesel | 504.45 | 352.8
Renewable, Intermittent [6] | 74442.06 | 16487.0916
Solar | 33828.78 | 0
Wind | 40613.28 | 16487.0916
Coastal | 5774.46 | 2348.3333
Panhandle | 4831.93 | 1967.1075
Other | 30006.89 | 12171.6507
Renewable, Other | 721.45 | 526.9658
Biomass | 142.25 | 130.8
Hydroelectric [4] | 579.2 | 396.1658
Energy Storage | 14501.27 | 5691.2778
Batteries | 14501.27 | 5691.2778
Other | 0 | 0
DC Tie Net Imports | 1220 | 719.8
Planned Resources [5]
Thermal | 143.7 | 143.7
Natural Gas | 143.7 | 143.7
Combined-cycle | 0 | 0
Combustion Turbine | 143.7 | 143.7
Internal Combustion Engine | 0 | 0
Steam Turbine | 0 | 0
Compressed Air Energy Storage | 0 | 0
Diesel | 0 | 0
Renewable, Intermittent [6] | 401.7 | 0
Solar | 401.7 | 0
Wind | 0 | 0
Coastal | 0 | 0
Panhandle | 0 | 0
Other | 0 | 0
Energy Storage | 1210.96 | 472.2744
Batteries | 1210.96 | 472.2744
Other | 0 | 0
Total Resources, MW | 179638.35 | 95336.7096
NOTES:
[1] Operational resources are those for which ERCOT has approved grid synchronization or full commercial operations. Unit level details for each resource category can be found in the Resource Details tab.
[2] Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. All gas-fired Private-Use Network (PUNs) units are reflected in the combined cycle fuel type row above. Generation and battery storage resources under extended outages with projected return dates longer than 3 years beyond the forecast month are excluded from the installed capacity totals.
[3] Expected Available Capacity for operational units accounts for thermal seasonal sustained capability ratings, hourly capacity contribution estimates for intermittent renewables, planned retirements, reductions due to co-located loads, unavailable Switchable Generation Resources (SWGRs), mothballed capacity, and expected Private Use Network (PUN) generator net exports to the grid. For planned projects, Expected Available Capacity is based on the maximum capacity reported by the developers and accounts for net changes due to repower or upgrade projects greater than one MW, and the established limits on the total MW Injection for designated Self-Limiting Facilities. Unit level details for each resource group above can be found in the Resource Details tab.
[4] Includes a small amount of hydro units that are considered intermittent resources (run-of-river Distributed Generation hydro units).
[5] Planned resources are those for which ERCOT expects to be approved for grid synchronization or has been assigned a “Model Ready Date" (for Small Generators) by the first of the month.
[6] Wind and solar values represent the 50th percentile values from hourly synthetic output profiles used in the PRRM. See the Background tab for more information.
Note on C9: R W MILLER STG 1, 75 MW, extended outage until 8/25/30. V H BRAUNIG STG 3 (RMR FROM 3/1/25 TO 3/1/27), 420 MW, Unavoidable Extension outage until 12/15/25 based on Unplanned Resource Outages Report.
Note on D9: R W MILLER STG 1, 75 MW, extended outage until 8/25/30. V H BRAUNIG STG 3 (RMR FROM 3/1/25 TO 3/1/27), 412 MW, Unavoidable Extension outage until 12/15/25 based on Unplanned Resource Outages Report.
Note on C11: SANDY CREEK U1, 1,008 MW, extended outage until 3/31/27
Note on D11: SANDY CREEK U1, 933 MW, extended outage until 3/31/27
Note on C13: Includes Life Cycle Power (LCP) Diesels Units listed in the ‘Reliability Must-Run (RMR) Capacity’ section of Resource Details tab.
Note on D13: Includes Life Cycle Power (LCP) Diesels Units listed in the ‘Reliability Must-Run (RMR) Capacity’ section of Resource Details tab.
Note on C24: CHISHOLM GRID, 102 MW, extended outage until 12/16/28
Note on D24: CHISHOLM GRID, 102 MW, extended outage until 12/16/28

## Low Wind-BESS Risk Profile
Combined Low Wind and Reduced Battery Energy Storage System Availability Risk Profile
Background and Methodology
To create a combined low wind and battery energy storage system (BESS) risk profile for Hour Ending 7 p.m. on the November peak load day, the model's hourly wind generation probability distributions are replaced with fixed values corresponding to a range of percentile values. The percentile values come from the base simulation for Hour Ending 7 p.m., and reflect the impact of the South Texas transmission interface constraint. To reflect low BESS availability, the amount of BESS capacity for Hour Ending 7 p.m. is reduced by 3,047 MW. This value reflects a 50% reduction relative to the amount expected under normal grid conditions for that hour. This reduction represents the lowered State of Charge (SOC) expected during a low capacity reserve day when BESS resources are deployed more often and for longer durations. (The lowest reserve day for November 2024 was used to determine the reduction amount.) All 10,000 model runs are restricted to the fixed wind generation and BESS availability values. No other changes have been made to the model, so probabilistic impacts of other variables such as loads, solar generation, and thermal unplanned outages are reflected in the simulation results.
Low Wind and Reduced Battery Energy Storage Availability Risk Profile Results for Hour Ending 7 p.m.
The following chart shows the relationship between EEA / EEA3 probabilities and wind output percentile values for two sensitivity scenarios: low wind output only (blue lines), and combined low wind and low BESS availability (orange lines). The percentiles represent the percentage of outcomes above the given values. For example, the 10th percentile indicates that 90% of all wind output values are above 6,648 MW. Note that the zero-percentile value reflects the minimum amount from the PRRM simulation for Hour Ending 8 p.m. (878 MW), rather than a zero MW outcome. The simulations indicate that reducing BESS availability by 3,047 MW for Hour Ending 7 p.m. increases the EEA probability by an average of 5.8 percentage points (or about 75%) for extremely low wind output levels. The EEA3 probability increases by an average of 4.0 percentage points (or about 77%). Extremely low wind output is defined here as an output no greater than the 5th percentile value, or 5,110 MW.

## Resource Details
Unit Capacities - November 2025
| UNIT NAME | INR | UNIT CODE | COUNTY | FUEL | ZONE | IN SERVICE | INSTALLED CAPACITY RATING (MW) | NOV. 2025 MORA
Operational Resources (Thermal)
4 | COMANCHE PEAK U1 |  | CPSES_UNIT1 | SOMERVELL | NUCLEAR | NORTH | 1990 | 1269 | 1222
5 | COMANCHE PEAK U2 |  | CPSES_UNIT2 | SOMERVELL | NUCLEAR | NORTH | 1993 | 1269 | 1209
6 | SOUTH TEXAS U1 |  | STP_STP_G1 | MATAGORDA | NUCLEAR | COASTAL | 1988 | 1365 | 1323.2
7 | SOUTH TEXAS U2 |  | STP_STP_G2 | MATAGORDA | NUCLEAR | COASTAL | 1989 | 1365 | 1310
8 | COLETO CREEK |  | COLETO_COLETOG1 | GOLIAD | COAL | SOUTH | 1980 | 655 | 655
9 | FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | FAYETTE | COAL | SOUTH | 1979 | 615 | 603
10 | FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | FAYETTE | COAL | SOUTH | 1980 | 615 | 603
11 | FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | FAYETTE | COAL | SOUTH | 1988 | 460 | 444
12 | J K SPRUCE U1 |  | CALAVERS_JKS1 | BEXAR | COAL | SOUTH | 1992 | 560 | 560
13 | J K SPRUCE U2 |  | CALAVERS_JKS2 | BEXAR | COAL | SOUTH | 2010 | 922 | 785
14 | LIMESTONE U1 |  | LEG_LEG_G1 | LIMESTONE | COAL | NORTH | 1985 | 893 | 831
15 | LIMESTONE U2 |  | LEG_LEG_G2 | LIMESTONE | COAL | NORTH | 1986 | 956.8 | 857
16 | MARTIN LAKE U1 |  | MLSES_UNIT1 | RUSK | COAL | NORTH | 1977 | 893 | 815
17 | MARTIN LAKE U2 |  | MLSES_UNIT2 | RUSK | COAL | NORTH | 1978 | 893 | 820
18 | MARTIN LAKE U3 |  | MLSES_UNIT3 | RUSK | COAL | NORTH | 1979 | 893 | 820
19 | OAK GROVE SES U1 |  | OGSES_UNIT1A | ROBERTSON | COAL | NORTH | 2010 | 916.8 | 855
20 | OAK GROVE SES U2 |  | OGSES_UNIT2 | ROBERTSON | COAL | NORTH | 2011 | 916.8 | 855
21 | SAN MIGUEL U1 |  | SANMIGL_G1 | ATASCOSA | COAL | SOUTH | 1982 | 430 | 391
22 | SANDY CREEK U1 |  | SCES_UNIT1 | MCLENNAN | COAL | NORTH | 2013 | 1008 | 932.6
23 | TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ROBERTSON | COAL | NORTH | 1990 | 174.6 | 155
24 | TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ROBERTSON | COAL | NORTH | 1991 | 174.6 | 155
25 | W A PARISH U5 |  | WAP_WAP_G5 | FORT BEND | COAL | HOUSTON | 1977 | 734.1 | 664
26 | W A PARISH U6 |  | WAP_WAP_G6 | FORT BEND | COAL | HOUSTON | 1978 | 734.1 | 663
27 | W A PARISH U7 |  | WAP_WAP_G7 | FORT BEND | COAL | HOUSTON | 1980 | 614.6 | 577
28 | W A PARISH U8 |  | WAP_WAP_G8 | FORT BEND | COAL | HOUSTON | 1982 | 653.99 | 610
29 | ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | BEXAR | GAS-CC | SOUTH | 2000 | 189 | 179.6
30 | ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | BEXAR | GAS-CC | SOUTH | 2000 | 189 | 179.6
31 | ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | BEXAR | GAS-CC | SOUTH | 2000 | 222 | 202.7
32 | ATKINS CTG 7 |  | ATKINS_ATKINSG7 | BRAZOS | GAS-GT | NORTH | 1973 | 21 | 19
33 | BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
34 | BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
35 | BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | NUECES | GAS-ST | COASTAL | 1974 | 352.8 | 292
36 | BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | NUECES | GAS-CC | COASTAL | 1976 | 351 | 322
37 | BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 178
38 | BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | BASTROP | GAS-CC | SOUTH | 2002 | 188 | 178
39 | BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | BASTROP | GAS-CC | SOUTH | 2002 | 242 | 236
40 | BEACHWOOD POWER STATION U1 |  | BCH_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
41 | BEACHWOOD POWER STATION U2 |  | BCH_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
42 | BEACHWOOD POWER STATION U3 |  | BCH_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
43 | BEACHWOOD POWER STATION U4 |  | BCH_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
44 | BEACHWOOD POWER STATION U5 |  | BCH_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
45 | BEACHWOOD POWER STATION U6 |  | BCH_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2022 | 60.5 | 45.5
46 | BEACHWOOD POWER STATION U7 |  | BCH_UNIT7 | BRAZORIA | GAS-GT | COASTAL | 2024 | 60.5 | 45.4
47 | BEACHWOOD POWER STATION U8 |  | BCH_UNIT8 | BRAZORIA | GAS-GT | COASTAL | 2024 | 60.5 | 45.4
48 | BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 160.5
49 | BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | BOSQUE | GAS-CC | NORTH | 2000 | 188.7 | 160.5
50 | BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | BOSQUE | GAS-CC | NORTH | 2001 | 188.7 | 159.5
51 | BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | BOSQUE | GAS-CC | NORTH | 2001 | 94.95 | 83.3
52 | BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | BOSQUE | GAS-CC | NORTH | 2009 | 254.15 | 221.5
53 | BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 168
54 | BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | FORT BEND | GAS-CC | HOUSTON | 2003 | 198.9 | 168
55 | BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | FORT BEND | GAS-CC | HOUSTON | 2003 | 275.57 | 270
56 | BROTMAN POWER STATION U1 |  | BTM_UNIT1 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
57 | BROTMAN POWER STATION U2 |  | BTM_UNIT2 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
58 | BROTMAN POWER STATION U3 |  | BTM_UNIT3 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
59 | BROTMAN POWER STATION U4 |  | BTM_UNIT4 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
60 | BROTMAN POWER STATION U5 |  | BTM_UNIT5 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
61 | BROTMAN POWER STATION U6 |  | BTM_UNIT6 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.5
62 | BROTMAN POWER STATION U7 |  | BTM_UNIT7 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 42.2
63 | BROTMAN POWER STATION U8 |  | BTM_UNIT8 | BRAZORIA | GAS-GT | COASTAL | 2023 | 60.5 | 45.2
64 | CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | HOWARD | GAS-GT | WEST | 1987 | 75 | 70
65 | CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | HOWARD | GAS-GT | WEST | 1987 | 75 | 70
66 | CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 46.5
67 | CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | CALHOUN | GAS-GT | COASTAL | 2017 | 60.5 | 46.5
68 | CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 46.5
69 | CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | HARRIS | GAS-GT | HOUSTON | 2017 | 60.5 | 46.5
70 | CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 158
71 | CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 158
72 | CEDAR BAYOU 4 STG |  | CBY4_ST04 | CHAMBERS | GAS-CC | HOUSTON | 2009 | 205 | 178
73 | CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | CHAMBERS | GAS-ST | HOUSTON | 1970 | 765 | 746
74 | CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | CHAMBERS | GAS-ST | HOUSTON | 1972 | 765 | 749
75 | COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | WHARTON | GAS-CC | SOUTH | 2007 | 87 | 84
76 | COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | WHARTON | GAS-CC | SOUTH | 2007 | 86.5 | 76.9
77 | COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | WHARTON | GAS-CC | SOUTH | 2008 | 86.7 | 84.4
78 | COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | WHARTON | GAS-CC | SOUTH | 2008 | 86.5 | 77.8
79 | COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | WHARTON | GAS-CC | SOUTH | 2007 | 107.2 | 103.7
80 | COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | WHARTON | GAS-CC | SOUTH | 2008 | 110.7 | 108
81 | COLORADO BEND II CTG 7 |  | CBECII_CT7 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 332.5
82 | COLORADO BEND II CTG 8 |  | CBECII_CT8 | WHARTON | GAS-CC | SOUTH | 2017 | 360.9 | 338.2
83 | COLORADO BEND II STG 9 |  | CBECII_STG9 | WHARTON | GAS-CC | SOUTH | 2017 | 508.5 | 482.8
84 | COLORADO BEND ENERGY CENTER CTG 11 |  | CBEC_GT11 | WHARTON | GAS-GT | SOUTH | 2023 | 41.65 | 39
85 | COLORADO BEND ENERGY CENTER CTG 12 |  | CBEC_GT12 | WHARTON | GAS-GT | SOUTH | 2023 | 41.65 | 39
86 | CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 168
87 | CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 163
88 | CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | HARRIS | GAS-CC | HOUSTON | 2002 | 192.1 | 163
89 | CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | HARRIS | GAS-CC | HOUSTON | 2002 | 150 | 128
90 | DANSBY CTG 2 |  | DANSBY_DANSBYG2 | BRAZOS | GAS-GT | NORTH | 2004 | 48 | 46.5
91 | DANSBY CTG 3 |  | DANSBY_DANSBYG3 | BRAZOS | GAS-GT | NORTH | 2010 | 50 | 48.5
92 | DANSBY STG 1 |  | DANSBY_DANSBYG1 | BRAZOS | GAS-ST | NORTH | 1978 | 120 | 108.5
93 | DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 49
94 | DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 49
95 | DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 49
96 | DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | TRAVIS | GAS-GT | SOUTH | 1989 | 56.7 | 49
97 | DECORDOVA CTG 1 |  | DCSES_CT10 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 72
98 | DECORDOVA CTG 2 |  | DCSES_CT20 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 71
99 | DECORDOVA CTG 3 |  | DCSES_CT30 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 70
100 | DECORDOVA CTG 4 |  | DCSES_CT40 | HOOD | GAS-GT | NORTH | 1990 | 89.48 | 71
101 | DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | HARRIS | GAS-CC | HOUSTON | 2002 | 203 | 194
102 | DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | HARRIS | GAS-CC | HOUSTON | 2002 | 215 | 206
103 | DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | HARRIS | GAS-CC | HOUSTON | 2002 | 203 | 194
104 | DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | HARRIS | GAS-CC | HOUSTON | 2002 | 215 | 206
105 | DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | HARRIS | GAS-CC | HOUSTON | 2014 | 199 | 179
106 | DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | HARRIS | GAS-CC | HOUSTON | 2002 | 290 | 290
107 | DENTON ENERGY CENTER IC A |  | DEC_AGR_A | DENTON | GAS-IC | NORTH | 2018 | 56.5 | 56.5
108 | DENTON ENERGY CENTER IC B |  | DEC_AGR_B | DENTON | GAS-IC | NORTH | 2018 | 56.5 | 56.5
109 | DENTON ENERGY CENTER IC C |  | DEC_AGR_C | DENTON | GAS-IC | NORTH | 2018 | 56.5 | 56.5
110 | DENTON ENERGY CENTER IC D |  | DEC_AGR_D | DENTON | GAS-IC | NORTH | 2018 | 56.5 | 56.5
111 | ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | ECTOR | GAS-GT | WEST | 2015 | 181 | 181
112 | ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | ECTOR | GAS-GT | WEST | 2015 | 181 | 181
113 | ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | ELLIS | GAS-CC | NORTH | 2002 | 260 | 212
114 | ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | ELLIS | GAS-CC | NORTH | 2002 | 140 | 117
115 | EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | HARRIS | GAS-GT | HOUSTON | 2009 | 40 | 38
116 | EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | HARRIS | GAS-GT | HOUSTON | 2009 | 40 | 38
117 | EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | HARRIS | GAS-GT | HOUSTON | 2009 | 40 | 38
118 | EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | HARRIS | GAS-GT | HOUSTON | 2009 | 40 | 38
119 | FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 173
120 | FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | LLANO | GAS-CC | SOUTH | 2014 | 185.3 | 173
121 | FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | LLANO | GAS-CC | SOUTH | 2014 | 204 | 186
122 | FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 169
123 | FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 161
124 | FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 161
125 | FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 169
126 | FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 161
127 | FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | KAUFMAN | GAS-CC | NORTH | 2003 | 196.7 | 161
128 | FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 409
129 | FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | KAUFMAN | GAS-CC | NORTH | 2003 | 422 | 409
130 | FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 155.2
131 | FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 155.2
132 | FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 155.4
133 | FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | FREESTONE | GAS-CC | NORTH | 2002 | 179.35 | 155.4
134 | FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 177.6
135 | FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | FREESTONE | GAS-CC | NORTH | 2002 | 190.74 | 176.5
136 | FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2018 | 129 | 119
137 | FRONTERA ENERGY CENTER CTG 1 |  | FRONT_EC_CT1 | HIDALGO | GAS-CC | SOUTH | 2023 | 177 | 177
138 | FRONTERA ENERGY CENTER CTG 2 |  | FRONT_EC_CT2 | HIDALGO | GAS-CC | SOUTH | 2023 | 177 | 177
139 | FRONTERA ENERGY CENTER STG |  | FRONT_EC_ST | HIDALGO | GAS-CC | SOUTH | 2023 | 184.5 | 184.5
140 | GRAHAM STG 1 |  | GRSES_UNIT1 | YOUNG | GAS-ST | WEST | 1960 | 239 | 239
141 | GRAHAM STG 2 |  | GRSES_UNIT2 | YOUNG | GAS-ST | WEST | 1969 | 390 | 390
142 | GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 58
143 | GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 55
144 | GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 55
145 | GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 48
146 | GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 63
147 | GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | HARRIS | GAS-GT | HOUSTON | 1976 | 72 | 57
148 | GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
149 | GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
150 | GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | HUNT | GAS-IC | NORTH | 2010 | 8.44 | 8.2
151 | GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 152
152 | GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 185 | 151
153 | GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | SAN PATRICIO | GAS-CC | COASTAL | 2000 | 100 | 75
154 | GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
155 | GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
156 | GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
157 | GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | GUADALUPE | GAS-CC | SOUTH | 2000 | 181 | 158
158 | GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 200
159 | GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | GUADALUPE | GAS-CC | SOUTH | 2000 | 204 | 200
160 | HANDLEY STG 3 |  | HLSES_UNIT3 | TARRANT | GAS-ST | NORTH | 1963 | 395 | 375
161 | HANDLEY STG 4 |  | HLSES_UNIT4 | TARRANT | GAS-ST | NORTH | 1976 | 435 | 435
162 | HANDLEY STG 5 |  | HLSES_UNIT5 | TARRANT | GAS-ST | NORTH | 1977 | 435 | 435
163 | HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 214
164 | HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | HAYS | GAS-CC | SOUTH | 2002 | 242 | 216
165 | HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 215
166 | HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | HAYS | GAS-CC | SOUTH | 2002 | 252 | 218
167 | HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 145
168 | HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | HIDALGO | GAS-CC | SOUTH | 2000 | 176.63 | 145
169 | HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | HIDALGO | GAS-CC | SOUTH | 2000 | 198.05 | 173
170 | JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150
171 | JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | JACK | GAS-CC | NORTH | 2006 | 198.9 | 150
172 | JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 167
173 | JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | JACK | GAS-CC | NORTH | 2011 | 198.9 | 167
174 | JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | JACK | GAS-CC | NORTH | 2006 | 320.6 | 285
175 | JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | JACK | GAS-CC | NORTH | 2011 | 320.6 | 295
176 | JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | JOHNSON | GAS-CC | NORTH | 1997 | 185 | 163
177 | JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | JOHNSON | GAS-CC | NORTH | 1997 | 107 | 106
178 | LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | DALLAS | GAS-ST | NORTH | 1970 | 397 | 392
179 | LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | DALLAS | GAS-ST | NORTH | 1973 | 531 | 523
180 | LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 161
181 | LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153
182 | LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 153
183 | LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | LAMAR | GAS-CC | NORTH | 2000 | 186 | 161
184 | LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
185 | LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | LAMAR | GAS-CC | NORTH | 2000 | 216 | 204
186 | LAREDO CTG 4 |  | LARDVFTN_G4 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 93
187 | LAREDO CTG 5 |  | LARDVFTN_G5 | WEBB | GAS-GT | SOUTH | 2008 | 98.5 | 90.2
188 | LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
189 | LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
190 | LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
191 | LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | BEXAR | GAS-GT | SOUTH | 2004 | 48 | 46
192 | LIGNIN (CHAMON 2) U1 |  | LIG_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 42.5
193 | LIGNIN (CHAMON 2) U2 |  | LIG_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2022 | 60.5 | 42.5
194 | LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 178
195 | LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | BASTROP | GAS-CC | SOUTH | 2001 | 202.5 | 172
196 | LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | BASTROP | GAS-CC | SOUTH | 2001 | 204 | 188
197 | MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 212.5
198 | MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | HIDALGO | GAS-CC | SOUTH | 2001 | 266.9 | 212.5
199 | MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | HIDALGO | GAS-CC | SOUTH | 2001 | 258.4 | 254.9
200 | MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | ELLIS | GAS-CC | NORTH | 2001 | 258 | 233
201 | MIDLOTHIAN ENERGY FACILITY CTG 2 |  | MDANP_CT2 | ELLIS | GAS-CC | NORTH | 2001 | 256 | 231
202 | MIDLOTHIAN ENERGY FACILITY CTG 3 |  | MDANP_CT3 | ELLIS | GAS-CC | NORTH | 2001 | 255 | 230
203 | MIDLOTHIAN ENERGY FACILITY CTG 4 |  | MDANP_CT4 | ELLIS | GAS-CC | NORTH | 2001 | 258 | 233
204 | MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | ELLIS | GAS-CC | NORTH | 2002 | 276 | 245
205 | MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | ELLIS | GAS-CC | NORTH | 2002 | 278 | 247
206 | MORGAN CREEK CTG 1 |  | MGSES_CT1 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 68
207 | MORGAN CREEK CTG 2 |  | MGSES_CT2 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
208 | MORGAN CREEK CTG 3 |  | MGSES_CT3 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 67
209 | MORGAN CREEK CTG 4 |  | MGSES_CT4 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 68
210 | MORGAN CREEK CTG 5 |  | MGSES_CT5 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 69
211 | MORGAN CREEK CTG 6 |  | MGSES_CT6 | MITCHELL | GAS-GT | WEST | 1988 | 89.4 | 69
212 | MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | DALLAS | GAS-ST | NORTH | 1956 | 122 | 122
213 | MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | DALLAS | GAS-ST | NORTH | 1958 | 118 | 118
214 | MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | DALLAS | GAS-ST | NORTH | 1967 | 568 | 568
215 | NUECES BAY CTG 8 |  | NUECES_B_NUECESG8 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
216 | NUECES BAY CTG 9 |  | NUECES_B_NUECESG9 | NUECES | GAS-CC | COASTAL | 2010 | 189.55 | 161
217 | NUECES BAY STG 7 |  | NUECES_B_NUECESG7 | NUECES | GAS-CC | COASTAL | 1972 | 351 | 322
218 | O W SOMMERS STG 1 |  | CALAVERS_OWS1 | BEXAR | GAS-ST | SOUTH | 1972 | 445 | 420
219 | O W SOMMERS STG 2 |  | CALAVERS_OWS2 | BEXAR | GAS-ST | SOUTH | 1974 | 435 | 410
220 | ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | ECTOR | GAS-CC | WEST | 2001 | 195.2 | 167.5
221 | ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | ECTOR | GAS-CC | WEST | 2001 | 189.1 | 159
222 | ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | ECTOR | GAS-CC | WEST | 2001 | 195.2 | 167.5
223 | ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | ECTOR | GAS-CC | WEST | 2001 | 189.1 | 159
224 | ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | ECTOR | GAS-CC | WEST | 2001 | 224 | 207.2
225 | ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | ECTOR | GAS-CC | WEST | 2001 | 224 | 207.2
226 | OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 46.5
227 | OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | VICTORIA | GAS-GT | SOUTH | 2022 | 60.5 | 46.5
228 | PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 217
229 | PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | GRAYSON | GAS-CC | NORTH | 2014 | 232 | 216
230 | PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | GRAYSON | GAS-CC | NORTH | 2014 | 353.1 | 307
231 | PANDA TEMPLE I POWER CTG 1 |  | PANDA_T1_TMPL1CT1 | BELL | GAS-CC | NORTH | 2014 | 232 | 219
232 | PANDA TEMPLE I POWER CTG 2 |  | PANDA_T1_TMPL1CT2 | BELL | GAS-CC | NORTH | 2014 | 232 | 206
233 | PANDA TEMPLE I POWER STG 1 |  | PANDA_T1_TMPL1ST1 | BELL | GAS-CC | NORTH | 2014 | 353.1 | 323
234 | PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.5
235 | PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | BELL | GAS-CC | NORTH | 2015 | 232 | 218.5
236 | PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | BELL | GAS-CC | NORTH | 2015 | 353.1 | 353.1
237 | PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 86
238 | PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | LAMAR | GAS-CC | NORTH | 1989 | 90.88 | 86
239 | PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | LAMAR | GAS-CC | NORTH | 1990 | 90 | 79
240 | PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 168
241 | PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | HARRIS | GAS-CC | HOUSTON | 2000 | 215.05 | 168
242 | PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | HARRIS | GAS-CC | HOUSTON | 2000 | 195.5 | 168
243 | PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
244 | PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
245 | PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
246 | PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | FRIO | GAS-IC | SOUTH | 2012 | 50.64 | 50.6
247 | PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | WARD | GAS-GT | WEST | 1988 | 89.4 | 64
248 | PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | WARD | GAS-GT | WEST | 1988 | 89.4 | 66
249 | PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | WARD | GAS-GT | WEST | 1988 | 89.4 | 65
250 | PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | WARD | GAS-GT | WEST | 1990 | 89.4 | 65
251 | PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | WARD | GAS-GT | WEST | 1990 | 89.4 | 66
252 | PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
253 | PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
254 | PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
255 | PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
256 | PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
257 | PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
258 | PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
259 | PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
260 | PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 61
261 | PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 62
262 | PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 52
263 | PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 56
264 | PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 56
265 | PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GALVESTON | GAS-GT | HOUSTON | 2018 | 65 | 55
266 | POWERLANE PLANT STG 1 (AS OF 10/1/2022, AVAILABLE 6/1 THROUGH 9/30) |  | STEAM1A_STEAM_1 | HUNT | GAS-ST | NORTH | 1966 | 18.75 | 0
267 | POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | HUNT | GAS-ST | NORTH | 1967 | 25 | 21.5
268 | POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | HUNT | GAS-ST | NORTH | 1978 | 43.2 | 36
269 | QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 81
270 | QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | ECTOR | GAS-CC | WEST | 2007 | 90.6 | 81
271 | QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 80
272 | QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | ECTOR | GAS-CC | WEST | 2008 | 90.6 | 80
273 | QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | ECTOR | GAS-CC | WEST | 2007 | 98.1 | 98
274 | QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | ECTOR | GAS-CC | WEST | 2008 | 98.1 | 98
275 | R W MILLER CTG 4 |  | MIL_MILLERG4 | PALO PINTO | GAS-GT | NORTH | 1994 | 116 | 104
276 | R W MILLER CTG 5 |  | MIL_MILLERG5 | PALO PINTO | GAS-GT | NORTH | 1994 | 116 | 104
277 | R W MILLER STG 1 |  | MIL_MILLERG1 | PALO PINTO | GAS-ST | NORTH | 1968 | 75 | 75
278 | R W MILLER STG 2 |  | MIL_MILLERG2 | PALO PINTO | GAS-ST | NORTH | 1972 | 120 | 120
279 | R W MILLER STG 3 |  | MIL_MILLERG3 | PALO PINTO | GAS-ST | NORTH | 1975 | 216.01 | 208
280 | RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | COLLIN | GAS-GT | NORTH | 2001 | 95 | 95
281 | RAY OLINGER STG 2 |  | OLINGR_OLING_2 | COLLIN | GAS-ST | NORTH | 1971 | 113.64 | 107
282 | RAY OLINGER STG 3 |  | OLINGR_OLING_3 | COLLIN | GAS-ST | NORTH | 1975 | 156.6 | 146
283 | RABBS POWER STATION U1 |  | RAB_UNIT1 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
284 | RABBS POWER STATION U2 |  | RAB_UNIT2 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
285 | RABBS POWER STATION U3 |  | RAB_UNIT3 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
286 | RABBS POWER STATION U4 |  | RAB_UNIT4 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
287 | RABBS POWER STATION U5 |  | RAB_UNIT5 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
288 | RABBS POWER STATION U6 |  | RAB_UNIT6 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
289 | RABBS POWER STATION U7 |  | RAB_UNIT7 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
290 | RABBS POWER STATION U8 |  | RAB_UNIT8 | FORT BEND | GAS-GT | HOUSTON | 2022 | 60.5 | 45.5
291 | REDGATE IC A |  | REDGATE_AGR_A | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
292 | REDGATE IC B |  | REDGATE_AGR_B | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
293 | REDGATE IC C |  | REDGATE_AGR_C | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
294 | REDGATE IC D |  | REDGATE_AGR_D | HIDALGO | GAS-IC | SOUTH | 2016 | 56.28 | 56.3
295 | REMY JADE POWER STATION U1 |  | JAD_UNIT1 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 45.4
296 | REMY JADE POWER STATION U2 |  | JAD_UNIT2 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 45.4
297 | REMY JADE POWER STATION U3 |  | JAD_UNIT3 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 45.4
298 | REMY JADE POWER STATION U4 |  | JAD_UNIT4 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 45.4
299 | REMY JADE POWER STATION U5 |  | JAD_UNIT5 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 45.4
300 | REMY JADE POWER STATION U6 |  | JAD_UNIT6 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 45.4
301 | REMY JADE POWER STATION U7 |  | JAD_UNIT7 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 45.4
302 | REMY JADE POWER STATION U8 |  | JAD_UNIT8 | HARRIS | GAS-GT | HOUSTON | 2024 | 60.5 | 45.4
303 | RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 203 | 172.8
304 | RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | GUADALUPE | GAS-CC | SOUTH | 2002 | 203 | 172.8
305 | RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | GUADALUPE | GAS-CC | SOUTH | 2002 | 203 | 172.8
306 | RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | GUADALUPE | GAS-CC | SOUTH | 2002 | 373.16 | 307
307 | SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
308 | SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 51
309 | SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | VICTORIA | GAS-CC | SOUTH | 2003 | 60.5 | 50
310 | SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | VICTORIA | GAS-CC | SOUTH | 2003 | 41.98 | 40
311 | SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 83
312 | SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | HARRIS | GAS-GT | HOUSTON | 1995 | 88.23 | 83
313 | SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
314 | SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
315 | SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
316 | SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | TRAVIS | GAS-GT | SOUTH | 2001 | 60.5 | 47
317 | SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | TRAVIS | GAS-CC | SOUTH | 2004 | 198.9 | 151
318 | SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47
319 | SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | TRAVIS | GAS-GT | SOUTH | 2010 | 60.5 | 47
320 | SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | TRAVIS | GAS-CC | SOUTH | 2004 | 191 | 148
321 | SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | CAMERON | GAS-GT | COASTAL | 2004 | 60.5 | 46
322 | SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CAMERON | GAS-CC | COASTAL | 1996 | 50 | 38
323 | SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CAMERON | GAS-CC | COASTAL | 1962 | 25 | 20
324 | SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | BASTROP | GAS-ST | SOUTH | 1965 | 136 | 130
325 | SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | BASTROP | GAS-ST | SOUTH | 1968 | 136 | 135
326 | SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | BASTROP | GAS-ST | SOUTH | 1972 | 351 | 336
327 | SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | COLORADO | GAS-IC | SOUTH | 2016 | 26.7 | 26.7
328 | SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | COLORADO | GAS-IC | SOUTH | 2016 | 26.7 | 26.7
329 | SPENCER STG U4 (AS OF 10/24/2022, AVAILABLE 3/1 THROUGH 11/30) |  | SPNCER_SPNCE_4 | DENTON | GAS-ST | NORTH | 1966 | 61 | 57
330 | SPENCER STG U5 (AS OF 10/24/2022, AVAILABLE 3/1 THROUGH 11/30) |  | SPNCER_SPNCE_5 | DENTON | GAS-ST | NORTH | 1973 | 65 | 61
331 | STRYKER CREEK STG 1 |  | SCSES_UNIT1A | CHEROKEE | GAS-ST | NORTH | 1958 | 177 | 167
332 | STRYKER CREEK STG 2 |  | SCSES_UNIT2 | CHEROKEE | GAS-ST | NORTH | 1965 | 502 | 502
333 | T H WHARTON CTG 1 |  | THW_THWGT_1 | HARRIS | GAS-GT | HOUSTON | 1967 | 16.32 | 14
334 | T H WHARTON POWER CTG 31 |  | THW_THWGT31 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 56
335 | T H WHARTON POWER CTG 32 |  | THW_THWGT32 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 56
336 | T H WHARTON POWER CTG 33 |  | THW_THWGT33 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 56
337 | T H WHARTON POWER CTG 34 |  | THW_THWGT34 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 56
338 | T H WHARTON POWER CTG 41 |  | THW_THWGT41 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 56
339 | T H WHARTON POWER CTG 42 |  | THW_THWGT42 | HARRIS | GAS-CC | HOUSTON | 1972 | 69 | 56
340 | T H WHARTON POWER CTG 43 |  | THW_THWGT43 | HARRIS | GAS-CC | HOUSTON | 1974 | 69 | 56
341 | T H WHARTON POWER CTG 44 |  | THW_THWGT44 | HARRIS | GAS-CC | HOUSTON | 1974 | 69 | 56
342 | T H WHARTON POWER CTG 51 |  | THW_THWGT51 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
343 | T H WHARTON POWER CTG 52 |  | THW_THWGT52 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
344 | T H WHARTON POWER CTG 53 |  | THW_THWGT53 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
345 | T H WHARTON POWER CTG 54 |  | THW_THWGT54 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
346 | T H WHARTON POWER CTG 55 |  | THW_THWGT55 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
347 | T H WHARTON POWER CTG 56 |  | THW_THWGT56 | HARRIS | GAS-GT | HOUSTON | 1975 | 85 | 57
348 | T H WHARTON POWER STG 3 |  | THW_THWST_3 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110
349 | T H WHARTON POWER STG 4 |  | THW_THWST_4 | HARRIS | GAS-CC | HOUSTON | 1974 | 113.1 | 110
350 | TEXAS CITY POWER CTG A |  | TXCTY_CTA | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 99.1
351 | TEXAS CITY POWER CTG B |  | TXCTY_CTB | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 99.1
352 | TEXAS CITY POWER CTG C |  | TXCTY_CTC | GALVESTON | GAS-CC | HOUSTON | 2000 | 129.06 | 99.1
353 | TEXAS CITY POWER STG |  | TXCTY_ST | GALVESTON | GAS-CC | HOUSTON | 2000 | 143.65 | 131.5
354 | TEXAS GULF SULPHUR CTG 1 |  | TGS_GT01 | WHARTON | GAS-GT | SOUTH | 1985 | 94 | 90
355 | TRINIDAD STG 6 |  | TRSES_UNIT6 | HENDERSON | GAS-ST | NORTH | 1965 | 239 | 235
356 | TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
357 | TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
358 | TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
359 | TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
360 | TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
361 | TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
362 | TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
363 | TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
364 | TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
365 | TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GALVESTON | GAS-GT | HOUSTON | 2021 | 60.5 | 45.4
366 | V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
367 | V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
368 | V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 48
369 | V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | BEXAR | GAS-GT | SOUTH | 2009 | 64.5 | 47
370 | VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 46.5
371 | VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2020 | 60.5 | 46.5
372 | VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 46.5
373 | VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | VICTORIA | GAS-GT | SOUTH | 2019 | 60.5 | 46.5
374 | VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | VICTORIA | GAS-CC | SOUTH | 2009 | 196.86 | 171
375 | VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | VICTORIA | GAS-CC | SOUTH | 2009 | 180.2 | 132
376 | W A PARISH CTG 1 |  | WAP_WAPGT_1 | FORT BEND | GAS-GT | HOUSTON | 1967 | 16.32 | 13
377 | W A PARISH STG 1 |  | WAP_WAP_G1 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
378 | W A PARISH STG 2 |  | WAP_WAP_G2 | FORT BEND | GAS-ST | HOUSTON | 1958 | 187.85 | 169
379 | W A PARISH STG 3 |  | WAP_WAP_G3 | FORT BEND | GAS-ST | HOUSTON | 1961 | 299.2 | 246
380 | W A PARISH STG 4 |  | WAP_WAP_G4 | FORT BEND | GAS-ST | HOUSTON | 1968 | 580.5 | 536
381 | WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | WICHITA | GAS-CC | WEST | 1987 | 20 | 19
382 | WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | WICHITA | GAS-CC | WEST | 1987 | 20 | 19
383 | WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | WICHITA | GAS-CC | WEST | 1987 | 20 | 19
384 | WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
385 | WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
386 | WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
387 | WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | FAYETTE | GAS-GT | SOUTH | 2009 | 60.5 | 44
388 | WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | WISE | GAS-CC | NORTH | 2004 | 275 | 245.4
389 | WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | WISE | GAS-CC | NORTH | 2004 | 275 | 245.4
390 | WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | WISE | GAS-CC | NORTH | 2004 | 298 | 298
391 | WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 245.3
392 | WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | HOOD | GAS-CC | NORTH | 2002 | 264.5 | 245.3
393 | WOLF HOLLOW POWER STG |  | WHCCS_STG | HOOD | GAS-CC | NORTH | 2002 | 300 | 270
394 | WOLF HOLLOW 2 CTG 4 |  | WHCCS2_CT4 | HOOD | GAS-CC | NORTH | 2017 | 360 | 330.8
395 | WOLF HOLLOW 2 CTG 5 |  | WHCCS2_CT5 | HOOD | GAS-CC | NORTH | 2017 | 360 | 331.3
396 | WOLF HOLLOW 2 STG 6 |  | WHCCS2_STG6 | HOOD | GAS-CC | NORTH | 2017 | 511.2 | 458.8
397 | NACOGDOCHES POWER |  | NACPW_UNIT1 | NACOGDOCHES | BIOMASS | NORTH | 2012 | 116.45 | 105
398 | FARMERS BRANCH LANDFILL GAS TO ENERGY |  | HBR_2UNITS | DENTON | BIOMASS | NORTH | 2011 | 3.2 | 3.2
399 | GRAND PRAIRIE LFG |  | TRIRA_1UNIT | DALLAS | BIOMASS | NORTH | 2015 | 4 | 4
400 | NELSON GARDENS LFG |  | 78252_4UNITS | BEXAR | BIOMASS | SOUTH | 2013 | 4.2 | 4.2
401 | WM RENEWABLE-AUSTIN LFG |  | SPRIN_4UNITS | TRAVIS | BIOMASS | SOUTH | 2007 | 6.4 | 6.4
402 | WM RENEWABLE-MESQUITE CREEK LFG |  | FREIH_2UNITS | COMAL | BIOMASS | SOUTH | 2011 | 3.2 | 3.2
403 | WM RENEWABLE-WESTSIDE LFG |  | WSTHL_3UNITS | PARKER | BIOMASS | NORTH | 2010 | 4.8 | 4.8
404 | Operational Capacity Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 74497.61 | 67114.2
405
406 | Operational Resources - Synchronized but not Approved for Commercial Operations (Thermal)
407 | OLNEY AGR1 | 24INR0647 | OLNEYTN_AGR1 | YOUNG | DIESEL | WEST | 2025 | 9.95 | 10
408 | TIMMERMAN POWER PLANT U1 | 25INR0223 | TIMPP_AGR1 | CALDWELL | GAS-IC | SOUTH | 2025 | 37.68 | 36
409 | TIMMERMAN POWER PLANT U2 | 25INR0223 | TIMPP_AGR2 | CALDWELL | GAS-IC | SOUTH | 2025 | 56.52 | 54
410 | TIMMERMAN POWER PLANT U3 | 25INR0223 | TIMPP_AGR3 | CALDWELL | GAS-IC | SOUTH | 2025 | 37.68 | 36
411 | TIMMERMAN POWER PLANT U4 | 25INR0223 | TIMPP_AGR4 | CALDWELL | GAS-IC | SOUTH | 2025 | 56.52 | 54
412 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Nuclear, Coal, Gas, Biomass) | [6 empty] | 198.35 | 190
413
414 | Operational Capacity Thermal Unavailable due to Extended Outage or Derate |  | THERMAL_UNAVAIL |  |  |  |  | -1503 | -1419.6
415 | Operational Capacity Thermal Total |  | THERMAL_OPERATIONAL |  |  |  |  | 73192.96 | 65884.6
416
417 | Operational Resources (Hydro)
418 | AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9
419 | AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | VAL VERDE | HYDRO | WEST | 1983 | 37.9 | 37.9
420 | AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 8
421 | AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | TRAVIS | HYDRO | SOUTH | 1940 | 9 | 9
422 | BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
423 | BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | LLANO | HYDRO | SOUTH | 1938 | 18.3 | 16
424 | BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | LLANO | HYDRO | SOUTH | 1950 | 18.3 | 17
425 | DENISON DAM 1 |  | DNDAM_DENISOG1 | GRAYSON | HYDRO | NORTH | 1944 | 50.8 | 49.5
426 | DENISON DAM 2 |  | DNDAM_DENISOG2 | GRAYSON | HYDRO | NORTH | 1948 | 50.8 | 49.5
427 | EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | MAVERICK | HYDRO | SOUTH | 1928 | 9.6 | 9.6
428 | FALCON HYDRO 1 |  | FALCON_FALCONG1 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
429 | FALCON HYDRO 2 |  | FALCON_FALCONG2 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
430 | FALCON HYDRO 3 |  | FALCON_FALCONG3 | STARR | HYDRO | SOUTH | 1954 | 12 | 12
431 | GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29
432 | GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | BURNET | HYDRO | SOUTH | 1951 | 29 | 29
433 | GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | COMAL | HYDRO | SOUTH | 1928 | 6 | 6
434 | INKS HYDRO 1 |  | INKSDA_INKS_G1 | LLANO | HYDRO | SOUTH | 1938 | 15 | 14
435 | MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | BURNET | HYDRO | SOUTH | 1951 | 21 | 21
436 | MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | BURNET | HYDRO | SOUTH | 1951 | 20 | 20
437 | MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
438 | MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
439 | MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | TRAVIS | HYDRO | SOUTH | 1941 | 36 | 36
440 | WHITNEY DAM HYDRO |  | WND_WHITNEY1 | BOSQUE | HYDRO | NORTH | 1953 | 22 | 22
441 | WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | BOSQUE | HYDRO | NORTH | 1953 | 22 | 22
442 | Operational Capacity Total (Hydro) | [6 empty] | 567.9 | 557.4
443 | Hydro Capacity Contribution (Top 20 Hours) |  | HYDRO_CAP_CONT |  | HYDRO |  |  | 567.9 | 384.8658
444
445 | Operational Hydro Resources, Settlement Only Distributed Generators (SODGs)
446 | GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | MCQUE_5UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 7.7 | 7.7
447 | GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | SCHUM_2UNITS | GUADALUPE | HYDRO | SOUTH | 1928 | 3.6 | 3.6
448 | Operational Hydro Resources Total, Settlement Only Distributed Generators (SODGs) | [6 empty] | 11.3 | 11.3
449 | Hydro SODG Capacity Contribution (Highest 20 Peak Load Hours) |  | HYDRO_CAP_CONT
450
451 | Operational Capacity Hydroelectric Unavailable due to Extended Outage or Derate |  | HYDRO_UNAVAIL |  | HYDRO |  |  | 0 | 0
452 | Operational Capacity Hydroelectric Total |  | HYDRO_OPERATIONAL |  | HYDRO |  |  | 579.2 | 396.1658
453
454 | Operational Resources (Switchable)
455 | ANTELOPE IC 1 |  | AEEC_ANTLP_1 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
456 | ANTELOPE IC 2 |  | AEEC_ANTLP_2 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
457 | ANTELOPE IC 3 |  | AEEC_ANTLP_3 | HALE | GAS-IC | PANHANDLE | 2016 | 56.04 | 56
458 | ELK STATION CTG 1 |  | AEEC_ELK_1 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 195
459 | ELK STATION CTG 2 |  | AEEC_ELK_2 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 195
460 | ELK STATION CTG 3 |  | AEEC_ELK_3 | HALE | GAS-GT | PANHANDLE | 2016 | 202 | 195
461 | TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
462 | TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
463 | TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | GRIMES | GAS-CC | NORTH | 2000 | 185 | 180
464 | TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | GRIMES | GAS-CC | NORTH | 2000 | 400 | 400
465 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | RUSK | GAS-CC | NORTH | 2001 | 179 | 162
466 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | RUSK | GAS-CC | NORTH | 2001 | 179 | 179
467 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | RUSK | GAS-CC | NORTH | 2001 | 179 | 178
468 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | RUSK | GAS-CC | NORTH | 2001 | 400 | 389
469 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 154
470 | TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 151
471 | TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | FANNIN | GAS-CC | NORTH | 2003 | 330 | 312
472 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 149
473 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | FANNIN | GAS-CC | NORTH | 2003 | 185 | 150
474 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | FANNIN | GAS-CC | NORTH | 2003 | 330 | 317
475 | Switchable Capacity Total | [6 empty] | 4066.12 | 3834
476
477 | Switchable Capacity Unavailable to ERCOT
478 | ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2016 | -56.04 | -56
479 | ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2016 | -56.04 | -56
480 | ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | HALE | GAS-IC | PANHANDLE | 2016 | -56.04 | -56
481 | ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2016 | -202 | -195
482 | ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2016 | -202 | -195
483 | ELK STATION CTG 3 |  | AEEC_ELK_3_UNAVAIL | HALE | GAS-GT | PANHANDLE | 2016 | -202 | -195
484 | TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1_UNAVAIL | RUSK | GAS-CC | NORTH | 2001 | 0 | 0
485 | TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2_UNAVAIL | RUSK | GAS-CC | NORTH | 2001 | -179 | -179
486 | TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3_UNAVAIL | RUSK | GAS-CC | NORTH | 2001 | 0 | 0
487 | TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4_UNAVAIL | RUSK | GAS-CC | NORTH | 2001 | 0 | 0
488 | TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101_UNAVAIL | FANNIN | GAS-CC | NORTH | 2003 | -185 | -149
489 | TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201_UNAVAIL | FANNIN | GAS-CC | NORTH | 2003 | 0 | 0
490 | TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST_UNAVAIL | FANNIN | GAS-CC | NORTH | 2003 | 0 | 0
491 | TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101_UNAVAIL | FANNIN | GAS-CC | NORTH | 2003 | 0 | 0
492 | Switchable Capacity Unavailable to ERCOT Total | [6 empty] | -1138.12 | -1081
493
494 | Available Mothball Capacity based on Owner's Return Probability |  | MOTH_AVAIL |  |  |  |  | 0 | 0
495
496 | Private-Use Network Capacity Contribution (PRRM 50th Pctl. Result) |  | PUN_CAP_CONT |  | GAS-CC |  |  | 10104 | 2034
497
498 | Operational Resources (Wind)
499 | AGUAYO WIND U1 |  | AGUAYO_UNIT1 | MILLS | WIND-O | NORTH | 2023 | 193.5 | 192.9
500 | AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | FISHER | WIND-O | WEST | 2021 | 36.7 | 36.7
501 | AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | FISHER | WIND-O | WEST | 2021 | 35.8 | 35.8
502 | AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | FISHER | WIND-O | WEST | 2021 | 177.7 | 177.7
503 | ANACACHO WIND |  | ANACACHO_ANA | KINNEY | WIND-O | SOUTH | 2012 | 99.83 | 99.8
504 | ANCHOR WIND U2 |  | ANCHOR_WIND2 | CALLAHAN | WIND-O | WEST | 2024 | 98.9 | 98.9
505 | ANCHOR WIND U3 |  | ANCHOR_WIND3 | CALLAHAN | WIND-O | WEST | 2024 | 90 | 90
506 | ANCHOR WIND U4 |  | ANCHOR_WIND4 | CALLAHAN | WIND-O | WEST | 2024 | 38.7 | 38.7
507 | ANCHOR WIND U5 |  | ANCHOR_WIND5 | CALLAHAN | WIND-O | WEST | 2024 | 19.3 | 19.3
508 | APOGEE WIND U1 |  | APOGEE_UNIT1 | THROCKMORTON | WIND-O | WEST | 2024 | 25 | 25
509 | APOGEE WIND U2 |  | APOGEE_UNIT2 | THROCKMORTON | WIND-O | WEST | 2024 | 14 | 14
510 | APOGEE WIND U3 |  | APOGEE_UNIT3 | THROCKMORTON | WIND-O | WEST | 2024 | 30.2 | 30.2
511 | APOGEE WIND U4 |  | APOGEE_UNIT4 | THROCKMORTON | WIND-O | WEST | 2024 | 115 | 115
512 | APOGEE WIND U5 |  | APOGEE_UNIT5 | THROCKMORTON | WIND-O | WEST | 2024 | 110 | 110
513 | APOGEE WIND U6 |  | APOGEE_UNIT6 | THROCKMORTON | WIND-O | WEST | 2024 | 24 | 24
514 | APOGEE WIND U7 |  | APOGEE_UNIT7 | THROCKMORTON | WIND-O | WEST | 2024 | 75 | 75
515 | APPALOOSA RUN WIND U1 |  | APPALOSA_UNIT1 | UPTON | WIND-O | WEST | 2024 | 157.9 | 157.9
516 | APPALOOSA RUN WIND U2 |  | APPALOSA_UNIT2 | UPTON | WIND-O | WEST | 2024 | 13.9 | 13.9
517 | AQUILLA LAKE WIND U1 |  | AQUILLA_U1_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 13.9 | 13.9
518 | AQUILLA LAKE WIND U2 |  | AQUILLA_U1_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 135.4 | 135.4
519 | AQUILLA LAKE 2 WIND U1 |  | AQUILLA_U2_23 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 7 | 7
520 | AQUILLA LAKE 2 WIND U2 |  | AQUILLA_U2_28 | HILL & LIMESTONE | WIND-O | NORTH | 2023 | 143.8 | 143.8
521 | AVIATOR WIND U1 |  | AVIATOR_UNIT1 | COKE | WIND-O | WEST | 2021 | 180.12 | 180.1
522 | AVIATOR WIND U2 |  | AVIATOR_UNIT2 | COKE | WIND-O | WEST | 2021 | 145.64 | 145.6
523 | AVIATOR WIND U3 |  | DEWOLF_UNIT1 | COKE | WIND-O | WEST | 2021 | 199.26 | 199.3
524 | BLACKJACK CREEK WIND U1 |  | BLACKJAK_UNIT1 | BEE | WIND-O | SOUTH | 2023 | 120 | 120
525 | BLACKJACK CREEK WIND U2 |  | BLACKJAK_UNIT2 | BEE | WIND-O | SOUTH | 2023 | 120 | 120
526 | BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | KENEDY | WIND-C | COASTAL | 2016 | 100 | 100
527 | BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | KENEDY | WIND-C | COASTAL | 2016 | 102 | 102
528 | BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | ANDREWS | WIND-O | WEST | 2021 | 90.2 | 90.2
529 | BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | ANDREWS | WIND-O | WEST | 2021 | 70.5 | 70.5
530 | BARTON CHAPEL WIND |  | BRTSW_BCW1 | JACK | WIND-O | NORTH | 2007 | 120 | 120
531 | BLUE SUMMIT WIND 1 A |  | BLSUMMIT_BLSMT1_5 | WILBARGER | WIND-O | WEST | 2013 | 132.84 | 132.8
532 | BLUE SUMMIT WIND 1 B |  | BLSUMMIT_BLSMT1_6 | WILBARGER | WIND-O | WEST | 2013 | 6.96 | 6.9
533 | BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WILBARGER | WIND-O | WEST | 2020 | 92.5 | 92.5
534 | BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WILBARGER | WIND-O | WEST | 2020 | 6.9 | 6.9
535 | BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WILBARGER | WIND-O | WEST | 2020 | 13.7 | 13.4
536 | BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WILBARGER | WIND-O | WEST | 2020 | 186.5 | 182.4
537 | BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | ARCHER | WIND-O | WEST | 2020 | 162 | 162
538 | BRISCOE WIND |  | BRISCOE_WIND | BRISCOE | WIND-P | PANHANDLE | 2015 | 149.85 | 149.8
539 | BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WILLACY | WIND-C | COASTAL | 2017 | 120 | 120
540 | BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WILLACY | WIND-C | COASTAL | 2017 | 108 | 108
541 | BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | ERATH | WIND-O | NORTH | 2017 | 44.9 | 44.9
542 | BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | ERATH | WIND-O | NORTH | 2017 | 55.7 | 55.7
543 | BUFFALO GAP WIND 1 |  | BUFF_GAP_UNIT1 | TAYLOR | WIND-O | WEST | 2006 | 120.6 | 120.6
544 | BUFFALO GAP WIND 2_1 |  | BUFF_GAP_UNIT2_1 | TAYLOR | WIND-O | WEST | 2007 | 115.5 | 115.5
545 | BUFFALO GAP WIND 2_2 |  | BUFF_GAP_UNIT2_2 | TAYLOR | WIND-O | WEST | 2007 | 117 | 117
546 | BUFFALO GAP WIND 3 |  | BUFF_GAP_UNIT3 | TAYLOR | WIND-O | WEST | 2008 | 170.2 | 170.2
547 | BULL CREEK WIND U1 |  | BULLCRK_WND1 | BORDEN | WIND-O | WEST | 2009 | 89 | 88
548 | BULL CREEK WIND U2 |  | BULLCRK_WND2 | BORDEN | WIND-O | WEST | 2009 | 91 | 90
549 | CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | STARR | WIND-O | SOUTH | 2019 | 115.2 | 115.2
550 | CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | STARR | WIND-O | SOUTH | 2019 | 122.4 | 122.4
551 | CACTUS FLATS WIND U1 |  | CFLATS_U1 | CONCHO | WIND-O | WEST | 2022 | 148.4 | 148.4
552 | CALLAHAN WIND |  | CALLAHAN_WND1 | CALLAHAN | WIND-O | WEST | 2004 | 123.1 | 123.1
553 | CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2016 | 165 | 165
554 | CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | SCURRY | WIND-O | WEST | 2007 | 134.42 | 130.5
555 | CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | SCURRY | WIND-O | WEST | 2007 | 123.6 | 120
556 | CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | OLDHAM | WIND-P | PANHANDLE | 2019 | 210.1 | 210.1
557 | CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | STERLING | WIND-O | WEST | 2007 | 231.7 | 231.7
558 | CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR2 | STERLING | WIND-O | WEST | 2007 | 149.5 | 149.5
559 | CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR3 | STERLING | WIND-O | WEST | 2008 | 200.9 | 200.9
560 | CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | STERLING | WIND-O | WEST | 2008 | 121.5 | 121.5
561 | CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WEBB | WIND-O | SOUTH | 2010 | 79.42 | 77.7
562 | CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WEBB | WIND-O | SOUTH | 2010 | 78.04 | 76.4
563 | CHALUPA WIND |  | CHALUPA_UNIT1 | CAMERON | WIND-C | COASTAL | 2021 | 173.25 | 173.3
564 | CHAMPION WIND |  | CHAMPION_UNIT1 | NOLAN | WIND-O | WEST | 2008 | 97.51 | 95.4
565 | CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | NUECES | WIND-C | COASTAL | 2017 | 150.6 | 150.6
566 | CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | NUECES | WIND-C | COASTAL | 2017 | 98.4 | 98.4
567 | COTTON PLAINS WIND |  | COTPLNS_COTTONPL | FLOYD | WIND-P | PANHANDLE | 2017 | 50.4 | 50.4
568 | CRANELL WIND |  | CRANELL_UNIT1 | REFUGIO | WIND-C | COASTAL | 2022 | 220 | 220
569 | CRAWFISH U1 |  | CRAWFISH_UNIT1 | WHARTON | WIND-O | SOUTH | 2025 | 163.2 | 159
570 | DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
571 | DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 126.5 | 126.5
572 | DESERT SKY WIND 1 A |  | DSKYWND1_UNIT_1A | PECOS | WIND-O | WEST | 2022 | 65.79 | 53.1
573 | DESERT SKY WIND 1 B |  | DSKYWND2_UNIT_2A | PECOS | WIND-O | WEST | 2022 | 65.79 | 50.4
574 | DESERT SKY WIND 2 A |  | DSKYWND1_UNIT_1B | PECOS | WIND-O | WEST | 2022 | 23.93 | 18.7
575 | DESERT SKY WIND 2 B |  | DSKYWND2_UNIT_2B | PECOS | WIND-O | WEST | 2022 | 14.74 | 8
576 | DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
577 | DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | CARSON | WIND-P | PANHANDLE | 2016 | 100.24 | 100.2
578 | EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 101.2 | 98
579 | EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 99 | 96
580 | ELBOW CREEK WIND |  | ELB_ELBCREEK | HOWARD | WIND-O | WEST | 2008 | 121.9 | 121.9
581 | ELECTRA WIND 1 |  | DIGBY_UNIT1 | WILBARGER | WIND-O | WEST | 2016 | 101.31 | 98.9
582 | ELECTRA WIND 2 |  | DIGBY_UNIT2 | WILBARGER | WIND-O | WEST | 2016 | 134.29 | 131.1
583 | EL ALGODON ALTO W U1 |  | ALGODON_UNIT1 | WILLACY | WIND-C | COASTAL | 2022 | 171.6 | 171.6
584 | EL ALGODON ALTO W U2 |  | ALGODON_UNIT2 | WILLACY | WIND-C | COASTAL | 2022 | 28.6 | 28.6
585 | ESPIRITU WIND |  | CHALUPA_UNIT2 | CAMERON | WIND-C | COASTAL | 2021 | 25.2 | 25.2
586 | FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | RANDALL | WIND-P | PANHANDLE | 2017 | 163.2 | 163.2
587 | FLAT TOP WIND I |  | FTWIND_UNIT_1 | MILLS | WIND-O | NORTH | 2018 | 200 | 200
588 | FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | SCURRY | WIND-O | WEST | 2017 | 79.8 | 79.8
589 | FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | SCURRY | WIND-O | WEST | 2017 | 75.6 | 75.6
590 | FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | FOARD | WIND-O | WEST | 2019 | 186.5 | 186.5
591 | FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | FOARD | WIND-O | WEST | 2019 | 163.8 | 163.8
592 | FOREST CREEK WIND |  | MCDLD_FCW1 | GLASSCOCK | WIND-O | WEST | 2007 | 125.19 | 123.2
593 | GOAT WIND |  | GOAT_GOATWIND | STERLING | WIND-O | WEST | 2008 | 80 | 80
594 | GOAT WIND 2 |  | GOAT_GOATWIN2 | STERLING | WIND-O | WEST | 2010 | 69.6 | 69.6
595 | GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | MILLS | WIND-O | NORTH | 2014 | 148.6 | 148.6
596 | GOODNIGHT WIND U1 |  | GOODNIT1_UNIT1 | ARMSTRONG | WIND-P | PANHANDLE | 2024 | 121 | 121
597 | GOODNIGHT WIND U2 |  | GOODNIT1_UNIT2 | ARMSTRONG | WIND-P | PANHANDLE | 2024 | 137.1 | 137.1
598 | GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | BORDEN | WIND-O | WEST | 2020 | 82 | 82
599 | GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | BORDEN | WIND-O | WEST | 2020 | 76 | 76
600 | GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | CARSON | WIND-P | PANHANDLE | 2014 | 107.4 | 107.4
601 | GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | CARSON | WIND-P | PANHANDLE | 2014 | 103.8 | 103.8
602 | GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_BRAZ_WND1 | SCURRY | WIND-O | WEST | 2023 | 120 | 120
603 | GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_BRAZ_WND2 | SCURRY | WIND-O | WEST | 2023 | 62.4 | 62.4
604 | GREEN PASTURES WIND I |  | GPASTURE_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
605 | GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | KNOX | WIND-O | WEST | 2021 | 98.7 | 98.7
606 | GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | KNOX | WIND-O | WEST | 2021 | 126.9 | 126.9
607 | GULF WIND I |  | TGW_T1 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
608 | GULF WIND II |  | TGW_T2 | KENEDY | WIND-C | COASTAL | 2021 | 141.6 | 141.6
609 | GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | HOWARD | WIND-O | WEST | 2016 | 119.93 | 119.9
610 | HACKBERRY WIND |  | HWF_HWFG1 | SHACKELFORD | WIND-O | WEST | 2008 | 165.6 | 163.5
611 | HEREFORD WIND G |  | HRFDWIND_WIND_G | DEAF SMITH | WIND-P | PANHANDLE | 2014 | 99.9 | 99.9
612 | HEREFORD WIND V |  | HRFDWIND_WIND_V | DEAF SMITH | WIND-P | PANHANDLE | 2014 | 100 | 100
613 | HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | REAGAN | WIND-O | WEST | 2018 | 152.5 | 152.5
614 | HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | REAGAN | WIND-O | WEST | 2018 | 147.5 | 147.5
615 | HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | HIDALGO | WIND-O | SOUTH | 2016 | 52 | 52
616 | HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | HIDALGO | WIND-O | SOUTH | 2016 | 98 | 98
617 | HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | HIDALGO | WIND-O | SOUTH | 2016 | 100 | 100
618 | HIDALGO II WIND |  | MIRASOLE_MIR13 | HIDALGO | WIND-O | SOUTH | 2021 | 50.4 | 50.4
619 | HIGH LONESOME W 1A |  | HI_LONE_WGR1A | CROCKETT | WIND-O | WEST | 2021 | 46 | 46
620 | HIGH LONESOME W 1B |  | HI_LONE_WGR1B | CROCKETT | WIND-O | WEST | 2021 | 52 | 52
621 | HIGH LONESOME W 1C |  | HI_LONE_WGR1C | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
622 | HIGH LONESOME W 2 |  | HI_LONE_WGR2 | CROCKETT | WIND-O | WEST | 2021 | 122.5 | 122.5
623 | HIGH LONESOME W 2A |  | HI_LONE_WGR2A | CROCKETT | WIND-O | WEST | 2021 | 25.3 | 25.3
624 | HIGH LONESOME W 3 |  | HI_LONE_WGR3 | CROCKETT | WIND-O | WEST | 2021 | 127.6 | 127.6
625 | HIGH LONESOME W 4 |  | HI_LONE_WGR4 | CROCKETT | WIND-O | WEST | 2021 | 101.6 | 101.6
626 | HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 134.81 | 131.1
627 | HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 101.69 | 98.9
628 | HORSE HOLLOW WIND 1 |  | H_HOLLOW_WND1 | TAYLOR | WIND-O | WEST | 2005 | 230 | 230
629 | HORSE HOLLOW WIND 2 |  | HHOLLOW2_WIND1 | TAYLOR | WIND-O | WEST | 2006 | 184 | 184
630 | HORSE HOLLOW WIND 3 |  | HHOLLOW3_WND_1 | TAYLOR | WIND-O | WEST | 2006 | 241.4 | 241.4
631 | HORSE HOLLOW WIND 4 |  | HHOLLOW4_WND1 | TAYLOR | WIND-O | WEST | 2006 | 115 | 115
632 | INADALE WIND 1 |  | INDL_INADALE1 | NOLAN | WIND-O | WEST | 2008 | 95 | 95
633 | INADALE WIND 2 |  | INDL_INADALE2 | NOLAN | WIND-O | WEST | 2008 | 102 | 102
634 | INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | PECOS | WIND-O | WEST | 2001 | 91.8 | 91.8
635 | INERTIA WIND U1 |  | INRT_W_UNIT1 | HASKELL | WIND-O | WEST | 2023 | 67.7 | 67.7
636 | INERTIA WIND U2 |  | INRT_W_UNIT2 | HASKELL | WIND-O | WEST | 2023 | 27.72 | 27.7
637 | INERTIA WIND U3 |  | INRT_W_UNIT3 | HASKELL | WIND-O | WEST | 2023 | 205.9 | 205.9
638 | JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WEBB | WIND-O | SOUTH | 2015 | 19.7 | 19.7
639 | JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WEBB | WIND-O | SOUTH | 2015 | 230 | 230
640 | JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WEBB | WIND-O | SOUTH | 2017 | 96 | 96
641 | JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WEBB | WIND-O | SOUTH | 2017 | 74 | 74
642 | JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WEBB | WIND-O | SOUTH | 2017 | 30 | 30
643 | JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 146.15 | 146.2
644 | JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | DEAF SMITH | WIND-P | PANHANDLE | 2015 | 153.55 | 153.6
645 | KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
646 | KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 103.32 | 103.3
647 | KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 100.42 | 100.4
648 | KEECHI WIND |  | KEECHI_U1 | JACK | WIND-O | NORTH | 2014 | 110 | 110
649 | KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
650 | KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
651 | KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | UPTON | WIND-O | WEST | 2001 | 40.5 | 40.5
652 | KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | UPTON | WIND-O | WEST | 2001 | 79.7 | 79.7
653 | LANGFORD WIND POWER |  | LGD_LANGFORD | TOM GREEN | WIND-O | WEST | 2009 | 159.96 | 160
654 | LACY CREEK WIND U1 |  | LACY_CRK_UNIT1 | GLASSCOCK | WIND-O | WEST | 2024 | 135.4 | 135.4
655 | LACY CREEK WIND U2 |  | LACY_CRK_UNIT2 | GLASSCOCK | WIND-O | WEST | 2024 | 15.12 | 15.1
656 | LACY CREEK WIND U3 |  | LACY_CRK_UNIT3 | GLASSCOCK | WIND-O | WEST | 2024 | 138.2 | 138.2
657 | LACY CREEK WIND U4 |  | LACY_CRK_UNIT4 | GLASSCOCK | WIND-O | WEST | 2024 | 12.6 | 10.1
658 | LAS MAJADAS WIND U1 |  | LMAJADAS_UNIT1 | WILLACY | WIND-C | COASTAL | 2023 | 110 | 110
659 | LAS MAJADAS WIND U2 |  | LMAJADAS_UNIT2 | WILLACY | WIND-C | COASTAL | 2023 | 24 | 24
660 | LAS MAJADAS WIND U3 |  | LMAJADAS_UNIT3 | WILLACY | WIND-C | COASTAL | 2023 | 138.6 | 138.6
661 | LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WILBARGER | WIND-O | WEST | 2019 | 183.7 | 183.7
662 | LOGANS GAP WIND I U1 |  | LGW_UNIT1 | COMANCHE | WIND-O | NORTH | 2015 | 106.3 | 106.3
663 | LOGANS GAP WIND I U2 |  | LGW_UNIT2 | COMANCHE | WIND-O | NORTH | 2015 | 103.85 | 103.8
664 | LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | SHACKELFORD | WIND-O | WEST | 2006 | 194 | 194
665 | LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | SHACKELFORD | WIND-O | WEST | 2007 | 98 | 98
666 | LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | SHACKELFORD | WIND-O | WEST | 2007 | 100 | 100
667 | LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
668 | LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | FLOYD | WIND-P | PANHANDLE | 2015 | 100 | 100
669 | LORAINE WINDPARK I |  | LONEWOLF_G1 | MITCHELL | WIND-O | WEST | 2010 | 48 | 48
670 | LORAINE WINDPARK II |  | LONEWOLF_G2 | MITCHELL | WIND-O | WEST | 2010 | 51 | 51
671 | LORAINE WINDPARK III |  | LONEWOLF_G3 | MITCHELL | WIND-O | WEST | 2011 | 25.5 | 25.5
672 | LORAINE WINDPARK IV |  | LONEWOLF_G4 | MITCHELL | WIND-O | WEST | 2011 | 24 | 24
673 | LOS VIENTOS III WIND |  | LV3_UNIT_1 | STARR | WIND-O | SOUTH | 2015 | 200 | 200
674 | LOS VIENTOS IV WIND |  | LV4_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 200 | 200
675 | LOS VIENTOS V WIND |  | LV5_UNIT_1 | STARR | WIND-O | SOUTH | 2016 | 110 | 110
676 | LOS VIENTOS WIND I |  | LV1_LV1A | WILLACY | WIND-C | COASTAL | 2013 | 200.1 | 200.1
677 | LOS VIENTOS WIND II |  | LV2_LV2 | WILLACY | WIND-C | COASTAL | 2013 | 201.6 | 201.6
678 | MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WILLACY | WIND-C | COASTAL | 2012 | 99.83 | 99.8
679 | MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WILLACY | WIND-C | COASTAL | 2012 | 103.5 | 103.5
680 | MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
681 | MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | PARMER | WIND-P | PANHANDLE | 2017 | 115.2 | 115.2
682 | MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | CONCHO | WIND-O | WEST | 2022 | 201.6 | 201.6
683 | MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | CONCHO | WIND-O | WEST | 2022 | 11.1 | 11.1
684 | MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | CONCHO | WIND-O | WEST | 2022 | 33.6 | 33.6
685 | MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | CONCHO | WIND-O | WEST | 2022 | 22.2 | 22.2
686 | MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | CONCHO | WIND-O | WEST | 2022 | 71.4 | 71.4
687 | MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | CONCHO | WIND-O | WEST | 2022 | 33.3 | 33.3
688 | MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | CONCHO | WIND-O | WEST | 2022 | 22 | 22
689 | MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | CONCHO | WIND-O | WEST | 2022 | 20 | 20
690 | MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | CONCHO | WIND-O | WEST | 2022 | 76.8 | 76.8
691 | MCADOO WIND |  | MWEC_G1 | DICKENS | WIND-P | PANHANDLE | 2008 | 150 | 150
692 | MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
693 | MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | DAWSON | WIND-O | WEST | 2015 | 105.61 | 105.6
694 | MIAMI WIND G1 |  | MIAM1_G1 | ROBERTS | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
695 | MIAMI WIND G2 |  | MIAM1_G2 | ROBERTS | WIND-P | PANHANDLE | 2014 | 144.3 | 144.3
696 | MIDWAY WIND |  | MIDWIND_UNIT1 | SAN PATRICIO | WIND-C | COASTAL | 2019 | 162.8 | 162.8
697 | MONTGOMERY RANCH WIND U1 |  | MONT_WND_UNIT1 | FOARD | WIND-O | WEST | 2024 | 106.13 | 105.9
698 | MONTGOMERY RANCH WIND U2 |  | MONT_WND_UNIT2 | FOARD | WIND-O | WEST | 2024 | 92.87 | 92.7
699 | NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | GLASSCOCK | WIND-O | WEST | 2017 | 196.6 | 196.6
700 | NOTREES WIND 1 |  | NWF_NWF1 | WINKLER | WIND-O | WEST | 2009 | 92.61 | 92.6
701 | NOTREES WIND 2 |  | NWF_NWF2 | WINKLER | WIND-O | WEST | 2009 | 60 | 60
702 | OCOTILLO WIND |  | OWF_OWF | HOWARD | WIND-O | WEST | 2008 | 54.6 | 54.6
703 | OLD SETTLER WIND |  | COTPLNS_OLDSETLR | FLOYD | WIND-P | PANHANDLE | 2017 | 151.2 | 151.2
704 | OVEJA WIND U1 |  | OVEJA_G1 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
705 | OVEJA WIND U2 |  | OVEJA_G2 | IRION | WIND-O | WEST | 2021 | 151.2 | 151.2
706 | PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | CAMERON | WIND-C | COASTAL | 2020 | 144.9 | 144.9
707 | PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2
708 | PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 109.15 | 109.2
709 | PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | CARSON | WIND-P | PANHANDLE | 2014 | 94.19 | 94.2
710 | PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | CARSON | WIND-P | PANHANDLE | 2014 | 96.6 | 96.6
711 | PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | HOWARD | WIND-O | WEST | 2008 | 149.16 | 148.5
712 | PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | HOWARD | WIND-O | WEST | 2019 | 123.25 | 121.9
713 | PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | HOWARD | WIND-O | WEST | 2022 | 106.92 | 106.9
714 | PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | HOWARD | WIND-O | WEST | 2022 | 108.54 | 108.5
715 | PAPALOTE CREEK WIND |  | PAP1_PAP1 | SAN PATRICIO | WIND-C | COASTAL | 2009 | 179.85 | 179.9
716 | PAPALOTE CREEK WIND II |  | COTTON_PAP2 | SAN PATRICIO | WIND-C | COASTAL | 2010 | 200.12 | 200.1
717 | PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | PECOS | WIND-O | WEST | 2001 | 91.7 | 91.7
718 | PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | PECOS | WIND-O | WEST | 2001 | 86 | 85.8
719 | PENASCAL WIND 1 |  | PENA_UNIT1 | KENEDY | WIND-C | COASTAL | 2009 | 160.8 | 160.8
720 | PENASCAL WIND 2 |  | PENA_UNIT2 | KENEDY | WIND-C | COASTAL | 2009 | 141.6 | 141.6
721 | PENASCAL WIND 3 |  | PENA3_UNIT3 | KENEDY | WIND-C | COASTAL | 2011 | 100.8 | 100.8
722 | PEYTON CREEK WIND |  | PEY_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2020 | 151.2 | 151.2
723 | PIONEER DJ WIND U1 |  | PIONR_DJ_UNIT1 | MIDLAND | WIND-O | WEST | 2025 | 124.08 | 124.1
724 | PIONEER DJ WIND U2 |  | PIONR_DJ_UNIT2 | MIDLAND | WIND-O | WEST | 2025 | 16.24 | 16.2
725 | PYRON WIND 1 |  | PYR_PYRON1 | NOLAN | WIND-O | WEST | 2008 | 128.47 | 131.2
726 | PYRON WIND 2 |  | PYR_PYRON2 | NOLAN | WIND-O | WEST | 2008 | 134.9 | 137.7
727 | RANCHERO WIND U1 |  | RANCHERO_UNIT1 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
728 | RANCHERO WIND U2 |  | RANCHERO_UNIT2 | CROCKETT | WIND-O | WEST | 2020 | 150 | 150
729 | RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 104.6
730 | RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | GLASSCOCK | WIND-O | WEST | 2015 | 109.15 | 102.7
731 | RED CANYON WIND |  | RDCANYON_RDCNY1 | BORDEN | WIND-O | WEST | 2006 | 89.6 | 89.6
732 | RELOJ DEL SOL WIND U1 |  | RELOJ_UNIT1 | ZAPATA | WIND-O | SOUTH | 2022 | 55.4 | 55.4
733 | RELOJ DEL SOL WIND U2 |  | RELOJ_UNIT2 | ZAPATA | WIND-O | SOUTH | 2022 | 48 | 48
734 | RELOJ DEL SOL WIND U3 |  | RELOJ_UNIT3 | ZAPATA | WIND-O | SOUTH | 2022 | 83.1 | 83.1
735 | RELOJ DEL SOL WIND U4 |  | RELOJ_UNIT4 | ZAPATA | WIND-O | SOUTH | 2022 | 22.8 | 22.8
736 | ROADRUNNER CROSSING WIND U1 |  | RRC_WIND_UNIT1 | EASTLAND | WIND-O | NORTH | 2025 | 98.7 | 98.7
737 | ROADRUNNER CROSSING WIND U2 |  | RRC_WIND_UNIT2 | EASTLAND | WIND-O | NORTH | 2025 | 27.72 | 27.7
738 | ROADRUNNER CROSSING WIND U3 |  | RRC_WIND_UNIT3 | EASTLAND | WIND-O | NORTH | 2025 | 126.9 | 126.9
739 | ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | VAL VERDE | WIND-O | WEST | 2017 | 121.9 | 121.9
740 | ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | VAL VERDE | WIND-O | WEST | 2017 | 27.44 | 27.4
741 | ROSCOE WIND |  | TKWSW1_ROSCOE | NOLAN | WIND-O | WEST | 2008 | 114 | 114
742 | ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | NOLAN | WIND-O | WEST | 2008 | 95 | 95
743 | ROUTE 66 WIND |  | ROUTE_66_WIND1 | CARSON | WIND-P | PANHANDLE | 2015 | 150 | 150
744 | RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
745 | RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | MCCULLOCH | WIND-O | SOUTH | 2021 | 89.9 | 89.9
746 | RTS WIND |  | RTS_U1 | MCCULLOCH | WIND-O | SOUTH | 2018 | 160 | 160
747 | SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
748 | SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | LYNN | WIND-O | WEST | 2022 | 169.2 | 169.2
749 | SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | DONLEY | WIND-P | PANHANDLE | 2017 | 64 | 64
750 | SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | DONLEY | WIND-P | PANHANDLE | 2017 | 110 | 110
751 | SAN ROMAN WIND |  | SANROMAN_WIND_1 | CAMERON | WIND-C | COASTAL | 2016 | 95.25 | 95.2
752 | SAND BLUFF WIND U1 |  | MCDLD_SB1_2 | GLASSCOCK | WIND-O | WEST | 2022 | 71.4 | 71.4
753 | SAND BLUFF WIND U2 |  | MCDLD_SB3_282 | GLASSCOCK | WIND-O | WEST | 2022 | 14.1 | 14.1
754 | SAND BLUFF WIND U3 |  | MCDLD_SB4_G87 | GLASSCOCK | WIND-O | WEST | 2022 | 4 | 4
755 | SENATE WIND |  | SENATEWD_UNIT1 | JACK | WIND-O | NORTH | 2012 | 150 | 150
756 | SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | JIM HOGG | WIND-O | SOUTH | 2015 | 78 | 78
757 | SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | BAYLOR | WIND-O | WEST | 2019 | 30.24 | 30.2
758 | SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | NUECES | WIND-C | COASTAL | 2021 | 226.1 | 226.1
759 | SHAMROCK WIND U1 |  | SHAMROCK_UNIT1 | CROCKETT | WIND-O | WEST | 2025 | 203.1 | 203
760 | SHAMROCK WIND U2 |  | SHAMROCK_UNIT2 | CROCKETT | WIND-O | WEST | 2025 | 20.9 | 20.9
761 | SHANNON WIND |  | SHANNONW_UNIT_1 | CLAY | WIND-O | WEST | 2015 | 204.1 | 204.1
762 | SHEEP CREEK WIND |  | SHEEPCRK_UNIT1 | EASTLAND | WIND-O | NORTH | 2024 | 150 | 150
763 | SHERBINO 2 WIND |  | KEO_SHRBINO2 | PECOS | WIND-O | WEST | 2011 | 132 | 132
764 | SILVER STAR WIND |  | FLTCK_SSI | ERATH | WIND-O | NORTH | 2008 | 52.8 | 52.8
765 | SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | FLOYD | WIND-P | PANHANDLE | 2015 | 102 | 102
766 | SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | FLOYD | WIND-P | PANHANDLE | 2015 | 98 | 98
767 | SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | FLOYD | WIND-P | PANHANDLE | 2016 | 148.5 | 148.5
768 | SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | FLOYD | WIND-P | PANHANDLE | 2016 | 151.8 | 151.8
769 | SOUTH TRENT WIND |  | STWF_T1 | NOLAN | WIND-O | WEST | 2008 | 101.2 | 98.2
770 | SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | OLDHAM | WIND-P | PANHANDLE | 2014 | 160.95 | 161
771 | SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | OLDHAM | WIND-P | PANHANDLE | 2015 | 98 | 98
772 | SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | OLDHAM | WIND-P | PANHANDLE | 2015 | 96 | 96
773 | STANTON WIND ENERGY |  | SWEC_G1 | MARTIN | WIND-O | WEST | 2008 | 123.6 | 120
774 | STELLA WIND |  | STELLA_UNIT1 | KENEDY | WIND-C | COASTAL | 2018 | 201 | 201
775 | STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | BORDEN | WIND-O | WEST | 2014 | 213.82 | 211.2
776 | STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | BORDEN | WIND-O | WEST | 2015 | 166.52 | 164.7
777 | SWEETWATER WIND 1 |  | SWEETWND_WND1 | NOLAN | WIND-O | WEST | 2003 | 42.5 | 42.5
778 | SWEETWATER WIND 2A |  | SWEETWN2_WND24 | NOLAN | WIND-O | WEST | 2006 | 16.8 | 16.8
779 | SWEETWATER WIND 2B |  | SWEETWN2_WND2 | NOLAN | WIND-O | WEST | 2004 | 110.8 | 110.8
780 | SWEETWATER WIND 3A |  | SWEETWN3_WND3A | NOLAN | WIND-O | WEST | 2011 | 33.6 | 33.6
781 | SWEETWATER WIND 3B |  | SWEETWN3_WND3B | NOLAN | WIND-O | WEST | 2011 | 118.6 | 118.6
782 | SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | NOLAN | WIND-O | WEST | 2007 | 125 | 125
783 | SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | NOLAN | WIND-O | WEST | 2007 | 112 | 112
784 | SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | NOLAN | WIND-O | WEST | 2007 | 85 | 85
785 | TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | LYNN | WIND-O | WEST | 2019 | 150 | 150
786 | TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | LYNN | WIND-O | WEST | 2019 | 150 | 150
787 | TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | HOWARD | WIND-O | WEST | 1999 | 27.72 | 27.7
788 | TG EAST WIND U1 |  | TRUSGILL_UNIT1 | KNOX | WIND-O | WEST | 2022 | 42 | 42
789 | TG EAST WIND U2 |  | TRUSGILL_UNIT2 | KNOX | WIND-O | WEST | 2022 | 44.8 | 44.8
790 | TG EAST WIND U3 |  | TRUSGILL_UNIT3 | KNOX | WIND-O | WEST | 2022 | 42 | 42
791 | TG EAST WIND U4 |  | TRUSGILL_UNIT4 | KNOX | WIND-O | WEST | 2022 | 207.2 | 207.2
792 | TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WEBB | WIND-O | SOUTH | 2019 | 150 | 150
793 | TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WEBB | WIND-O | SOUTH | 2019 | 23 | 23
794 | TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WEBB | WIND-O | SOUTH | 2019 | 127.5 | 127.5
795 | TRENT WIND 1 A |  | TRENT_TRENT | NOLAN | WIND-O | WEST | 2001 | 38.3 | 38.3
796 | TRENT WIND 1 B |  | TRENT_UNIT_1B | NOLAN | WIND-O | WEST | 2018 | 15.6 | 15.6
797 | TRENT WIND 2 |  | TRENT_UNIT_2 | NOLAN | WIND-O | WEST | 2018 | 50.5 | 50.5
798 | TRENT WIND 3 A |  | TRENT_UNIT_3A | NOLAN | WIND-O | WEST | 2018 | 38.3 | 38.3
799 | TRENT WIND 3 B |  | TRENT_UNIT_3B | NOLAN | WIND-O | WEST | 2018 | 13.8 | 13.8
800 | TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | ARCHER | WIND-O | WEST | 2012 | 103.4 | 103.4
801 | TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | ARCHER | WIND-O | WEST | 2012 | 94.6 | 94.6
802 | TSTC WEST TEXAS WIND |  | ROSC2_1UNIT | NOLAN | WIND-O | WEST | 2008 | 2 | 2
803 | TURKEY TRACK WIND |  | TTWEC_G1 | NOLAN | WIND-O | WEST | 2008 | 174.6 | 169.5
804 | TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | COOKE | WIND-O | NORTH | 2016 | 125.6 | 125.6
805 | VENADO WIND U1 |  | VENADO_UNIT1 | ZAPATA | WIND-O | SOUTH | 2021 | 105 | 105
806 | VENADO WIND U2 |  | VENADO_UNIT2 | ZAPATA | WIND-O | SOUTH | 2021 | 96.6 | 96.6
807 | VERA WIND 1 |  | VERAWIND_UNIT1 | KNOX | WIND-O | WEST | 2021 | 12 | 12
808 | VERA WIND 2 |  | VERAWIND_UNIT2 | KNOX | WIND-O | WEST | 2021 | 7.2 | 7.2
809 | VERA WIND 3 |  | VERAWIND_UNIT3 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
810 | VERA WIND 4 |  | VERAWIND_UNIT4 | KNOX | WIND-O | WEST | 2021 | 22 | 22
811 | VERA WIND 5 |  | VERAWIND_UNIT5 | KNOX | WIND-O | WEST | 2021 | 100.8 | 100.8
812 | VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | BAYLOR | WIND-O | WEST | 2015 | 150 | 150
813 | VORTEX WIND U1 |  | VORTEX_WIND1 | THROCKMORTON | WIND-O | WEST | 2024 | 153.6 | 153.6
814 | VORTEX WIND U2 |  | VORTEX_WIND2 | THROCKMORTON | WIND-O | WEST | 2024 | 24.2 | 24.2
815 | VORTEX WIND U3 |  | VORTEX_WIND3 | THROCKMORTON | WIND-O | WEST | 2024 | 158.4 | 158.4
816 | VORTEX WIND U4 |  | VORTEX_WIND4 | THROCKMORTON | WIND-O | WEST | 2022 | 14 | 14
817 | WAKE WIND 1 |  | WAKEWE_G1 | DICKENS | WIND-P | PANHANDLE | 2016 | 114.91 | 114.9
818 | WAKE WIND 2 |  | WAKEWE_G2 | DICKENS | WIND-P | PANHANDLE | 2016 | 142.35 | 142.3
819 | WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WILLACY | WIND-C | COASTAL | 2021 | 116.6 | 116.6
820 | WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WILLACY | WIND-C | COASTAL | 2021 | 123.2 | 123.2
821 | WESTERN TRAIL WIND (AJAX WIND) U1 |  | AJAXWIND_UNIT1 | WILBARGER | WIND-O | WEST | 2022 | 225.6 | 225.6
822 | WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WILBARGER | WIND-O | WEST | 2022 | 141 | 141
823 | WHIRLWIND ENERGY |  | WEC_WECG1 | FLOYD | WIND-P | PANHANDLE | 2007 | 59.8 | 57
824 | WHITETAIL WIND |  | EXGNWTL_WIND_1 | WEBB | WIND-O | SOUTH | 2012 | 92.34 | 92.3
825 | WHITE MESA WIND U1 |  | WHMESA_UNIT1 | CROCKETT | WIND-O | WEST | 2022 | 152.3 | 152.3
826 | WHITE MESA 2 WIND U1 |  | WHMESA_UNIT2_23 | CROCKETT | WIND-O | WEST | 2022 | 13.92 | 13.9
827 | WHITE MESA 2 WIND U2 |  | WHMESA_UNIT2_28 | CROCKETT | WIND-O | WEST | 2022 | 183.3 | 183.3
828 | WHITE MESA 2 WIND U3 |  | WHMESA_UNIT3_23 | CROCKETT | WIND-O | WEST | 2022 | 18.6 | 18.6
829 | WHITE MESA 2 WIND U4 |  | WHMESA_UNIT3_28 | CROCKETT | WIND-O | WEST | 2022 | 132.54 | 132.5
830 | WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
831 | WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | HASKELL | WIND-O | WEST | 2017 | 125 | 125
832 | WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | SCHLEICHER | WIND-O | WEST | 2020 | 199.5 | 199.5
833 | WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | ARCHER | WIND-O | WEST | 2014 | 67.62 | 67.6
834 | WKN MOZART WIND |  | MOZART_WIND_1 | KENT | WIND-O | WEST | 2012 | 30 | 30
835 | WOLF RIDGE WIND |  | WHTTAIL_WR1 | COOKE | WIND-O | NORTH | 2008 | 121.5 | 121.5
836 | YOUNG WIND U1 |  | YNG_WND_UNIT1 | YOUNG | WIND-O | WEST | 2025 | 197.4 | 193
837 | YOUNG WIND U2 |  | YNG_WND_UNIT2 | YOUNG | WIND-O | WEST | 2025 | 152.28 | 148.9
838 | YOUNG WIND U3 |  | YNG_WND_UNIT3 | YOUNG | WIND-O | WEST | 2025 | 149.46 | 146.1
839 | Operational Capacity Total (Wind) | [6 empty] | 35990.66 | 35862.7
840
841 | Operational Resources (Wind) - Synchronized but not Approved for Commercial Operations
842 | ANCHOR WIND U1 | 21INR0546 | ANCHOR_WIND1 | CALLAHAN | WIND-O | WEST | 2025 | 16 | 16
843 | BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | CALLAHAN | WIND-O | WEST | 2025 | 195 | 195
844 | BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | CALLAHAN | WIND-O | WEST | 2025 | 145 | 145
845 | BIG SAMPSON WIND U1 | 16INR0104 | BIGSAMWD_UNIT1 | CROCKETT | WIND-O | WEST | 2025 | 132.9 | 132.5
846 | BIG SAMPSON WIND U2 | 16INR0104 | BIGSAMWD_UNIT2 | CROCKETT | WIND-O | WEST | 2025 | 132.5 | 132.5
847 | BOARD CREEK WP U1 | 21INR0324 | BOARDCRK_UNIT1 | NAVARRO | WIND-O | NORTH | 2025 | 108.8 | 108.8
848 | BOARD CREEK WP U2 | 21INR0324 | BOARDCRK_UNIT2 | NAVARRO | WIND-O | NORTH | 2025 | 190.4 | 190.4
849 | CANYON WIND U1 | 18INR0030 | CANYONWD_UNIT1 | SCURRY | WIND-O | WEST | 2025 | 146.64 | 144
850 | CANYON WIND U2 | 18INR0030 | CANYONWD_UNIT2 | SCURRY | WIND-O | WEST | 2025 | 2.52 | 2.5
851 | CANYON WIND U3 | 18INR0030 | CANYONWD_UNIT3 | SCURRY | WIND-O | WEST | 2025 | 59.22 | 58.2
852 | CANYON WIND U4 | 18INR0030 | CANYONWD_UNIT4 | SCURRY | WIND-O | WEST | 2025 | 20.16 | 19.8
853 | CANYON WIND U5 | 18INR0030 | CANYONWD_UNIT5 | SCURRY | WIND-O | WEST | 2025 | 67.68 | 66.5
854 | CANYON WIND U6 | 18INR0030 | CANYONWD_UNIT6 | SCURRY | WIND-O | WEST | 2025 | 12.6 | 12.4
855 | COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | SCURRY | WIND-O | WEST | 2025 | 90 | 90
856 | COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | SCURRY | WIND-O | WEST | 2025 | 26.6 | 26.6
857 | COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | SCURRY | WIND-O | WEST | 2025 | 126 | 126
858 | EL SUAZ RANCH U1 | 20INR0097 | ELSAUZ_UNIT1 | WILLACY | WIND-C | COASTAL | 2025 | 153 | 153
859 | EL SUAZ RANCH U2 | 20INR0097 | ELSAUZ_UNIT2 | WILLACY | WIND-C | COASTAL | 2025 | 148.5 | 148.5
860 | FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | BEE | WIND-O | SOUTH | 2025 | 130.2 | 130.2
861 | FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | BEE | WIND-O | SOUTH | 2025 | 84 | 84
862 | FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | BEE | WIND-O | SOUTH | 2025 | 54 | 54
863 | HART WIND 2 | 24INR0116 | HART_WND_UNIT1 | CASTRO | WIND-P | PANHANDLE | 2025 | 163.4 | 163.4
864 | HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | GLASSCOCK | WIND-O | WEST | 2025 | 162.1 | 162.1
865 | RAY GULF WIND | 22INR0517 | MAG_UNIT1 | MATAGORDA | WIND-O | COASTAL | 2025 | 97.5 | 96.5
866 | MAGNET WING U2 (LANE CITY WIND) | 22INR0517 | MAG_UNIT2 | MATAGORDA | WIND-C | COASTAL | 2025 | 102 | 100.8
867 | MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | NOLAN | WIND-O | WEST | 2025 | 182.4 | 182.4
868 | MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | STARR | WIND-O | SOUTH | 2025 | 201.6 | 201.6
869 | MONTE CRISTO 1 WIND | 19INR0054 | MONTECR1_WIND1 | HIDALGO | WIND-O | SOUTH | 2025 | 234.5 | 234.5
870 | PEYTON CREEK WIND II | 20INR0155 | PCT_UNIT1 | MATAGORDA | WIND-C | COASTAL | 2025 | 236 | 234.1
871 | PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | LIMESTONE | WIND-O | NORTH | 2025 | 153 | 153
872 | PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | LIMESTONE | WIND-O | NORTH | 2025 | 147 | 147
873 | PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | MILLS | WIND-O | NORTH | 2025 | 187.2 | 187.2
874 | PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | MILLS | WIND-O | NORTH | 2025 | 115.2 | 115.2
875 | WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | FISHER | WIND-O | WEST | 2024 | 209.4 | 209.4
876 | WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | FISHER | WIND-O | WEST | 2024 | 209.5 | 209.5
877 | WILDWIND U1 | 20INR0033 | WILDWIND_UNIT1 | COOKE | WIND-O | NORTH | 2025 | 18.4 | 18.4
878 | WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | COOKE | WIND-O | NORTH | 2025 | 48 | 48
879 | WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | COOKE | WIND-O | NORTH | 2025 | 6.3 | 6.3
880 | WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | COOKE | WIND-O | NORTH | 2025 | 54.6 | 54.6
881 | WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | COOKE | WIND-O | NORTH | 2025 | 52.8 | 52.8
882 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Wind) | [6 empty] | 4622.62 | 4612.7
883
884 | Operational Resources (Solar)
885 | 7V SOLAR |  | 7RNCHSLR_UNIT1 | FAYETTE | SOLAR | SOUTH | 2025 | 139.5 | 139.2
886 | 7V SOLAR U2 |  | 7RNCHSLR_UNIT2 | FAYETTE | SOLAR | SOUTH | 2025 | 95.54 | 95.2
887 | 7V SOLAR U3 |  | 7RNCHSLR_UNIT3 | FAYETTE | SOLAR | SOUTH | 2025 | 5.57 | 5.6
888 | ACACIA SOLAR |  | ACACIA_UNIT_1 | PRESIDIO | SOLAR | WEST | 2012 | 10 | 10
889 | AIRPORT ROAD LONEWOLFE PHASE ONE |  | AIRPRTRD_LONEWOLFE | MITCHELL | SOLAR | WEST | 2023 | 1 | 1
890 | ALEXIS SOLAR |  | ALEXIS_ALEXIS | BROOKS | SOLAR | SOUTH | 2019 | 10 | 10
891 | ANDROMEDA SOLAR U1 |  | ANDMDSLR_UNIT1 | SCURRY | SOLAR | WEST | 2024 | 158.8 | 158
892 | ANDROMEDA SOLAR U2 |  | ANDMDSLR_UNIT2 | SCURRY | SOLAR | WEST | 2024 | 162.4 | 162
893 | ANGELO SOLAR |  | ANG_SLR_UNIT1 | TOM GREEN | SOLAR | WEST | 2025 | 195.41 | 195
894 | ANSON SOLAR U1 |  | ANSON1_UNIT1 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
895 | ANSON SOLAR U2 |  | ANSON1_UNIT2 | JONES | SOLAR | WEST | 2022 | 100.8 | 100
896 | ARAGORN SOLAR |  | ARAGORN_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 188.2 | 185
897 | ASH CREEK SOLAR U1 |  | ASCK_SLR_SOLAR1 | HILL | SOLAR | NORTH | 2025 | 206.8 | 203.3
898 | ASH CREEK SOLAR U2 |  | ASCK_SLR_SOLAR2 | HILL | SOLAR | NORTH | 2025 | 210.94 | 207.3
899 | AUREOLA SOLAR U1 |  | AURO_SLR_UNIT1 | MILAM | SOLAR | SOUTH | 2024 | 201.66 | 200.4
900 | AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | HASKELL | SOLAR | WEST | 2021 | 74.9 | 74.9
901 | AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | HASKELL | SOLAR | WEST | 2021 | 153.5 | 153.5
902 | BECK 1 |  | CECSOLAR_BECK1 | BEXAR | SOLAR | SOUTH | 2016 | 1 | 1
903 | BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PECOS | SOLAR | WEST | 2017 | 50 | 49.1
904 | BIG ELM SOLAR |  | BELM_SLR_UNIT1 | BELL | SOLAR | NORTH | 2025 | 200.99 | 200.2
905 | BKVSOLAR_BKVSOLAR1 |  | BKVSOLAR_BKVSOLAR1 | DENTON | SOLAR | NORTH | 2024 | 2.5 | 2.5
906 | BLUE WING 1 SOLAR |  | BROOK_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.6 | 7.6
907 | BLUE WING 2 SOLAR |  | ELMEN_1UNIT | BEXAR | SOLAR | SOUTH | 2010 | 7.3 | 7.3
908 | BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | STERLING | SOLAR | WEST | 2019 | 30 | 30
909 | BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | STERLING | SOLAR | WEST | 2021 | 100 | 100
910 | BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | STERLING | SOLAR | WEST | 2021 | 15 | 15
911 | BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | DAWSON | SOLAR | WEST | 2018 | 101.6 | 101.6
912 | BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | DAWSON | SOLAR | WEST | 2018 | 50 | 50
913 | BOVINE SOLAR LLC |  | BOVINE_BOVINE | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
914 | BOVINE SOLAR LLC |  | BOVINE2_BOVINE2 | AUSTIN | SOLAR | SOUTH | 2018 | 5 | 5
915 | BPL FILES SOLAR |  | FILESSLR_PV1 | HILL | SOLAR | NORTH | 2023 | 146.09 | 145
916 | BRIGHTSIDE SOLAR |  | BRIGHTSD_UNIT1 | BEE | SOLAR | SOUTH | 2022 | 53.4 | 50
917 | BRIGHT ARROW SOLAR U1 |  | BR_ARROW_UNIT1 | HOPKINS | SOLAR | NORTH | 2025 | 127.3 | 127
918 | BRIGHT ARROW SOLAR U2 |  | BR_ARROW_UNIT2 | HOPKINS | SOLAR | NORTH | 2025 | 173.9 | 173
919 | BRONSON SOLAR I |  | BRNSN_BRNSN | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
920 | BRONSON SOLAR II |  | BRNSN2_BRNSN2 | FORT BEND | SOLAR | HOUSTON | 2018 | 5 | 5
921 | CASCADE SOLAR I |  | CASCADE | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
922 | CASCADE SOLAR II |  | CASCADE2 | WHARTON | SOLAR | SOUTH | 2018 | 5 | 5
923 | CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | UPTON | SOLAR | WEST | 2018 | 180 | 180
924 | CATAN SOLAR |  | CS10_CATAN | KARNES | SOLAR | SOUTH | 2020 | 10 | 10
925 | CHISUM SOLAR |  | CHISUM_CHISUM | LAMAR | SOLAR | NORTH | 2018 | 10 | 10
926 | COMMERCE_SOLAR |  | X443PV1_SWRI_PV1 | BEXAR | SOLAR | SOUTH | 2019 | 5 | 5
927 | CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 125.7 | 125.7
928 | CORAL SOLAR U1 |  | CORALSLR_SOLAR1 | FALLS | SOLAR | NORTH | 2024 | 97.7 | 96.2
929 | CORAL SOLAR U2 |  | CORALSLR_SOLAR2 | FALLS | SOLAR | NORTH | 2024 | 56.3 | 55.4
930 | CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | WEBB | SOLAR | SOUTH | 2021 | 202.6 | 202.6
931 | CROWN SOLAR |  | CRWN_SLR_UNIT1 | FALLS | SOLAR | NORTH | 2024 | 101.3 | 100.1
932 | DANCIGER SOLAR U1 |  | DAG_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100
933 | DANCIGER SOLAR U2 |  | DAG_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2023 | 101.4 | 100
934 | DILEO SOLAR |  | DILEOSLR_UNIT1 | BOSQUE | SOLAR | NORTH | 2023 | 71.4 | 71.4
935 | DP24X001_RETAMADG |  | DP24X001_RETAMADG | DIMMIT | SOLAR | SOUTH | 2021 | 1.8 | 1.8
936 | EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | TRAVIS | SOLAR | SOUTH | 2021 | 144 | 144
937 | EDDY SOLAR II |  | EDDYII_EDDYII | MCLENNAN | SOLAR | NORTH | 2018 | 10 | 10
938 | EIFFEL SOLAR |  | EIFSLR_UNIT1 | LAMAR | SOLAR | NORTH | 2023 | 241 | 240
939 | ELARA SOLAR |  | ELARA_SL_UNIT1 | FRIO | SOLAR | SOUTH | 2022 | 132.4 | 132.4
940 | ELLIS SOLAR |  | ELLISSLR_UNIT1 | ELLIS | SOLAR | NORTH | 2023 | 81.3 | 80
941 | EMERALD GROVE SOLAR (PECOS SOLAR POWER I) |  | EGROVESL_UNIT1 | CRANE | SOLAR | WEST | 2023 | 109.5 | 108
942 | ESTONIAN SOLAR FARM U1 |  | ESTONIAN_SOLAR1 | DELTA | SOLAR | NORTH | 2025 | 88.4 | 88.3
943 | ESTONIAN SOLAR FARM U2 |  | ESTONIAN_SOLAR2 | DELTA | SOLAR | NORTH | 2025 | 114.4 | 114.1
944 | EUNICE SOLAR U1 |  | EUNICE_PV1 | ANDREWS | SOLAR | WEST | 2021 | 189.6 | 189.6
945 | EUNICE SOLAR U2 |  | EUNICE_PV2 | ANDREWS | SOLAR | WEST | 2021 | 237.1 | 237.1
946 | FENCE POST SOLAR U1 |  | FENCESLR_SOLAR1 | NAVARRO | SOLAR | NORTH | 2025 | 138.88 | 138
947 | FENCE POST SOLAR U2 |  | FENCESLR_SOLAR2 | NAVARRO | SOLAR | NORTH | 2025 | 97.98 | 98
948 | FIFTH GENERATION SOLAR 1 |  | FIFTHGS1_FGSOLAR1 | TRAVIS | SOLAR | SOUTH | 2016 | 6.8 | 6.8
949 | FIVE WELLS SOLAR U1 |  | FIVEWSLR_UNIT1 | BELL | SOLAR | NORTH | 2025 | 194.42 | 194.4
950 | FIVE WELLS SOLAR U2 |  | FIVEWSLR_UNIT2 | BELL | SOLAR | NORTH | 2025 | 126.97 | 127
951 | FOWLER RANCH |  | FWLR_SLR_UNIT1 | CRANE | SOLAR | WEST | 2020 | 152.5 | 150
952 | FRFWS_FAIRFIELD |  | FRFWS_FAIRFIELD | FREESTONE | SOLAR | NORTH | 2024 | 4 | 4
953 | FRYE SOLAR U1 |  | FRYE_SLR_UNIT1 | SWISHER | SOLAR | PANHANDLE | 2024 | 250.9 | 250
954 | FRYE SOLAR U2 |  | FRYE_SLR_UNIT2 | SWISHER | SOLAR | PANHANDLE | 2024 | 251.1 | 250
955 | FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PECOS | SOLAR | WEST | 2015 | 22 | 22
956 | FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PECOS | SOLAR | WEST | 2017 | 126 | 121.1
957 | GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | CONCHO | SOLAR | WEST | 2021 | 250 | 250
958 | GALLOWAY 2 SOLAR |  | GALLOWAY_SOLAR2 | CONCHO | SOLAR | WEST | 2024 | 111.1 | 110
959 | GOLD_SPIKE 1 |  | 19599_1_GOLD_SPIKE | TARRANT | SOLAR | NORTH | 2025 | 1.3 | 1.3
960 | GOLD_SPIKE 2 |  | 19599_2_GOLD_SPIKE | TARRANT | SOLAR | NORTH | 2025 | 0.8 | 0.8
961 | GOLD_SPIKE 3 |  | 19599_GOLD_SPIKE | TARRANT | SOLAR | NORTH | 2025 | 1.9 | 1.9
962 | GOLINDA SOLAR |  | GOLINDA_UNIT1 | FALLS | SOLAR | NORTH | 2024 | 101.1 | 100.1
963 | GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PECOS | SOLAR | WEST | 2021 | 126.3 | 124.6
964 | GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PECOS | SOLAR | WEST | 2021 | 132.2 | 130.4
965 | GRIFFIN SOLAR |  | GRIFFIN_GRIFFIN | MCLENNAN | SOLAR | NORTH | 2019 | 5 | 5
966 | GRIZZLY RIDGE SOLAR |  | GRIZZLY_SOLAR1 | HAMILTON | SOLAR | NORTH | 2023 | 101.7 | 100
967 | HALO SOLAR |  | HALO_SLR_UNIT1 | BELL | SOLAR | NORTH | 2024 | 251.15 | 250.4
968 | HIGHWAY 56 |  | HWY56_HWY56 | GRAYSON | SOLAR | NORTH | 2017 | 5.3 | 5.3
969 | HM SEALY SOLAR 1 |  | SEALY_1UNIT | AUSTIN | SOLAR | SOUTH | 2015 | 1.6 | 1.6
970 | HOLLYWOOD SOLAR U1 |  | HOL_UNIT1 | WHARTON | SOLAR | SOUTH | 2024 | 178.88 | 175.3
971 | HOLLYWOOD SOLAR U2 |  | HOL_UNIT2 | WHARTON | SOLAR | SOUTH | 2024 | 186.07 | 178.1
972 | HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | NOLAN | SOLAR | WEST | 2020 | 102.2 | 102.2
973 | HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | NOLAN | SOLAR | WEST | 2020 | 102.3 | 102.3
974 | HOPKINS SOLAR U1 |  | HOPKNSLR_UNIT1 | HOPKINS | SOLAR | NORTH | 2024 | 175.35 | 174.8
975 | HOPKINS SOLAR U2 |  | HOPKNSLR_UNIT2 | HOPKINS | SOLAR | NORTH | 2024 | 76.17 | 75.8
976 | HORIZON SOLAR |  | HRZN_SLR_UNIT1 | FRIO | SOLAR | SOUTH | 2024 | 203.5 | 200
977 | HPWHSOL_WILDHORSESOLAR |  | HPWHSOL_WILDHORSESOLAR | HOWARD | SOLAR | WEST | 2024 | 10 | 10
978 | IMPACT SOLAR |  | IMPACT_UNIT1 | LAMAR | SOLAR | NORTH | 2021 | 198.5 | 198.5
979 | INFINITE PHOTON ENERGY |  | INFINITE_PHOTON_ENERGY | MITCHELL | SOLAR | WEST | 2025 | 4 | 4
980 | JADE SOLAR U1 |  | JADE_SLR_UNIT1 | SCURRY | SOLAR | WEST | 2024 | 158.8 | 158
981 | JADE SOLAR U2 |  | JADE_SLR_UNIT2 | SCURRY | SOLAR | WEST | 2024 | 162.4 | 162
982 | JUNO SOLAR PHASE I |  | JUNO_UNIT1 | BORDEN | SOLAR | WEST | 2021 | 162.1 | 162.1
983 | JUNO SOLAR PHASE II |  | JUNO_UNIT2 | BORDEN | SOLAR | WEST | 2021 | 143.5 | 143.5
984 | KELLAM SOLAR |  | KELAM_SL_UNIT1 | VAN ZANDT | SOLAR | NORTH | 2020 | 59.8 | 59.8
985 | LAMPASAS_HIGHWAY183LAMPASAS |  | LAMPASAS_HIGHWAY183 | BURNET | SOLAR | SOUTH | 2025 | 7.5 | 7.5
986 | LAPETUS SOLAR |  | LAPETUS_UNIT_1 | ANDREWS | SOLAR | WEST | 2020 | 100.7 | 100.7
987 | LEON |  | LEON_LEON | HUNT | SOLAR | NORTH | 2017 | 10 | 10
988 | LILY SOLAR |  | LILY_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2021 | 147.6 | 147.6
989 | LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | BORDEN | SOLAR | WEST | 2021 | 98.5 | 98.5
990 | LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | BORDEN | SOLAR | WEST | 2021 | 128.3 | 128.3
991 | LONGBOW SOLAR |  | LON_SOLAR1 | BRAZORIA | SOLAR | COASTAL | 2024 | 78.2 | 77
992 | LSSEALY_LOCALSUNSEALY |  | LSSEALY_LOCALSUNSEALY | AUSTIN | SOLAR | SOUTH | 2023 | 1.6 | 1.6
993 | MALAKOFF |  | MALAKOFF | HENDERSON | SOLAR | NORTH | 2024 | 5 | 5
994 | MANDORLA SOLAR |  | MAND_SLR_UNIT1 | MILAM | SOLAR | SOUTH | 2024 | 251.45 | 250.5
995 | MARLIN |  | MARLIN_MARLIN | FALLS | SOLAR | NORTH | 2017 | 5.3 | 5.3
996 | MARS SOLAR (DG) |  | MARS_MARS | WEBB | SOLAR | SOUTH | 2019 | 10 | 10
997 | MCLEAN (SHAKES) SOLAR |  | MCLNSLR_UNIT1 | DIMMIT | SOLAR | SOUTH | 2023 | 207.4 | 200
998 | MERCURY SOLAR U1 |  | MERCURY_PV1 | HILL | SOLAR | NORTH | 2025 | 203.5 | 200
999 | MERCURY SOLAR U2 |  | MERCURY_PV2 | HILL | SOLAR | NORTH | 2025 | 203.5 | 200
1000 | MEXIA_MEXIA |  | MEXIA_MEXIA | LIMESTONE | SOLAR | NORTH | 2024 | 4 | 4
1001 | MEXIA1_MEXIA1 |  | MEXIA1_MEXIA1 | LIMESTONE | SOLAR | NORTH | 2024 | 4 | 4
1002 | MEXIA2_MEXIA2 |  | MEXIA2_MEXIA2 | LIMESTONE | SOLAR | NORTH | 2024 | 4 | 4
1003 | MISAE SOLAR U1 |  | MISAE_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 121.4 | 121.4
1004 | MISAE SOLAR U2 |  | MISAE_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2021 | 118.6 | 118.6
1005 | MLKF1_MALAKOFF1 |  | MLKF1_MALAKOFF1 | HENDERSON | SOLAR | NORTH | 2024 | 5 | 5
1006 | MLKF2_MALAKOFF2 |  | MLKF2_MALAKOFF2 | HENDERSON | SOLAR | NORTH | 2024 | 5 | 5
1007 | MUSTANG CREEK SOLAR U1 |  | MUSTNGCK_SOLAR1 | JACKSON | SOLAR | SOUTH | 2023 | 61 | 60
1008 | MUSTANG CREEK SOLAR U2 |  | MUSTNGCK_SOLAR2 | JACKSON | SOLAR | SOUTH | 2023 | 91.25 | 90
1009 | NEBULA SOLAR (RAYOS DEL SOL) U1 |  | NEBULA_UNIT1 | CAMERON | SOLAR | COASTAL | 2022 | 137.5 | 137.5
1010 | NOBLE SOLAR U1 |  | NOBLESLR_SOLAR1 | DENTON | SOLAR | NORTH | 2022 | 148.8 | 146.7
1011 | NOBLE SOLAR U2 |  | NOBLESLR_SOLAR2 | DENTON | SOLAR | NORTH | 2022 | 130.2 | 128.3
1012 | NORTH GAINESVILLE |  | NGNSVL_NGAINESV | COOKE | SOLAR | NORTH | 2017 | 5.2 | 5.2
1013 | OBERON SOLAR |  | OBERON_UNIT_1 | ECTOR | SOLAR | WEST | 2020 | 180 | 180
1014 | OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | BEXAR | SOLAR | SOUTH | 2013 | 39.18 | 39.2
1015 | OCI ALAMO 2 SOLAR-ST. HEDWIG |  | STHWG_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 4.4 | 4.4
1016 | OCI ALAMO 3-WALZEM SOLAR |  | WALZM_UNIT1 | BEXAR | SOLAR | SOUTH | 2014 | 5.5 | 5.5
1017 | OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | KINNEY | SOLAR | SOUTH | 2014 | 37.62 | 37.6
1018 | OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | UVALDE | SOLAR | SOUTH | 2015 | 100 | 100
1019 | OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PECOS | SOLAR | WEST | 2016 | 110.2 | 110.2
1020 | OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | HASKELL | SOLAR | WEST | 2016 | 112 | 112
1021 | ORANGE GROVE SOLAR |  | OGS_SLR_UNIT1 | JIM WELLS | SOLAR | SOUTH | 2025 | 130.6 | 130
1022 | PEGASUS_PEGASUS |  | PEGASUS_PEGASUS | UPTON | SOLAR | WEST | 2024 | 10 | 10
1023 | PEREGRINE SOLAR U1 |  | PERE_SLR_UNIT1 | GOLIAD | SOLAR | SOUTH | 2025 | 152.83 | 152.2
1024 | PEREGRINE SOLAR U2 |  | PERE_SLR_UNIT2 | GOLIAD | SOLAR | SOUTH | 2025 | 148.28 | 147.7
1025 | PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | WINKLER | SOLAR | WEST | 2019 | 125.14 | 125.1
1026 | PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | WINKLER | SOLAR | WEST | 2019 | 128.05 | 128.1
1027 | PHOENIX SOLAR |  | PHOENIX_UNIT1 | FANNIN | SOLAR | NORTH | 2021 | 83.9 | 83.9
1028 | PISGAH RIDGE SOLAR U1 |  | PISGAH_SOLAR1 | NAVARRO | SOLAR | NORTH | 2024 | 189.4 | 186.5
1029 | PISGAH RIDGE SOLAR U2 |  | PISGAH_SOLAR2 | NAVARRO | SOLAR | NORTH | 2024 | 64.4 | 63.5
1030 | PITTS DUDIK SOLAR U1 |  | PITTSDDK_UNIT1 | HILL | SOLAR | NORTH | 2023 | 49.6 | 49.6
1031 | PLAINVIEW SOLAR (RAMSEY SOLAR) U1 |  | PLN_UNIT1 | WHARTON | SOLAR | SOUTH | 2025 | 270 | 257
1032 | PLAINVIEW SOLAR (RAMSEY SOLAR) U2 |  | PLN_UNIT2 | WHARTON | SOLAR | SOUTH | 2025 | 270 | 257
1033 | PORTER SOLAR U1 |  | PORT_SLR_UNIT1 | DENTON | SOLAR | NORTH | 2025 | 245.83 | 245
1034 | POWERFIN KINGSBERY |  | PFK_PFKPV | TRAVIS | SOLAR | SOUTH | 2017 | 2.6 | 2.6
1035 | PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | ANDREWS | SOLAR | WEST | 2020 | 153.6 | 153.6
1036 | PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | ANDREWS | SOLAR | WEST | 2020 | 150 | 150
1037 | PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | ANDREWS | SOLAR | WEST | 2021 | 126.5 | 126.5
1038 | PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | ANDREWS | SOLAR | WEST | 2021 | 126.4 | 126.4
1039 | QUEEN SOLAR U1 |  | QUEEN_SL_SOLAR1 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
1040 | QUEEN SOLAR U2 |  | QUEEN_SL_SOLAR2 | UPTON | SOLAR | WEST | 2020 | 102.5 | 102.5
1041 | QUEEN SOLAR U3 |  | QUEEN_SL_SOLAR3 | UPTON | SOLAR | WEST | 2020 | 97.5 | 97.5
1042 | QUEEN SOLAR U4 |  | QUEEN_SL_SOLAR4 | UPTON | SOLAR | WEST | 2020 | 107.5 | 107.5
1043 | RADIAN SOLAR U1 |  | RADN_SLR_UNIT1 | BROWN | SOLAR | NORTH | 2023 | 161.41 | 158.9
1044 | RADIAN SOLAR U2 |  | RADN_SLR_UNIT2 | BROWN | SOLAR | NORTH | 2023 | 166.02 | 162.9
1045 | RAMBLER SOLAR |  | RAMBLER_UNIT1 | TOM GREEN | SOLAR | WEST | 2020 | 211.19 | 200
1046 | RATLIFF SOLAR (CONCHO VALLEY SOLAR) |  | RATLIFF_SOLAR1 | TOM GREEN | SOLAR | WEST | 2023 | 162.43 | 159.8
1047 | RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8
1048 | RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PECOS | SOLAR | WEST | 2016 | 78.75 | 78.8
1049 | REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PECOS | SOLAR | WEST | 2021 | 222 | 222
1050 | REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PECOS | SOLAR | WEST | 2021 | 28 | 28
1051 | RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | COSERVSS_CSS1 | DENTON | SOLAR | NORTH | 2015 | 2 | 2
1052 | RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PECOS | SOLAR | WEST | 2018 | 155.44 | 150
1053 | RIPPEY SOLAR |  | RIPPEY_UNIT1 | COOKE | SOLAR | NORTH | 2020 | 59.8 | 59.8
1054 | ROWLAND SOLAR I |  | ROW_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 101.7 | 100
1055 | ROWLAND SOLAR II |  | ROW_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2024 | 200.7 | 200
1056 | SIGNAL SOLAR |  | SIG_SLR_UNIT1 | HUNT | SOLAR | NORTH | 2025 | 51.6 | 50
1057 | SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | BREWSTER | SOLAR | WEST | 2018 | 50 | 50
1058 | SPARTA SOLAR U1 |  | SPARTA_UNIT1 | BEE | SOLAR | SOUTH | 2023 | 147.5 | 146
1059 | SPARTA SOLAR U2 |  | SPARTA_UNIT2 | BEE | SOLAR | SOUTH | 2023 | 104.9 | 104
1060 | SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | UPTON | SOLAR | WEST | 2017 | 157.5 | 157.5
1061 | STERLING |  | STRLING_STRLING | HUNT | SOLAR | NORTH | 2018 | 10 | 10
1062 | STRATEGIC SOLAR 1 |  | STRATEGC_UNIT1 | ELLIS | SOLAR | NORTH | 2022 | 135 | 127.1
1063 | SUN VALLEY U1 |  | SUNVASLR_UNIT1 | HILL | SOLAR | NORTH | 2024 | 165.75 | 165.8
1064 | SUN VALLEY U2 |  | SUNVASLR_UNIT2 | HILL | SOLAR | NORTH | 2024 | 86.19 | 86.2
1065 | SUNEDISON CPS3 SOMERSET 1 SOLAR |  | SOME1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5.6 | 5.6
1066 | SUNEDISON RABEL ROAD SOLAR |  | VALL1_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
1067 | SUNEDISON SOMERSET 2 SOLAR |  | SOME2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 5 | 5
1068 | SUNEDISON VALLEY ROAD SOLAR |  | VALL2_1UNIT | BEXAR | SOLAR | SOUTH | 2012 | 9.9 | 9.9
1069 | SUNRAY |  | SUN_SLR_UNIT_1 | UVALDE | SOLAR | SOUTH | 2024 | 203.5 | 200
1070 | TALCOWST_TALCO |  | TALCOWST_TALCO | TITUS | SOLAR | NORTH | 2024 | 7.5 | 7.5
1071 | TAVENER U1 (FORT BEND SOLAR) |  | TAV_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2023 | 149.5 | 149.5
1072 | TAVENER U2 (FORT BEND SOLAR) |  | TAV_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2023 | 100.4 | 100.4
1073 | TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PECOS | SOLAR | WEST | 2021 | 125.9 | 125.9
1074 | TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PECOS | SOLAR | WEST | 2021 | 128.9 | 128.9
1075 | TAYGETE SOLAR 2 U1 |  | TAYGETE2_UNIT1 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9
1076 | TAYGETE SOLAR 2 U2 |  | TAYGETE2_UNIT2 | PECOS | SOLAR | WEST | 2023 | 101.9 | 101.9
1077 | TEXAS SOLAR NOVA U1 |  | NOVA1SLR_UNIT1 | KENT | SOLAR | WEST | 2024 | 126.81 | 126
1078 | TEXAS SOLAR NOVA U2 |  | NOVA1SLR_UNIT2 | KENT | SOLAR | WEST | 2024 | 126.7 | 126
1079 | TIERRA BONITA SOLAR U1 |  | TRBT_SLR_PV1 | PECOS | SOLAR | WEST | 2024 | 150 | 149.6
1080 | TIERRA BONITA SOLAR U2 |  | TRBT_SLR_PV2 | PECOS | SOLAR | WEST | 2024 | 156.9 | 156.3
1081 | TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | CULBERSON | SOLAR | WEST | 2021 | 136.8 | 136.8
1082 | TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | CULBERSON | SOLAR | WEST | 2021 | 131.1 | 131.1
1083 | TPE ERATH SOLAR |  | ERATH_ERATH21 | ERATH | SOLAR | NORTH | 2021 | 10 | 10
1084 | TRN_TRINITYBAY |  | TRN_TRINITYBAY | CHAMBERS | SOLAR | HOUSTON | 2024 | 1.5 | 1.5
1085 | TRUE NORTH SOLAR U1 |  | TNS_SLR_UNIT1 | FALLS | SOLAR | NORTH | 2024 | 119.35 | 118.8
1086 | TRUE NORTH SOLAR U2 |  | TNS_SLR_UNIT2 | FALLS | SOLAR | NORTH | 2024 | 119.45 | 118.9
1087 | VANCOURT SOLAR |  | VANCOURT_UNIT1 | CAMERON | SOLAR | COASTAL | 2023 | 45.7 | 45.7
1088 | VISION SOLAR 1 |  | VISION_UNIT1 | NAVARRO | SOLAR | NORTH | 2022 | 129.2 | 120.7
1089 | WAGYU SOLAR |  | WGU_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2021 | 120 | 120
1090 | WALNUT SPRINGS |  | WLNTSPRG_1UNIT | BOSQUE | SOLAR | NORTH | 2016 | 10 | 10
1091 | WAYMARK SOLAR |  | WAYMARK_UNIT1 | UPTON | SOLAR | WEST | 2018 | 182 | 182
1092 | WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | TRAVIS | SOLAR | SOUTH | 2011 | 26.7 | 26.7
1093 | WEST MOORE II |  | WMOOREII_WMOOREII | GRAYSON | SOLAR | NORTH | 2018 | 5 | 5
1094 | WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | REEVES | SOLAR | WEST | 2019 | 100 | 100
1095 | WESTORIA SOLAR U1 |  | WES_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6
1096 | WESTORIA SOLAR U2 |  | WES_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2022 | 101.6 | 101.6
1097 | WHITESBORO |  | WBORO_WHTSBORO | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
1098 | WHITESBORO II |  | WBOROII_WHBOROII | GRAYSON | SOLAR | NORTH | 2017 | 5 | 5
1099 | WHITEWRIGHT |  | WHTRT_WHTRGHT | FANNIN | SOLAR | NORTH | 2017 | 10 | 10
1100 | WHSOLAR_WILDHORSE_SOLAR |  | WHSOLAR_WILDHORSE_SOLAR | HOWARD | SOLAR | WEST | 2024 | 10 | 10
1101 | XE MURAT [ADLONG] SOLAR |  | ADL_SOLAR1 | HARRIS | SOLAR | HOUSTON | 2025 | 60.14 | 60
1102 | YELLOW JACKET SOLAR |  | YLWJACKET_YLWJACKET | BOSQUE | SOLAR | NORTH | 2018 | 5 | 5
1103 | ZIER SOLAR |  | ZIER_SLR_PV1 | KINNEY | SOLAR | SOUTH | 2024 | 161.28 | 160
1104 | Operational Capacity Total (Solar) | [6 empty] | 21273.26 | 21093.1
1105
1106 | Operational Resources (Solar) - Synchronized but not Approved for Commercial Operations
1107 | AZALEA SPRINGS SOLAR | 19INR0110 | AZSP_SLR_SOLAR1 | ANGELINA | SOLAR | NORTH | 2025 | 181 | 180
1108 | BAKER BRANCH SOLAR U1 | 23INR0026 | BAKE_SLR_UNIT1 | LAMAR | SOLAR | NORTH | 2026 | 234.84 | 233.9
1109 | BAKER BRANCH SOLAR U2 | 23INR0026 | BAKE_SLR_UNIT2 | LAMAR | SOLAR | NORTH | 2026 | 234.57 | 233.9
1110 | BIG STAR SOLAR U1 | 21INR0413 | BIG_STAR_UNIT1 | BASTROP | SOLAR | SOUTH | 2025 | 132.27 | 130
1111 | BIG STAR SOLAR U2 | 21INR0413 | BIG_STAR_UNIT2 | BASTROP | SOLAR | SOUTH | 2025 | 70.83 | 70
1112 | BLEVINS SOLAR U2 | 23INR0118 | BLVN_SLR_SOLAR2 | FALLS | SOLAR | NORTH | 2025 | 132.02 | 132
1113 | BLEVINS SOLAR U3 | 23INR0118 | BLVN_SLR_SOLAR3 | FALLS | SOLAR | NORTH | 2025 | 139.74 | 138
1114 | BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | GRIMES | SOLAR | NORTH | 2025 | 69 | 69
1115 | BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | GRIMES | SOLAR | NORTH | 2025 | 141 | 141
1116 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2025 | 217.5 | 217.5
1117 | BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2025 | 221.3 | 221.3
1118 | CHILLINGHAM SOLAR U1 | 23INR0070 | CHIL_SLR_SOLAR1 | BELL | SOLAR | NORTH | 2025 | 174.3 | 173
1119 | CHILLINGHAM SOLAR U2 | 23INR0070 | CHIL_SLR_SOLAR2 | BELL | SOLAR | NORTH | 2025 | 178.1 | 177
1120 | COMPADRE SOLAR U1 | 24INR0023 | CMPD_SLR_SOLAR1 | HILL | SOLAR | NORTH | 2025 | 195.17 | 194.5
1121 | COMPADRE SOLAR U2 | 24INR0023 | CMPD_SLR_SOLAR2 | HILL | SOLAR | NORTH | 2025 | 211.37 | 211.2
1122 | COTTONWOOD BAYOU SOLAR I U1 | 19INR0134 | CTW_SOLAR1 | BRAZORIA | SOLAR | COASTAL | 2025 | 175.69 | 175
1123 | COTTONWOOD BAYOU SOLAR I U2 | 19INR0134 | CTW_SOLAR2 | BRAZORIA | SOLAR | COASTAL | 2025 | 175.71 | 175
1124 | DAMAZO (SECOND DIVISION) SOLAR | 20INR0248 | DMA_SOLAR1 | BRAZORIA | SOLAR | COASTAL | 2025 | 100.2 | 100
1125 | DANISH FIELDS SOLAR U1 | 20INR0069 | DAN_UNIT1 | WHARTON | SOLAR | SOUTH | 2025 | 301.3 | 300
1126 | DANISH FIELDS SOLAR U2 | 20INR0069 | DAN_UNIT2 | WHARTON | SOLAR | SOUTH | 2025 | 151 | 150.2
1127 | DANISH FIELDS SOLAR U3 | 20INR0069 | DAN_UNIT3 | WHARTON | SOLAR | SOUTH | 2025 | 150.5 | 149.8
1128 | DELILAH SOLAR 1 U1 | 22INR0202 | DELILA_1_G1 | LAMAR | SOLAR | NORTH | 2025 | 153.54 | 150
1129 | DELILAH SOLAR 1 U2 | 22INR0202 | DELILA_1_G2 | LAMAR | SOLAR | NORTH | 2025 | 153.54 | 150
1130 | DELILAH SOLAR 2 U1 | 22INR0203 | DELILA_2_G1 | RED RIVER | SOLAR | NORTH | 2025 | 107.09 | 105
1131 | DELILAH SOLAR 2 U2 | 22INR0203 | DELILA_2_G2 | RED RIVER | SOLAR | NORTH | 2025 | 103.4 | 100
1132 | DELILAH SOLAR 2 U3 | 22INR0203 | DELILA_2_G3 | RED RIVER | SOLAR | NORTH | 2025 | 107.09 | 105
1133 | DIVER SOLAR U1 | 25INR0105 | DIVR_SLR_SOLAR1 | LIMESTONE | SOLAR | NORTH | 2025 | 71 | 69.8
1134 | DIVER SOLAR U2 | 25INR0105 | DIVR_SLR_SOLAR2 | LIMESTONE | SOLAR | NORTH | 2025 | 155.2 | 155.2
1135 | DRY CREEK SOLAR I | 23INR0286 | DRCK_SLR_SOLAR1 | HENDERSON | SOLAR | NORTH | 2026 | 200.1 | 200
1136 | EASTBELL MILAM SOLAR | 21INR0203 | EBELLSLR_UNIT1 | MILAM | SOLAR | SOUTH | 2025 | 244.86 | 240
1137 | EASTBELL MILAM SOLAR II | 24INR0208 | EBELLSL2_UNIT1 | MILAM | SOLAR | SOUTH | 2025 | 150.6 | 150
1138 | ELIZA SOLAR | 21INR0368 | ELZA_SLR_SOLAR1 | KAUFMAN | SOLAR | NORTH | 2025 | 151.7 | 151
1139 | FAGUS SOLAR PARK 1 SLF | 20INR0091 | FAGUSSLR_UNIT1 | CHILDRESS | SOLAR | PANHANDLE | 2026 | 186.83 | 185.7
1140 | FAGUS SOLAR PARK 2 SLF | 25INR0672 | FAGUSSLR_UNIT2 | CHILDRESS | SOLAR | PANHANDLE | 2025 | 166.42 | 165.8
1141 | FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | FORT BEND | SOLAR | HOUSTON | 2025 | 179.6 | 119.3
1142 | FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | FORT BEND | SOLAR | HOUSTON | 2025 | 171.9 | 159.9
1143 | GRANSOLAR TEXAS ONE | 22INR0511 | GRAN_SLR_UNIT1 | MILAM | SOLAR | SOUTH | 2025 | 50.19 | 50
1144 | GRIMES COUNTY SOLAR U1 | 23INR0160 | GRIM_SLR_UNIT1 | GRIMES | SOLAR | NORTH | 2025 | 104.46 | 103.8
1145 | GRIMES COUNTY SOLAR U2 | 23INR0160 | GRIM_SLR_UNIT2 | GRIMES | SOLAR | NORTH | 2025 | 79.87 | 79.4
1146 | GRIMES COUNTY SOLAR U3 | 23INR0160 | GRIM_SLR_UNIT3 | GRIMES | SOLAR | NORTH | 2025 | 26.92 | 26.8
1147 | HORNET SOLAR U1 | 23INR0021 | HRNT_SLR_UNIT1 | SWISHER | SOLAR | PANHANDLE | 2025 | 200.65 | 200
1148 | HORNET SOLAR U2 | 23INR0021 | HRNT_SLR_UNIT2 | SWISHER | SOLAR | PANHANDLE | 2025 | 200.54 | 200
1149 | HORNET SOLAR U3 | 23INR0021 | HRNT_SLR_UNIT3 | SWISHER | SOLAR | PANHANDLE | 2025 | 201.18 | 200
1150 | HOVEY (BARILLA SOLAR 1B) | 12INR0059b | HOVEY_UNIT2 | PECOS | SOLAR | WEST | 2025 | 7.41 | 7.4
1151 | JUNGMANN SOLAR | 22INR0356 | JUNG_SLR_UNIT1 | MILAM | SOLAR | SOUTH | 2025 | 40.21 | 40
1152 | MARKUM SOLAR | 20INR0230 | MRKM_SLR_PV1 | MCLENNAN | SOLAR | NORTH | 2025 | 161.5 | 161
1153 | MORROW LAKE SOLAR | 19INR0155 | MROW_SLR_SOLAR1 | FRIO | SOLAR | SOUTH | 2025 | 202.2 | 200
1154 | MYRTLE SOLAR U1 | 19INR0041 | MYR_UNIT1 | BRAZORIA | SOLAR | COASTAL | 2025 | 171.6 | 167.2
1155 | MYRTLE SOLAR U2 | 19INR0041 | MYR_UNIT2 | BRAZORIA | SOLAR | COASTAL | 2025 | 149.6 | 145.8
1156 | NORTON SOLAR | 19INR0035 | NRTN_SLR_SOLAR1 | RUNNELS | SOLAR | WEST | 2025 | 125.54 | 125
1157 | ORIANA SOLAR | 24INR0093 | ORIANA_UNIT1 | VICTORIA | SOLAR | SOUTH | 2025 | 180.67 | 180.1
1158 | OUTPOST SOLAR U1 | 23INR0007 | OUTP_SLR_UNIT1 | WEBB | SOLAR | SOUTH | 2025 | 257.95 | 257
1159 | OUTPOST SOLAR U2 | 23INR0007 | OUTP_SLR_UNIT2 | WEBB | SOLAR | SOUTH | 2025 | 259.11 | 258.2
1160 | PARLIAMENT SOLAR U1 | 23INR0044 | PAR_UNIT1 | WALLER | SOLAR | HOUSTON | 2025 | 243.2 | 242.7
1161 | PARLIAMENT SOLAR U2 | 23INR0044 | PAR_UNIT2 | WALLER | SOLAR | HOUSTON | 2025 | 240.2 | 239.4
1162 | PHOTON SOLAR U1 | 25INR0493 | PHO_SOLAR1 | WHARTON | SOLAR | SOUTH | 2025 | 129.59 | 129.1
1163 | PHOTON SOLAR U2 | 25INR0493 | PHO_SOLAR2 | WHARTON | SOLAR | SOUTH | 2025 | 106.07 | 105.7
1164 | PHOTON SOLAR U3 | 23INR0111 | PHO_SOLAR3 | WHARTON | SOLAR | SOUTH | 2025 | 109.99 | 109.6
1165 | PHOTON SOLAR U4 | 25INR0673 | PHO_SOLAR4 | WHARTON | SOLAR | SOUTH | 2025 | 105.98 | 105.7
1166 | PINE FOREST SOLAR U1 | 20INR0203 | PINEFRST_UNIT1 | HOPKINS | SOLAR | NORTH | 2025 | 242.7 | 242.7
1167 | PINE FOREST SOLAR U2 | 20INR0203 | PINEFRST_UNIT2 | HOPKINS | SOLAR | NORTH | 2025 | 58.9 | 58.9
1168 | ROSELAND SOLAR U1 | 20INR0205 | ROSELAND_SOLAR1 | FALLS | SOLAR | NORTH | 2025 | 254 | 250
1169 | ROSELAND SOLAR U2 | 20INR0205 | ROSELAND_SOLAR2 | FALLS | SOLAR | NORTH | 2025 | 137.8 | 135.6
1170 | ROSELAND SOLAR U3 | 22INR0506 | ROSELAND_SOLAR3 | FALLS | SOLAR | NORTH | 2025 | 116.2 | 114.4
1171 | SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | LAMAR | SOLAR | NORTH | 2026 | 128.42 | 125
1172 | SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | LAMAR | SOLAR | NORTH | 2026 | 128.42 | 125
1173 | SAMSON SOLAR 2 U1 | 21INR0490 | SAMSON_1_G3 | LAMAR | SOLAR | NORTH | 2025 | 101.52 | 100
1174 | SAMSON SOLAR 2 U2 | 21INR0490 | SAMSON_1_G4 | LAMAR | SOLAR | NORTH | 2025 | 101.52 | 100
1175 | SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | LAMAR | SOLAR | NORTH | 2026 | 128.42 | 125
1176 | SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | LAMAR | SOLAR | NORTH | 2026 | 128.42 | 125
1177 | SBRANCH SOLAR PROJECT | 22INR0205 | SBE_UNIT1 | WHARTON | SOLAR | SOUTH | 2025 | 233.5 | 233.5
1178 | STAMPEDE SOLAR U1 | 22INR0409 | STAM_SLR_SOLAR1 | HOPKINS | SOLAR | NORTH | 2025 | 77.75 | 77
1179 | STAMPEDE SOLAR U2 | 22INR0409 | STAM_SLR_SOLAR2 | HOPKINS | SOLAR | NORTH | 2025 | 178.55 | 178
1180 | STARR SOLAR RANCH U1 | 20INR0216 | STAR_SLR_UNIT1 | STARR | SOLAR | SOUTH | 2025 | 70.45 | 70
1181 | STARR SOLAR RANCH U2 | 20INR0216 | STAR_SLR_UNIT2 | STARR | SOLAR | SOUTH | 2025 | 66.28 | 66
1182 | STILLHOUSE SOLAR | 24INR0166 | STLHS_SL_PV1 | BELL | SOLAR | NORTH | 2025 | 210.8 | 210
1183 | STONERIDGE SOLAR U1 | 24INR0031 | STRG_SLR_UNIT1 | MILAM | SOLAR | SOUTH | 2025 | 184.1 | 184.1
1184 | STONERIDGE SOLAR U2 | 24INR0031 | STRG_SLR_UNIT2 | MILAM | SOLAR | SOUTH | 2025 | 17.5 | 17.5
1185 | TEXAS SOLAR NOVA 2 U1 | 20INR0269 | NOVA2SLR_UNIT1 | KENT | SOLAR | WEST | 2025 | 202.37 | 200
1186 | TRES BAHIAS SOLAR | 20INR0266 | TREB_SLR_SOLAR1 | CALHOUN | SOLAR | COASTAL | 2025 | 196.29 | 195
1187 | TULSITA SOLAR U1 | 21INR0223 | TUL_SLR_UNIT1 | GOLIAD | SOLAR | SOUTH | 2025 | 128.08 | 127.8
1188 | TULSITA SOLAR U2 | 21INR0223 | TUL_SLR_UNIT2 | GOLIAD | SOLAR | SOUTH | 2025 | 128.12 | 127.8
1189 | TYSON NICK SOLAR | 20INR0222 | TYSN_SLR_UNIT1 | LAMAR | SOLAR | NORTH | 2025 | 90.5 | 90
1190 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Solar) | [6 empty] | 12555.52 | 12391.2
1191
1192 | Operational Resources (Storage)
1193 | AE-TELVIEW ESS |  | TV_BESS | FORT BEND | STORAGE | HOUSTON | 2024 | 9.96 | 10
1194 | AL PASTOR BESS |  | ALP_BESS_BESS1 | DAWSON | STORAGE | WEST | 2024 | 103.1 | 100.3
1195 | ANCHOR BESS U1 |  | ANCHOR_BESS1 | CALLAHAN | STORAGE | WEST | 2022 | 35.2 | 35.2
1196 | ANCHOR BESS U2 |  | ANCHOR_BESS2 | CALLAHAN | STORAGE | WEST | 2022 | 36.3 | 36.3
1197 | ANEMOI ENERGY STORAGE |  | ANEM_ESS_BESS1 | HIDALGO | STORAGE | SOUTH | 2024 | 200.9 | 200
1198 | ANGELO STORAGE |  | ANG_SLR_BESS1 | TOM GREEN | STORAGE | WEST | 2025 | 102.97 | 100
1199 | ANGLETON BESS |  | AE_BESS | BRAZORIA | STORAGE | COASTAL | 2025 | 9.9 | 9.9
1200 | ANOLE BESS |  | ANOL_ESS_BES1 | DALLAS | STORAGE | NORTH | 2025 | 247.1 | 240
1201 | AZURE SKY BESS |  | AZURE_BESS1 | HASKELL | STORAGE | WEST | 2021 | 77.6 | 77.6
1202 | BAT CAVE |  | BATCAVE_BES1 | MASON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
1203 | BAY CITY BESS |  | BAY_CITY_BESS | MATAGORDA | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1204 | BELDING TNP (TRIPLE BUTTE BATTERY) |  | BELD_BELU1 | PECOS | STORAGE | WEST | 2021 | 9.18 | 7.5
1205 | BLUE JAY BESS |  | BLUEJAY_BESS1 | GRIMES | STORAGE | NORTH | 2022 | 51.6 | 50
1206 | BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | WILBARGER | STORAGE | WEST | 2017 | 30 | 30
1207 | BOCO BESS |  | BOCO_ESS_ESS1 | BORDEN | STORAGE | WEST | 2024 | 154 | 150
1208 | BRIGHT ARROW STORAGE U1 |  | BR_ARROW_BESS1 | HOPKINS | STORAGE | NORTH | 2025 | 49.34 | 48.3
1209 | BRIGHT ARROW STORAGE U2 |  | BR_ARROW_BESS2 | HOPKINS | STORAGE | NORTH | 2025 | 52.77 | 51.7
1210 | BRP ALVIN |  | ALVIN_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10
1211 | BRP ANGLETON |  | ANGLETON_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10
1212 | BRP BRAZORIA |  | BRAZORIA_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2020 | 9.95 | 10
1213 | BRP DICKINSON |  | DICKNSON_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10
1214 | BRP DICKENS BESS U1 |  | DKNS_ESS_BES1 | DICKENS | STORAGE | PANHANDLE | 2024 | 50.2 | 50
1215 | BRP DICKENS BESS U2 |  | DKNS_ESS_BES2 | DICKENS | STORAGE | PANHANDLE | 2024 | 50.2 | 50
1216 | BRP DICKENS BESS U3 |  | DKNS_ESS_BES3 | DICKENS | STORAGE | PANHANDLE | 2024 | 50.2 | 50
1217 | BRP DICKENS BESS U4 |  | DKNS_ESS_BES4 | DICKENS | STORAGE | PANHANDLE | 2024 | 50.2 | 50
1218 | BRP HEIGHTS |  | HEIGHTTN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2020 | 9.95 | 10
1219 | BRP HYDRA BESS |  | HYDR_ESS_BES1 | PECOS | STORAGE | WEST | 2024 | 200.8 | 200
1220 | BRP LIBRA BESS |  | LBRA_ESS_BES1 | GUADALUPE | STORAGE | SOUTH | 2024 | 201.02 | 200
1221 | BRP LOOP 463 |  | L_463S_UNIT1 | VICTORIA | STORAGE | SOUTH | 2021 | 9.95 | 10
1222 | BRP LOPENO |  | LOPENO_UNIT1 | ZAPATA | STORAGE | SOUTH | 2021 | 9.95 | 10
1223 | BRP MAGNOLIA |  | MAGNO_TN_UNIT1 | GALVESTON | STORAGE | HOUSTON | 2022 | 9.95 | 10
1224 | BRP ODESSA SW |  | ODESW_UNIT1 | ECTOR | STORAGE | WEST | 2020 | 9.95 | 10
1225 | BRP PALEO BESS |  | PALE_ESS_BES1 | HALE | STORAGE | PANHANDLE | 2024 | 200.8 | 200
1226 | BRP PAVO BESS U1 |  | PAVO_ESS_BESS1 | PECOS | STORAGE | WEST | 2024 | 87.9 | 87.5
1227 | BRP PAVO BESS U2 |  | PAVO_ESS_BESS2 | PECOS | STORAGE | WEST | 2024 | 87.9 | 87.5
1228 | BRP PUEBLO I |  | BRP_PBL1_UNIT1 | MAVERICK | STORAGE | SOUTH | 2021 | 9.95 | 10
1229 | BRP PUEBLO II |  | BRP_PBL2_UNIT1 | MAVERICK | STORAGE | SOUTH | 2021 | 9.95 | 10
1230 | BRP RANCHTOWN |  | K0_UNIT1 | BEXAR | STORAGE | SOUTH | 2021 | 9.95 | 10
1231 | BRP SWEENY |  | SWEENY_UNIT1 | BRAZORIA | STORAGE | COASTAL | 2022 | 9.95 | 10
1232 | BRP TORTOLAS BESS |  | TORT_ESS_BESS1 | BRAZORIA | STORAGE | COASTAL | 2025 | 50.3 | 50
1233 | BRP ZAPATA I |  | ZAPATA_UNIT1 | ZAPATA | STORAGE | SOUTH | 2020 | 9.95 | 10
1234 | BRP ZAPATA II |  | ZAPATA_UNIT2 | ZAPATA | STORAGE | SOUTH | 2021 | 9.95 | 10
1235 | BURKSOL BESS (DONEGAL BESS) |  | BKSL_ESS_BESS1 | DICKENS | STORAGE | PANHANDLE | 2025 | 103.27 | 100
1236 | BYRD RANCH STORAGE |  | BYRDR_ES_BESS1 | BRAZORIA | STORAGE | COASTAL | 2022 | 50.6 | 50
1237 | CALLISTO I ENERGY CENTER U1 |  | CLO_BESS1 | HARRIS | STORAGE | HOUSTON | 2024 | 101.5 | 100
1238 | CALLISTO I ENERGY CENTER U2 |  | CLO_BESS2 | HARRIS | STORAGE | HOUSTON | 2024 | 101.5 | 100
1239 | CAMERON STORAGE (SABAL STORAGE) |  | CAMWIND_BESS1 | CAMERON | STORAGE | COASTAL | 2024 | 16.67 | 16.4
1240 | CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | UPTON | STORAGE | WEST | 2018 | 9.9 | 9.9
1241 | CATARINA BESS |  | CATARINA_BESS | DIMMIT | STORAGE | SOUTH | 2022 | 9.95 | 9.9
1242 | CENTURY BESS |  | CNTRY_BESS1 | TARRANT | STORAGE | NORTH | 2024 | 9.88 | 9.9
1243 | CEDARVALE BESS |  | CEDRVALE_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1244 | CHILLINGHAM STORAGE |  | CHIL_SL1_BESS1 | BELL | STORAGE | NORTH | 2025 | 153.93 | 150
1245 | CHISHOLM GRID |  | CHISMGRD_BES1 | TARRANT | STORAGE | NORTH | 2021 | 101.7 | 0
1246 | CITRUS CITY BESS |  | CITRUSCY_BESS1 | HIDALGO | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1247 | CISCO BESS |  | CISC_BESS | EASTLAND | STORAGE | NORTH | 2024 | 9.9 | 9.9
1248 | CONTINENTAL BESS |  | CONTINEN_BESS1 | STARR | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1249 | COMMERCE ST ESS |  | X4_SWRI | BEXAR | STORAGE | SOUTH | 2020 | 10 | 10
1250 | CONNOLLY STORAGE |  | CNLY_ESS_BESS_1 | WISE | STORAGE | NORTH | 2024 | 125.41 | 125
1251 | CORAL STORAGE U1 |  | CORALSLR_BESS1 | FALLS | STORAGE | NORTH | 2023 | 48.4 | 47.6
1252 | CORAL STORAGE U2 |  | CORALSLR_BESS2 | FALLS | STORAGE | NORTH | 2023 | 52.2 | 51.4
1253 | COYOTE SPRINGS BESS |  | COYOTSPR_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1254 | CROCKETT BESS |  | CR_BESS1 | HARRIS | STORAGE | HOUSTON | 2024 | 9.88 | 9.9
1255 | CROSBY BESS |  | CS_BESS | HARRIS | STORAGE | HOUSTON | 2025 | 9.9 | 9.9
1256 | CROSS TRAILS STORAGE |  | CROSSTRL_BESS1 | SCURRY | STORAGE | WEST | 2025 | 58.29 | 57
1257 | CROSSETT POWER U1 |  | CROSSETT_BES1 | CRANE | STORAGE | WEST | 2021 | 101.5 | 100
1258 | CROSSETT POWER U2 |  | CROSSETT_BES2 | CRANE | STORAGE | WEST | 2021 | 101.5 | 100
1259 | DAMON STORAGE |  | DA_BESS | BRAZORIA | STORAGE | COASTAL | 2025 | 4.98 | 5
1260 | DANISH FIELDS STORAGE U1 |  | DAN_BESS1 | WHARTON | STORAGE | SOUTH | 2025 | 77.8 | 76.3
1261 | DANISH FIELDS STORAGE U2 |  | DAN_BESS2 | WHARTON | STORAGE | SOUTH | 2025 | 75.1 | 73.7
1262 | DECORDOVA BESS U1 |  | DCSES_BES1 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1263 | DECORDOVA BESS U2 |  | DCSES_BES2 | HOOD | STORAGE | NORTH | 2022 | 67.3 | 66.5
1264 | DECORDOVA BESS U3 |  | DCSES_BES3 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1265 | DECORDOVA BESS U4 |  | DCSES_BES4 | HOOD | STORAGE | NORTH | 2022 | 64.2 | 63.5
1266 | DESERT WILLOW BESS |  | DSWL_ESS_BES1 | ELLIS | STORAGE | NORTH | 2025 | 154.4 | 150
1267 | DIBOLL BESS |  | DIBOL_BESS | ANGELINA | STORAGE | NORTH | 2023 | 9.95 | 9.9
1268 | DOGFISH BESS |  | DGFS_ESR_BESS1 | PECOS | STORAGE | WEST | 2025 | 78.2 | 75
1269 | EBONY ENERGY STORAGE |  | EBNY_ESS_BESS1 | COMAL | STORAGE | SOUTH | 2024 | 201.2 | 200
1270 | ENDURANCE PARK STORAGE |  | ENDPARKS_ESS1 | SCURRY | STORAGE | WEST | 2022 | 51.5 | 50
1271 | ELIZA STORAGE |  | ELZA_SLR_BES1 | KAUFMAN | STORAGE | NORTH | 2025 | 100.4 | 100
1272 | ESTONIAN ENERGY STORAGE |  | ESTONIAN_BES1 | DELTA | STORAGE | NORTH | 2023 | 101.6 | 101.6
1273 | EUNICE STORAGE |  | EUNICE_BES1 | ANDREWS | STORAGE | WEST | 2020 | 40.3 | 40.3
1274 | FALFUR BESS |  | FALFUR_BESS | BROOKS | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1275 | FALFURRIAS BESS |  | FALFUR1_BESS1 | BROOKS | STORAGE | SOUTH | 2025 | 9.8 | 9.8
1276 | FARMERSVILLE BESS |  | FRMRSVLW_BESS | COLLIN | STORAGE | NORTH | 2024 | 9.9 | 9.9
1277 | FARMERSVILLE WEST BESS 2 |  | FRMRSVL1_BES2 | COLLIN | STORAGE | NORTH | 2025 | 9.9 | 9.9
1278 | FAULKNER BESS |  | FAULKNER_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1279 | FENCE POST BESS U1 |  | FENCESLR_BESS1 | NAVARRO | STORAGE | NORTH | 2023 | 72.01 | 70
1280 | FIVE WELLS STORAGE |  | FIVEWSLR_BESS1 | BELL | STORAGE | NORTH | 2024 | 228.54 | 220
1281 | FLAT TOP BATTERY |  | FLAT_TOP_FLATU1 | REEVES | STORAGE | WEST | 2020 | 9.9 | 9.9
1282 | FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | REEVES | STORAGE | WEST | 2021 | 101.5 | 100
1283 | FORT DUNCAN BESS |  | FTDUNCAN_BESS_GEN | MAVERICK | STORAGE | SOUTH | 2025 | 101.6 | 100
1284 | FORT MASON BESS |  | FORTMA_BESS1 | MASON | STORAGE | SOUTH | 2025 | 9.99 | 10
1285 | GAMBIT BATTERY |  | GAMBIT_BESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 102.4 | 100
1286 | GARDEN CITY EAST BESS |  | GRDNE_BESS | GLASSCOCK | STORAGE | WEST | 2023 | 9.95 | 9.9
1287 | GEORGETOWN SOUTH (RABBIT HILL ESS) |  | GEORSO_ESS_1 | WILLIAMSON | STORAGE | SOUTH | 2019 | 9.9 | 9.9
1288 | GIGA TEXAS ENERGY STORAGE |  | GIGA_ESS_BESS_1 | TRAVIS | STORAGE | SOUTH | 2024 | 125.31 | 125
1289 | GOMEZ BESS |  | GOMZ_BESS | REEVES | STORAGE | WEST | 2023 | 9.95 | 9.9
1290 | GREAT KISKADEE STORAGE |  | GKS_BESS_BESS1 | HIDALGO | STORAGE | SOUTH | 2025 | 102.46 | 100
1291 | GREGORY BESS |  | GREGORY_BESS1 | SAN PATRICIO | STORAGE | COASTAL | 2024 | 9.9 | 9.9
1292 | HAMILTON BESS U1 |  | HAMILTON_BESS | VAL VERDE | STORAGE | WEST | 2023 | 9.9 | 9.9
1293 | HEARN ROAD BESS |  | HEARN_RD_BESS1 | NUECES | STORAGE | COASTAL | 2025 | 9.8 | 9.8
1294 | HIGH LONESOME BESS |  | HI_LONEB_BESS1 | CROCKETT | STORAGE | WEST | 2022 | 51.1 | 50
1295 | HOLCOMB BESS |  | HOLCOMB_BESS | LA SALLE | STORAGE | SOUTH | 2022 | 9.95 | 9.9
1296 | HOLY ESS U1 |  | HLY_BESS1 | HARRIS | STORAGE | HOUSTON | 2024 | 104.66 | 102.2
1297 | HOLY ESS U2 |  | HLY_BESS2 | HARRIS | STORAGE | HOUSTON | 2024 | 104.66 | 102.2
1298 | HOUSE MOUNTAIN BESS |  | HOUSEMTN_BESS1 | BREWSTER | STORAGE | WEST | 2023 | 61.5 | 60
1299 | HUMMINGBIRD STORAGE |  | HMNG_ESS_BESS1 | DENTON | STORAGE | NORTH | 2024 | 100.38 | 100
1300 | INADALE ESS |  | INDL_ESS | NOLAN | STORAGE | WEST | 2017 | 9.9 | 9.9
1301 | JOHNSON CITY BESS |  | JOHNCI_UNIT_1 | BLANCO | STORAGE | SOUTH | 2020 | 2.25 | 2.3
1302 | JARVIS BESS U1 |  | JAR_BES1 | BRAZORIA | STORAGE | COASTAL | 2025 | 149.29 | 147.2
1303 | JARVIS BESS U2 |  | JAR_BES2 | BRAZORIA | STORAGE | COASTAL | 2025 | 157.71 | 157.7
1304 | JUDKINS BESS |  | JDKNS_BESS | ECTOR | STORAGE | WEST | 2024 | 9.95 | 10
1305 | JUNCTION BESS |  | JUNCTION_BESS | KIMBLE | STORAGE | SOUTH | 2023 | 9.95 | 9.9
1306 | JUNCTION NORTH BESS |  | JUNORTH1_BES1 | KIMBLE | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1307 | KINGSBERY ENERGY STORAGE SYSTEM |  | KB_ESS_KB_ESS | TRAVIS | STORAGE | SOUTH | 2017 | 1.5 | 1.5
1308 | LIGGETT SWITCH BESS |  | LIGSW_BESS1 | DALLAS | STORAGE | NORTH | 2025 | 9.88 | 9.9
1309 | LILY STORAGE |  | LILY_BESS1 | KAUFMAN | STORAGE | NORTH | 2021 | 51.7 | 50
1310 | LIMOUSIN OAK STORAGE |  | LMO_BESS1 | GRIMES | STORAGE | NORTH | 2024 | 100.42 | 100
1311 | LONESTAR BESS |  | LONESTAR_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9
1312 | LONGBOW BESS |  | LON_BES1 | BRAZORIA | STORAGE | COASTAL | 2024 | 180.8 | 174
1313 | LUFKIN SOUTH BESS |  | LFSTH_BESS | ANGELINA | STORAGE | NORTH | 2024 | 9.95 | 10
1314 | MADERO GRID U1 |  | MADERO_UNIT1 | HIDALGO | STORAGE | SOUTH | 2022 | 100.79 | 100
1315 | MADERO GRID U2 (IGNACIO GRID) |  | MADERO_UNIT2 | HIDALGO | STORAGE | SOUTH | 2022 | 100.79 | 100
1316 | MAINLAND BESS |  | MAINLAND_BESS | GALVESTON | STORAGE | HOUSTON | 2024 | 9.9 | 9.9
1317 | MAYBERRY II BESS |  | MAYBERRY_BESS2 | HIDALGO | STORAGE | SOUTH | 2025 | 9.99 | 9.9
1318 | MIDWAY BESS U1 |  | MIDWY_BESS1 | ECTOR | STORAGE | WEST | 2025 | 9.95 | 10
1319 | MINERAL WELLS EAST BESS |  | MNWLE_BESS | PALO PINTO | STORAGE | NORTH | 2023 | 9.95 | 9.9
1320 | MU ENERGY STORAGE SYSTEM |  | MU_ESS_MU_ESS | TRAVIS | STORAGE | SOUTH | 2018 | 1.5 | 1.5
1321 | MUENSTER BESS |  | MUENSTER_BESS1 | COOKE | STORAGE | NORTH | 2025 | 9.9 | 9.9
1322 | MUSTANG BAYOU BESS |  | MU_BESS | BRAZORIA | STORAGE | COASTAL | 2025 | 9.99 | 10
1323 | MUSTANG CREEK STORAGE |  | MUSTNGCK_BES1 | JACKSON | STORAGE | SOUTH | 2023 | 71.49 | 70.5
1324 | MYRTLE STORAGE U1 |  | MYR_BES1 | BRAZORIA | STORAGE | COASTAL | 2025 | 76.93 | 76.3
1325 | MYRTLE STORAGE U2 |  | MYR_BES2 | BRAZORIA | STORAGE | COASTAL | 2025 | 74.27 | 73.7
1326 | NOBLE STORAGE U1 |  | NOBLESLR_BESS1 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5
1327 | NOBLE STORAGE U2 |  | NOBLESLR_BESS2 | DENTON | STORAGE | NORTH | 2022 | 63.5 | 62.5
1328 | NORTH ALAMO BESS |  | N_ALAMO_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1329 | NORTH COLUMBIA (ROUGHNECK STORAGE) |  | NCO_ESS1 | BRAZORIA | STORAGE | COASTAL | 2021 | 51.75 | 50
1330 | NORTH FORK |  | NF_BRP_BES1 | WILLIAMSON | STORAGE | SOUTH | 2021 | 100.5 | 100.5
1331 | NORTH MERCEDES BESS |  | N_MERCED_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1332 | NOTREES BATTERY FACILITY |  | NWF_NBS | WINKLER | STORAGE | WEST | 2012 | 36 | 33.7
1333 | OLNEY BESS |  | OLNEYTN_BESS | YOUNG | STORAGE | WEST | 2023 | 9.95 | 9.9
1334 | PADUA GRID BESS |  | PAD1_ESS_BESS1 | BEXAR | STORAGE | SOUTH | 2025 | 51.1 | 50
1335 | PAULINE BESS |  | PAULN_BESS | HENDERSON | STORAGE | NORTH | 2024 | 9.95 | 10
1336 | PAVLOV BESS |  | PAVLOV_BESS | MATAGORDA | STORAGE | COASTAL | 2024 | 9.9 | 9.9
1337 | PEARSALL BESS |  | PEARSAL3_BES1 | FRIO | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1338 | PHOTON STORAGE U1 |  | PHO_BES1 | WHARTON | STORAGE | SOUTH | 2025 | 152.74 | 150
1339 | PHOTON STORAGE U2 |  | PHO_BES2 | WHARTON | STORAGE | SOUTH | 2025 | 152.74 | 150
1340 | PORT LAVACA BATTERY |  | PRTLAVS_BESS1 | CALHOUN | STORAGE | COASTAL | 2019 | 9.9 | 9.9
1341 | PIRATE BESS |  | PIRATE1_BESS1 | SAN PATRICIO | STORAGE | COASTAL | 2025 | 9.8 | 9.8
1342 | PYOTE TNP (SWOOSE BATTERY) |  | PYOTE_SWOOSEU1 | WARD | STORAGE | WEST | 2021 | 9.9 | 9.9
1343 | PYRON BESS 2A |  | PYR_ESS2A | NOLAN | STORAGE | WEST | 2022 | 15.1 | 15.1
1344 | PYRON BESS 2B |  | PYR_ESS2B | NOLAN | STORAGE | WEST | 2022 | 15.1 | 15.1
1345 | PYRON ESS |  | PYR_ESS | NOLAN | STORAGE | WEST | 2017 | 9.9 | 9.9
1346 | QUEEN BESS |  | QUEEN_BA_BESS1 | UPTON | STORAGE | WEST | 2022 | 51.1 | 50
1347 | RATTLESNAKE BESS |  | RTLSNAKE_BESS | WARD | STORAGE | WEST | 2022 | 9.95 | 9.9
1348 | REGIS MOORE FIELD BESS |  | MOORE_FL_BESS1 | HIDALGO | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1349 | REGIS PALACIOS BESS |  | PALACIOS_BESS1 | MATAGORDA | STORAGE | COASTAL | 2024 | 9.9 | 9.9
1350 | REPUBLIC ROAD STORAGE |  | RPUBRDS_ESS1 | ROBERTSON | STORAGE | NORTH | 2021 | 51.75 | 50
1351 | RIO GRANDE CITY BESS 2 |  | RIO_GRAN_BESS2 | STARR | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1352 | RIVER BEND (BRAZOS BEND BESS) |  | RBN_BESS1 | FORT BEND | STORAGE | HOUSTON | 2024 | 101.64 | 100
1353 | RIVER VALLEY STORAGE U1 |  | RVRVLYS_ESS1 | WILLIAMSON | STORAGE | SOUTH | 2022 | 51.5 | 50
1354 | RIVER VALLEY STORAGE U2 |  | RVRVLYS_ESS2 | WILLIAMSON | STORAGE | SOUTH | 2022 | 51.5 | 50
1355 | RODEO RANCH ENERGY STORAGE U1 |  | RRANCHES_UNIT1 | REEVES | STORAGE | WEST | 2023 | 150.4 | 150
1356 | RODEO RANCH ENERGY STORAGE U2 |  | RRANCHES_UNIT2 | REEVES | STORAGE | WEST | 2023 | 150.4 | 150
1357 | ROSELAND STORAGE |  | ROSELAND_BESS1 | FALLS | STORAGE | NORTH | 2022 | 51.6 | 50
1358 | RUSSEK STREET BESS |  | RUSSEKST_BESS | REAGAN | STORAGE | WEST | 2024 | 9.9 | 9.9
1359 | SADDLEBACK BESS |  | SADLBACK_BESS | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1360 | SANDLAKE BESS |  | SANDLAK1_BESS | REEVES | STORAGE | WEST | 2024 | 9.99 | 10
1361 | SARAGOSA BESS |  | SGSA_BESS1 | REEVES | STORAGE | WEST | 2022 | 9.95 | 9.9
1362 | SCREWBEAN BESS |  | SBEAN_BESS | CULBERSON | STORAGE | WEST | 2022 | 9.95 | 9.9
1363 | SHEEP CREEK STORAGE |  | SHEEPCRK_BESS1 | EASTLAND | STORAGE | NORTH | 2024 | 142.1 | 135.1
1364 | SILICON HILL STORAGE U1 |  | SLCNHLS_ESS1 | TRAVIS | STORAGE | SOUTH | 2021 | 51.8 | 50
1365 | SILICON HILL STORAGE U2 |  | SLCNHLS_ESS2 | TRAVIS | STORAGE | SOUTH | 2021 | 51.8 | 50
1366 | SMT ELSA |  | ELSA_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1367 | SMT GARCENO BESS |  | GARCENO_BESS | MATAGORDA | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1368 | SMT LOS FRESNOS |  | L_FRESNO_BESS | CAMERON | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1369 | SMT MAYBERRY BESS |  | MAYBERRY_BESS | HIDALGO | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1370 | SMT RIO GRANDE CITY BESS |  | RIO_GRAN_BESS | STARR | STORAGE | SOUTH | 2023 | 9.99 | 9.9
1371 | SMT SANTA ROSA |  | S_SNROSA_BESS | CAMERON | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1372 | SNYDER |  | DPCRK_UNIT1 | SCURRY | STORAGE | WEST | 2021 | 9.95 | 10
1373 | SP TX-12B BESS |  | SPTX12B_BES1 | UPTON | STORAGE | WEST | 2021 | 25.1 | 25.1
1374 | STAMPEDE BESS U1 |  | STAM_SLR_BESS1 | HOPKINS | STORAGE | NORTH | 2023 | 73 | 70
1375 | ST. GALL I ENERGY STORAGE |  | SGAL_BES_BESS1 | PECOS | STORAGE | WEST | 2024 | 101.5 | 100
1376 | SUN VALLEY BESS U1 |  | SUNVASLR_BESS1 | HILL | STORAGE | NORTH | 2023 | 54.08 | 53.3
1377 | SUN VALLEY BESS U2 |  | SUNVASLR_BESS2 | HILL | STORAGE | NORTH | 2023 | 47.32 | 46.7
1378 | SWEETWATER BESS |  | SWTWR_UNIT1 | NOLAN | STORAGE | WEST | 2021 | 9.95 | 9.9
1379 | SWOOSE II |  | SWOOSEII_BESS1 | WARD | STORAGE | WEST | 2021 | 101.5 | 100
1380 | TIMBERWOLF BESS |  | TBWF_ESS_BES1 | CRANE | STORAGE | WEST | 2023 | 150.34 | 150
1381 | TOYAH POWER STATION |  | CHERRYCR_BESS | REEVES | STORAGE | WEST | 2021 | 9.95 | 9.9
1382 | TURQUOISE STORAGE |  | TURQBESS_BESS1 | HUNT | STORAGE | NORTH | 2023 | 196.2 | 190
1383 | TYNAN BESS |  | TYNAN01_BESS1 | BEE | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1384 | VAL VERDE BESS |  | MV_VALV4_BESS | HIDALGO | STORAGE | SOUTH | 2024 | 9.9 | 9.9
1385 | VORTEX BESS |  | VORTEX_BESS1 | THROCKMORTON | STORAGE | WEST | 2022 | 121.8 | 121.8
1386 | WEST COLUMBIA (PROSPECT STORAGE) |  | WCOLLOCL_BSS_U1 | BRAZORIA | STORAGE | COASTAL | 2019 | 9.9 | 9.9
1387 | WEST HARLINGEN BESS |  | W_HARLIN_BESS | CAMERON | STORAGE | COASTAL | 2023 | 9.99 | 9.9
1388 | WESTOVER BESS |  | WOVER_UNIT1 | ECTOR | STORAGE | WEST | 2021 | 9.95 | 10
1389 | WEIL TRACT BESS |  | WEIL_TRC_BESS | NUECES | STORAGE | COASTAL | 2023 | 9.95 | 9.9
1390 | WIGEON WHISTLE BESS |  | WIG_ESS_BES1 | COLLIN | STORAGE | NORTH | 2024 | 122.9 | 120
1391 | WOLF TANK STORAGE |  | WFTANK_ESS1 | WEBB | STORAGE | SOUTH | 2023 | 150.4 | 150
1392 | WORSHAM BATTERY |  | WORSHAM_BESS1 | REEVES | STORAGE | WEST | 2019 | 9.9 | 9.9
1393 | ZIER STORAGE U1 |  | ZIER_SLR_BES1 | KINNEY | STORAGE | SOUTH | 2024 | 40.08 | 40
1394 | Operational Capacity Total (Storage) | [6 empty] | 10576.29 | 10320.3
1395
1396 | Operational Resources (Storage) - Synchronized but not Approved for Commercial Operations
1397 | ANDROMEDA STORAGE SLF U1 | 24INR0630 | ANDMDSLR_BESS1 | SCURRY | STORAGE | WEST | 2025 | 82.04 | 81.9
1398 | ANDROMEDA STORAGE SLF U2 | 24INR0630 | ANDMDSLR_BESS2 | SCURRY | STORAGE | WEST | 2025 | 78.31 | 78.1
1399 | ANTLIA BESS | 22INR0349 | ANTL_ESS_BES1 | VAL VERDE | STORAGE | WEST | 2025 | 72.38 | 70
1400 | AVILA BESS | 23INR0287 | AVIL_ESS_BES1 | PECOS | STORAGE | WEST | 2025 | 164.28 | 160
1401 | BEXAR ESS | 23INR0381 | BEXAR_ES_BESS1 | BEXAR | STORAGE | SOUTH | 2025 | 102.3 | 100
1402 | BIG STAR STORAGE | 21INR0469 | BIG_STAR_BESS | BASTROP | STORAGE | SOUTH | 2025 | 80 | 80
1403 | BLEVINS STORAGE | 23INR0119 | BLVN_SLR_BESS1 | FALLS | STORAGE | NORTH | 2025 | 188.24 | 180
1404 | BOCANOVA BESS | 25INR0467 | BCNV_ESS_BESS1 | BRAZORIA | STORAGE | COASTAL | 2025 | 150.46 | 150
1405 | CACHI BESS | 22INR0388 | CACH_ESS_BESS1 | GUADALUPE | STORAGE | SOUTH | 2025 | 205.46 | 200
1406 | CARINA BESS | 22INR0353 | CARN_ESS_BES1 | NUECES | STORAGE | COASTAL | 2025 | 154.11 | 150
1407 | CARRIZO SPRINGS BESS | 25INR0592 | CARRIZO_BESS1 | DIMMIT | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1408 | CORAZON STORAGE | 23INR0343 | CORAZON_BESS1 | WEBB | STORAGE | SOUTH | 2025 | 204.8 | 200
1409 | COTTONWOOD BAYOU STORAGE | 21INR0443 | CTW_BESS1 | BRAZORIA | STORAGE | COASTAL | 2025 | 153.03 | 150
1410 | EVELYN BATTERY ENERGY STORAGE SYSTEM | 24INR0460 | EVLN_ESS_BESS1 | GALVESTON | STORAGE | HOUSTON | 2025 | 227.9 | 220
1411 | GEARS BESS | 24INR0595 | GZ_BESS1 | HARRIS | STORAGE | HOUSTON | 2025 | 9.9 | 9.9
1412 | GOODWIN BESS | 25INR0594 | GOODWIN_BESS1 | HIDALGO | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1413 | IEP ORCHARD BESS | 23INR0556 | OR_BESS | FORT BEND | STORAGE | HOUSTON | 2025 | 9.99 | 10
1414 | INERTIA BESS | 22INR0328 | INRT_W_BESS_1 | HASKELL | STORAGE | WEST | 2025 | 13 | 13
1415 | JADE STORAGE U1 | 24INR0629 | JADE_SLR_BESS1 | SCURRY | STORAGE | WEST | 2025 | 78.53 | 78.1
1416 | JADE STORAGE U2 | 24INR0629 | JADE_SLR_BESS2 | SCURRY | STORAGE | WEST | 2025 | 82.27 | 81.9
1417 | LAURELES BESS | 23INR0499 | LAURELES_BESS | CAMERON | STORAGE | COASTAL | 2025 | 9.9 | 9.9
1418 | LOWER RIO BESS | 22INR0468 | LOWR_ESS_BESS1 | HIDALGO | STORAGE | SOUTH | 2025 | 60.37 | 60
1419 | MEDINA LAKE BESS | 24INR0499 | MEDILA_BESS1 | BANDERA | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1420 | MILTON BESS | 23INR0552 | MILTON_BESS1 | KARNES | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1421 | OLMITO BESS | 25INR0649 | OLMITO_BESS1 | CAMERON | STORAGE | COASTAL | 2025 | 9.99 | 10
1422 | PINE FOREST BESS | 22INR0526 | PINEFRST_BESS1 | HOPKINS | STORAGE | NORTH | 2025 | 200.74 | 200
1423 | PLATINUM STORAGE U1 | 22INR0554 | PLATINUM_BES1 | FANNIN | STORAGE | NORTH | 2025 | 152.9 | 148.3
1424 | PLATINUM STORAGE U2 | 22INR0554 | PLATINUM_BES2 | FANNIN | STORAGE | NORTH | 2025 | 157 | 151.7
1425 | PRAIRIE CREEK BESS | 24INR0662 | PRCRK_BESS1 | DALLAS | STORAGE | NORTH | 2025 | 9.9 | 9.9
1426 | RADIAN STORAGE SLF U1 | 24INR0631 | RADN_SLR_BESS1 | BROWN | STORAGE | NORTH | 2025 | 78.26 | 78.1
1427 | RADIAN STORAGE SLF U2 | 24INR0631 | RADN_SLR_BESS2 | BROWN | STORAGE | NORTH | 2025 | 81.99 | 81.9
1428 | SHAMROCK ENERGY STORAGE (SLF) | 24INR0568 | SHAMROCK_BESS1 | CROCKETT | STORAGE | WEST | 2025 | 99.33 | 99.3
1429 | SP JAGUAR BESS U1 | 24INR0039 | JAG_SLR_BESS1 | MCLENNAN | STORAGE | NORTH | 2025 | 157.1 | 150
1430 | SP JAGUAR BESS U2 | 24INR0039 | JAG_SLR_BESS2 | MCLENNAN | STORAGE | NORTH | 2025 | 157.15 | 150
1431 | SPENCER BESS | 24INR0545 | SP_BESS | HARRIS | STORAGE | HOUSTON | 2025 | 9.9 | 9.9
1432 | ST. GALL II ENERGY STORAGE | 22INR0525 | SGAL_BES_BESS2 | PECOS | STORAGE | WEST | 2025 | 102.5 | 100
1433 | STONERIDGE BESS | 25INR0389 | STRG_SLR_BESS1 | MILAM | STORAGE | SOUTH | 2025 | 101.9 | 100
1434 | TANZANITE STORAGE U1 | 22INR0549 | TANZ_ESS_BES1 | HENDERSON | STORAGE | NORTH | 2025 | 132.9 | 128.9
1435 | TANZANITE STORAGE U2 | 22INR0549 | TANZ_ESS_BES2 | HENDERSON | STORAGE | NORTH | 2025 | 132.9 | 128.9
1436 | TORRECILLAS BESS | 23INR0529 | TORR_BESS1 | WEBB | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1437 | WALSTROM BESS | 22INR0540 | WAL_BESS_1 | AUSTIN | STORAGE | SOUTH | 2025 | 205.31 | 200
1438 | XE MURAT [ADLONG] STORAGE | 24INR0329 | ADL1_BESS1 | HARRIS | STORAGE | HOUSTON | 2025 | 60.14 | 60
1439 | Operational Capacity - Synchronized but not Approved for Commercial Operations Total (Storage) | [6 empty] | 4026.68 | 3939.2
1440
1441 | Reliability Must-Run (RMR) and Other Resource Agreement Units
1442 | A4 PEARSALL DGR U1 | 26INR0675 | A4_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 35 | 24.9
1443 | A4 PEARSALL DGR U2 | 26INR0675 | A4_DGR2 | BEXAR | DIESEL | SOUTH | 2025 | 35 | 24.9
1444 | K2 NACOGDOCHES DGR U1 | 26INR0681 | K2_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 29.4 | 21.5
1445 | K2 NACOGDOCHES DGR U2 | 26INR0681 | K2_DGR2 | BEXAR | DIESEL | SOUTH | 2025 | 29.4 | 21.5
1446 | P2 HIGHLAND HILLS DGR U1 | 26INR0666 | P2_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 40.9 | 24.9
1447 | P2 HIGHLAND HILLS DGR U2 | 26INR0666 | P2_DGR2 | BEXAR | DIESEL | SOUTH | 2025 | 40.9 | 24.9
1448 | Q1 VALLEY ROAD DGR | 26INR0676 | Q1_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 29.4 | 21.5
1449 | V H BRAUNIG STG 3 (RMR FROM 3/1/25 TO 3/1/27) |  | BRAUNIG_VHB3 | BEXAR | GAS-ST | SOUTH | 1970 | 420 | 412
1450 | V2 BROOKS FIELD DGR U1 | 26INR0694 | V2_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 32 | 22.6
1451 | V2 BROOKS FIELD DGR U2 | 26INR0694 | V2_DGR2 | BEXAR | DIESEL | SOUTH | 2025 | 32 | 22.6
1452 | V2 BROOKS FIELD DGR U3 | 26INR0694 | V2_DGR3 | BEXAR | DIESEL | SOUTH | 2025 | 32 | 22.6
1453 | V4 PALO ALTO DGR | 25INR0777 | V4_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 40.9 | 24.9
1454 | X1 MEDINA BASE DGR | 26INR0674 | X1_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 29.4 | 21.5
1455 | Z0 BECK ROAD DGR U1 | 26INR0683 | Z0_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 29.4 | 21.5
1456 | Z0 BECK ROAD DGR U2 | 26INR0683 | Z0_DGR2 | BEXAR | DIESEL | SOUTH | 2025 | 29.4 | 21.5
1457 | Z5 SOUTHTON DGR | 26INR0684 | Z5_DGR1 | BEXAR | DIESEL | SOUTH | 2025 | 29.4 | 21.5
1458 | RMR and Other Resource Agreement Capacity Total |  | RMR_CAP_CONT |  |  |  |  | 914.5 | 754.8
1459
1460 | Capacity Pending Retirement |  | PENDRETIRE_CAP |  |  |  |  | 0 | 0
1461
1462 | Non-Synchronous Tie Resources
1463 | EAST TIE |  | DC_E | FANNIN | OTHER | NORTH |  | 600 | 600
1464 | NORTH TIE |  | DC_N | WILBARGER | OTHER | WEST |  | 220 | 220
1465 | LAREDO VFT TIE |  | DC_L | WEBB | OTHER | SOUTH |  | 100 | 100
1466 | SHARYLAND RAILROAD TIE |  | DC_R | HIDALGO | OTHER | SOUTH |  | 300 | 300
1467 | Non-Synchronous Ties Total | [6 empty] | 1220 | 1220
1468
1469 | Planned Thermal Resources with Executed SGIA, Air Permit, GHG Permit, Proof of Adequate Water Supplies, Financial Commitment, and Notice to Proceed
1470 | CALPINE FREESTONE PEAKER 1 (TEF) | 26INR0049 |  | FREESTONE | GAS-GT | NORTH | 2026 | 0 | 0
1471 | CALPINE FREESTONE PEAKER 2 (TEF) | 26INR0109 |  | FREESTONE | GAS-GT | NORTH | 2026 | 0 | 0
1472 | CEDAR BAYOU5 (TEF) | 23INR0029 |  | CHAMBERS | GAS-CC | HOUSTON | 2027 | 0 | 0
1473 | CEDARVALE GAS | 25INR0710 |  | WARD | GAS-IC | WEST | 2026 | 0 | 0
1474 | COYOTE SPRINGS AGR1 | 24INR0645 |  | REEVES | DIESEL | WEST | 2025 | 0 | 0
1475 | ENCHANTED ROCK NEWPP | 22INR0546 |  | HARRIS | GAS-IC | HOUSTON | 2026 | 0 | 0
1476 | FRIENDSWOOD G CTG 2 | 24INR0456 |  | HARRIS | GAS-GT | HOUSTON | 2025 | 143.7 | 143.7
1477 | NRG THW GT 345 (TEF) | 24INR0482 |  | HARRIS | GAS-GT | HOUSTON | 2026 | 0 | 0
1478 | PYOTE GAS | 25INR0718 |  | WARD | GAS-IC | WEST | 2026 | 0 | 0
1479 | ROCK ISLAND GENERATING (TEF) | 27INR0321 |  | COLORADO | GAS-IC | SOUTH | 2027 | 0 | 0
1480 | SADDLEBACK AGR1 | 24INR0646 |  | REEVES | DIESEL | WEST | 2025 | 0 | 0
1481 | UHLAND MAXWELL EXPANSION | 25INR0503 |  | CALDWELL | GAS-IC | SOUTH | 2026 | 0 | 0
1482 | Planned Thermal Resources Total (Nuclear, Coal, Gas, Diesel, Biomass) | [6 empty] | 143.7 | 143.7
1483
1484 | Planned Wind Resources with Executed SGIA, Financial Commitment, and Notice to Proceed
1485 | AQUILLA LAKE 3 WIND | 22INR0499 |  | HILL | WIND-O | NORTH | 2027 | 0 | 0
1486 | CAROL WIND | 20INR0217 |  | POTTER | WIND-P | PANHANDLE | 2026 | 0 | 0
1487 | CASCABEL WIND 1 | 24INR0424 |  | ZAPATA | WIND-O | SOUTH | 2027 | 0 | 0
1488 | CASCABEL WIND 2 | 23INR0561 |  | ZAPATA | WIND-O | SOUTH | 2027 | 0 | 0
1489 | CORRALITOS WIND 1 | 24INR0505 |  | ZAPATA | WIND-O | SOUTH | 2027 | 0 | 0
1490 | CORRALITOS WIND 2 | 24INR0506 |  | ZAPATA | WIND-O | SOUTH | 2027 | 0 | 0
1491 | DUNDEE NORTH WIND | 27INR0004 |  | WILBARGER | WIND-O | WEST | 2027 | 0 | 0
1492 | DUNDEE SOUTH A WIND | 27INR0005 |  | BAYLOR | WIND-O | WEST | 2027 | 0 | 0
1493 | DUNDEE SOUTH B WIND | 27INR0011 |  | BAYLOR | WIND-O | WEST | 2027 | 0 | 0
1494 | GOODNIGHT WIND II | 23INR0637 |  | ARMSTRONG | WIND-P | PANHANDLE | 2027 | 0 | 0
1495 | HONEY MESQUITE WIND FARM | 26INR0447 |  | GLASSCOCK | WIND-O | WEST | 2026 | 0 | 0
1496 | HYFUELS WESTERN FARMLAND WIND | 26INR0021 |  | VICTORIA | WIND-O | SOUTH | 2027 | 0 | 0
1497 | LA CASA WIND | 21INR0240 |  | STEPHENS | WIND-O | NORTH | 2026 | 0 | 0
1498 | LAUREL WIND ENERGY CENTER | 27INR0056 |  | PECOS | WIND-O | WEST | 2027 | 0 | 0
1499 | MONTE ALTO I WIND | 19INR0022 |  | WILLACY | WIND-C | COASTAL | 2028 | 0 | 0
1500 | MONTE ALTO 2 WIND | 19INR0023 |  | WILLACY | WIND-C | COASTAL | 2027 | 0 | 0
1501 | RUBICON ALPHA WIND | 24INR0291 |  | HASKELL | WIND-O | WEST | 2027 | 0 | 0
1502 | SIETE | 20INR0047 |  | WEBB | WIND-O | SOUTH | 2026 | 0 | 0
1503 | YELLOW CAT WIND | 25INR0018 |  | NAVARRO | WIND-O | NORTH | 2027 | 0 | 0
1504 | WATER VALLEY WIND ENERGY | 20INR0247 |  | TOM GREEN | WIND-O | WEST | 2027 | 0 | 0
1505 | Planned Capacity Total (Wind) | [6 empty] | 0 | 0
1506
1507 | Planned Solar Resources with Executed SGIA, Financial Commitment, and Notice to Proceed
1508 | ALILA SOLAR | 23INR0093 |  | SAN PATRICIO | SOLAR | COASTAL | 2027 | 0 | 0
1509 | ANSON SOLAR CENTER, PHASE II | 20INR0242 |  | JONES | SOLAR | WEST | 2025 | 0 | 0
1510 | ARGENTA SOLAR | 25INR0060 |  | BEE | SOLAR | SOUTH | 2027 | 0 | 0
1511 | ARMADILLO SOLAR | 21INR0421 |  | NAVARRO | SOLAR | NORTH | 2026 | 0 | 0
1512 | ARROYO SOLAR | 20INR0086 |  | CAMERON | SOLAR | COASTAL | 2028 | 0 | 0
1513 | AUSTIN BAYOU SOLAR | 25INR0102 |  | BRAZORIA | SOLAR | COASTAL | 2027 | 0 | 0
1514 | BARRETT SOLAR | 24INR0477 |  | RAINS | SOLAR | NORTH | 2026 | 0 | 0
1515 | BIGWAY SOLAR I | 27INR0127 |  | KING | SOLAR | WEST | 2028 | 0 | 0
1516 | BIGWAY SOLAR II | 27INR0128 |  | KING | SOLAR | WEST | 2028 | 0 | 0
1517 | BLUE SKY SOL | 22INR0455 |  | CROCKETT | SOLAR | WEST | 2027 | 0 | 0
1518 | BRIGGS SOLAR | 23INR0059 |  | HASKELL | SOLAR | WEST | 2027 | 0 | 0
1519 | BUZIOS SOLAR | 24INR0399 |  | MOTLEY | SOLAR | PANHANDLE | 2026 | 0 | 0
1520 | BYNUM SOLAR PROJECT | 24INR0181 |  | CORYELL | SOLAR | NORTH | 2025 | 0 | 0
1521 | CACHENA SOLAR SLF | 23INR0027 |  | WILSON | SOLAR | SOUTH | 2027 | 0 | 0
1522 | CALICHE MOUND SOLAR | 23INR0056 |  | DEAF SMITH | SOLAR | PANHANDLE | 2026 | 0 | 0
1523 | CAMINO SANTIAGO SOLAR | 22INR0605 |  | MILAM | SOLAR | SOUTH | 2027 | 0 | 0
1524 | CANNIBAL DRAW SOLAR | 26INR0452 |  | GLASSCOCK | SOLAR | WEST | 2028 | 0 | 0
1525 | CANTALOUPE SOLAR | 23INR0116 |  | REEVES | SOLAR | WEST | 2028 | 0 | 0
1526 | CASCADE SOLAR | 23INR0091 |  | BRAZORIA | SOLAR | COASTAL | 2026 | 0 | 0
1527 | CHARGER SOLAR | 23INR0047 |  | REFUGIO | SOLAR | COASTAL | 2026 | 0 | 0
1528 | CIBELES SOLAR | 24INR0356 |  | MCLENNAN | SOLAR | NORTH | 2027 | 0 | 0
1529 | CRADLE SOLAR | 23INR0150 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 0 | 0
1530 | CROWDED STAR SOLAR | 20INR0241 |  | JONES | SOLAR | WEST | 2026 | 0 | 0
1531 | CROWDED STAR SOLAR II | 22INR0274 |  | JONES | SOLAR | WEST | 2026 | 0 | 0
1532 | CUCHILLAS SOLAR | 24INR0059 |  | WEBB | SOLAR | SOUTH | 2027 | 0 | 0
1533 | DESERT VINE SOLAR | 22INR0307 |  | ZAPATA | SOLAR | SOUTH | 2026 | 0 | 0
1534 | DEVILLE SOLAR | 22INR0262 |  | CALLAHAN | SOLAR | WEST | 2026 | 0 | 0
1535 | DIAMONDBACK SOLAR | 20INR0162 |  | STARR | SOLAR | SOUTH | 2027 | 0 | 0
1536 | DONEGAL SOLAR | 23INR0089 |  | DICKENS | SOLAR | PANHANDLE | 2027 | 0 | 0
1537 | DORADO SOLAR | 22INR0261 |  | CALLAHAN | SOLAR | WEST | 2025 | 0 | 0
1538 | DOVE RUN SOLAR | 21INR0326 |  | DUVAL | SOLAR | SOUTH | 2027 | 0 | 0
1539 | DR SOLAR | 22INR0454 |  | CULBERSON | SOLAR | WEST | 2026 | 0 | 0
1540 | DUFFY SOLAR | 23INR0057 |  | MATAGORDA | SOLAR | COASTAL | 2027 | 0 | 0
1541 | ECHOLS CREEK SOLAR | 25INR0368 |  | LAMAR | SOLAR | NORTH | 2027 | 0 | 0
1542 | ELDORA SOLAR | 24INR0337 |  | MATAGORDA | SOLAR | COASTAL | 2026 | 0 | 0
1543 | ERATH COUNTY SOLAR | 23INR0202 |  | ERATH | SOLAR | NORTH | 2026 | 0 | 0
1544 | FAGUS SOLAR PARK 3 SLF | 26INR0524 |  | CHILDRESS | SOLAR | PANHANDLE | 2026 | 0 | 0
1545 | FELIX EAST SOLAR | 27INR0007 |  | WILBARGER | SOLAR | WEST | 2027 | 0 | 0
1546 | FELIX NORTH SOLAR | 22INR0209 |  | WILBARGER | SOLAR | WEST | 2027 | 0 | 0
1547 | FELIX WEST SOLAR | 27INR0012 |  | WILBARGER | SOLAR | WEST | 2027 | 0 | 0
1548 | FEWELL SOLAR | 23INR0367 |  | LIMESTONE | SOLAR | NORTH | 2027 | 0 | 0
1549 | FUNSTON SOLAR (ALTERNATIVE POI LONE STAR) | 29INR0015 |  | JONES | SOLAR | WEST | 2027 | 0 | 0
1550 | GAIA SOLAR | 24INR0141 |  | NAVARRO | SOLAR | NORTH | 2026 | 0 | 0
1551 | GARCITAS CREEK SOLAR | 23INR0223 |  | JACKSON | SOLAR | SOUTH | 2026 | 0 | 0
1552 | GLASGOW SOLAR | 24INR0206 |  | NAVARRO | SOLAR | NORTH | 2027 | 0 | 0
1553 | GP SOLAR | 23INR0045 |  | VAN ZANDT | SOLAR | NORTH | 2027 | 0 | 0
1554 | GREATER BRYANT G SOLAR | 23INR0300 |  | MIDLAND | SOLAR | WEST | 2026 | 0 | 0
1555 | GREYHOUND SOLAR | 21INR0268 |  | ECTOR | SOLAR | WEST | 2026 | 0 | 0
1556 | GREYHOUND SOLAR - PHASE E | 26INR0669 |  | ECTOR | SOLAR | WEST | 2025 | 150.7 | 150.7
1557 | GREYHOUND SOLAR - PHASE F | 26INR0670 |  | ECTOR | SOLAR | WEST | 2025 | 0 | 0
1558 | HANSON SOLAR | 23INR0086 |  | COLEMAN | SOLAR | WEST | 2027 | 0 | 0
1559 | HICKERSON SOLAR | 21INR0359 |  | BOSQUE | SOLAR | NORTH | 2025 | 0 | 0
1560 | HIGH CHAP SOLAR | 25INR0068 |  | BRAZORIA | SOLAR | COASTAL | 2028 | 0 | 0
1561 | HIGH NOON SOLAR | 24INR0124 |  | HILL | SOLAR | NORTH | 2028 | 0 | 0
1562 | HOLLOW BRANCH CREEK SOLAR | 24INR0422 |  | LEON | SOLAR | NORTH | 2027 | 0 | 0
1563 | HONEYCOMB SOLAR | 22INR0559 |  | BEE | SOLAR | SOUTH | 2026 | 0 | 0
1564 | HORNET SOLAR II SLF | 25INR0282 |  | SWISHER | SOLAR | PANHANDLE | 2027 | 0 | 0
1565 | HOYTE SOLAR | 23INR0235 |  | MILAM | SOLAR | SOUTH | 2027 | 0 | 0
1566 | INDIGO SOLAR | 21INR0031 |  | FISHER | SOLAR | WEST | 2026 | 0 | 0
1567 | INERTIA SOLAR | 22INR0374 |  | HASKELL | SOLAR | WEST | 2027 | 0 | 0
1568 | ISAAC SOLAR | 25INR0232 |  | MATAGORDA | SOLAR | COASTAL | 2026 | 0 | 0
1569 | LAMKIN SOLAR | 22INR0220 |  | COMANCHE | SOLAR | NORTH | 2027 | 0 | 0
1570 | LANGER SOLAR | 23INR0030 |  | BOSQUE | SOLAR | NORTH | 2027 | 0 | 0
1571 | LAVACA BAY SOLAR | 23INR0084 |  | MATAGORDA | SOLAR | COASTAL | 2026 | 0 | 0
1572 | LEIGHTON SOLAR SLF | 24INR0298 |  | LIMESTONE | SOLAR | NORTH | 2027 | 0 | 0
1573 | LEON SOLAR PARK | 26INR0023 |  | LEON | SOLAR | NORTH | 2026 | 0 | 0
1574 | LIMEWOOD SOLAR | 23INR0249 |  | BELL | SOLAR | NORTH | 2026 | 0 | 0
1575 | LONG POINT SOLAR | 19INR0042 |  | BRAZORIA | SOLAR | COASTAL | 2026 | 0 | 0
1576 | LUNIS CREEK SOLAR SLF | 21INR0344 |  | JACKSON | SOLAR | SOUTH | 2027 | 0 | 0
1577 | LUPINUS SOLAR 1 | 24INR0150 |  | FRANKLIN | SOLAR | NORTH | 2027 | 0 | 0
1578 | MALDIVES SOLAR (ALTERNATE POI) | 25INR0400 |  | SCURRY | SOLAR | WEST | 2028 | 0 | 0
1579 | MALEZA SOLAR | 21INR0220 |  | WHARTON | SOLAR | SOUTH | 2026 | 0 | 0
1580 | MATAGORDA SOLAR | 22INR0342 |  | MATAGORDA | SOLAR | COASTAL | 2027 | 0 | 0
1581 | MIDPOINT SOLAR | 24INR0139 |  | HILL | SOLAR | NORTH | 2025 | 0 | 0
1582 | MILLER'S BRANCH I | 22INR0270 |  | HASKELL | SOLAR | WEST | 2025 | 0 | 0
1583 | MILLERS BRANCH SOLAR II | 24INR0044 |  | HASKELL | SOLAR | WEST | 2026 | 0 | 0
1584 | MILLERS BRANCH SOLAR III | 26INR0521 |  | HASKELL | SOLAR | WEST | 2026 | 0 | 0
1585 | MIRANDA SOLAR PROJECT | 24INR0161 |  | MCMULLEN | SOLAR | SOUTH | 2027 | 0 | 0
1586 | MOCCASIN SOLAR | 26INR0269 |  | STONEWALL | SOLAR | WEST | 2027 | 0 | 0
1587 | MRG GOODY SOLAR | 23INR0225 |  | LAMAR | SOLAR | NORTH | 2026 | 0 | 0
1588 | NABATOTO SOLAR NORTH | 21INR0428 |  | LEON | SOLAR | NORTH | 2027 | 0 | 0
1589 | NAZARETH SOLAR | 16INR0049 |  | CASTRO | SOLAR | PANHANDLE | 2026 | 0 | 0
1590 | NEW HICKORY SOLAR | 20INR0236 |  | JACKSON | SOLAR | SOUTH | 2026 | 0 | 0
1591 | NIGHTFALL SOLAR SLF | 21INR0334 |  | UVALDE | SOLAR | SOUTH | 2026 | 0 | 0
1592 | NORIA SOLAR DCC | 23INR0061 |  | NUECES | SOLAR | COASTAL | 2026 | 0 | 0
1593 | NORTHINGTON SOLAR | 25INR0319 |  | WHARTON | SOLAR | SOUTH | 2027 | 0 | 0
1594 | OCI COBB CREEK SOLAR | 25INR0229 |  | HILL | SOLAR | NORTH | 2026 | 0 | 0
1595 | PADRINO SOLAR | 25INR0166 |  | HILL | SOLAR | NORTH | 2026 | 0 | 0
1596 | PIEDRA SOLAR | 25INR0168 |  | FREESTONE | SOLAR | NORTH | 2026 | 0 | 0
1597 | PINNINGTON SOLAR | 24INR0010 |  | JACK | SOLAR | NORTH | 2026 | 0 | 0
1598 | PITTS DUDIK II | 24INR0364 |  | HILL | SOLAR | NORTH | 2026 | 0 | 0
1599 | QUANTUM SOLAR | 21INR0207 |  | HASKELL | SOLAR | WEST | 2026 | 0 | 0
1600 | REDONDA SOLAR | 23INR0162 |  | ZAPATA | SOLAR | SOUTH | 2026 | 0 | 0
1601 | RENEGADE PROJECT (DAWN SOLAR) | 20INR0255 |  | DEAF SMITH | SOLAR | PANHANDLE | 2026 | 0 | 0
1602 | ROCINANTE SOLAR | 23INR0231 |  | GONZALES | SOLAR | SOUTH | 2026 | 0 | 0
1603 | RODEO SOLAR | 19INR0103 |  | ANDREWS | SOLAR | WEST | 2026 | 0 | 0
1604 | ROWDY CREEK SOLAR | 24INR0186 |  | LAMAR | SOLAR | NORTH | 2027 | 0 | 0
1605 | SANPAT SOLAR | 25INR0052 |  | SAN PATRICIO | SOLAR | COASTAL | 2027 | 0 | 0
1606 | SANPAT SOLAR II | 25INR0081 |  | SAN PATRICIO | SOLAR | COASTAL | 2027 | 0 | 0
1607 | SHAULA I SOLAR | 22INR0251 |  | DEWITT | SOLAR | SOUTH | 2026 | 0 | 0
1608 | SHAULA II SOLAR | 22INR0267 |  | DEWITT | SOLAR | SOUTH | 2026 | 0 | 0
1609 | SHAW SOLAR | 23INR0078 |  | BANDERA | SOLAR | SOUTH | 2026 | 0 | 0
1610 | SHORT CREEK SOLAR | 24INR0201 |  | WICHITA | SOLAR | WEST | 2027 | 0 | 0
1611 | SOLACE SOLAR | 23INR0031 |  | HASKELL | SOLAR | WEST | 2026 | 0 | 0
1612 | SOL MARINA ENERGY CENTER | 26INR0241 |  | ELLIS | SOLAR | NORTH | 2027 | 0 | 0
1613 | SP JAGUAR SOLAR | 24INR0038 |  | MCLENNAN | SOLAR | NORTH | 2027 | 0 | 0
1614 | SPACE CITY SOLAR | 21INR0341 |  | WHARTON | SOLAR | SOUTH | 2027 | 0 | 0
1615 | STARLING SOLAR | 23INR0035 |  | GONZALES | SOLAR | SOUTH | 2027 | 0 | 0
1616 | SUN CACTUS SOLAR | 25INR0109 |  | DUVAL | SOLAR | SOUTH | 2027 | 0 | 0
1617 | SYPERT BRANCH SOLAR PROJECT | 24INR0070 |  | MILAM | SOLAR | SOUTH | 2026 | 0 | 0
1618 | TANGLEWOOD SOLAR | 23INR0054 |  | BRAZORIA | SOLAR | COASTAL | 2025 | 251 | 251
1619 | TEHUACANA CREEK SOLAR SLF | 24INR0188 |  | NAVARRO | SOLAR | NORTH | 2027 | 0 | 0
1620 | THREE CANES SOLAR SLF | 26INR0543 |  | NAVARRO | SOLAR | NORTH | 2027 | 0 | 0
1621 | THREE W SOLAR | 25INR0055 |  | HILL | SOLAR | NORTH | 2026 | 0 | 0
1622 | TIGER SOLAR | 23INR0244 |  | JONES | SOLAR | WEST | 2027 | 0 | 0
1623 | TOKIO SOLAR | 23INR0349 |  | MCLENNAN | SOLAR | NORTH | 2027 | 0 | 0
1624 | TROJAN SOLAR | 23INR0296 |  | COOKE | SOLAR | NORTH | 2026 | 0 | 0
1625 | ULYSSES SOLAR | 21INR0253 |  | COKE | SOLAR | WEST | 2026 | 0 | 0
1626 | UVA CREEK SOLAR | 26INR0359 |  | BORDEN | SOLAR | WEST | 2028 | 0 | 0
1627 | XE BONHAM SOLAR 1 | 25INR0199 |  | LIMESTONE | SOLAR | NORTH | 2026 | 0 | 0
1628 | XE HERMES SOLAR | 23INR0344 |  | BELL | SOLAR | NORTH | 2025 | 0 | 0
1629 | YAUPON SOLAR SLF | 24INR0042 |  | MILAM | SOLAR | SOUTH | 2027 | 0 | 0
1630 | ZEISSEL SOLAR | 24INR0258 |  | KNOX | SOLAR | WEST | 2028 | 0 | 0
1631 | Planned Capacity Total (Solar) | [6 empty] | 401.7 | 401.7
1632
1633 | Planned Storage Resources with Executed SGIA, Financial Commitment, and Notice to Proceed
1634 | ABILENE ELMCREEK BESS | 25INR0701 |  | TAYLOR | STORAGE | WEST | 2025 | 0 | 0
1635 | ABILENE INDUSTRIAL PARK BESS | 25INR0702 |  | TAYLOR | STORAGE | WEST | 2025 | 0 | 0
1636 | ALAMO STREET BESS | 25INR0763 |  | PECOS | STORAGE | WEST | 2025 | 0 | 0
1637 | ALDRIN 138 BESS | 25INR0421 |  | BRAZORIA | STORAGE | COASTAL | 2027 | 0 | 0
1638 | ALDRIN 345 BESS | 25INR0425 |  | BRAZORIA | STORAGE | COASTAL | 2027 | 0 | 0
1639 | AMADOR STORAGE | 24INR0472 |  | VAN ZANDT | STORAGE | NORTH | 2025 | 0 | 0
1640 | ANATOLE RENEWABLE ENERGY STORAGE | 24INR0355 |  | HENDERSON | STORAGE | NORTH | 2027 | 0 | 0
1641 | ANSON BAT | 22INR0457 |  | JONES | STORAGE | WEST | 2026 | 0 | 0
1642 | APACHE HILL BESS | 25INR0231 |  | HOOD | STORAGE | NORTH | 2026 | 0 | 0
1643 | APPLE BESS | 26INR0574 |  | ECTOR | STORAGE | WEST | 2026 | 0 | 0
1644 | ARGENTA STORAGE | 25INR0061 |  | BEE | STORAGE | SOUTH | 2027 | 0 | 0
1645 | ARROYO STORAGE | 24INR0306 |  | CAMERON | STORAGE | COASTAL | 2026 | 0 | 0
1646 | ATASCOCITA BESS | 25INR0713 |  | HARRIS | STORAGE | HOUSTON | 2026 | 0 | 0
1647 | BACKBONE CREEK BESS | 24INR0313 |  | BURNET | STORAGE | SOUTH | 2026 | 0 | 0
1648 | BARTON BRANCH IA | 22INR0504 |  | ROBERTSON | STORAGE | NORTH | 2026 | 0 | 0
1649 | BERRY BESS1 | 25INR0743 |  | HARRIS | STORAGE | HOUSTON | 2025 | 0 | 0
1650 | BESS STADIUM | 25INR0696 |  | JIM WELLS | STORAGE | SOUTH | 2026 | 0 | 0
1651 | BIG ELM STORAGE | 23INR0469 |  | BELL | STORAGE | NORTH | 2027 | 0 | 0
1652 | BIRD DOG BESS | 22INR0467 |  | LIVE OAK | STORAGE | SOUTH | 2026 | 0 | 0
1653 | BLACK & GOLD ENERGY STORAGE | 24INR0386 |  | MENARD | STORAGE | WEST | 2027 | 0 | 0
1654 | BLACK SPRINGS BESS SLF | 24INR0315 |  | PALO PINTO | STORAGE | NORTH | 2025 | 120.7 | 120.7
1655 | BLANQUILLA BESS | 24INR0528 |  | NUECES | STORAGE | COASTAL | 2026 | 0 | 0
1656 | BLUE SKIES BESS | 25INR0046 |  | HILL | STORAGE | NORTH | 2027 | 0 | 0
1657 | BLUE SUMMIT ENERGY STORAGE | 25INR0492 |  | WILBARGER | STORAGE | WEST | 2026 | 0 | 0
1658 | BORDERTOWN BESS | 23INR0354 |  | STARR | STORAGE | SOUTH | 2026 | 0 | 0
1659 | BRACERO PECAN STORAGE | 26INR0034 |  | REEVES | STORAGE | WEST | 2027 | 0 | 0
1660 | BRIGGS STORAGE | 24INR0058 |  | HASKELL | STORAGE | WEST | 2027 | 0 | 0
1661 | BROOKVIEW ROAD BESS | 27INR0243 |  | HARRIS | STORAGE | HOUSTON | 2028 | 0 | 0
1662 | BROTHERTON STORAGE | 25INR0432 |  | ANDERSON | STORAGE | NORTH | 2026 | 0 | 0
1663 | BRP DIRAN BESS | 23INR0137 |  | WHARTON | STORAGE | SOUTH | 2028 | 0 | 0
1664 | BUDA BESS | 25INR0650 |  | HAYS | STORAGE | SOUTH | 2026 | 0 | 0
1665 | BUFFALO CREEK BESS | 26INR0405 |  | FORT BEND | STORAGE | HOUSTON | 2026 | 0 | 0
1666 | BYPASS BATTERY STORAGE | 23INR0336 |  | FORT BEND | STORAGE | HOUSTON | 2025 | 0 | 0
1667 | CALLISTO II ENERGY CENTER | 22INR0558 |  | HARRIS | STORAGE | HOUSTON | 2026 | 0 | 0
1668 | CANNIBAL DRAW STORAGE | 26INR0453 |  | GLASSCOCK | STORAGE | WEST | 2028 | 0 | 0
1669 | CARAMBOLA BESS (SMT MCALLEN II) | 24INR0436 |  | HIDALGO | STORAGE | SOUTH | 2026 | 0 | 0
1670 | CARTWHEEL BESS 1 | 23INR0494 |  | HOPKINS | STORAGE | NORTH | 2025 | 154.2 | 154.2
1671 | CASTOR BESS | 23INR0358 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 0 | 0
1672 | CITRUS FLATTS BESS | 24INR0294 |  | CAMERON | STORAGE | COASTAL | 2026 | 0 | 0
1673 | CITY BREEZE BESS | 25INR0271 |  | MATAGORDA | STORAGE | COASTAL | 2026 | 0 | 0
1674 | CONEFLOWER STORAGE PROJECT | 23INR0425 |  | CHAMBERS | STORAGE | HOUSTON | 2027 | 0 | 0
1675 | COTULLA BESS 2 | 24INR0638 |  | LA SALLE | STORAGE | SOUTH | 2025 | 9.9 | 9.9
1676 | COUNTY ROAD BESS | 26INR0512 |  | REEVES | STORAGE | WEST | 2026 | 0 | 0
1677 | CROWNED HERON BESS | 24INR0405 |  | FORT BEND | STORAGE | HOUSTON | 2025 | 154.2 | 154.2
1678 | CROWNED HERON BESS 2 | 24INR0493 |  | FORT BEND | STORAGE | HOUSTON | 2026 | 0 | 0
1679 | DAMON BESS 2 | 23INR0603 |  | BRAZORIA | STORAGE | COASTAL | 2026 | 0 | 0
1680 | DAMON BESS3 | 23INR0790 |  | BRAZORIA | STORAGE | COASTAL | 2025 | 10 | 10
1681 | DESNA BESS | 24INR0128 |  | BRAZORIA | STORAGE | COASTAL | 2026 | 0 | 0
1682 | DESTINY STORAGE | 24INR0397 |  | HARRIS | STORAGE | HOUSTON | 2026 | 0 | 0
1683 | DIOS BESS | 25INR0441 |  | JACKSON | STORAGE | SOUTH | 2027 | 0 | 0
1684 | DOS RIOS ENERGY STORAGE SLF | 24INR0476 |  | MILAM | STORAGE | SOUTH | 2027 | 0 | 0
1685 | DOWNTOWN BESS | 25INR0764 |  | PECOS | STORAGE | WEST | 2025 | 0 | 0
1686 | EAST HARRISON BESS | 25INR0648 |  | CAMERON | STORAGE | COASTAL | 2025 | 10 | 10
1687 | ECHOLS CREEK STORAGE | 25INR0369 |  | LAMAR | STORAGE | NORTH | 2027 | 0 | 0
1688 | ELDORA BESS | 24INR0338 |  | MATAGORDA | STORAGE | COASTAL | 2026 | 0 | 0
1689 | ELIO BESS | 25INR0103 |  | BRAZORIA | STORAGE | COASTAL | 2027 | 0 | 0
1690 | ELM STREET BESS | 25INR0655 |  | REEVES | STORAGE | WEST | 2026 | 0 | 0
1691 | ELM STREET BESS2 | 25INR0765 |  | REEVES | STORAGE | WEST | 2025 | 0 | 0
1692 | EMPIRE CENTRAL BESS | 24INR0659 |  | DALLAS | STORAGE | NORTH | 2025 | 9.9 | 9.9
1693 | ESCONDIDO BESS | 25INR0593 |  | MAVERICK | STORAGE | SOUTH | 2026 | 0 | 0
1694 | EVAL STORAGE | 22INR0401 |  | CAMERON | STORAGE | COASTAL | 2028 | 0 | 0
1695 | FERDINAND GRID BESS | 22INR0422 |  | BEXAR | STORAGE | SOUTH | 2026 | 0 | 0
1696 | FIRST CAPITOL BESS | 26INR0226 |  | BRAZORIA | STORAGE | COASTAL | 2026 | 0 | 0
1697 | GAIA STORAGE | 24INR0140 |  | NAVARRO | STORAGE | NORTH | 2026 | 0 | 0
1698 | GEARS BESS2 | 25INR0742 |  | HARRIS | STORAGE | HOUSTON | 2025 | 0 | 0
1699 | GLASGOW STORAGE | 24INR0207 |  | NAVARRO | STORAGE | NORTH | 2027 | 0 | 0
1700 | GRIZZLY RIDGE BESS SLF | 22INR0596 |  | HAMILTON | STORAGE | NORTH | 2026 | 0 | 0
1701 | GUNNAR BESS | 24INR0491 |  | HIDALGO | STORAGE | SOUTH | 2026 | 0 | 0
1702 | HARLINGEN #1 BESS 1 | 26INR0691 |  | CAMERON | STORAGE | COASTAL | 2026 | 0 | 0
1703 | HEADCAMP BESS | 23INR0401 |  | PECOS | STORAGE | WEST | 2025 | 0 | 0
1704 | HIDDEN LAKES BESS | 23INR0617 |  | GALVESTON | STORAGE | HOUSTON | 2026 | 0 | 0
1705 | HIDDEN VALLEY BESS | 24INR0594 |  | HARRIS | STORAGE | HOUSTON | 2025 | 9.9 | 9.9
1706 | HIGH NOON STORAGE | 24INR0126 |  | HILL | STORAGE | NORTH | 2028 | 0 | 0
1707 | HIGHWAY 6 BESS | 26INR0520 |  | BRAZOS | STORAGE | NORTH | 2026 | 0 | 0
1708 | HOCKLEY BESS | 25INR0602 |  | HARRIS | STORAGE | HOUSTON | 2026 | 0 | 0
1709 | HONEYCOMB STORAGE SLF | 23INR0392 |  | BEE | STORAGE | SOUTH | 2026 | 0 | 0
1710 | HORNET STORAGE II SLF | 25INR0283 |  | SWISHER | STORAGE | PANHANDLE | 2027 | 0 | 0
1711 | HOUSTON IV BESS | 24INR0584 |  | HARRIS | STORAGE | HOUSTON | 2026 | 0 | 0
1712 | IRON BELT ENERGY STORAGE | 25INR0208 |  | BORDEN | STORAGE | WEST | 2026 | 0 | 0
1713 | KNAPP BESS | 25INR0747 |  | SCURRY | STORAGE | WEST | 2025 | 9.9 | 9.9
1714 | LANGER STORAGE | 23INR0266 |  | BOSQUE | STORAGE | NORTH | 2027 | 0 | 0
1715 | LANTANA BESS | 25INR0647 |  | NUECES | STORAGE | COASTAL | 2025 | 10 | 10
1716 | LAUREL STORAGE ENERGY CENTER | 27INR0080 |  | PECOS | STORAGE | WEST | 2027 | 0 | 0
1717 | LEAKEY BESS | 23INR0548 |  | REAL | STORAGE | SOUTH | 2026 | 0 | 0
1718 | LEOPARD BESS | 27INR0224 |  | VICTORIA | STORAGE | SOUTH | 2028 | 0 | 0
1719 | LIMEWOOD STORAGE | 23INR0248 |  | BELL | STORAGE | NORTH | 2028 | 0 | 0
1720 | LONGFELLOW BESS I | 24INR0453 |  | PECOS | STORAGE | WEST | 2026 | 0 | 0
1721 | LONGFELLOW BESS II | 24INR0455 |  | PECOS | STORAGE | WEST | 2026 | 0 | 0
1722 | LOUISA ENERGY STORAGE | 24INR0108 |  | BEXAR | STORAGE | SOUTH | 2029 | 0 | 0
1723 | LUCKY BLUFF BESS SLF | 24INR0295 |  | ERATH | STORAGE | NORTH | 2025 | 100.8 | 100.8
1724 | LUPINUS STORAGE 3 | 24INR0490 |  | FRANKLIN | STORAGE | NORTH | 2026 | 0 | 0
1725 | LYSSY BESS | 25INR0597 |  | WILSON | STORAGE | SOUTH | 2025 | 0 | 0
1726 | MALLARD BESS | 25INR0101 |  | COLLIN | STORAGE | NORTH | 2026 | 0 | 0
1727 | MCCAMEY'S CASTLE BATTERY | 25INR0557 |  | UPTON | STORAGE | WEST | 2025 | 0 | 0
1728 | MEADOW PARK BESS | 26INR0699 |  | TARRANT | STORAGE | NORTH | 2026 | 0 | 0
1729 | MEDINA CITY BESS | 24INR0502 |  | BANDERA | STORAGE | SOUTH | 2026 | 0 | 0
1730 | MESQUITE BESS | 25INR0697 |  | CAMERON | STORAGE | COASTAL | 2026 | 0 | 0
1731 | MIDNIGHT SUN ENERGY STORAGE | 24INR0442 |  | CROCKETT | STORAGE | WEST | 2028 | 0 | 0
1732 | MIDPOINT STORAGE | 24INR0138 |  | HILL | STORAGE | NORTH | 2025 | 0 | 0
1733 | MRG GOODY STORAGE | 24INR0305 |  | LAMAR | STORAGE | NORTH | 2026 | 0 | 0
1734 | NORIA STORAGE | 23INR0062 |  | NUECES | STORAGE | COASTAL | 2026 | 0 | 0
1735 | NORTH EDINBURG BESS 1 | 26INR0682 |  | HIDALGO | STORAGE | SOUTH | 2026 | 0 | 0
1736 | OCI COBB CREEK ESS | 25INR0233 |  | HILL | STORAGE | NORTH | 2026 | 0 | 0
1737 | ORANGE GROVE BESS | 23INR0331 |  | JIM WELLS | STORAGE | SOUTH | 2027 | 0 | 0
1738 | ORIANA BESS | 24INR0109 |  | VICTORIA | STORAGE | SOUTH | 2026 | 0 | 0
1739 | PADUA GRID BESS UNIT 2 | 24INR0533 |  | BEXAR | STORAGE | SOUTH | 2026 | 0 | 0
1740 | PADUA GRID BESS UNIT 3 | 28INR0024 |  | BEXAR | STORAGE | SOUTH | 2026 | 0 | 0
1741 | PAJARITA BESS | 22INR0466 |  | CAMERON | STORAGE | COASTAL | 2028 | 0 | 0
1742 | PALMVIEW BESS | 24INR0628 |  | HIDALGO | STORAGE | SOUTH | 2025 | 0 | 0
1743 | PARADISO BESS | 23INR0200 |  | ATASCOSA | STORAGE | SOUTH | 2028 | 0 | 0
1744 | PIEDRA BESS | 25INR0169 |  | FREESTONE | STORAGE | NORTH | 2026 | 0 | 0
1745 | PINTAIL PASS BESS | 24INR0302 |  | SAN PATRICIO | STORAGE | COASTAL | 2025 | 207.3 | 207.3
1746 | POTEET BESS | 25INR0715 |  | ATASCOSA | STORAGE | SOUTH | 2025 | 0 | 0
1747 | PROJECT LYNX BESS | 25INR0329 |  | NUECES | STORAGE | COASTAL | 2026 | 0 | 0
1748 | PURPLE SAGE BESS 1 | 25INR0391 |  | COLLIN | STORAGE | NORTH | 2027 | 0 | 0
1749 | PURPLE SAGE BESS 2 | 25INR0392 |  | COLLIN | STORAGE | NORTH | 2027 | 0 | 0
1750 | QUANTUM STORAGE | 26INR0310 |  | HASKELL | STORAGE | WEST | 2026 | 0 | 0
1751 | RAMSEY STORAGE | 21INR0505 |  | WHARTON | STORAGE | SOUTH | 2027 | 0 | 0
1752 | RED EGRET BESS | 24INR0281 |  | GALVESTON | STORAGE | HOUSTON | 2026 | 0 | 0
1753 | RESACA OASIS STORAGE | 27INR0399 |  | CAMERON | STORAGE | COASTAL | 2027 | 0 | 0
1754 | ROADRUNNER CROSSING BESS SLF | 23INR0538 |  | EASTLAND | STORAGE | NORTH | 2025 | 150.4 | 0
1755 | ROCINANTE BESS | 23INR0232 |  | GONZALES | STORAGE | SOUTH | 2026 | 0 | 0
1756 | ROCK CREEK BESS | 26INR0407 |  | KENDALL | STORAGE | SOUTH | 2028 | 0 | 0
1757 | ROCK ROSE ENERGY BESS | 26INR0201 |  | FORT BEND | STORAGE | HOUSTON | 2026 | 0 | 0
1758 | ROCKEFELLER STORAGE | 22INR0239 |  | SCHLEICHER | STORAGE | WEST | 2027 | 0 | 0
1759 | ROWDY CREEK BESS | 24INR0187 |  | LAMAR | STORAGE | NORTH | 2027 | 0 | 0
1760 | RUTILE BESS | 24INR0485 |  | RUNNELS | STORAGE | WEST | 2026 | 0 | 0
1761 | RYAN ENERGY STORAGE | 20INR0246 |  | CORYELL | STORAGE | NORTH | 2026 | 0 | 0
1762 | SCENIC WOODS BESS | 25INR0712 |  | HARRIS | STORAGE | HOUSTON | 2026 | 0 | 0
1763 | SE EDINBURG BESS | 24INR0642 |  | HIDALGO | STORAGE | SOUTH | 2025 | 0 | 0
1764 | SEINE BESS | 23INR0140 |  | FOARD | STORAGE | WEST | 2027 | 0 | 0
1765 | SEVEN FLAGS BESS | 23INR0351 |  | WEBB | STORAGE | SOUTH | 2025 | 0 | 0
1766 | SHEPARD ENERGY STORAGE | 25INR0262 |  | GALVESTON | STORAGE | HOUSTON | 2027 | 0 | 0
1767 | SHERBINO II BESS SLF | 26INR0296 |  | PECOS | STORAGE | WEST | 2026 | 0 | 0
1768 | SKIPJACK ENERGY STORAGE | 26INR0189 |  | BRAZORIA | STORAGE | COASTAL | 2028 | 0 | 0
1769 | SODA LAKE BESS 1 | 23INR0501 |  | CRANE | STORAGE | WEST | 2025 | 0 | 0
1770 | SOHO BESS | 23INR0419 |  | BRAZORIA | STORAGE | COASTAL | 2026 | 0 | 0
1771 | SOHO II BESS | 25INR0162 |  | BRAZORIA | STORAGE | COASTAL | 2026 | 0 | 0
1772 | SOL MARINA ENERGY CENTER BESS | 26INR0242 |  | ELLIS | STORAGE | NORTH | 2027 | 0 | 0
1773 | SOLACE STORAGE | 26INR0309 |  | HASKELL | STORAGE | WEST | 2026 | 0 | 0
1774 | SOSA STORAGE | 25INR0131 |  | MADISON | STORAGE | NORTH | 2027 | 0 | 0
1775 | SOWERS STORAGE | 22INR0552 |  | KAUFMAN | STORAGE | NORTH | 2026 | 0 | 0
1776 | STARLING STORAGE | 23INR0181 |  | GONZALES | STORAGE | SOUTH | 2027 | 0 | 0
1777 | STOCKYARD GRID BATT | 21INR0492 |  | TARRANT | STORAGE | NORTH | 2026 | 0 | 0
1778 | TAORMINA STORAGE | 23INR0479 |  | BEXAR | STORAGE | SOUTH | 2029 | 0 | 0
1779 | TE SMITH STORAGE | 22INR0555 |  | ROCKWALL | STORAGE | NORTH | 2025 | 0 | 0
1780 | TEHUACANA CREEK BESS SLF | 24INR0189 |  | NAVARRO | STORAGE | NORTH | 2027 | 0 | 0
1781 | THIRD COAST BESS | 23INR0361 |  | JACKSON | STORAGE | SOUTH | 2026 | 0 | 0
1782 | THOMAS CAMERON BESS | 24INR0543 |  | LAMPASAS | STORAGE | NORTH | 2027 | 0 | 0
1783 | TIDWELL PRAIRIE II BATT | 22INR0503 |  | ROBERTSON | STORAGE | NORTH | 2026 | 0 | 0
1784 | TIDWELL PRAIRIE STORAGE 1 | 21INR0517 |  | ROBERTSON | STORAGE | NORTH | 2025 | 204 | 204
1785 | TIERRA SECA BESS | 23INR0364 |  | VAL VERDE | STORAGE | WEST | 2025 | 0 | 0
1786 | TWO BROTHERS BATTERY ENERGY STORAGE SYSTEM | 24INR0425 |  | VICTORIA | STORAGE | SOUTH | 2027 | 0 | 0
1787 | TWO FORKS BESS | 24INR0198 |  | COOKE | STORAGE | NORTH | 2027 | 0 | 0
1788 | VERTUS ENERGY STORAGE | 26INR0333 |  | GALVESTON | STORAGE | HOUSTON | 2026 | 0 | 0
1789 | WHARTON BESS | 22INR0608 |  | WHARTON | STORAGE | SOUTH | 2025 | 0 | 0
1790 | WILLIS STORAGE | 25INR0370 |  | RAINS | STORAGE | NORTH | 2027 | 0 | 0
1791 | WIZARD BESS | 25INR0300 |  | GALVESTON | STORAGE | HOUSTON | 2025 | 0 | 0
1792 | XE HERMES STORAGE | 24INR0365 |  | BELL | STORAGE | NORTH | 2025 | 0 | 0
1793 | ZEYA BESS | 23INR0290 |  | GALVESTON | STORAGE | HOUSTON | 2026 | 0 | 0
1794 | SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * |  | PLANNED_SMALL_GEN_NO_MRD |  | STORAGE |  |  | 49.76 | 49.76
1795 | Planned Capacity Total (Storage) | [6 empty] | 1210.96 | 1060.56
1796
1797 | Mothballed Resources
1798 | BRANDON (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | BRANDON_UNIT1 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 25 | 20
1799 | V H BRAUNIG STG 1 (INDEFINITE MOTHBALL AS OF 3/31/2025) |  | BRAUNIG_VHB1 | BEXAR | GAS-ST | SOUTH | 1966 | 225 | 217
1800 | V H BRAUNIG STG 2 (INDEFINITE MOTHBALL AS OF 3/31/2025) |  | BRAUNIG_VHB2 | BEXAR | GAS-ST | SOUTH | 1968 | 240 | 230
1801 | R MASSENGALE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G6 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
1802 | R MASSENGALE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G7 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 20 | 18
1803 | R MASSENGALE STG (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G8 | LUBBOCK | GAS-CC | PANHANDLE | 2021 | 58.9 | 38
1804 | RAY OLINGER STG 1 (INDEFINITE MOTHBALL AS OF 4/5/22) |  | OLINGR_OLING_1 | COLLIN | GAS-ST | NORTH | 1967 | 78 | 78
1805 | TEXAS BIG SPRING WIND B (INDEFINITE MOTHBALL STATUS AS ON 1/1/24) |  | SGMTN_SIGNALM2 | HOWARD | WIND-O | WEST | 1999 | 6.6 | 6.6
1806 | TY COOKE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT2 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 18.7 | 14
1807 | TY COOKE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT3 | LUBBOCK | GAS-GT | PANHANDLE | 2021 | 26.6 | 17
1808 | WICHITA FALLS STG 4 (INDEFINITE MOTHBALL STATUS AS ON 11/1/23) |  | WFCOGEN_UNIT4 | WICHITA | GAS-CC | WEST | 1987 | 20 | 17
1809 | Total Mothballed Capacity | [6 empty] | 738.8 | 673.6
1810
1811 | Retiring Resources Unavailable to ERCOT (since last CDR/MORA)
1812 | Total Retiring Capacity | [6 empty] | 0 | 0
Capacity changes due to planned repower/upgrade projects are reflected in the operational units' ratings upon receipt and ERCOT approval of updated resource registration system information. Interconnection requests for existing resources that involve MW capacity changes are indicated with a code in the “Generation Interconnection Project Code” column.
For battery storage ("Energy Storage Resources"), the capacity contribution is estimated for the entire BESS fleet and reported in the "Monthly Outlook" and "Capacity by Resource Category tabs."
The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Planned projects for which maximum seasonal sustained capacity ratings have been provided are used in lieu of capacities entered into the online Resource Integration and Ongoing Operations - Interconnection Services (RIOO-IS) system.
Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Resources Services (RIOO-RS) system.
Pertaining to the 'Reliability Must-Run (RMR) and Other Emergency Generation Capacity Agreement Units' line items, the following diesel units have been approved for Synchronization as of 8/27/25, A4 PEARSALL DGR, P2 HIGHLAND HILLS DGR, X1 MEDINA BASE DGR, Z5 SOUTHTON DGR. All diesel units are expected to be in-service before November 1, 2025.
Note on I414: SANDY CREEK U1, 1,008 MW, extended outage until 3/31/27 R W MILLER STG 1, 75 MW, extended outage until 8/25/30 V H BRAUNIG STG 3, 420 MW Gas-Steam, Unavoidable Extension outage until 12/15/25 based on Unplanned Resource Outages Report.
Note on J414: SANDY CREEK U1, 933 MW, extended outage until 3/31/27 R W MILLER STG 1, 75 MW, extended outage until 8/25/30 V H BRAUNIG STG 3, 412 MW Gas-Steam, Unavoidable Extension outage until 12/15/25 based on Unplanned Resource Outages Report.
Note on J1245: CHISHOLM GRID, 102 MW, extended outage until 12/16/28

## PRRM Percentile Results
Probabilistic Reserve Risk Model (PRRM) Percentile Results
Gross Demand by Hour, MW (Accounts for rooftop solar, electric vehicle, and Large Load electricity consumption adjustments; excludes demand response program deployments)
| Percentiles | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| 0% | 43175.4812 | 42049.8476 | 41423.7211 | 41291.5177 | 41835.1332 | 44259.0751 | 45558.6688 | 46640.942 | 47730.9712 | 48953.8915 | 49317.0358 | 49420.7156 | 49335.2095 | 48669.5793 | 48318.0885 | 48167.8086 | 48528.9962 | 49468.1345 | 50175.2956 | 50616.9748 | 50493.428 | 49677.3433 | 47408.7325 | 45107.0589
| 10% | 43753.7333 | 42613.0241 | 41978.5119 | 41844.5378 | 42395.434 | 44957.7984 | 47834.0226 | 48970.3482 | 49313.3137 | 49664.7873 | 49967.037 | 50074.5506 | 50018.8469 | 50323.5404 | 50354.4281 | 50400.1561 | 50710.6571 | 51711.6741 | 52681.2194 | 52928.1438 | 52099.7165 | 50327.6537 | 48043.6809 | 45711.1808
| 20% | 44216.7483 | 43063.9678 | 42422.7409 | 42287.3492 | 42844.075 | 45378.1383 | 48306.2089 | 49424.1149 | 49692.8626 | 50135.1332 | 50455.057 | 50565.6361 | 50500.1258 | 50713.3488 | 50758.8238 | 50778.1837 | 51093.4502 | 52102.9457 | 53903.6484 | 53326.8456 | 52504.4521 | 50817.0448 | 48551.0715 | 46194.9101
| 30% | 44668.312 | 43503.7587 | 42855.9833 | 42719.2089 | 43281.6203 | 45762.9689 | 48840.4791 | 49970.7492 | 50060.2566 | 50566.5137 | 50895.274 | 51013.0636 | 50936.5637 | 51081.555 | 51076.0745 | 51234.3364 | 51499.8398 | 52526.9802 | 54499.8267 | 53778.1405 | 52896.1233 | 51260.682 | 49034.4552 | 46666.6758
| 40% | 45166.5294 | 43988.987 | 43333.9865 | 43195.6865 | 43764.3709 | 46105.6006 | 49367.7041 | 50510.1753 | 50367.0916 | 50952.7924 | 51294.3065 | 51417.692 | 51325.4398 | 51388.4943 | 51623.467 | 51783.8883 | 52051.2272 | 53092.2043 | 55088.1435 | 54358.6668 | 53226.1079 | 51658.2919 | 49527.9823 | 47180.4956
| 50% | 45755.0867 | 44562.1999 | 43898.6642 | 43758.5621 | 44322.06 | 46447.7638 | 49889.0604 | 51043.5968 | 50851.3531 | 51331.6649 | 51689.6444 | 51815.3994 | 51712.9383 | 51903.6601 | 52166.0595 | 52328.5906 | 52598.3157 | 53649.119 | 55668.6326 | 54932.731 | 53699.1272 | 52054.588 | 50007.7139 | 47759.8345
| 60% | 46419.6191 | 45209.4072 | 44536.2346 | 44389.8756 | 44880.2834 | 46751.7978 | 50475.8236 | 51643.9389 | 51449.4341 | 51681.3837 | 52063.1512 | 52198.8606 | 52064.9904 | 52506.1105 | 52776.8166 | 52942.4226 | 53214.1336 | 54273.1568 | 56315.8298 | 55578.8146 | 54330.7019 | 52426.5835 | 50457.718 | 48287.3501
| 70% | 47351.4478 | 46115.2948 | 45405.3754 | 45149.391 | 45431.3267 | 47402.2477 | 51179.4963 | 52363.8961 | 52166.6798 | 52360.5265 | 52669.3436 | 52780.0709 | 52722.4039 | 53236.1817 | 53513.7331 | 53681.7161 | 53957.1563 | 55024.4819 | 57092.5813 | 56350.2584 | 55088.1147 | 53054.1429 | 50883.896 | 48781.3711
| 80% | 48572.5621 | 47188.5466 | 46340.7505 | 45853.1356 | 45953.2303 | 48201.9834 | 52042.959 | 53247.3411 | 53046.7975 | 53243.9146 | 53557.9419 | 53670.5373 | 53603.438 | 54122.6005 | 54403.4337 | 54571.1116 | 54855.0418 | 55940.2962 | 58038.1617 | 57287.2575 | 56017.5207 | 53949.2332 | 51485.5384 | 49272.3881
| 90% | 49494.1432 | 48008.4011 | 47054.2337 | 46460.2586 | 46653.5727 | 49497.3271 | 53441.5221 | 54678.2699 | 54472.337 | 54674.7513 | 54997.2175 | 55096.9303 | 54989.7571 | 55531.2679 | 55812.673 | 55987.8724 | 56275.1455 | 57396.2734 | 59553.7432 | 58768.4119 | 57490.6923 | 55399.0241 | 52869.1218 | 50302.3486
| 100% | 65932.2965 | 66265.2598 | 66471.4894 | 67178.6641 | 68556.6696 | 72042.3202 | 76418.452 | 76766.1578 | 73825.1538 | 70498.4063 | 66759.2653 | 63741.2077 | 60788.7071 | 61395.5592 | 61716.1906 | 61909.9216 | 62227.5807 | 63457.5157 | 65834.03 | 65233.4825 | 65758.02 | 65890.1349 | 63931.6686 | 62960.2505
Solar Generation by Hour, MW
| Percentiles | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| 0% | 0 | 0 | 0 | 0 | 0 | 0 | 7.5321e-09 | 0.10516 | 151.2407 | 3189.7205 | 3544.6355 | 2755.6788 | 1136.8567 | -372.0674 | -894.139 | -1365.5588 | -2473.8382 | 321.2826 | 0 | 0 | 0 | 0 | 0 | 0
| 10% | 0 | 0 | 0 | 0 | 0 | 0 | 2.4169e-05 | 146.6186 | 3077.0229 | 5464.3494 | 6965.8872 | 7770.3814 | 8262.4074 | 8133.9642 | 7708.3822 | 6413.8425 | 4065.4241 | 364.3884 | 0 | 0 | 0 | 0 | 0 | 0
| 20% | 0 | 0 | 0 | 0 | 0 | 0 | 0.00030463 | 355.4118 | 4449.369 | 7450.9468 | 9159.8573 | 10069.2414 | 10572.8299 | 10616.9559 | 10382.3555 | 9149.1965 | 5580.8878 | 413.2945 | 0 | 0 | 0 | 0 | 0 | 0
| 30% | 0 | 0 | 0 | 0 | 0 | 0 | 0.0022502 | 596.0759 | 5647.9211 | 9437.951 | 11144.8233 | 11980.2625 | 12381.3951 | 12432.8297 | 12376.3009 | 11164.5464 | 6655.201 | 472.031 | 0 | 0 | 0 | 0 | 0 | 0
| 40% | 0 | 0 | 0 | 0 | 0 | 0 | 0.013171 | 918.0803 | 6752.1221 | 11387.5678 | 12988.1529 | 13656.6515 | 13959.3707 | 14063.8523 | 14074.2473 | 12835.6363 | 7563.2977 | 547.2586 | 0 | 0 | 0 | 0 | 0 | 0
| 50% | 0 | 0 | 0 | 0 | 0 | 0 | 0.052909 | 1279.8551 | 7912.5954 | 13353.7041 | 14807.4552 | 15216.1395 | 15331.9618 | 15380.4654 | 15580.4617 | 14374.4512 | 8422.544 | 635.312 | 0 | 0 | 0 | 0 | 0 | 0
| 60% | 0 | 0 | 0 | 0 | 0 | 0 | 0.18568 | 1723.5829 | 9179.0859 | 15313.1325 | 16567.0247 | 16736.732 | 16687.0601 | 16682.4991 | 16905.2028 | 15792.4358 | 9218.4004 | 752.5512 | 0 | 0 | 0 | 0 | 0 | 0
| 70% | 0 | 0 | 0 | 0 | 0 | 0 | 0.60689 | 2315.7646 | 10598.7585 | 17531.0143 | 18489.0572 | 18297.8097 | 18033.8953 | 18020.5637 | 18357.939 | 17269.054 | 10130.2076 | 928.3425 | 0 | 0 | 0 | 0 | 0 | 0
| 80% | 0 | 0 | 0 | 0 | 0 | 0 | 1.8364 | 3192.0631 | 12484.062 | 19806.4853 | 20430.257 | 19879.4822 | 19469.2624 | 19519.24 | 19888.6079 | 18842.7209 | 11153.6971 | 1205.9197 | 0 | 0 | 0 | 0 | 0 | 0
| 90% | 0 | 0 | 0 | 0 | 0 | 0 | 5.6278 | 4585.9701 | 15124.571 | 22555.5679 | 22796.0852 | 21863.9865 | 21239.65 | 21198.9012 | 21637.6015 | 20518.1519 | 12627.543 | 1764.6462 | 0 | 0 | 0 | 0 | 0 | 0
| 100% | 0 | 0 | 0 | 0 | 0 | 0 | 63.794 | 8465.0141 | 20865.7705 | 26421.489 | 26692.5192 | 25478.9067 | 25025.2747 | 25211.8283 | 25139.6087 | 23584.2838 | 18452.5994 | 16652.5452 | 0 | 0 | 0 | 0 | 0 | 0
Wind Generation by Hour, MW
| Percentiles | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
| 0% | 418.5084 | 738.7102 | 598.9713 | 858.3323 | 797.4217 | 811.9531 | 672.2553 | 687.826 | 1901.4678 | 785.4047 | 1635.2112 | 659.1411 | 765.2568 | 819.3945 | 1004.2371 | 433.7818 | 562.883 | 726.275 | 878.0775 | 531.2635 | 591.0417 | 503.2365 | -376.3913 | -385.0733
| 10% | 9028.2427 | 9293.2552 | 9013.9549 | 8628.5734 | 8675.7612 | 8452.728 | 7599.8859 | 7396.9141 | 5742.8165 | 6501.43 | 5257.2422 | 6620.248 | 5698.5102 | 5600.0137 | 5254.5305 | 4928.6413 | 5008.9768 | 5649.3617 | 6646.1113 | 8208.4991 | 8663.7683 | 10638.6442 | 8883.4161 | 8541.9668
| 20% | 12517.3917 | 12645.3736 | 12241.563 | 11943.0101 | 11789.25 | 11434.3431 | 10745.3089 | 10425.5813 | 7904.5557 | 9196.1784 | 7449.657 | 9186.4978 | 7646.0259 | 7679.5299 | 7130.1781 | 6789.3401 | 6765.7551 | 7544.5707 | 8990.8877 | 11286.6247 | 11855.8848 | 14354.778 | 12673.4038 | 12400.15
| 30% | 15172.0684 | 14903.3761 | 14713.9196 | 14336.0884 | 14255.048 | 13779.2511 | 13202.0792 | 12673.1276 | 10031.5638 | 11352.0855 | 9766.8865 | 11541.8845 | 9349.7053 | 9389.5518 | 8828.7935 | 8400.3914 | 8384.4574 | 9293.2283 | 10977.1369 | 13515.5927 | 14301.5973 | 17541.4487 | 15611.6399 | 15314.2097
| 40% | 17366.0753 | 17009.4901 | 16886.7857 | 16375.1128 | 16174.9867 | 15830.6988 | 15180.6976 | 14602.1203 | 12257.5799 | 13393.8524 | 12160.1142 | 13480.6561 | 11112.5923 | 11087.046 | 10502.1842 | 10064.1715 | 10048.6391 | 11004.7413 | 12887.4194 | 15633.6661 | 16396.6163 | 19925.5069 | 17994.8775 | 17863.1543
| 50% | 19430.1595 | 19014.826 | 18828.6116 | 18318.8135 | 18001.8726 | 17739.4125 | 17164.1498 | 16484.1032 | 14515.8904 | 15442.4512 | 14754.1554 | 15426.3085 | 12934.757 | 12848.2806 | 12237.8298 | 11802.3151 | 11745.8671 | 12831.528 | 14770.3035 | 17619.5777 | 18270.6516 | 22153.4977 | 20230.8702 | 20173.4175
| 60% | 21316.3503 | 20885.66 | 20705.4957 | 20159.3415 | 19806.7213 | 19505.0541 | 19072.8004 | 18388.2006 | 17101.2798 | 17414.667 | 17628.7274 | 17358.6607 | 14859.2392 | 14844.2325 | 14200.4798 | 13648.5914 | 13637.2659 | 14715.1188 | 16753.8841 | 19621.17 | 20179.1765 | 24115.6547 | 22305.3601 | 22148.1156
| 70% | 23149.4183 | 22885.6157 | 22674.6708 | 22067.1644 | 21764.9683 | 21419.7616 | 21006.5963 | 20448.5707 | 19614.2474 | 19485.8789 | 20404.5572 | 19529.0645 | 17075.9929 | 17301.3466 | 16505.3172 | 15868.0397 | 15749.743 | 16966.5256 | 19031.7252 | 21522.6079 | 22136.8453 | 25927.3133 | 24131.0694 | 24012.3013
| 80% | 25366.9038 | 25046.5065 | 24743.843 | 24223.171 | 23914.0079 | 23626.3693 | 23143.5482 | 22713.1968 | 22453.8897 | 21767.4992 | 23366.0671 | 22108.2286 | 19907.9334 | 20327.1061 | 19392.0531 | 18711.2231 | 18639.441 | 19693.6555 | 21848.3212 | 23860.0785 | 24446.5178 | 27568.8036 | 25820.3913 | 25656.5911
| 90% | 27784.5308 | 27637.48 | 27428.0816 | 26961.9872 | 26613.9296 | 26195.1883 | 25837.2609 | 25543.8394 | 25554.5716 | 25091.6563 | 26483.5577 | 25293.1597 | 23968.056 | 24396.8874 | 23594.5933 | 23110.2297 | 22812.2176 | 23765.8878 | 25543.9707 | 26975.7956 | 27197.1443 | 29254.3865 | 27506.5458 | 27298.8944
| 100% | 34878.9086 | 35001.4995 | 34739.3713 | 34266.7654 | 33743.7986 | 33790.9412 | 32853.6526 | 34156.95 | 32414.1603 | 34049.0288 | 32819.8102 | 34450.2892 | 34123.6675 | 34126.3664 | 33404.7751 | 34118.8605 | 33980.2203 | 34161.2047 | 34291.5456 | 34705.3187 | 34531.4864 | 34254.951 | 30076.0262 | 30192.4209
Unplanned Thermal Outages-Daily, MW
| Percentiles | 1: Unplanned Thermal Outages
| 0% | 1: 10867
| 10% | 1: 12972
| 20% | 1: 13944
| 30% | 1: 14731
| 40% | 1: 15445
| 50% | 1: 16133
| 60% | 1: 16835
| 70% | 1: 17583
| 80% | 1: 18448
| 90% | 1: 19656
| 100% | 1: 22994

## Background
Background
Capacity Available for Operating Reserves (CAFOR)
CAFOR Formula: = Monthly Maximum Expected Resource Generation Capability – Demand – Thermal Outages + Pre-EEA Resources if CAFOR < 3,000 MW + EEA Resources if CAFOR < 2,500 MW Note that winter storm scenarios also account for incremental unplanned wind outages due to severe storm events. The synthetic wind profiles used in the Probabilistic Reserve Risk Model (PRRM) account for normal availability.
The MORA uses CAFOR reserve thresholds of 2,500 and 1,500 MW to indicate, respectively, the risk that an Energy Emergency Alert and controlled outages may be triggered during the time of the forecasted monthly peak load day. These threshold levels are intended to be proxies to the 2,500 and 1,500 MW Physical Responsive Capability (PRC) thresholds. While PRC is a real-time capability measure for Resources that can quickly respond to system disturbance, ERCOT believes that the 2,500 and 1,500 MW CAFOR thresholds are appropriate indicators for the risk of Emergency Conditions given the uncertainties in predicting system conditions months in advance.
Wind and Solar Capacity Values
Hourly capacity contributions for specific wind and solar capacity values come from hourly synthetic generation profiles prepared for existing sites and planned sites expected to generate power by the beginning of the month. Every site has multiple profiles representing hourly generation for each historical weather year going back to 1980. The profiles are used to develop hourly probability distributions for the Probabilistic Reserve Risk Model.
Probabilistic Modeling
For MORA development, ERCOT uses an in-house-developed model called the Probabilistic Reserve Risk Model (PRRM). The model uses Monte Carlo simulation techniques to generate 10,000 outcomes for Capacity Available for Operating Reserves (CAFOR). The model incorporates hourly risk variables, which are the load and resource-specific capacity amounts expressed as hourly or daily probability distributions based on historical data and forecast assumptions.
The risk variables comprise the following:
● | Monthly Peak Load - The Peak load variable is negatively correlated with a system-average temperature probability distribution. (For the winter months, the lower the temperature selected by the model for a simulation, the higher the peak load selected.) The model also uses multiple normalized hourly load shapes to simulate loads for the hourly range; load shapes reflect actual hourly loads for historical monthly peak load days.
● | Wind Production - Hourly probability distributions are fitted to hourly synthetic production profiles. Profiles are developed for each operational and planned wind site with wind output values aggregated to system values. The profiles reflect weather-year variability back to 1980. Temporal correlations between hourly probability distributions are applied to simulate hourly wind speed persistence effects. Note that synthetic wind profiles do not reflect actual observed generation. They are based on meteorological and power conversion models that together simulate what wind production would be for existing and planned sites at the start of the month based on historical hourly weather patterns.
● | Solar Production - Hourly probability distributions are fitted to hourly synthetic production profiles lust like wind. Temporal correlations between hourly probability distributions are applied to simulate hourly solar irradiance persistence effects. Note that synthetic solar profiles do not reflect actual observed generation. They are based on meteorological and power conversion models that together simulate what solar production would be for the existing and planned sites at the start of the month based on historical hourly weather patterns.
● | Low Ambient Temperature Curve - A range of hourly average Texas-wide low temperatures (for the winter months). The low temperature probability distribution is correlated with both the peak load and cold-weather-related thermal outage probability distributions.
● | Typical Unplanned Thermal Outages based on Normal Weather - A range of daily unplanned outage amounts based on assessment month history for the past three years. For the winter months, outages during major winter storms are excluded from the probability distributions. The Expected Thermal Outages - Unplanned line item in 'Deterministic results based on normal system conditions for the hour with highest risk of reserve shortages' table in the Monthly Outlook tab are based on the P50 output from the PRRM run for the reporting month.
● | Extreme-Weather-Related Thermal Outages - For the winter months, the probability distribution reflects a range of daily unplanned weather-related outage amounts scaled from zero MW to the maximum amount observed during Winter Storm Uri. The probability distribution is correlated with the Low Ambient Temperature curve. An outage reduction amount, reflecting availability of generating units that participate in the Firm Fuel Supply Service (FFSS) program, is also modeled. The FFSS outage reduction amounts vary based on the total capacity procured for the given winter season and the negative correlation between low temperature and weather-related outages. For example, the February 2025 model reflects an FFSS outage reduction range from 67 MW to 168 MW, with the outage amount for each simulation outcome dependent on the selected low temperature.
● | Switchable Generation Resources Currently Serving Neighboring Grids - The model includes individual probability distributions for each SWGR currently serving customers in the Southwest Power Pool that are able to switch to ERCOT if allowed based on prevailing power supply contracts. Such SWGRs are designated as the "Controlling Party" in the most current ERCOT-SPP Coordination Plan. (The Plan is consistent with the "Notices of Unavailable Capacity for Switchable Generation Resources" provided to ERCOT.) The probability distributions are binary—each unit is made available or not, with the probability of being available based on analysis of Current Operating Plan (COP) data covering Winter Storm Elliott and the EEA event on November 6, 2023. This variable is treated an available Pre-EEA resource in the model, and assumes that this SWGR capacity may be available if requested by ERCOT to address an Energy Emergency.
● | Remaining Non-Synchronous Tie Transfers - The model uses the DC Tie capacity contribution amounts cited in recent Capacity, Demand and Reserves (CDR) reports as the base amounts. A probability distribution represents the remaining transfer capability that may be available during an ERCOT Energy Emergency. This variable is treated is an available Pre-EEA resource in the model.
● | Weather-related Outage Reduction Success Rate due to Weatherization - The model uses a triangular probability distribution to reflect a percentage range of outage reduction amounts, currently set to a likeliest value of 85% and minimum and maximum values of 80% and 90%, respectively. The probability distribution will be modified as actual success rate data is accumulated over time.
The model also includes several resource variables that are not associated with probability distributions, but are dynamic in that their capacity values are dependent on other variable values calculated by the model. These include the following:
● | Battery Energy Storage System (BESS) Capacity Contribution - Beginning with the April 2025 MORA, ERCOT modified the methodology for determining BESS hourly capacity contributions. ERCOT uses the average hourly maximum SCED Base Point possible from available State of Charge (SOC), without discounting SOC needed to support Ancillary Service Supply Resource Responsibilities. The calculations are performed for days during the prior year's reporting month that represent the peak load day, lowest operating reserve day, and/or day(s) when an EEA or winter storm event occurred. The BP values are expressed as capacity factors by dividing by the installed BESS capacity for the month. The final step is to multiply the capacity factors by the aggregate installed capacity values for the forecast month reported in the MORA Resource Details tab.
● | Price-Responsive Demand Reduction (Winter Months) - ERCOT's Demand Forecasting & Analysis department conducted an analysis of price responsive demand reduction that occurred during the mid-January 2024 winter storm event (WS Heather). The reduction, mainly coming from industrial/commercial sector customers and Bitcoin miners (LFLs), was driven by high market prices. The estimated reduction was approximately 7,000 MW during the January 16th peak load hour (Hour Ending 8:00 a.m.) The impact during a similar storm event in February 2025 is estimated at 5,000 MW for the peak load hour. The LFL contribution to this total is based on the methodology described in the "Estimating Peak Electricity Consumption for Operational and Planned Large Flexible Loads" section below. The model triggers this demand reduction if a severe winter storm (at least as severe as Winter Storm Elliott) or extremely high net loads occurs for a given simulation outcome. The price responsive demand impact varies for each hour based on the pattern seen during WS Heather.
● | Incremental Price Responsive Demand Reduction (Summer Months) - The summer monthly load forecasts account for historically typical price-responsive demand reduction, largely driven by customers participating in Transmission and Distribution Provider (TDSP) "Four-Coincident Peak" programs. To account for incremental price responsive demand reduction that may occur during a summer month with high load and/or wholesale electricity prices, ERCOT developed incremental PRD load reductions based on data gathered from the 2024 PRD survey and other meter data. The 2024 PRD report (https://www.ercot.com/mp/data-products/data-product-details?id=NP3-110) provides data for summer month peak load and net peak load hours, which was used to shape PRD reduction amounts for each of the 24 simulation hours. This load reduction amount is assumed to become available when CAFOR drops below the 2,500 MW threshold. The incremental PRD-based load reductions are triggered when an hourly net load exceeds a high threshold indicative of reserve capacity scarcity conditions.
● | Private Use Network (PUN) Generator Injection - PUN generator injection comes from hourly average historical MW output levels for the peak load day of the most recent historical month. (For example, the values for March 2025 come from output values for the peak load day for March 2024.) The hourly output levels are converted into capacity factors that are multiplied by the expected PUN installed capacity at the start of each month to derive the hourly PUN injection amounts. A similar set of capacity factors is also calculated for the historical day with the lowest Physical Responsive Reserve (PRC) amount. Use of the alternate PUN capacity factors are triggered when there are extreme low temperatures leading to a morning peak load. For winter months, the model will also add an incremental amount of PUN generator capacity when the model selects an extremely low temperature, indicative of system stress conditions and opportunities for the PUN owners to take advantage of high market prices.
● | Planned Thermal Outage Adjustments due to ERCOT Advance Action Notices (Spring and Fall Months) - A sufficient inventory of "post-mortem" reports for Advance Action Notices have been accumulated since AANs were enacted to provide reasonable estimates of reduced planned outages due to (1) voluntary postponement by generation operators due to AAN issuance, and (2) required postponements due to issuance of ERCOT Outage Adjustment Schedules. Voluntary planned outage postponements are triggered by high hourly net loads indicative of a potential Energy Condition.
Large Flexible Load Consumption Forecast
The LFL Forecast is derived using a linear model driven by seasonal variables and observed LFL behavior. The LFL pattern indicates a reduction to 50% over the coincident peak hours for the months of June, July, August, and September and to 15% over the net-load peak hours for these months.
Modeling of Coastal Wind Generation Curtailment due to New Generic Transmission Constraints
A new contributor to reserve shortage risk is the potential need, under certain grid conditions, to limit power transfers from South Texas into the San Antonio region. Conditions could cause overloads on the lines that make up the South Texas export and import interfaces, necessitating South Texas generation curtailments and potential firm load shedding to avoid cascading outages. The risk is greatest when the ERCOT Region has extremely high net loads in the early evening hours. This issue will be addressed with mitigation measures including the construction of the San Antonio South Reliability Project, which is anticipated to be completed by Summer 2027. To model this generation curtailment risk, ERCOT evaluated the net load and coastal wind curtailment conditions at the time of the November 6th, 2023, Energy Emergency Alert event. To simulate the risk of a similar event, the PRRM was modified in the following ways: 1. Synthetic wind profiles by site were divided into Coastal and Non-coastal aggregation categories, and hourly probability distributions were developed accounting for time-coincident correlations between Non-coastal and Coastal hourly wind generation. 2. With the South Texas wind curtailment functionality turned on, the model will curtail coastal wind generation when (1) total system net load for a given hour reaches a trigger amount, expressed as a percentage of the gross load, and (2) unplanned thermal outages for the hour exceed a trigger amount. Analysis of net load and unplanned thermal outages at the time of the November 6, 2023, EEA event was used to determine the two trigger criteria. 3. CPS Energy is increasing line clearances to provide an Emergency & Load shed Rating different than the Normal Rating. The rating changes should allow for an additional ~550 MW of generation South of the Interconnection Reliability Operating Limit (IROL). The amount of coastal wind curtailment has been reduced by this amount.