## Slide 1
RTCBTF
September 25, 2025
Balancing Operations Planning Staff
RTC-RUC AS Deployment Factors for Go Live

## Slide 2: Introduction
ERCOT has been actively working on analysis to formulate a strategy for setting Ancillary Service (AS) Deployment Factors (DFs) in Reliability Unit Commitment (RUC) studies in RTC.
For immediate use after Go-Live ERCOT expects to set DFs in a manner that minimizes manual operator action to change these (to reduce the risk of human error).
Post-RTC Go-Live, as more experience with RTC is gained, ERCOT intends to transition to setting deployment factors informed by forecasted uncertainty a day or two days prior to the Operating Day.
  This approach will require system changes both to determine the appropriate DFs and establish a workflow that updates the ERCOT systems with these.
Today’s presentation will
  Summarize salient features of RTC-RUC and
  Provide insights into the approach/methodology ERCOT is considering to use to establish DFs for of each AS type to be used for Go Live.

## Slide 3: RUC with Implementation of RTC+B Project
DRUC and HRUC will be the tools to assess if enough capacity is available (and in the right locations) to ensure RTC SCED will have enough capacity (and State of Charge) to solve for energy and Ancillary Services.
Similar to today, ESRs will NOT be seen as OFF and are therefore NOT available to be RUCed. In other words, the RUC software will NOT RUC an ESR to come online. (ESRs should have a status of “ON”, “ONOS” “ONTEST”, “ONEMR”, “ONHOLD” or “OUT.” “OUT” should be used only if the resource is “broken.”)
In evaluating the capability of the online Resources (and those shown off-line), the full capability of the Resources (including ESRs) planned to be available will be “fair game” for the RUC software. In other words, with the RTC+B implementation the RUC software will not assume Ancillary Services are carried by any particular Resource and will consider all possibilities of where to carry Ancillary Services for future hours.
The RUC software will use the Hour Beginning SoC (HB SoC) provided by the QSEs in their COPS for each ESR to appropriately limit the possible use/capability of each ESR.
The RUC process self-schedules ESRs to their HB SoC. The process of self-scheduling evaluates the change in the COP submitted HB SoC (change in stored energy SoC) across two consecutive hours and determines the best use of that change in energy – combination of charging or discharging the ESR as Base Points and/or procuring Ancillary Services considering Deployment Factors for that hour.
Deployment Factors (DFs) are used to simulate deployment of Ancillary Services for an hour. (Deployment Factors could be 0, 1 or between 0 and 1. There will be a projected DF for each AS and for each hour.)

## Slide 4: RUC with Implementation of RTC+B Project, Contd.
The RUC Capacity Short calculations will use optimization techniques to minimize a QSE’s potential energy and/or Ancillary Service shortfall. This optimization process, will also consider the change in the COP submitted HB SOC across consecutive hours for an ESR to determine the best use of that change in energy to cover the QSE’s energy and Ancillary Services position for each hour in the RUC study period.
Links to background information on RUC Capacity Short Calculation:
  RTC B Modifications to RUC Capacity Short Calcs 02192024 v2.pptx
  RTC B Additional examples RUC Capacity Short Calcs 03172024 v1.pptx
  RTC+B Modifications to RUC Capacity Short Calcs 03172024 (This is a spreadsheet)

## Slide 5: Deployment Factors: Go-live
Outlined below is the approach ERCOT is considering to adopt for setting AS deployment Factors in RUC studies following RTC+B go-live
  ECRS and Non-Spin
    Note that current RUC studies, in accordance with paragraph 1 of Nodal Protocol Section 5.5.2, RUC effectively uses a deployment factor of 1 for Ancillary Services.
    ERCOT’s preference is to continue with similar level of conservatism as is used in today’s RUC for these two services, i.e. use a deployment factor of 1 for ECRS and Non-Spin for all hours.
  Regulation Up and Down
    Can be 1 or lower based on historical Regulation deployed (MWh) as a percentage of total procurement, by month, by hour.
    Regulation deployment data for 2024 and 2025 shows (1) year over year growth, (2) seasonal (higher averages in Summer) and (3) time of day variations (linked to sunrise and sunset.
    ERCOT is actively working on converting these observations into a methodology for establishing DFs for Regulation.
  RRS
    This is expected to be a small value (and not 1) that applies across all hours.
    ERCOT is actively analyzing historical RRS usage as a percentage of total procurement, by month, by hour to derive insights on what value can be appropriate.
  For frequency related AS like Reg Up, RRS and ECRS, to ensure that the RUC studies appropriately account for energy used to recover from unit trip type events and remain compliant with NERC BAL-002 requirements, ERCOT is also considering if a floor of 25% is needed.

## Slide 6: Regulation Up 2024 - Average
Bins | Count |  | Stats | Min | Max | Avg
10% | 25 |  | All | 0.52% | 41.05% | 17.55%
20% | 181 |  | Winter | 6.36% | 30.51% | 17.13%
30% | 74 |  | Spring | 11.51% | 32.54% | 16.99%
40% | 7 |  | Summer | 0.52% | 41.05% | 18.01%
50% | 1 |  | Fall | 6.09% | 34.87% | 18.07%
75% | 0 |  |  |  |  | 
100% | 0 |  |  |  |  | 
Overflow | 0 |  |  |  |  | 

## Slide 7: Regulation Up 2025 - Average
Bins | Count |  | Stats | Min | Max | Avg
10% | 25 |  | All | 3.00% | 41.02% | 19.29%
20% | 75 |  | Winter | 4.75% | 37.18% | 18.42%
30% | 78 |  | Spring | 4.13% | 34.94% | 18.41%
40% | 12 |  | Summer | 3.00% | 41.02% | 20.76%
50% | 2 |  | Fall | N/A | N/A | N/A
75% | 0 |  |  |  |  | 
100% | 0 |  |  |  |  | 
Overflow | 0 |  |  |  |  | 

## Slide 8: Regulation Up 2025 - Max
Bins | Count |  | Stats | Min | Max | Avg
10% | 0 |  | All | 17.15% | 88.20% | 54.01%
20% | 3 |  | Winter | 24.85% | 88.20% | 52.74%
30% | 10 |  | Spring | 24.04% | 83.88% | 54.72%
40% | 16 |  | Summer | 17.15% | 77.54% | 54.15%
50% | 39 |  | Fall | N/A | N/A | N/A
75% | 115 |  |  |  |  | 
100% | 9 |  |  |  |  | 
Overflow | 0 |  |  |  |  | 

## Slide 9: Regulation Down 2024 - Average
Bins | Count |  | Stats | Min | Max | Avg
10% | 10 |  | All | 6.12% | 58.68% | 23.37%
20% | 80 |  | Winter | 7.82% | 36.96% | 23.19%
30% | 148 |  | Spring | 8.79% | 35.85% | 24.14%
40% | 48 |  | Summer | 6.12% | 58.68% | 23.19%
50% | 1 |  | Fall | 7.79% | 41.15% | 22.97%
75% | 1 |  |  |  |  | 
100% | 0 |  |  |  |  | 
Overflow | 0 |  |  |  |  | 

## Slide 10: Regulation Down 2025 - Average
Bins | Count |  | Stats | Min | Max | Avg
10% | 8 |  | All | 4.71% | 59.42% | 23.35%
20% | 72 |  | Winter | 5.23% | 44.18% | 22.62%
30% | 78 |  | Spring | 4.71% | 56.00% | 23.39%
40% | 18 |  | Summer | 5.90% | 59.42% | 23.79%
50% | 10 |  | Fall | N/A | N/A | N/A
75% | 6 |  |  |  |  | 
100% | 0 |  |  |  |  | 
Overflow | 0 |  |  |  |  | 

## Slide 11: Regulation Down 2025 - Max
Bins | Count |  | Stats | Min | Max | Avg
10% | 0 |  | All | 18.86% | 93.75% | 65.76%
20% | 1 |  | Winter | 21.89% | 93.35% | 64.81%
30% | 3 |  | Spring | 18.86% | 92.69% | 66.12%
40% | 9 |  | Summer | 27.91% | 93.75% | 66.02%
50% | 23 |  | Fall | N/A | N/A | N/A
75% | 90 |  |  |  |  | 
100% | 66 |  |  |  |  | 
Overflow | 0 |  |  |  |  | 

## Slide 12: Next Steps
ERCOT will use stakeholder feedback and will continue refining the methodology for establishing DFs for use immediately after Go-Live in the coming days. ERCOT will aim to provide an update in the upcoming RTCB meetings.
Post-RTC Go-Live, as more experience with RTC is gained, ERCOT intends to transition to setting deployment factors informed by forecasted uncertainty a day or two days prior to the Operating Day.