## Slide 1
ERCOT 2025 UFLS Survey Results
ERCOT Compliance

## Slide 2: Background on the ERCOT UFLS Survey and Requirements
ERCOT coordinated and conducted the 2025 survey with ERCOT Transmission Operators (TOs.) The survey serves to ensure that the required automatic under-frequency load shed circuits are configured to provide the appropriate load relief in an under-frequency event.
The table below is taken from the ERCOT Nodal Operating Guides, Section 2.6.1 (1), Requirements for Under-Frequency Load Shedding, and lists the required load shed amounts:
Frequency Threshold | Load Relief
59.3 Hz | At least 5% of the TO Load
59.1 Hz | A total of at least 5% of the TO Load
58.9 Hz | A total of at least 15% of the TO Load
58.7 Hz | A total of at least 15% of the TO Load
58.5 Hz | A total of at least 25% of the TO Load
ERCOT Nodal Operating Guides, Section 2.6.1 (2)
  ERCOT will, prior to the peak each year, survey each TO’s compliance with the automatic Load shedding requirements described in paragraph (1) above, and report its findings to the Technical Advisory Committee (TAC). For purposes of determining a TO’s compliance with this annual survey requirement, TO Load will be the total amount of Load being served by the DSPs that the TO represents, as well as the TO’s transmission-level Customer Load, at the specified time of the survey.

## Slide 3: 2025 UFLS Survey Activity Timeline
Below is the timeline reflecting the survey dates and activities:
Date | Activity
March 20th | Announcement of survey timeline to OWG
April 8th | Market Notice sent to Authorized TO Representatives
May 8th @ 11:00 AM | Date and time of survey
July 8th | Survey results due to ERCOT
August 18th | Results reported to OWG
September 11th | Results reported to ROS
October 22nd | Results reported to TAC

## Slide 4: Survey Results
The overall results of the 2025 UFLS survey are reflected in the table below:
TOs successfully met the UFLS requirements for all five thresholds.
The ERCOT load at the time of the survey was 54,343 MW. In comparison, the 2024 survey overall result was 30.83% at 55,616 MW of load.
Frequency Threshold | Minimum Requirement | Survey Measurement
59.3 Hz | At least 5% of the TO Load | 6.66%
59.1 Hz | A total of at least 5% of the TO Load | 8.47%
58.9 Hz | A total of at least 15% of the TO Load | 18.26%
58.7 Hz | A total of at least 15% of the TO Load | 20.16%
58.5 Hz | A total of at least 25% of the TO Load | 30.66%

## Slide 5: Annual UFLS Survey – Standard UFLS Stages, NOGRR247
NOGRR247 approved on 10/12/2023 and effective no earlier than October 1, 2026, modifies the ERCOT automatic UFLS program by increasing the number of Load shed stages from three to five and changing the TO Load relief amounts to uniformly increment by 5% for each stage. The NOGRR also adds a UFLS minimum time delay of six cycles (0.1 seconds).
Frequency Threshold | Minimum Requirement | Delay to Trip
59.3 Hz | At least 5% of the TO Load | At least six cycles but no more than 30 cycles
59.1 Hz | A total of at least 10% of the TO Load | At least six cycles but no more than 30 cycles
58.9 Hz | A total of at least 15% of the TO Load | At least six cycles but no more than 30 cycles
58.7 Hz | A total of at least 20% of the TO Load | At least six cycles but no more than 30 cycles
58.5 Hz | A total of at least 25% of the TO Load | At least six cycles but no more than 30 cycles
Reference: ERCOT Nodal Operating Guides Section 2: System Operations and Control Requirements

## Slide 6: Survey Results – Standard UFLS Stages, NOGRR247 Implementation (In Progress)
ERCOT TOs have begun implementation of the additional UFLS stages. Five TO Entities have submitted capability totaling:
Frequency Threshold | Survey Percentage | Survey Load
59.1 Hz | 1.81% | 938.49 MW
58.7 Hz | 1.91% | 989.05 MW

## Slide 7: Annual UFLS Survey – Anti-Stall UFLS Stages, NOGRR226
ERCOT Nodal Operating Guides 2.6.1 (3)
A TO may meet the Load relief requirements of the Supplemental anti-stall UFLS stages by utilizing Load that would otherwise be utilized to meet the 59.1 Hz, 58.9 Hz, 58.7 Hz, and 58.5 Hz standard UFLS stages. In this circumstance, the TO’s Load relief responsibility at the 59.1 Hz, 58.9 Hz, 58.7 Hz, and 58.5 Hz standard UFLS stages is reduced by the amount of Load already shed in the supplemental anti-stall UFLS stages. A TO may not meet the Load relief requirements of the supplemental anti-stall UFLS stages by utilizing Load that the TO needs to meet the 59.3 Hz standard UFLS stages. Implementation is voluntary at this time, but will be mandatory no earlier than October 1, 2026:
Reference: ERCOT Nodal Operating Guides Section 2: System Operations and Control Requirements
Frequency Threshold | Minimum Requirement | Delay to Trip
59.5 Hz | At least 1.5% of the TO Load | 90 seconds
59.5 Hz | A total of at least 3.0% of the TO Load | 120 seconds
59.5 Hz | A total of at least 4.5% of the TO Load | 150 seconds

## Slide 8: Survey Results – Anti-Stall UFLS Stages, NOGRR226 Implementation (In Progress)
ERCOT TOs have begun implementation of the Supplemental/Anti-Stall UFLS Stages. Five TO Entities have submitted capability totaling:
59.5 HZ Timing Threshold | Survey Percentage | Survey Load
90 Sec | .31% | 160.12 MW
120 Sec | .53% | 116.01 MW
150 Sec | .73% | 103.64 MW

## Slide 9: Conclusion
ERCOT Compliance appreciates all entities participation in the 2025 UFLS Survey.
Questions or Comments?