## Slide 1: Only Rational Deployment Factors for RTC Go-Live and Beyond
Shams Siddiqi, Ph.D.
Hunt Energy Network (HEN)
(512) 619-3532
shams@crescentpower.net
RTCBTF Meeting
October 27, 2025

## Slide 2: Executive Summary
  ERCOT should model reality, not double-count risk. Setting Deployment Factors to zero for services like ECRS and Non-Spin keeps RUC and SCED consistent, prevents unnecessary thermal commitments, and protects customers from higher costs.
  Problem: ERCOT’s proposed Deployment Factors (DF = 1) for ECRS and Non-Spin cause a mismatch between how resources are “awarded” in RUC and how they actually operate in SCED. This leads to false RUC scarcity, price suppression, and unnecessary thermal commitments. E.g., if ESRs are already providing these services every five minutes in real time, ERCOT shouldn’t pretend in RUC that they can’t. Doing so forces ERCOT to commit extra gas plants unnecessarily- driving up costs and distorting prices.
  Solution: Set DF = 0 for ECRS, Non-Spin, and RRS so that RUC and SCED stay consistent. This aligns modeling with real-time operations, prevents artificial commitments, and ensures ESRs aren’t unfairly penalized. Keep Reg-Up and Reg-Down DFs based on actual deployment history and also use a 4-hour duration for Non-Spin in RUC to reflect energy sustainability needs.
  Why: This isn’t a “battery favoritism” issue — it’s about market integrity and accurate modeling:
  Consistency: RUC and SCED should use the same assumptions to avoid inconsistency.
  Efficiency: Avoids unnecessary thermal commitments.
  Fairness: Prevents un-hedgeable RUC short charges for ESRs.
  Reliability: Still ensures all services meet their energy-duration requirements.

## Slide 3: Only Rational Choice for DFs for RTC Go-Live and Beyond
Extra RUC
Bad DF=1
The ONLY rational choice for DFs are as follows:
  RRS Deployment Factor = 0 (Note: when SCED awards RRS for a SCED interval to an ESR, that ESR is not deployed for Energy within that SCED interval)
  Reg-Up Deployment Factor based on deployment history (Note: when SCED awards Reg-Up for a SCED interval to an ESR, that ESR is deployed for Energy discharge by LFC within the SCED interval)
  Reg-Down Deployment Factor based on deployment history (Note: when SCED awards Reg-Down for a SCED interval to an ESR, that ESR is deployed for Energy charge by LFC within the SCED interval)
  ECRS Deployment Factor = 0 (Note: when SCED awards ECRS for a SCED interval to an ESR, that ESR is not deployed for Energy within that SCED interval)
  Non-Spin Deployment Factor = 0 (Note: when SCED awards Non-Spin for a SCED interval to an ESR, that ESR is not deployed for Energy within that SCED interval)
Fix Real-Time and RUC duration inconsistencies.
Price Suppression
ESR Exposure
Aligned RUC
Good DF=0
Stable Prices
Reliability

## Slide 4: Introduction – ERCOT’s Analysis and Conclusion
To inform appropriate duration needs for every AS type under Real Time Co-optimization (RTC) paradigm, ERCOT has conducted analysis of the (1) duration of historic risks that drive the need for these reserves and (2) length of historic deployment events, some of these deployments occurred in response to the sustained risks.
The subsequent slides provide summary of the analysis that was conducted.
Below is a summary of the minimum duration for various AS type that ERCOT is recommending based on this analysis. Red text identify values that are different from or not stated in the current RTC Protocols.
*Note FRRS is being eliminated with RTC.
AS Type | Real Time |  | Qualification |  | RUC
 | Duration | Protocol Reference | Duration | Protocol Reference | Duration Award and Deployment
Regulation Service* | 30 minutes | 8.1.1.3.1 (2) | 30 minutes | 8.1.1.2.1.1 (5) | 1 hour
Responsive Reserve Service (excluding FFR) | 30 minutes | 8.1.1.3.2 (4) | 30 minutes | 8.1.1.2.1.2 (9) | 1 hour
ERCOT Contingency Reserve Service | 1 hour | 8.1.1.3.4 (2) | 1 hour | 8.1.1.2.1.7 (3) | 1 hour
Non-Spinning Reserve Service | 4 hours | 8.1.1.3.3 (2) | 4 hours | 8.1.1.2.1.3 (8) | 1 hour

## Slide 5: Correct RUC Duration Req – DO NOT Distort RUC with Bad DF
ERCOT’s analysis of Duration Requirements for Real-Time and Qualification already account for conservative probabilities of the various AS types being awarded Energy instead of AS in future SCED intervals to address forecast and other uncertainties.
RUC only awards AS type to a Resource if the Resource has sufficient SOC to meet both RUC Duration and expected Energy deployment given by DFs.
With correction: 100MW ESR only providing Reg-Up with HB-SOC=50MWh and DF=0.2 can be “awarded” 100MW of ESR by RUC in first hour. Next hour, HB-SOC=30MWh and the ESR can only be “awarded” 60MW of Reg-Up by RUC
Note: there are two Δt in RUC: the first Δt reflects the Duration requirement for the AS type (which is what is given in the table below) and the other Δt is the RUC “award” and deployment interval which are always 1 hour for all AS.
With these changes, SCED awards and RUC “awards” will be consistent – avoiding unnecessary RUCs resulting in price suppression and exposure that can’t be hedged and unwarranted RUC short exposure for ESRs
*Note FRRS is being eliminated with RTC.
AS Type | Real Time |  | Qualification |  | RUC
 | Duration | Protocol Reference | Duration | Protocol Reference | Duration
Regulation Service* | 30 minutes | 8.1.1.3.1 (2) | 30 minutes | 8.1.1.2.1.1 (5) | 30 minutes
Responsive Reserve Service (excluding FFR) | 30 minutes | 8.1.1.3.2 (4) | 30 minutes | 8.1.1.2.1.2 (9) | 30 minutes
ERCOT Contingency Reserve Service | 1 hour | 8.1.1.3.4 (2) | 1 hour | 8.1.1.2.1.7 (3) | 1 hour
Non-Spinning Reserve Service | 4 hours | 8.1.1.3.3 (2) | 4 hours | 8.1.1.2.1.3 (8) | 4 hour

## Slide 6: Bad DFs result in Increased RUCs and Unwarranted ESR Exposure
ERCOT’s proposed DF=1 for ECRS and Non-Spin and Non-Spin Duration of 1-hour results in terrible outcomes.
Consider self-committed thermals exactly meet net load for the day with 3,000MW of additional offline thermals and 3,000MW of ESR with HB-SOC=3,000MWh for all hours of the day [Note: if the ESR charges and discharges within this day, then, of course, the HB-SOC should reflect such charging/discharging]
With ECRS DF=1, RUC cannot “award” ECRS any of the 3,000MW ESR and must RUC and “award” 3,000MW of thermals to meet AS Plan (assuming cost of RUC commitment is below RUC ECRS ASDC)
In SCED, 3,000MW ESR will be awarded 3,000MW ECRS for all 5-minute intervals of the day
If these ESRs had DAM or bilateral sales, then ESRs are charged RUC short charges (due to snapshot at time of RUC) even though in SCED they provided ECRS all day!
Market distortions: price suppression due to 3,000MW of totally unnecessary thermal RUC (thermals may experience operational issues/limits), unjustified RUC short charges to ESRs and other shorts, distort ESR DAM and bilateral participation,
With 1-hour Non-Spin duration, consider 3,000MW of ESR with HB-SOC=3,000MWh and DF=1.
If HB-SOC=0 for next hour, RUC may “award” 3,000MW of Non-Spin to ESRs in this hour. This is totally inconsistent with SCED which would award at most 750MW of Non-Spin to ESRs in that hour.
Of course, DF=1 for Non-Spin has the same issues as described for ECRS above.
Table below shows the impact of these recommendations in red text.

## Slide 7: Solution: DF=0 for ECRS & Non-Spin; 4-hour Non-Spin Duration
Consider self-committed thermals exactly meet net load for the day with 3,000MW of additional offline thermals and 3,000MW of ESR with HB-SOC=3,000MWh for all hours of the day [Note: if the ESR charges and discharges within this day, then, of course, the HB-SOC should reflect such charging/discharging]
With ECRS DF=0, RUC can “award” ECRS to all 3,000MW ESR and would not RUC thermals to meet AS Plan
In SCED, 3,000MW ESR will be awarded 3,000MW ECRS for all 5-minute intervals of the day
If these ESRs had DAM or bilateral sales, then ESRs are not exposed to RUC short charges
RUC and SCED consistency avoids unnecessary RUC, price suppression and unwarranted ESR exposure
ECRS and Non-Spin awarded ESRs both in SCED and RUC always maintain 1-hour and 4-hour SOC in order to meet any forecast or other uncertainties as ERCOT has argued for,
With 4-hour Non-Spin duration, consider 3,000MW of ESR with HB-SOC=12,000MWh for all hours and DF=0 [Note: ERCOT proposes 1-hour Non-Spin duration – 4-hour Non-Spin duration is reserving enough SOC equivalent to 1-hour duration plus DF=1 for solar ramp-down hour +/- 1-hour but in a manner consistent with SCED.
RUC can “award” 3,000MW of Non-Spin to ESRs for the entire day. This is totally consistent with SCED which would award 3,000MW of Non-Spin to ESRs for all intervals in that day.
DF=0 for RRS, ECRS and Non-Spin is the correct value for RTC Go-Live and thereafter – this value should not be adjusted after Go-Live for reasons above.
Today’s highly conservative RUC has DF=0 for all AS, including Reg-Up and Reg-Down.
Today, ESRs can provide AS with much less SOC than the corresponding AS duration requirements; under RTC and these changes, ESRs must have SOC sufficient to meet corresponding AS duration requirements to be awarded AS in SCED and RUC.

## Slide 8: Stakeholder Call to Action
Stakeholders had historically taken the lead in designing the ERCOT market – Stakeholders need to lead on RTC design related issues like this, AORDC/ASDC design to reflect AS scarcity values, and mechanisms to ensure adequate SOC control by ESRs under RTC
For RTC go-live, let’s align DFs with operational reality — DF = 0 for ECRS, Non-Spin, and RRS ensures efficient, reliable, and fair market outcomes.