## Slide 1
AEPTX, CPS, Oncor and CenterPoint Texas 765-kV-STEP Eastern Backbone Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
November 19, 2025

## Slide 2: Overview
AEP Texas (AEPTX), CPS Energy (CPS), Oncor Electric Delivery and CenterPoint Energy Houston Electric, LLC (CEHE) jointly submitted the Texas 765-kV-STEP Eastern Backbone Project to the Regional Planning Group (RPG) in July 2025
    This Tier 1 proposed project submission is estimated to cost $9.384 billion and will require a Certificate of Convenience and Necessity (CCN)
    Addresses the statewide extra-high voltage reliability needs identified in the 2024 Regional Transmission Plan (RTP) driven by rapidly growing electrical demand

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
In the 2024 RTP, the forecasted summer peak demand for 2030 exceeded 150 GW, of which approximately 50 GW is large load
The unprecedented load growth prompted discussions about introducing a 765-kV backbone infrastructure to the ERCOT Transmission Grid
The 2024 RTP performed a comprehensive evaluation for determining the 765-kV transmission plan to satisfy the reliability need by 2030
The 2024 RTP developed the 765-kV Strategic Transmission Expansion Plan (STEP) Core Plan to address the 2030 base case reliability needs
The 2024 RTP sensitivity analysis with a reduced load level (~20 GW less overall load) showed major portions of the 765-kV STEP Core Plan will still be needed to meet the reduced demand
The Texas 765-kV-STEP Eastern Backbone Project submission is a subset of the 765-kV STEP Core Plan.

## Slide 5: Comparison of Project Options
ERCOT performed a comprehensive evaluation for determining the 765-kV transmission plan to satisfy the need in the 2024 RTP evaluation
ERCOT conducted extensive engineering analysis of the 765-kV plan and obtained substantial review and input from Transmission and Distribution Service Providers (TDSPs) and other stakeholders in the ERCOT region through the RPG meetings. As a culmination of these efforts, ERCOT has proposed the 765-kV STEP Core Plan during 2024 RTP study
The Texas 765-kV-STEP Eastern Backbone Project submission is a subset of the 765-kV STEP Core Plan

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for 765-kV STEP Core Plan, which the Texas 765-kV-STEP Eastern Backbone Project is a subset of, and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that:
  765-kV STEP Core Plan, which the Texas 765-kV-STEP Eastern Backbone Project is a subset of, did not introduce any significant additional congestion within the study area
  No potential future generation studied impacts the Texas 765-kV-STEP Eastern Backbone Project
  Starting 2024, ERCOT RTP adopted a new methodology of having one summer peak case for each study year with non-coincident peaks for each of the Weather Zones, which eliminates the load scaling impact

## Slide 8: Overall Project Summary
Four (4) new 765-kV substations
Approximately 1,109 miles of new 765-kV single-circuit transmission lines
Eleven (11) new 765/345-kV transformers
Five (5) 300 MVAr Bus Switch Shunt Reactors (1,500 MVAr total)
Six (6) 300 MVAr Line Switch Shunt Reactors (1,800 MVAr total)
Forty-Three (43) new 765-kV Circuit Breakers
Twenty-Six (26) new 345-kV Circuit Breakers

## Slide 9: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Texas 765-kV-STEP Eastern Backbone Project to address the statewide extra-high voltage reliability needs identified in the 2024 RTP driven by rapidly growing electrical demand
TSPs expect to implement the upgrades between 2030 and 2032
Estimated Capital Cost: $9.384 billion

## Slide 10: ERCOT Recommendation
  CCN filling will be required to:
    Construct a new Dinosaur to Watermill 765-kV single-circuit transmission line, requiring a new right of way (ROW), approximately 78.0-mile;
    Construct a new Watermill to Martin Lake 765-kV single-circuit transmission line, requiring a new ROW, approximately 152.4-mile;
    Construct a new Martin Lake to Hillje 765-kV single-circuit transmission line, requiring a new ROW, approximately 292.8-mile;
    Construct a new Hillje to Blu Lacy 765-kV single-circuit transmission line, requiring a new ROW, approximately 142.8-mile;
    Construct a new Blu Lacy to Howard 765-kV single-circuit transmission line, requiring a new ROW, approximately 139.2-mile;
    Construct a new Howard to Bell East 765-kV single-circuit transmission line, requiring a new ROW, approximately 170.4-mile; and
    Construct a new Bell East to Watermill 765-kV single-circuit transmission line, requiring a new ROW, approximately 133.2-mile.

## Slide 11: ERCOT Recommendation
Construct a new Blu Lacy 765/345-kV Substation and Install;
  Five (5) 765-kV Circuit Breakers in a ring bus configuration expandable to breaker-and-a-half configuration;
  Four (4) 765-kV, 300 MVAr Switch Shunt Reactors (100 MVAr/phase);
    Two (2) Bus Switch Shunts each with a Circuit Breaker; and
    Two (2) Line Switch Shunts each with a Circuit Breaker.
  Eleven (11) 345-kV Circuit Breakers in a seven-position (7) breaker-and-a-half configuration; and
  Three (3) 765/345-kV transformers rated to at least 2,403 MVA Normal and 2,772 MVA Emergency;
Construct a new Watermill 765-kV Switchyard and Install;
  Twelve (12) Circuit Breakers in a double-bus, double-breaker configuration; and
  Reactive device on 765-kV line*.
*Potential additional reactive support for operational support and flexibility

## Slide 12: ERCOT Recommendation
At Existing Watermill 345-kV Substation;
  Install six (6) Circuit Breakers in a breaker-and-a-half configuration.
At Watermill 765/345-kV Substation Install;
  Three (3) 765/345-kV transformers, rated to at least 2,403 MVA Normal and 2,772 MVA Emergency.
Construct a new Martin Lake 765-kV Switchyard and Install;
  Eight (8) Circuit Breakers in a double-bus, double-breaker configuration; and
  Reactive device on 765-kV line*.
At Existing Martin Lake 345-kV Substation;
  Install four (4) Circuit Breakers in a double-bus, double-breaker configuration.
At Martin Lake 765/345-kV Substation Install;
  Two (2) 765/345-kV transformers, rated to at least 2,403 MVA Normal and 2,772 MVA Emergency.
*Potential additional reactive support for operational support and flexibility

## Slide 13: ERCOT Recommendation
Construct a new Hillje 765-kV Substation and Install;
  Install eight (8) Circuit Breakers in a breaker-and-a-half configuration.
At Existing Hillje 345-kV Substation;
  Expand breaker-and-a-half configuration by adding two (2) new bays; and
  Install five (5) Circuit Breakers in expanded breaker-and-a-half configuration.
At Hillje 765/345-kV Substation Install;
  Three (3) 765/345-kV transformers, rated to at least 2,403 MVA Normal and 2,772 MVA Emergency;
  Two (2) 300 MVAr Line Shunt Reactors; and
  Two (2) 300 MVAr Bus Shunt Reactors.
Install two (2) 765-kV Circuit Breakers in a double-bus, double-breaker configuration at New Substation 2 [Dinosaur];
Install reactive device on 765-kV line at New Substation 2 [Dinosaur]*;
*Potential additional reactive support for operational support and flexibility

## Slide 14: ERCOT Recommendation
Install four (4) 765-kV Circuit Breakers in a double-bus, double-breaker configuration at East Bell Substation;
Install reactive device on 765-kV line at East Bell Substation*;
Install four (4) 765-kV Circuit Breakers in a double-bus, double-breaker configuration at Howard 765-kV Substation;
  Install two (2) 300 MVAr 765-kV Line Shunt Reactors at Howard Substation; and
  Install one (1) 300 MVAr 765-kV Bus Shunt Reactor at Howard Substation.
Construct a new Dinosaur to Watermill 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,603 MVA, which will require a new right of way (ROW), approximately 78.0-mile;
Construct a new Watermill to Martin Lake 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,603 MVA, which will require a new ROW, approximately 152.4-mile;
*Potential additional reactive support for operational support and flexibility

## Slide 15: ERCOT Recommendation
Construct a new Martin Lake to Hillje 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,603 MVA, which will require a new ROW, approximately 292.8-mile;
Construct a new Hillje to Blu Lacy 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,603 MVA, which will require a new ROW, approximately 142.8-mile;
Construct a new Blu Lacy to Howard 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,603 MVA, which will require a new ROW, approximately 139.2-mile;
Construct a new Howard to Bell East 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,603 MVA, which will require a new ROW, approximately 170.4-mile; and
Construct a new Bell East to Watermill 765-kV single-circuit transmission line, with normal and emergency ratings of at least 7,603 MVA, which will require a new ROW, approximately 133.2-mile.

## Slide 16: ERCOT Recommendation