## Slide 1
Oncor Connell 345/138-kV Switch and Connell to Rockhound 345-kV Double-Circuit Line Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
November 19, 2025

## Slide 2: Overview
Oncor submitted the Connell 345/138-kV Switch and Connell to Rockhound 345-kV Double-Circuit Project for Regional Planning Group (RPG) review in June 2024
    This Tier 1 Oncor proposed project submission was estimated to cost $110.62 million and will require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues in Martin and Midland Counties in the Far West Weather Zone

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violations in Martin and Midland Counties in the Far West Weather Zone
System improvement is needed to meet reliability planning criteria
Contingency Category* | # of Unsolved Contingencies | # of Thermal Overloads | # of Bus Voltage Violations
N-0 (P0) | None | None | None
N-1 (P1, P2-1, P7) | None | None | None
G-1+N-1 (P3)* | None | None | None
X-1+N-1 (P6-2)** | None | 2 | None
*G-1 Generator tested: Odessa Ector CC1
**X-1 Transformers tested: Midland East T1, Morgan Creek T3, Rockhound T1

## Slide 5: Comparison of Project Options (Continued)
ERCOT analyzed three separate options
Option 1 addresses the reliability violations, meets ERCOT and NERC Reliability Criteria, improves long-term load-serving capability and is feasible
ERCOT recommends Option 1 as the preferred option
*Cost estimates were provided by the TSP
**The cost estimates were not provided because the option was either deemed infeasible by Oncor or did not meet ERCOT and NERC Reliability Criteria
 | Option |  | 
 | 1 | 2 | 3
Meets ERCOT and NERC Reliability Criteria | Yes | Yes | No
Improves Operational Flexibility | Yes | Yes | Yes
Improves Long-Term Load-Serving Capability | Yes | Yes | Yes
Require CCN (~miles) | Yes (13.2) | No | No
Cost Estimate* (~$M) | $110.62 | N/A** | N/A**
Feasible | Yes | No | Yes

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 1 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 1 did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 1 to address reliability issues in Martin and Midland Counties in the Far West Weather Zone
TSP expects to implement the upgrades by December 2026
Estimated Capital Cost: $110.62 million
  CCN filling will be required to:
    Construct the new 345-kV double-circuit line from Connell to Rockhound, requiring approximately 13-mile new right of way (ROW);

## Slide 9: ERCOT Recommendation
Construct a new Connell 345/138-kV switching station approximately 1.0 mile west of existing Oncor Glass Ranch Switch, with two new 600 MVA (nameplate) 345/138-kV transformers, in a 6-breaker 345-kV breaker-and-a-half bus arrangement and a 10-breaker 138-kV breaker-and-a-half bus arrangement, with all 345-kV equipment will be rating at least 2988 MVA and 138-kV at least 765 MVA;
Construct two new Connell to Rockhound 345-kV lines, with conductors rated to at least 2988 MVA, in a new (estimated 13.0 mile) ROW, installed on new, common double-circuit towers;
Install two new 345-kV circuit breakers at Oncor’s existing Rockhound 345-kV Switch, rated at least 2988 MVA;
Install two new 138-kV circuit breakers at Oncor’s existing Sale Ranch 138-kV Switch, rated at least 765 MVA;
Disconnect Oncor’s existing Tall City to Sale Ranch 138-kV line at structure 1/9;

## Slide 10: ERCOT Recommendation
Rebuild 9.0-mile portion of Oncor’s existing single circuit 19.2-mile Sale Ranch to Glass Ranch to Tall City 138-kV line from Sale Ranch to existing 1/9 Structure and replace 9.0-mile portion with two new conductors, rated to at least 614 MVA, installed on new, common double-circuit towers;
Construct two new Connell Switch to 1/9 structure 138-kV lines, with conductors rated to at least 614 MVA, in a new (estimated 0.1-mile) ROW, installed on new, common double-circuit towers configured to create a Connell Switch to Sale Ranch 138-kV double-circuit line;
Construct a new single Connell Switch to 1/9 structure 138-kV line, with conductor rated to at least 614 MVA, in a new (estimated 0.1-mile) ROW, installed in one position on new double-circuit towers leaving one position vacant and configured to create a new Connell Switch to Tall City 138-kV line; and
Reconfigure Oncor’s existing Red Sand 138-kV POD to be connected to the south circuit on the new Connell to Sale Ranch 138-kV double circuit line.

## Slide 11: ERCOT Recommendation