## Slide 1
Oncor and AEPSC Drill Hole to Sand Lake to Solstice 765-kV Line Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
November 19, 2025

## Slide 2: Overview
Oncor and American Electric Power Service Corporation (AEPSC) jointly submitted the Drill Hole to Sand Lake to Solstice 765-kV Line Project to the Regional Planning Group (RPG) in July 2025
    This Tier 1 proposed project submission is estimated to cost $742.2 million and will require a Certificate of Convenience and Necessity (CCN)
    Addresses the statewide extra-high voltage reliability needs identified in the 2024 Regional Transmission Plan (RTP) driven by rapidly growing electrical demand

## Slide 3: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 4: Project Need
In the 2024 RTP, the forecasted summer peak demand for 2030 exceeded 150 GW, of which approximately 50 GW is large load
The unprecedented load growth prompted discussions about introducing a 765-kV backbone infrastructure to the ERCOT Transmission Grid
The 2024 RTP performed a comprehensive evaluation for determining the 765-kV transmission plan to satisfy the reliability need by 2030
The 2024 RTP developed the 765-kV Strategic Transmission Expansion Plan (STEP) Core Plan to address the 2030 base case reliability needs
The 2024 RTP sensitivity analysis with a reduced load level (~20 GW less overall load) showed major portions of the 765-kV STEP Core Plan will still be needed to meet the reduced demand
The Drill Hole to Sand Lake to Solstice 765-kV Line Project submission is a subset of the 765-kV STEP Core Plan

## Slide 5: Comparison of Project Options
ERCOT performed a comprehensive evaluation for determining the 765-kV transmission plan to satisfy the need in the 2024 RTP evaluation
ERCOT conducted extensive engineering analysis of the 765-kV plan and obtained substantial review and input from Transmission and Distribution Service Providers (TDSPs) and other stakeholders in the ERCOT region through the RPG meetings. As a culmination of these efforts, ERCOT has proposed the 765-kV STEP Core Plan during 2024 RTP study
The Drill Hole to Sand Lake to Solstice 765-kV Line Project submission is a subset of the 765-kV STEP Core Plan

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for 765-kV STEP Core Plan, which the Drill Hole to Sand Lake to Solstice 765-kV Line Project is a subset of, and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that:
  765-kV STEP Core Plan, which the Drill Hole to Sand Lake to Solstice 765-kV Line Project is a subset of, did not introduce any significant additional congestion within the study area
  No potential future generation studied impacts the Drill Hole to Sand Lake to Solstice 765-kV Line Project
  Starting 2024, ERCOT RTP adopted a new methodology of having one summer peak case for each study year with non-coincident peaks for each of the Weather Zones, which eliminates the load scaling impact

## Slide 8: Overall Project Summary
  Approximately 104.4 miles of new 765-kV single-circuit transmission line:
  Drill Hole to Sand Lake 765-kV single-circuit transmission line, approximately 57.6 miles
  Sand Lake to Solstice 765-kV single-circuit transmission line approximately 46.8 miles
Seven (7) additional 765-kV circuit breakers:
  Two (2) at the newly approved Drill Hole 765-kV Switch
  Four (4) at the newly approved Sand Lake 765-kV Switch
  One (1) at the newly approved Solstice 765-kV Switch

## Slide 9: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Drill Hole to Sand Lake to Solstice 765-kV Line Project to address the statewide extra-high voltage reliability needs identified in the 2024 RTP driven by rapidly growing electrical demand
TSPs expect to implement the upgrades by Summer 2030
Estimated Capital Cost: $742.2 million
  CCN filling will be required to:
    Construct a new Drill Hole to Sand Lake 765-kV single-circuit transmission line requiring a new right of way (ROW), approximately 57.6-mile; and
    Construct a new Sand Lake to Solstice 765-kV single-circuit transmission line requiring a new ROW, approximately 46.8-mile.

## Slide 10: ERCOT Recommendation
Install two 765-kV circuit breakers rated at 4000 A or greater in a breaker-and-a-half arrangement at the newly approved Drill Hole 765-kV Switch;
Install four 765-kV circuit breakers rated at 4000 A or greater in a breaker-and-a-half arrangement at the newly approved Sand Lake 765-kV Switch;
Install one 765-kV circuit breaker rated at 4000 A or greater in a double-bus, double-breaker arrangement at the newly approved Solstice 765-kV Switch;
Construct a new Drill Hole to Sand Lake 765-kV single-circuit transmission line using a conductor rated at 5382 A or greater with normal and emergency ratings of at least 7602 MVA, which will require a new ROW, approximately 57.6-mile; and
Construct a new Sand Lake to Solstice 765-kV single-circuit transmission line using a conductor rated at 5382 A or greater with normal and emergency ratings of at least 7602 MVA, which will require a new ROW, approximately 46.8-mile.

## Slide 11: ERCOT Recommendation