## Slide 1: 135PGRR Large Load Interconnection Queue Process Revision
Planning Working Group 11/18/25

## Slide 2: Summary
Discussion of Load used in Studies
Discussion of Large Load Study Timeline
Conflicts with approved Planning Guide Language
Proposed Resolution – PGRR135

## Slide 3: Three – Bucket Methodology
ERCOT Uses a 3 Bucket Methodology for loads that are included in studies
  Bucket 1 – “Must Study” – Loads that must be included in studies for approval
  Bucket 2 – “Maybes” – Loads that may move from Bucket 2 to Bucket 1 in the study process
    Allows sensitivity tests be run on as many of these loads as possible to streamline approvals
    List is generally too large to be effective
  Bucket 3 – Everything
If loads move from 2 to 1 and other studies don’t reflect that load – Restudies required
  ERCOT Criteria – Load moves from 2 to 1 with Steady State Study approval and Signed Interconnection
  There are critical flaws with this approach
Must Study
Maybes
Everything
SS Approved
Signed IA
Studies Ready for Review
Information & Scoping Mtg
Because chaos needed a filing system.

## Slide 4: TSP Large Load Study Timeline
TSPs utilize different processes for large load interconnections
  Primary difference surrounds when Interconnection is signed
ERCOT’s process moves certain TSP loads into “Bucket 1” much faster than others
  Patently discriminatory
Forces other TSPs into endless Restudy Doom-Loop (stuck on stupid)
  Significant time lost
Raises costs on the other TSP loads
  Available MWs taken
  “Low hanging fruit” projects taken
certain un-nAmEd Participants
Most Everybody Else
Request Filed
Scoping Mtg
Steady State
SS to ERCOT
SS Approval
Interconnection Signed
Load moved to Bucket 1
Dynamic Sty
DS to ERCOT
Final Appr
Request Filed
Scoping Mtg
Steady State
SS to ERCOT
SS Approval
Interconnection Signed
Dynamic Sty
DS to ERCOT
Final Appr
Load moved to Bucket 1
Restudies!!!
Line-cutting loads: proof that electrons aren’t the only things trying to move fast.

## Slide 5: Conflicts with Planning Guide Language
Current PUC approved Planning Guide Language (from PGRR115) does not allow this practice:
9.3.4.1 Steady-State Analysis
(1) The steady-state interconnection study base case shall be created from the most recently approved Steady State Working Group (SSWG) base case appropriate for the desired Initial Energization date of the Load. The lead TSP shall remove from the study base case all Transmission Facilities it determines may significantly impact study results that will not be in service before Initial Energization of the proposed Load, as identified in the preliminary LLIS study scope. The steady-state analysis shall include other relevant Large Loads and any transmission upgrades included in the LCPs for those Large Loads that have a complete LLIS per paragraph (6) of Section 9.4, LLIS Report and Follow-up, and that have met the requirements of Section 9.5, Interconnection Agreements and Responsibilities. The lead TSP may include other transmission projects and Substantiated Load in the study base case. All modifications to the SSWG base case made as part of the study assumptions shall be documented in the LLIS report.
Planning Guide Section 9.5.1 is included in the appendix, but references things like
  The TSP having Notice to Proceed to construction and
  Financial security being posted
ERCOT has not filed a PGRR to change this policy
Appears to be in violation of the clear intent of the Planning Guides
Language to come out of grey box next month
Transmission planning isn’t a buffet — you don’t just grab capacity off someone else’s plate.

## Slide 6: So Why Is ERCOT Doing This?
Short answer – we’re not exactly sure
Indication provided in forums
  Current language does not reserve enough capacity fast enough – leads to overbuild potential
  Needed a tool that locks up capacity sooner and this was the only one they could produce
When confronted on the discrimination in August, ERCOT’s response – they don’t control when TSPs sign interconnections
  EXACTLY!!! SO WHY ARE YOU USING IT?
Anything this discriminatory on its face should never have been allowed
This plan has big ‘what if we didn’t think this through’ energy.

## Slide 7: Proposed Solution – PGRR135
PGRR allows ERCOT to require restudy for loads that have:
  Completed Steady State Studies; and
  Posted financial security
This may be too late in the process so additional alternatives:
  Alt 1 - All loads that have completed Steady State Studies
  Alt 2 – Create new financial requirement at study onset and completed Steady State Studies
  Alt 3 – Continue with current Planning Guide language
Open to others
At this point, a coin flip would qualify as process improvement.

## Slide 8: Questions?
ERCOT built a policy in a vacuum. The stakeholders supplied the screaming.

## Slide 9: Appendix – Planning Guide Section 9.5.1
9.5.1 Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility (1) For a Large Load not co-located with a Generation Resource Facility, ERCOT shall not allow Initial Energization prior to receiving one of the following: (a) Confirmation from the interconnecting Transmission Service Provider (TSP) that: (i) All required interconnection agreements or equivalent service extension agreements with the Interconnecting Large Load Entity (ILLE) and, if applicable, directly affected TSP(s) have been executed; (ii) The interconnecting TSP has received written acknowledgement from the ILLE of the ILLE’s obligations to: (A) Notify the interconnecting TSP of changes to the Large Load project information or to the load composition, technology, or parameters, as described in Section 9.2.3, Modification of Large Load Project Information; and (B) Maintain Load consumption at or below the level(s) of peak Demand established in the Load Commissioning Plan; (iii) The interconnecting TSP has received notice to proceed with the construction of all required interconnection Facilities; and (iv) The interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security, applicable payments, and/or other agreements required to fund all required interconnection Facilities; or (b) A letter from a duly authorized person from a Municipally Owned Utility (MOU) or Electric Cooperative (EC) confirming its intent to construct and operate applicable Large Load and interconnect such Large Load to its transmission system.