## Slide 1
Regulation Bias Analysis Post SCR-773
October 2025
ERCOT
Operations Planning
PDCWG | November 14th, 2025

## Slide 2
Discussion Points
Current GTBD Parameters & References
Metric to measure Regulation bias and performance
Regulation Deployed comparison for last three months.
Total Regulation (net) Deployed Comparison
Regulation Deployed 15-minute interval comparison by each hour for 2023, 2024, and 2025 months
Regulation Exhaustion Rate
Regulation bias for consecutive 5-min SCED intervals
Time Error & Contributing Factors
Summary

## Slide 3: Current GTBD Parameters
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 – K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 – 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 – 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 – 2:10 PM – PWRR Threshold from 10 to 15 MW/min
3/19/19 – 2:15 PM – PWRR Threshold from 15 to 20 MW/min
4/01/19 – 10:00 AM – K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 – 1:15 PM – Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – 1:10 PM – K5 changed from 0.4 to 0.5, Max Integral ACE feedback changed from 160 to 200, PWRR Threshold changed from 25 to 30
6/17/20 – 10 AM - PWRR Calculation method changed from Direct to Interpolated
9/1/20 – 11 AM - Max Integral ACE Feedback changed from 200 to 250
9/3/20 – 3 PM - Max Integral ACE Feedback changed from 250 to 300
9/4/20 – 3 PM - Max Integral ACE Feedback changed from 300 to 250
6/1/21 – 10:00 AM – K8 Changed from 0 to 0.5, PSRR Threshold changed to 10
6/2/21 – 10:00 AM – PSRR Threshold changed from 10 to 20
6/3/21 – 10:00 AM – K8 Changed from 0.5 to 0.75
6/4/21 – 10:00 AM – K8 Changed from 0.75 to 1
9/2/21 – 10:00 AM – PSRR Threshold changed to 30
6/7/22 – 10:30 AM – K7 Changed from 0 to 0.5, PDCTRR Min/Max Threshold changed to 10 MW/min
6/8/22 – 10:30 AM – PDCTRR Min/Max Threshold changed from 10 to 20 MW/min
6/9/22 – 10:30 AM – K7 Changed from 0.5 to 0.75
6/10/22 – 10:30 AM – K7 Changed from 0.07 to 1.0
7/21/22 – 10:00 AM–Max Integral ACE Feedback changed from 250 to 350
7/21/22 – 05:10 PM – K5 Changed from 0.5 to 1
7/22/22 – 09:40 PM – K5 Changed from 1 to 0.5
7/27/22 – 08:40 AM – PSRR Threshold changed to 40 MW/min
6/12/23 - PSRR dynamic threshold enabled. The Max PSSR started at 80 MW/min for sunrise and sunset hours
6/15/23 – The Max PSRR threshold increased to 100 MW/min for sunrise and sunset hours
10/26/23 – Max Integral ACE Feedback changed from 350 to 250
3/7/24 – PSRR threshold increased from 100 MW/Min to 120 MW/Min
05/30/24 – Max Integral ACE Feedback changed from 250 MW to 350 MW
8/28/24 – PSS Dynamic Threshold changed from 120 MW/Min – 180 MW/Min
10/31/24– K5 changed to 0.5 to 1 to correct the time error
11/1/24 - K5 changed from 1 to 0.75
11/5/24 – K5 changed from 0.75 to 0.5
11/18/24 – K5 changed from 0.5 to 0.75
11/22/24 – K5 changed from 0.75 to 0.5
3/5/25 – K5 changed from 0.5 to 0.75
3/6/25 – K5 changed from 0.75 to 1
3/7/25 – Max Ace Integral Feedback changed from 350 MW to 400 MW
3/7/25 – PSRR Dynamic Threshold for sunrise and sunset changed from 180 MW/Min to 225 MW/Min
3/11/25 – Max Ace Integral Feedback changed from 400 MW to 350 MW
3/12/25 – K5 changed from 1 to 0.5
6/6/25 – K5 changed from 0.5 to 0.75
6/13/25 – K5 changes from 0.75 to 0.5

## Slide 4: Projected Wind Ramp Rate MAE
Notes: For intra-hour wind ramp forecast, SCED PWRR MAE is smaller than the Persistence forecast with more errors occur during ramping hours.

## Slide 5: Projected Wind Ramp Rate Error
Notes: More errors during ramping hours

## Slide 6: Projected Solar Ramp Rate MAE
Notes: For intra-hour solar ramp forecast, SCED PSRR is generally performing better when compared to the persistence forecast, particularly during the most significant solar ramp hours.

## Slide 7: Projected Solar Ramp Rate Error
Notes: Similar to wind, generally we see greater forecast errors during ramping periods.

## Slide 8: References
Notes: Reference Hours

## Slide 9
Metrics to Measure SCR-773 Performance
Trend and monitor the regulation deployed by hour.
Set target of 50 MW for total regulation deployed by hour for peak hours.
Set target of 85% for the number of intervals where regulation deployment was both up and down for peak hours.
Track the Regulation exhaustion rate for all hours (not to exceed 5%).
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5 minute intervals for peak hours.

## Slide 10: Total Regulation Deployed Comparison
Total regulation deployed for the last three months.

## Slide 11: Total Regulation Deployed Comparison - Monthly
Notes: Total regulation deployed comparison in the last 3 months: Overall regulation deployment trends follow the previous two months.

## Slide 12: Metric 1: Regulation Deployed Comparisons
Trend and monitor the regulation deployed by hour.

## Slide 13: Regulation Deployed Comparison
Notes: For 2025, the trend is biased towards Reg Down, with an exception for Peak hours.

## Slide 14: Regulation Deployed Comparison
Notes: Similar levels of reg up deployment overall compared to previous years with only few instances where more reg up is deployed during sunset hours.

## Slide 15: Regulation Deployed Comparison
Notes: Overall Regulation down deployment in September 2025 is consistent with that of the previous two years. There was an increase in regulation down deployment during Up-Ramp hours.

## Slide 16: Metric 2: Total Regulation Deployed Comparisons
Set target of 50MW for total regulation deployed by hour for peak hours.

## Slide 17: Total Regulation Deployed Comparison
Notes: Total regulation deployed compared with the previous two years.

## Slide 18: Metric 3: 15-min Intervals Where Both REGUP/REGDN Were Deployed
Set target of 85% for the number of intervals where regulation deployment was both up and down.

## Slide 19: “Zero” Crossing Regulation
Notes: Zero crossing regulation is generally higher than the last two years. The lower zero crossing percentages are seen during up-ramp hours.

## Slide 20: “Zero” Crossing Regulation
Notes: Overall, we see that it is above 70% for all periods in 2025.

## Slide 21: Metric 4: Regulation Exhaustion Rate
Track the regulation exhaustion rate for all hours (not to exceed 5%.)

## Slide 22: Regulation Exhaustion Rate
Notes: Average regulation up exhaustion rate for all hours is 1.61%.

## Slide 23: Regulation Exhaustion Rate
Notes: Average regulation down exhaustion rate for all hours is 4.46%.
What’s the issue with HE 9-12?

## Slide 24: Metric 5: Stats on REGUP Bias for Consecutive 5-min Intervals
Using a 50MW filter, target 15 occurrences or less per month for regulation bias of six or more consecutive 5-minute intervals for peak hours.

## Slide 25: Regulation Bias for Consecutive SCED Intervals
Notes: Regulation up bias occurrence for consecutive SCED intervals for all hours is 136 and peak hours is 48.

## Slide 26: Regulation Bias for Consecutive SCED Intervals
Notes: Regulation down bias occurrence for consecutive SCED intervals. For all hours is 161 and peak hours is 21.

## Slide 27: Time Error and Contributing Factors
Accumulated Time Error, Load and Wind Ramp, PWRR Error, Start-Up/Shut-Down Hours, STLF Error, and Expected Generation Deviation.

## Slide 28: Time Error Accumulation

## Slide 29: Load Profile
Notes: Load is seeing an overall increase compared to the last two years.

## Slide 30: Net Load Profile
Notes: The total load is more than the last year.
More Net Load during Up ramp hours.
Net Load: dashed line.

## Slide 31: Load Ramp
Notes: Overall hourly load ramp trend remained similar compared to the last couple of years.

## Slide 32: Wind Profile
Notes: Wind generation is slightly lower than last year

## Slide 33: Start-Up & Shut-Down Hours
Notes: Net Capacity on Start-Up/ShutDown are generally following the trends of the last two years. More capacity during sunset hours

## Slide 34: Short-Term Load Forecast Error
Notes: Forecast – Actual
+ve Error => Over forecasted load
-ve Error +> Under forecasted load
During Up-Ramp hours we see an under forecasted load, and an over forecasted load during off peak and peak hours

## Slide 35: STLF Error Chart
Notes: Error = Forecast – Actual
Min, Max, 10th, 90th percentile
15-minute intervals
Max Positive Forecast Error:
10/2025 HE10 -> 495 MW
Max Negative Forecast Error:
10/2025 HE9 -> -625 MW

## Slide 36: Expected Generation Deviation
Notes: Largest expected generation deviation occurs during solar ramps. We see a positive average expected generation deviation in October.

## Slide 37: Non-SCED Qualified Large Load (NSLL) Ramping
Notes: 1-min NSLL ramp values were examined in bins of 10 MWs (as tracked on x-axis) and the average rate of intervals during which regulation was exhausted (i.e. remaining regulation was less than 5 MW) was computed (as tracked on y-axis).
NSLL includes Large Loads and Steel Mills that are not following SCED dispatch.
Trend is the same: we see low correlation between regulation exhaustion and NSLL ramp

## Slide 38: Questions?
Thank you!