## Slide 1
PGRR134
ERCOT feedback
These comments address both the original PGRR and the redlines proposed by the Joint Commenters in comments dated November 14, 2025.
PLWG – November 18, 2025

## Slide 2: PGRR134
ERCOT supports, in principle, the concept of accounting for the flexibility offered by Controllable Load Resources (CLRs) in the planning and interconnection processes with the reforms provided by NPRR1188.
However, ERCOT has the following major concerns on the specifics of this PGRR, detailed in the following slides:
  Structure of proposed language
  Points in the language that are not clear
  Key concepts that are missing and may require an NPRR
  Request for Urgency
ERCOT notes these concerns are the result of its initial review and may not be comprehensive.

## Slide 3: PGRR134 – Structural Concerns
ERCOT does not believe Section 4 of the Planning Guide is the right place for the language describing the treatment of CLRs during the interconnection process. This language is more appropriately placed in Section 9.
The language in 4.1.1.1(8) references many operational concepts such as resource status codes and Real-Time Energy Bids, that are not relevant in planning assessments.
A load cannot qualify as a CLR prior to taking power, as contemplated by this PGRR.

## Slide 4: PGRR134 – Language that is not clear
4.1.1.1 (8) – It is unclear when the evaluation of the CLR takes place in the interconnection process. The main paragraph references the “ILLE’s notice that it is ready to take service” but subparagraph (a) states that the TSP must evaluate the proposed CLR prior to the QSA (which is earlier).
(8)(a) – ERCOT would like clarity on which TSP is required to evaluate the proposed CLR to determine if it impacts other Large Load requests. Is this TSP expected to study the impacts of the request on all Large Loads or only Large Loads on the TSP’s system?
(9) – ERCOT would like clarity on what constitutes “unanticipated system impacts” and what would be required for the TSP to make that determination.

## Slide 5: PGRR134 – Missing Concepts
While 4.1.1.1(9) speaks to conditions that would allow a load studied as a CLR to de-register as a CLR. However, there is no requirement in this PGRR that the load register as a CLR in the first place or remain a CLR until transmission upgrades are completed.
  ERCOT would need significantly more robust requirements in this area to support this PGRR. A companion NPRR likely would be required.
In order for this concept to work, modifications to SCED methodology would be needed to ensure SCED dispatches the CLR for the constraint rather than letting the constraint violate.
  A companion NPRR likely is needed here too.
  ERCOT recommends this issue be discussed at WMS or WMWG once this PGRR is closer to being finalized.
Once the language currently drafted in Section 4 is relocated to Section 9 of the Planning Guide, new language will be needed in the Planning Guide to define how CLRs should be modeled and studied transmission planning outside of the Large Load interconnection process.

## Slide 6: PGRR134 – Urgency
ERCOT understands the desire expressed by PGRR134 sponsors to update the Planning Guide to account for the flexibility offered by CLRs after the implementation of NPRR1188 as soon as possible.
However, given the complexity of this PGRR, the key concepts that have not yet been included, and the amount of time until NPRR1188 is implemented, ERCOT believes there is sufficient time to work on this PGRR through the stakeholder process on normal timelines.
ERCOT also does not believe this PGRR meets the criteria for Urgency described in Nodal Protocol 21.5(2).
For these reasons, ERCOT does not support granting Urgency to PGRR134.