## Cutover Plan - QSEs&TSPs
RTC+B - Go-Live - Cutover Plan (External - QSEs/TSPs) - 12/04/2025 21:00 - 12/05/2025 03:00
Step | Start Time | End Time | SubSystem | Tasks / Steps | Responsible Entity/Resources | Status | Notes
RTC+B Pre Go-Live Steps - QSEs Systems Readiness
1 | 2025-11-13 | 2025-12-01 |  | QSEs to send the Notifications listener URLs to ERCOT for Go-Live | QSEs |  | Even if QSEs are not changing their listener URLs and plan to use current production listener URLs from Go-Live, they are still expected to submit listener URL information to ERCOT.
2 | 2025-11-13 | 2025-12-04 |  | QSEs to continue to verify telemetry and fix failed telemetry points. | QSEs |  | ERCOT has been sending out the emails with failed telemetry points report to fix telemetry issues as soon as possible.
3 | 2025-12-03 | 2025-12-04 |  | QSEs to verify that their RTC+B EMS AGC/SCADA Calcs/Scripts and Market/COP Interfaces are setup and ready for Go-Live | QSEs
4 | 2025-12-03 | 2025-12-04 |  | QSEs to update their Go-Live Market Systems and Outage Scheduler Systems with RTC+B code, new API URLs and Production Certificates etc. | QSEs
5 | 2025-12-01 | 2025-12-04 |  | QSEs to verify all their resources UDSP telemetry point in their ICCP/SCADA is setup correctly and receiving good quality UDSP signal from ERCOT ICCP. | QSEs
6 | 2025-12-01 | 2025-12-04 |  | ERCOT to configure and enable Market Notifications listener URLs (submitted by QSEs) in Market Trials RTC+B system. This means ERCOT will continue to send Market Notifications to these listener URLs from Go-Live as well. | ERCOT
Parallel Telemetry and Market Submissions
7 | 2025-12-01 | 2025-12-04 |  | QSEs to verify that RTC+B ICCP/EMS and Market systems are updated with latest model. | QSEs
8 | 2025-12-01 | 2025-12-05 |  | oQSEs to continue to send production quality telemetry to both RTC+B and Current Production (Pre-RTC). oQSEs are expected to send production quality telemetry to current production (Pre-RTC) until approximately 06:00 AM on 12/05. | QSEs
9 | 2025-12-01 | 2025-12-04 |  | oQSEs to continue to submit production quality real-time market submissions (COP, TPO, AS Offers, ESR Bids/Offers, Output Schedules etc.) utilizing their parallel RTC+B Market Systems until Go-Live. oUntil Go-Live (Unitl 12/04 23:56), QSEs are expected to submit real-time Market Submissions into Current Production (Pre-RTC) even for OD 12/05 in parallel to RTC+B. This is required in case Cutback is requested by ERCOT. | QSEs |  | o ERCOT will start the outreach to QSEs from 4pm on 12/03 on any observed Market submission issues.
10 | 2025-12-03 | 2025-12-04 |  | QSEs to verify that RTC+B ICCP/EMS and Market systems are updated with latest model. | QSEs
Webex Communication
11 | 2025-12-04 21:00 | 2025-12-05 03:00 |  | Webex Conference Call will be open for QSEs & TSPs IT/OT staff | ERCOT |  | ERCOT will send out Go-Live Webex conference call details to QSEs AR, BAR, RTC+B AE and TSPs.
12 | 2025-12-04 21:00 | 2025-12-04 21:15 |  | QSEs & TSP IT/OT staff to join the Webex Conference Call | QSEs & TSPs IT/OT Staff |  | At least one participant from each QSE is required to be on the call to coordinate the Go-Live Cutover with ERCOT and provide status updates during entire time of Go-Live and support any telemetry and market & Outage submissions issues. ERCOT prefers only 2-3 participants from each company (to keep the population of attendees limited). These participants should be staff that can provide Market, Outage submissions API Cutover and EMS AGC & SCADA applications etc. cutover status and help resolve any QSE telemetry and market issues and QSEs/TSPs outage submissions issues during Go-Live. If you are a QSE and data agent for other QSEs (providing ICCP telemetry services and/or having EMS/GMS applications services, and/or market & outage submissions services), you are expected to provide updates & support in the webex call for those QSEs. QSEs and TSPs participants are requested to join the call with Participant name <QSE Name - Participant Name>
13 | 2025-12-04 21:00 | 2025-12-05 03:00 |  | QSE & TSP IT/OT staff shall provide their system cutover status in Webex chat by sending the message in the following format: QSE Name - Status (Example: ABC - Cutover Complete, XYZ - Cutover ran into issues). TSP Name - Status (Example: ABC - Cutover Complete, XYZ - Cutover ran into issues). QSEs & TSPs can report issues through the call using Webex chat (directly to ERCOT SMEs or using general/All Participants webex chat) | QSEs & TSPs IT/OT Staff |  | If QSE runs into critical issues during their EMS/SCADA cutover that can not be resolved within 5 minutes, QSE shall notify ERCOT by sending the message in Webex chat with nature of the issue, resolution status and confirming that their resources are holding at their current generation. If QSE runs into critical issues during their Market and Outage Submissions API cutovers and can not be resolved within 10-15 minutes. QSE shall notify ERCOT by sending the message in Webex chat with nature of the issue, resolution status. Same with TSPs API cutover.
Market Submissions/Telemetry Issues and Cutover Readiness Support - 21:30-23:30
14 | 2025-12-04 21:30 | 2025-10-30 23:30 |  | oERCOT and QSEs to work and resolve any market submission issues and/or telemetry issues through Webex communication. oERCOT staff will be available to support QSE's & TSP Cutover Readiness in preparation for Go-Live. | ERCOT and QSEs & TSPs IT/OT Staff
RTC+B Go-Live Cutover Steps
15 | 2025-12-04 22:30 | 2025-12-04 22:45 |  | Get final confirmation from ERCOT Control Room to start the Go-Live Cutover activities from 12/4 23:00:00
16 | 2025-12-04 23:00 | 2025-12-04 23:15 |  | ERCOT Control Room will make hotline call around 23:00:00 to notify QSEs/TOs on RTC+B Go-Live. | ERCOT Control Room
17 | 2025-12-04 23:00 | 12/4/2025 23:30:00 PM | NDCRC | Deploy RTC+B Code into NDCRC | ERCOT
18 | 2025-12-04 23:30 | 2025-12-04 23:45 | NDCRC | o NDCRC system is updated with RTC+B code and available for generating units test submissions. oQSEs to login into NDCRC and verify. | QSEs
19 | 2025-12-04 23:30 | 2025-12-04 23:35 | Current Production (Pre-RTC) Outage Scheduler (UI/API) | Shutdown Current Production (Pre-RTC) Outage Scheduler UI and API Services. | ERCOT
20 | 2025-12-04 23:30 | 2025-12-05 | RTC+B Outage Scheduler (UI/API) | oStop RTC+B Outage Scheduler UI and API Services for Cutover oStart the Outage Scheduler Cutover **Cutover takes approximately 30 minutes to complete** | ERCOT |  | ERCOT Outage Scheduler UI/API Services will be down for 30 minutes.
21 | 2025-12-04 23:55 | 2025-12-04 23:55 | Current Production (Pre-RTC) SCED | 11:55 PM SCED is run, results are send out to Market and Market Notifications are sent out to QSEs listeners | ERCOT
22 | 2025-12-04 23:56 | 2025-12-04 23:57 | Current Production (Pre-RTC) SCED | Shutdown Current Production (Pre-RTC) SCED/HRUC and other Market Applications | ERCOT
23 | 2025-12-04 23:56 | 2025-12-04 23:57 | Current Production (Pre-RTC) Market Submissions (UI/API) | Shutdown Current Production (Pre-RTC) Market Manager UI and Market Submissions API Services. | ERCOT
24 | 2025-12-04 23:56 | 2025-12-05 | RTC+B Market Submissions (UI/API) | o Stop RTC+B Market Manager UI and Market Submissions API Services for Cutover o Start the Cutover *** Cutover will complete within 5 minutes*** | ERCOT |  | ERCOT Market Submissions UI/API Services (including EWS Get Reports) will be down for 5-10 minutes.
25 | 2025-12-04 23:56 | 2025-12-05 00:01 | ercot.com Public Dashboards and CDR Reports | o Start ercot.com Public Dashboards and CDR Reports Cutover to RTC+B o Cutover will complete by around 00:01:00 and ercot.com dashboards are updated and CDR Reports get generated from RTC+B | ERCOT
26 | 2025-12-04 23:59 | 2025-12-05 | ICCP | a. Perform Taylor QSE ICCP systems fail over to cutover to RTC+B EMS. b. Verify all QSE ICCP links and ISD links are up and get the telemetry | ERCOT
27 | 2025-12-05 | 2025-12-05 | RTC+B SCED | Confirm 12/05 00:00 Interval RTC+B SCED is completed and results are sent out to Market. *** QSE Resources will be following UDSP based on 00:00 interval SCED Solution*** | ERCOT
28 | 2025-12-05 | 2025-12-05 00:01 | EMS AGC/SCADA Calcs/Scripts | ****QSEs to wait until ERCOT gives instructions through Webex Call on this step**** a. QSEs to Cutover to their EMS AGC/SCADA Calcs/Scripts etc. to RTC+B and start following UDSP. ***QSEs cutover should complete within 30-60 seconds***. b. QSEs to report the cutover status to ERCOT through Webex chat | QSEs |  | QSEs should not automate the Cutover based on UDBP or another telemetry points data quality. QSEs IT/OT staff should wait for ERCOT instructions through Webex call to perform their systems Cutover.
29 | 2025-12-05 | 2025-12-05 00:02 | ICCP | a. Perform Bastrop QSE ICCP systems fail over to cutover to RTC+B EMS. B. Verify all QSE ICCP links and ISD links are up and get the telemetry | ERCOT
30 | 2025-12-05 00:02 | 2025-12-05 00:02 | ICCP | Verify that following outbound telemetry points common to both Pre-RTC and RTC+B systems are getting updated from the RTC+B EMS (New Current Production). Similarly, verify that all existing system level telemetry points are getting updated from RTC+B EMS. BP/LMP/SBBH/SCCT/NDPL/RDPL/MMEC/KVM/KVT | ERCOT
31 | 2025-12-05 00:02 | 2025-12-05 00:05 | ICCP/SCADA/EMS | ERCOT to verify QSEs are following RTC+B (New Current Production) UDSP and report any issues to QSEs through Webex chat. | ERCOT
32 | 2025-12-05 00:02 | 2025-12-05 00:05 | ICCP/SCADA/EMS | QSEs to verify their resources are following RTC+B UDSP and report any issues to ERCOT through Webex chat. | QSEs
33 | 2025-12-05 00:02 | 2025-12-05 00:05 | ICCP/SCADA/EMS | QSEs to provide their systems cutover status through Webex chat (created for communicating to designated ERCOT contacts Only) in the format mentioned above. ***This step is same as above step 23.b with continuation of same action***. | QSEs
34 | 2025-12-05 00:05 | 2025-12-05 00:05 | ICCP/SCADA/EMS | Disable Old Production (Pre-RTC) UDBP, Regulation and other non-RTC+B outbound telemetry points in ERCOT Bastrop and Taylor ICCP Systems. ***This means these telemetry points value will be stale with suspect quality approximately from 12/05 00:04:30 AM until these points are removed during DEC_ML2 Model on Operating Day 12/10*** | ERCOT
35 | 2025-12-05 00:05 | 2025-12-05 00:15 | RTC+B Market Submissions -API | ****QSEs to wait until ERCOT gives instructions through Webex Call on this step**** a. QSEs to Cutover their Go-Live Market Systems/APIs to below new Internet and WAN API End-Point URLs. Internet API URL: https://misapi.ercot.com/NodalAPI/EWS/ WAN API URL: https://api.wan.ercot.com/NodalAPI/EWS/ oMake sure that current production certificates and API Public Key (available at link https://www.ercot.com/services/mdt/webservices) are installed in Go-Live Market API System. oNote that ERCOT DNS and IP Addresses remain same as Pre-RTC ***QSEs Market Systems/APIs cutover should complete within 10 minutes***. b. QSEs to report the Market Systems/APIs cutover status to ERCOT through Webex chat c. QSEs to start submitting market submissions (real-time, day ahead and trades etc.) into ERCOT RTC+B market system (new Production) | QSEs |  | From around 00:15, QSEs will be able to submit market submissions (real-time, day ahead and trades etc.) into ERCOT RTC+B market system (new Production).
36 | 2025-12-05 00:05 | 2025-12-05 00:15 | RTC+B Outage Submissions - API | ****QSEs/TSPs to wait until ERCOT gives instructions through Webex Call on this step**** a. QSEs/TSPs to Cutover their Go-Live Outage Scheduler Systems/APIs to below new Internet and WAN API End-Point URLs. Internet API URL: https://misapi.ercot.com/NodalAPI/EWS/ WAN API URL: https://api.wan.ercot.com/NodalAPI/EWS/ oMake sure that current production certificate and API Public Key (available at link https://www.ercot.com/services/mdt/webservices) are installed in Go-Live Outages API System. oNote that ERCOT DNS and IP Addresses remain same as Pre-RTC ***QSEs/TSPs Outage Scheduler System/APIs cutover should complete within 10 minutes***. b. QSEs to report Outage Scheduler Systems/APIs cutover status to ERCOT through Webex chat c. QSEs/TSPs to start the Outage submissions into ERCOT RTC+B outage scheduler (new Production). | QSEs/TSPs |  | From around 00:15, QSEs/TSPs will be able to start submit outages into ERCOT RTC+B Outage Scheduler(new Production).
37 | 2025-12-05 00:05 | 2025-12-05 00:15 | EWS Get Reports | EWS Get Reports Functionality will be cutover to RTC+B and will be made available for Market Participants to get Reports through EWS API calls by 00:05 | ERCOT
38 | 2025-12-05 00:05 | 2025-12-05 00:30 | RTC+B Market Submissions -UI | o RTC+B Market Manager UI will be up and running from 00:05. o Market Manager UI Go-Live URL will be same as Pre-RTC. Https://mis.ercot.com/mmsui oERCOT and QSEs to verify Market Manager UI is working as expected | ERCOT/QSEs
39 | 2025-12-05 00:05 | 2025-12-05 00:30 | RTC+B Outage Scheduler UI | o RTC+B Outage Scheduler UI will be up and running from 00:05 o Outage Scheduler UI Go-Live URL will be same as Pre-RTC. Https://mis.ercot.com/osui o ERCOT and QSEs/TSPs to verify Outage Scheduler UI is working as expected | ERCOT/QSEs/TSPs
RTC+B is LIVE
40 | 2025-12-05 00:30 | 2025-12-05 00:45 | RTC+B Market Submissions -API | Verify QSEs are able to submit/query market submissions without any issues and get the confirmation from QSEs. | ERCOT/QSEs
41 | 2025-12-05 00:30 | 2025-12-05 00:45 | RTC+B Outage Submissions - API | Verify QSEs & TSPs are able to submit/query outages without any issues and get the confirmation from QSEs/TSPs. | ERCOT/QSEs/TSPs
42 | 2025-12-05 01:00 | 2025-12-05 01:00 | Public API | Public API Cutover to RTC+B Reports will be completed by 01:00 AM | ERCOT/QSEs/TSPs
43 | 2025-12-05 00:45 | 2025-12-05 01:00 |  | After above Go-Live cutover are completed, Control Room makes hotline call to QSEs/TOs announcing RTC+B is LIVE and ERCOT is operating under RTC+B and posts a message on the MIS for ALL QSEs as well. | ERCOT Control Room
Monitoring and Stabilization
44 | 2025-12-05 01:00 | 2025-12-05 03:00 | ICCP/SCADA/EMS | oMonitor Telemetry to RTC+B (new Production) and Pre-RTC (old Production) and fix any issues identified | QSEs/ERCOT
45 | 2025-12-05 01:00 | 2025-12-05 03:00 | EMS/SCED | oVerify that all QSE Resources are following UDSP and Frequency control is managed as expected. o Verify SCED AS Awards and Prices | ERCOT/QSEs
46 | 2025-12-05 01:00 | 2025-12-05 03:00 | Market Submissions | oMonitor Real-Time and 12/06 OD Day-Ahead Market Submissions and fix any issues identified. | QSEs/ERCOT
47 | 2025-12-05 01:00 | 2025-12-05 03:00 | Outage Submissions | oMonitor Outage Submissions and fix any issues identified. | QSEs/ERCOT
48 | 2025-12-05 01:00 | 2025-12-05 03:00 | CDR Reports and Dashboards | oERCOT to verify CDR Reports are getting posted as expected oQSEs to verify that they download CDR Reports directly from MIS and can use Get Reports EWS calls to download the CDR Reports. | QSEs/ERCOT
RTC+B Go-Live Cutover completed
49 | 2025-12-05 03:00 | 2025-12-05 03:00 |  | Verify all Go-Live activities are completed, capture the QSEs/TSPs feedback/Questions/Issues and close the webex Conference call | ERCOT

## High Level Cutback Plan
Cutback to Pre-RTC - In the event Critical issue is identified immediately after Go-Live that has significant impacts on Grid Reliability and Issue can not be fixed immediately
Step | SubSystem | Tasks / Steps | Responsible Entity/Resources | Status | Notes
1 |  | Get confirmation from ERCOT Control Room to cutback to Pre-RTC | ERCOT
2 |  | ERCOT Control Room to make hot line call to QSEs/TOs and inform about cutback to Pre-RTC. | ERCOT Control Room
3 | Pre-RTC SCED | oBring up Pre-RTC MMS system and run SCED oVerify SCED results o Release SCED solution to EMS | ERCOT |  | Pre-RTC SCED will run based on the real-time Market Submissions came in before Go-Live for OD 12/05
4 | ICCP | Enable ERCOT current Production UDBP, Regulation and other non-RTC+B outbound telemetry points in ERCOT Bastrop and Taylor ICCP Systems. ***This means these telemetry points values will show latest values with good quality *** ***QSE resources should continue to follow RTC+B UDSP signal until cutback is completed*** | ERCOT
5 | ICCP | Perform Taylor QSE ICCP systems fail over to cutback to Current Production EMS from RTC+B EMS. Verify all QSE ICCP links and ISD links are up and get the telemetry | ERCOT
6 | Pre-RTC EMS AGC/SCADA/Scripts | ****QSEs to wait until ERCOT gives instructions through Webex Call on this step**** a. QSEs to Cutback to their EMS AGC/SCADA Calcs/Scripts etc. to Current Production and start following current production UDBP and Regulation Instructions. ***QSEs cutback should complete within 30-60 seconds***. b. QSEs to report the cutback status to ERCOT through Webex chat. | QSEs
7 | ICCP | Perform Bastrop QSE ICCP systems fail over to cutback to Current Production EMS from RTC+B EMS. Verify all QSE ICCP links and ISD links are up and get the telemetry. | ERCOT
8 | ICCP | Verify that following outbound telemetry points common to both current and RTC+B systems are getting updated from the Current Production EMS. Similarly, verify that all existing system level telemetry points are getting updated from Current Production EMS. BP/LMP/SBBH/SCCT/NDPL/RDPL/MMEC/KVM/KVT | ERCOT
9 | ICCP/SCADA/EMS | ERCOT to verify QSEs are following Current Production UDBP & Regulation Instructions and report any issues to QSEs through Webex chat. | ERCOT
10 | ICCP/SCADA/EMS | QSEs to verify that their resources are following Current Production UDBP & Regulation Instructions and report any issues to QSEs through Webex chat. | QSEs
11 |  | QSEs to provide their systems cutback status through Webex chat (created for communicating to designated ERCOT contacts Only) in the format mentioned above. ***This step is same as above step 6.b with continuation of same action***. | QSEs
12 |  | After all QSEs cutback to current Production from RTC+B is completed, Control Room makes hotline call to QSEs/TOs announcing cutback to Pre-RTC is completed and also posts a message on the MIS for ALL QSEs as well. | ERCOT Control Room
13 |  | oERCOT will request QSEs to Cutback to Pre-RTC Market Submissions and Outage Submissions APIs if issue resolution is expected to take several hours. oIn this case, ERCOT will also request TSPs to cutback to Pre-RTC Outage Submissions APIs | ERCOT/QSEs/TSPs