## Slide 1
Resource Integration Topics
Jenifer Fernandes
ERCOT
Resource Integration Working Group
December 17th, 2025

## Slide 2: Quarterly Stability Assessment (QSA)
Planning Guide 5.3.5
Next Deadline for QSA
If a GINR is not included in QSA, its Initial Synchronization date will be automatically delayed to the next quarter
All-Inclusive Generation Resource Initial Synchronization Date | Last Day for an IE to meet prerequisites as listed in paragraph (4) below | Completion of Quarterly Stability Assessment
Upcoming January, February, March | Prior August 1 | End of October
Upcoming April, May, June | Prior November 1 | End of January
Upcoming July, August, September | Prior February 1 | End of April
Upcoming October, November, December | Prior May 1 | End of July

## Slide 3: Quarterly Stability Assessment (QSA)
Planning Guide 5.3.5, Quarterly Stability Assessment
Issue’s seen in previous QSA’s
  10 day comment period for FIS
    Needs to be complete before QSA deadline
    TSPs need to plan for it
  Dynamic/PSCAD Model Review
    Dependent on FIS Stability study
    Need to meet PG 6.9 15 to 30 days prior to QSA deadline
PSSE Model Quality Test Required
PSCAD Model Quality Test, Unit Model Validation and Template is required. PSCAD template is required starting August 1st QSA.
TSAT Model Required – If PSSE model is UDM, then TSAT model should be UDM and should include MQT

## Slide 4: QSA 45 day deadline
FIS studies finalized and posted in RIOO-IS 45 days prior to quarterly stability assessment deadline.
Dynamic models (PSEE, PSCAD, TSAT (UDM)) and MQT report submitted in RIOO-IS.
From Planning guide Section 5.3.5 (2): Last Day for an IE to meet prerequisites as listed in paragraph (4) below | 45 day deadline
Prior August 1 | June 17
Prior November 1 | September 17
Prior February 1 | December 18
Prior May 1 | March 17

## Slide 5: Commissioning Phase Coordination
At least 30 days before the RE plans to submit Checklist Part 1 for Energization, the RE is required to submit a completed Commissioning Plan Template.
Once the Commissioning Plan is submitted to RIOO-IS, ERCOT will schedule a Commissioning Kickoff Call to review the plan and discuss the project’s schedule and/or any other relevant commissioning activities regarding Part 1 (Energization), Part 2 (Synchronization), and Part 3 (Commercial Operations).
After the kickoff call, any subsequent calls will be arranged as needed. It is essential to submit a clear agenda to ERCOT for review before setting up a call. To coordinate, please contact the RI Engineer responsible for tracking the INR in RIOO-IS. Note that bi-weekly commissioning calls will no longer be scheduled

## Slide 6: Co-Located Load less than 75MW with New or Existing Gen
Resource Entities (RE), Interconnecting Entities (IE), and Load Entities (LE) that intend to co-locate loads of less than 75MW with new or existing generation must submit the Load Information Form to Resource Integration (ResourceIntegrationDepartment@ercot.com). The Load Information Form for less than 75MW is available on the Resource Integration webpage.
For new Interconnection Requests (INRs), the Load Information Form must be submitted as an attachment when the IE plans to co-locate with a new or existing load.

## Slide 7: Energization Requirements for Co-located Loads less than 75MW
Planning studies: TDSP confirmation that all necessary studies are complete and the TDSP agrees with connecting the load.
Reactive study: The reactive study must demonstrate that the Resource meets its VSS (NP 3.15) requirement with the added Load. For Loads under 20MW, the RE should provide a written attestation that the Resource fulfills its VSS obligation with the additional Load.
Interconnection Agreements: one of the following has been completed
  Amendments to the SGIA indicating New Netting Loads have been signed by all three parties (TDSP, RE, Load Entity). OR
  Amendments to the SGIA indicating New Netting Loads has been signed by the TDSP and the RE and the TDSP has submitted a written notification agreeing to proceed with the energization of the new load per the amended SGIA. OR
  Written notification from the TDSP agreeing to proceed with the energization of the New Netting Load per the approved studies.

## Slide 8: Energization Requirements for Co-located Loads less than 75MW
ESP Meter: EPS Meter Design Proposal including the New Netting Loads has been approved by ERCOT Metering Department
Dynamic Model & MQT for IBRs: Dynamic Models and MQT with the added Load is submitted and approved by Dynamics. Dynamic Models should be submitted to Dynamicmodels@ercot.com and the phrase “IBR proposed modification_Resource_Co-located Load less than 75MW”.
Modeling the Load: Updated Resource Registration Data that includes the addition of the New Netting Loads and any other topology changes at the Station. In addition, the Production Load Date that the Network Operations Model has been updated, including required telemetry. Furthermore, prerequisites #1-4 must be met prior to ERCOT approval to add the New Netting Load.
Checklist List Part 1 to Energize the New Netting Loads and associated equipment has been submitted in RIOO-IS for generation in the interconnection process or RIOO-RS for other generation.

## Slide 9: Active RR’s
PGRR132: Update to Standard Generation Interconnection Agreement (SGIA) Requirement
NPRR1272: Voltage Support at Private Use Networks
PGRR120:SSO Risk Reduction for Generator Interconnection
NOGRR272: Advanced Grid Support Requirements for Inverter-Based ESRs – PUC Approval
PGRR124: ESR Maintenance Exception to Modifications

## Slide 10: Generation Interconnection Requests
1999 active generation interconnection requests totaling 432 GW as of October 31, 2025 (Solar 158 GW, Wind 46 GW, Gas 48 GW, Battery 176 GW, and Other 4 GW) (Excludes capacity associated with projects designated as Inactive per Planning Guide Section 5.7.6)
Chart: Large Generator Monthly Capacity by GIM Milestone plus Project Count, 13-Month Rolling Basis
| Nov-24 | Dec-24 | Jan-25 | Feb-25 | Mar-25 | Apr-25 | May-25 | Jun-25 | Jul-25 | Aug-25 | Sep-25 | Oct-25 | Nov-25
# Signed Interconnect Agreement | 449 | 447 | 445 | 460 | 491 | 507 | 511 | 510 | 517 | 535 | 532 | 530 | 528
# Completed Full Study | 156 | 147 | 133 | 121 | 112 | 105 | 106 | 114 | 119 | 111 | 117 | 116 | 122
# in Full Study | 1070 | 1103 | 1163 | 1200 | 1207 | 1212 | 1223 | 1237 | 1242 | 1201 | 1196 | 1164 | 1159
# Screening Study Complete | 126 | 120 | 119 | 113 | 113 | 102 | 89 | 88 | 86 | 82 | 94 | 94 | 91
# Initial Screening study | 21 | 22 | 16 | 19 | 19 | 29 | 21 | 27 | 27 | 33 | 20 | 11 | 9
GW Capacity | 377.0299 | 378.7444 | 388.6158 | 399.0073 | 404.457 | 410.8736 | 408.9081 | 419.6478 | 432.1004 | 427.4415 | 431.1647 | 431.2039 | 434.4146

## Slide 11: Generation Interconnection Requests
Small Gen- 28 projects Not Model Ready, 57 projects Model Ready
Chart: Small Generator Monthly Capacity by GIM Milestone plus Project Count, 13-Month Rolling Basis
| Nov-24 | Dec-24 | Jan-25 | Feb-25 | Mar-25 | Apr-25 | May-25 | Jun-25 | Jul-25 | Aug-25 | Sep-25 | Oct-25 | Nov-25
# Not Model Ready | 33 | 32 | 30 | 24 | 26 | 32 | 31 | 28 | 23 | 23 | 29 | 28 | 28
# Model Ready | 48 | 46 | 46 | 50 | 50 | 50 | 50 | 50 | 52 | 56 | 54 | 56 | 57
MW Capacity | 755.62 | 726.03 | 701.78 | 682.08 | 706.9 | 767.07 | 762.84 | 733.06 | 703.44 | 741.48 | 770.99 | 780.98 | 790.97
Chart: Small Generator Monthly Capacity by GIM Milestone plus Project Count, 13-Month Rolling Basis
| Nov-24 | Dec-24 | Jan-25 | Feb-25 | Mar-25 | Apr-25 | May-25 | Jun-25 | Jul-25 | Aug-25 | Sep-25 | Oct-25 | Nov-25
# Not Model Ready | 33 | 32 | 30 | 24 | 26 | 32 | 31 | 28 | 23 | 23 | 29 | 28 | 28
# Model Ready | 48 | 46 | 46 | 50 | 50 | 50 | 50 | 50 | 52 | 56 | 54 | 56 | 57
MW Capacity | 755.62 | 726.03 | 701.78 | 682.08 | 706.9 | 767.07 | 762.84 | 733.06 | 703.44 | 741.48 | 770.99 | 780.98 | 790.97

## Slide 12: Other contact information
ResourceIntegrationDepartment@ercot.com is distribution list for Resource Integration department
Mailing List
  RESOURCE_INTEGRATION@LISTS.ERCOT.COM

## Slide 13: Questions?
Thank you!