## TitlePage
Report on the Capacity, Demand and Reserves
(CDR) in the ERCOT Region, 2026-2030
December 19, 2025

## Contents
Table of Contents
Tab | Notes
Disclaimer | Please read
MAIN REPORT
Findings & Discussion | Overview and highlights of the CDR
Load-Resource Scenarios | Presents condensed demand-resource summaries for the summer and winter seasons based on alternative peak demand and/or resource scenarios
Seasonal Summary | Shows load forecasts, resource capacities and reserve margins for the next five summer, winter, spring, fall seasons, for both the expected Peak Load hour and Peak Net Load Hour
RESOURCE REPORTING TABLES
Unit Details | List of registered resources and capabilities used in determining the capacity contributions by Season
New CDR-Eligible Resources | A table listing those planned resources that have met the criteria to be included in the CDR since the last CDR release
DATA INPUT-PROCESSING TABLES
Several tabs with source and intermediate data processing tables used to support other tabs
ExpectedResources | Capacity contributions for Hydroelectric, Private-Use Networks (PUNs), Non-Synchronous Ties, Unconfirmed Planned Retirements, Capacity Pending Retirement, Energy Storage ELCC each aggregated by season-year, feeding into the Seasonal Summary tab.
ELCCs | Effective Load Carrying Capability percentages used for wind, solar and storage resources by season-year, feeding into the Seasonal Summary.
Load | Intermediate calculation sheet that aggregates LongTermLoadForecast data into seasonal peak demand values, applying adjustments for rooftop PV and identifying peak dates/hours for each season-year, feeding into the Seasonal Summary.
DemandIntegration | Load Resources, Controllable Load Resources, Emergency Response Service adjustments by season-year, feeding into the Seasonal Summary tab.
LoadResourceScenarios | Calculation sheet used to support the various Load and Generation assumptions found in the Load-Resource Scenarios tab.
LongTermLoadForecast | Hourly data from the ERCOT Adjusted Forecast prepared in April 2025 used in the Load tab.
WindProfiles | Hourly wind generation profiles based on 2008 historical weather year, used to support the calculation of the peak net load hours for each season-year time horizon.
SolarProfiles | Hourly solar generation profiles based on 2008 historical weather year, used to support the calculation of the peak net load hours for each season-year time horizon.
Seasons | Reference table defining the 20 season-year combinations used as column headers throughout the workbook.
DOCUMENTATION
Acronyms | List of acronyms used in the CDR data tables
Definitions | Definitions of terms used in the CDR
Wind-Solar Region Mapping | Tables that list the counties in the ERCOT region assigned to the CDR Wind and Solar Regions
Background | An overview of the CDR's purpose and key concepts needed to interpret results

## Disclaimer
Disclaimer
FOR PLANNING PURPOSES ONLY
This CDR report has been prepared using data provided by ERCOT and Market Participants. The data may contain errors or become obsolete and thereby affect the accuracy of report results. ERCOT MAKES NO WARRANTY, EXPRESS OR IMPLIED, INCLUDING ANY WARRANTY OF MERCHANTABILITY OR FITNESS FOR ANY PARTICULAR PURPOSE, AND DISCLAIMS ANY AND ALL LIABILITY WITH RESPECT TO THE ACCURACY OF SAME OR THE FITNESS OR APPROPRIATENESS OF SAME FOR ANY PARTICULAR USE. THIS ERCOT REPORT IS SUPPLIED WITH ALL FAULTS. The specific suitability for any use of the CDR report and its accuracy should be confirmed by each ERCOT Market Participant that contributed data.

## Findings & Discussion
CDR - Findings & Discussion
Overview
| ● | This CDR reflects an early December 2025 snapshot of expected resources and loads based on prescriptive rules (ERCOT Protocols), load forecasting methodologies, and information from resource developers/owners and transmission companies. The CDR provides a deterministic view of future resource adequacy along with several alternative load and planned resource scenarios designed to capture a range of potential reserve margin outcomes. Since the CDR is based on forecasted information as of a certain point in time, state/federal policy and regulatory changes, economic developments, market design initiatives, evolving grid management practices, and technology improvements, can significantly alter the long-term resource adequacy outcome as reflected in this CDR.
| ● | The most impactful resource adequacy development since the May 2025 CDR release are provisions in Texas Senate Bill 6 (SB6), signed into law in June 2025, that establish new interconnection requirements for Large Loads and ERCOT authority to curtail Large Load consumption before and during declared grid emergencies. Although the CDR-related ERCOT Nodal Protocols—Specifically, Section 3.2.6.3, Firm Peak Load and Firm Peak Net Load Estimates—does not yet reflect rules for treatment of the SB6 Large Load provisions, this CDR nevertheless includes reserve margin scenarios reflecting assumptions for Large Load curtailment given future grid emergency conditions. These curtailment assumptions, starting for summer 2027, are necessarily preliminary and high-level given that new SB6-related rules depend on the outcome of several Commission rulemaking proceedings and ERCOT Protocol changes.
| ● | The base scenario in this CDR—using "Protocol Prescribed" capacity resources and the ERCOT Adjusted Load Forecast—indicates that summer and winter Planning Reserve Margins for 2026 through 2030 decrease significantly from year to year, and cross over to negative values in 2028 in line with the trends reported in the May 2025 CDR. The base scenario's summer 2026 Planning Reserve Margins are 18.3% for the peak Load hour (Hour Ending 5:00 p.m. Central Standard Time) and 20.9% for the peak Net Load hour (Hour Ending 9:00 p.m. CST).
| ● | This CDR includes three alternative Planning Reserve Margin scenarios in addition to the base scenario. In addition to capturing potential Large Load curtailment impacts resulting from Texas Senate Bill 6 provisions, two of the three scenarios define reserve margin bookends by varying the magnitude of Large Loads along with the amount and timing of Texas Energy Fund (TEF) project capacity reflected in the ERCOT interconnection queue. Scenario descriptions and results are available
here.
CDR Load Forecast
| ● | This CDR is based on the ERCOT Adjusted Forecast prepared in March-April 2025. The load forecast data and associated forecast methodology document are available here:
https://www.ercot.com/files/docs/2025/04/08/ErcotAdjustedForecast.xlsb
https://www.ercot.com/files/docs/2025/04/08/2025-LTLF-Report.pdf
| ● | The following table shows the cumulative amount of new planned loads, by type, included in the ERCOT Adjusted Forecast update for summer 2026-2030. The last column indicates the average annual growth rate.
New TSP-Reported Loads Added to the April 2025 ERCOT Adjusted Load Forecast Cumulative MW
|  |  | Large Load Type | Summer 2026 | Summer 2027 | Summer 2028 | Summer 2029 | Summer 2030 | Avg. Annual Growth Rate (%)
|  |  | Contracted Loads* | 4893.9254 | 8653.7616 | 15335.7588 | 17129.7096 | 19559.6158 | 41.39%
|  |  | TSP Officer Letter Loads** | 2733.4686 | 7420.3483 | 16792.3638 | 21232.6651 | 28223.0419 | 79.26%
|  |  | Total | 7627.394 | 16074.1099 | 32128.1226 | 38362.3747 | 47782.6577 | 58.21%
* Contracted Loads: All planned loads with signed interconnection agreements reported to ERCOT by the loads' Transmission Service Providers
** All planned loads documented in a TSP officer letter. (An officer letter is an attestation indicating confidence that loads are expected to be interconnected even though the interconnection agreement has not been signed yet.)
| ● | The following table shows the summer peak Load and peak Net Load forecasts for 2026-2030, along with the associated peak load hours:
[5 empty] | Load for the peak Load hour |  | Load for the peak Net Load hour (Load minus wind and solar generation)
|  |  |  | Year | Base Summer Forecast | Summer Peak Load Hour (Hour Ending) | Base Summer Forecast | Summer Peak Net Load Hour (Hour Ending)
|  |  |  | 2026 | 94159.0572 | 5:00 p.m. | 81411.4696 | 9:00 p.m.
|  |  |  | 2027 | 103724.645 | 5:00 p.m. | 91088.1988 | 9:00 p.m.
|  |  |  | 2028 | 120875.1453 | 5:00 p.m. | 108314.4289 | 9:00 p.m.
|  |  |  | 2029 | 127905.3033 | 5:00 p.m. | 115532.3506 | 9:00 p.m.
|  |  |  | 2030 | 138010.4599 | 5:00 p.m. | 126198.0097 | 9:00 p.m.
Planning Reserve Margins for the Peak Load and Peak Net Load Hours
| ● | The following charts show the summer and winter Planning Reserve Margin trends for the scenario based on the ERCOT Adjusted Load Forecast and Protocol-prescribed resource capacity. Trends are shown for the peak Load and peak Net Load hours. For the winter, both peak Load and peak Net Load Margins enter negative territory beginning winter 2028/29. The lower and sharply downward trajectory of the Margins is due to (1) high load growth largely driven by new Loads reported by Transmission Service Providers, (2) a lower capacity contribution from wind and solar resources due to the use of Effective Load Carrying Capabilities, (3) fewer planned resources that result from applying additional eligibility criteria to be included in Planning Reserve Margins.
| ● | The following waterfall chart shows the Reserve Margin capacity components for summer 2026 that contribute to the differences in Planning Reserve Margins reported in the May 2025 CDR compared to the December 2025 CDR. (Crimson bars signify components that reduce Reserve Margin capacity whereas green bars signify components that increase Reserve Margin capacity.)
Notes: ELCC stands for Effective Load Carrying Capability. Delays to planned projects by fuel type, after accounting for ELCC, were 139 MW Solar and 1,517 MW Storage. Miscellaneous resource changes include new CDR-eligible planned projects, new operational thermal units not listed in the May 2025 CDR (Life Cycle Power Units), new unavailable switchable generation unit, summer seasonal rating changes, PUN contribution updates, and planned project cancelations. Miscellaneous load changes cover updates to following Load Resource categories displayed in the Seasonal Summary tab: Load Resources, Controllable Load Resources not included in Load Resources, Emergency Responsive Service, and Distribution Voltage Reduction.
Planned Resource Trends
| ● | The table below shows the changes in resource capacity additions for summer 2026-2030 by resource category. Only those projects that have met the CDR eligibility criteria are included. Solar is expected to continue out-pacing the other resource types in terms of installed capacity growth, followed by Energy Storage Resources (battery energy storage).
Planned Generation Capacity Additions by Summer Season (Projects that met CDR Eligibility Criteria and based on Summer Seasonal Ratings)
|  |  |  | Summer 2026 | Summer 2027 | Summer 2028 | Summer 2029 | Summer 2030 | Trend
|  |  | Thermal (Natural Gas and Diesel) | 1118.8 | 1334.8 | 2008.8 | 3308.8 | 3308.8
|  |  | Battery Energy Storage | 5074.07 | 13236.49 | 19913.55 | 22912.5 | 22912.5
|  |  | Dispatchable Total | 6192.87 | 14571.29 | 21922.35 | 26221.3 | 26221.3
|  |  | Solar | 3958.8 | 14857.4 | 24869.4 | 28928.9 | 29441.4
|  |  | Wind | 148.4 | 1340.4 | 4553 | 4793 | 4793
|  |  | Non-Dispatchable Total | 4107.2 | 16197.8 | 29422.4 | 33721.9 | 34234.4
|  |  | Total | 10300.07 | 30769.09 | 51344.75 | 59943.2 | 60455.7

## Load-Resource Scenarios
Load-Resource Scenarios
(Scenario assumption details are provided below the Reserve Margin charts)
| Peak Load Hour: | Peak Load Hour: | Peak Load Hour: | Peak Load Hour: | Peak Load Hour: | Peak Net Load Hour: | Peak Net Load Hour: | Peak Net Load Hour: | Peak Net Load Hour: | Peak Net Load Hour:
| Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer | Summer
Table 1: Summer Load and Resource Scenarios | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Firm Peak Load -- ERCOT Adjusted, MW | 88639.0572 | 98134.645 | 115225.1453 | 122195.3033 | 132240.4599 | 75971.4696 | 85583.1988 | 102744.4289 | 109892.3506 | 120483.0097
Scenario 1: Base Case with Senate Bill 6 Large Load curtailment impact | 88639.0572 | 85444.4875 | 88149.9885 | 89298.0854 | 90955.4083 | 75971.4696 | 72893.0412 | 75669.2722 | 76995.1328 | 79197.9581
Scenario 2: Base Case with 25% decrease in Large Load + Senate Bill 6 Large Load curtailment impact | 88639.0572 | 84598.4994 | 86886.7471 | 87931.7962 | 89331.0068 | 75971.4696 | 72047.0531 | 74406.0307 | 75628.8436 | 77573.5565
Scenario 3: Base Case with TSP Provided Large Loads replacing ERCOT Adjusted Large Loads + Senate Bill 6 Large Load curtailment impact | 88639.0572 | 92580.7783 | 96279.2206 | 98960.8801 | 100347.7212 | 75971.4696 | 80029.3321 | 83798.5043 | 86657.9275 | 88590.271
Total Capacity -- Protocol Prescribed, MW | 104849.9853 | 109349.8485 | 113693.1969 | 115079.5937 | 115501.3246 | 91874.564 | 94582.065 | 96347.9852 | 97029.4109 | 97408.4109
Scenario 2: Includes all Texas Energy Fund projects (regardless of Planning Guide Sec. 6.9(1) milestone conditions) | 104849.9853 | 110678.3485 | 117298.0969 | 119124.4937 | 120622.5246 | 91874.564 | 95910.565 | 99952.8852 | 101074.3109 | 102529.6109
Scenario 3: One-year TEF project delays for those meeting Planning Guide Sec. 6.9(1) conditions (excluding "brownfield" sites) | 104013.9853 | 108806.0485 | 112597.1969 | 112683.5937 | 114405.3246 | 91038.564 | 94038.265 | 95251.9852 | 94633.4109 | 96312.4109
Reserve Margins (%)
Protocol-prescribed | 18.29% | 11.43% | -1.33% | -5.823% | -12.66% | 20.93% | 10.51% | -6.226% | -11.71% | -19.15%
Scenario 1: Base Case with SB6 Large Load curtailment impact | 18.29% | 27.98% | 28.98% | 28.87% | 26.99% | 20.93% | 29.75% | 27.33% | 26.02% | 22.99%
Scenario 2: High Reserve Margin Bookend with SB6 Large Load curtailment impact, lower Large Load growth, maximum TEF capacity | 18.29% | 30.83% | 35% | 35.47% | 35.03% | 20.93% | 33.12% | 34.33% | 33.65% | 32.17%
Scenario 3: Low Reserve Margin Bookend with SB6 Large Load curtailment impact, higher Large Load growth, TEF capacity delays | 17.35% | 17.53% | 16.95% | 13.87% | 14.01% | 19.83% | 17.5% | 13.67% | 9.203% | 8.717%
| Peak Load Hour: | Peak Load Hour: | Peak Load Hour: | Peak Load Hour: | Peak Load Hour: | Peak Net Load Hour: | Peak Net Load Hour: | Peak Net Load Hour: | Peak Net Load Hour: | Peak Net Load Hour:
| Winter | Winter | Winter | Winter | Winter | Winter | Winter | Winter | Winter | Winter
Table 2: Winter Load and Resource Scenarios | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031
Firm Peak Load -- ERCOT Adjusted, MW | 78123.5579 | 93575.1588 | 108443.2952 | 120024.7268 | 126838.966 | 73550.7342 | 89065.4059 | 103662.6622 | 114986.2895 | 121531.6218
Scenario 1: Base Case with Senate Bill 6 Large Load curtailment impact | 78123.5579 | 72587.6145 | 75546.0774 | 78739.6751 | 81419.6201 | 73550.7342 | 68077.8616 | 70765.4444 | 73701.2378 | 76112.2759
Scenario 2: Base Case with 25% decrease in Large Load + Senate Bill 6 Large Load curtailment impact | 78123.5579 | 71442.6494 | 74179.7882 | 77115.2736 | 79698.4911 | 73550.7342 | 66932.8964 | 69399.1552 | 72076.8363 | 74391.1469
Scenario 3: Base Case with TSP Provided Large Loads replacing ERCOT Adjusted Large Loads + Senate Bill 6 Large Load curtailment impact | 78123.5579 | 80072.3595 | 82021.4603 | 86682.0312 | 89915.8807 | 73550.7342 | 75562.6065 | 77240.8273 | 81643.5939 | 84608.5365
Total Capacity -- Protocol Prescribed, MW | 95388.422 | 97611.465 | 99491.5287 | 99292.4148 | 99707.4148 | 94656.7064 | 96825.468 | 98648.8855 | 98473.0339 | 98888.0339
Scenario 2: Includes all Texas Energy Fund projects (regardless of Planning Guide Sec. 6.9(1) milestone conditions) | 95388.422 | 99463.365 | 103549.4287 | 103350.3148 | 105392.6148 | 94656.7064 | 98677.368 | 102706.7855 | 102530.9339 | 104573.2339
Scenario 3: One-year TEF project delays for those meeting Planning Guide Sec. 6.9(1) conditions (excluding "brownfield" sites) | 94494.422 | 97033.665 | 96988.5287 | 98139.4148 | 98554.4148 | 93762.7064 | 96247.668 | 96145.8855 | 97320.0339 | 97735.0339
Reserve Margins (%)
Protocol-prescribed | 22.1% | 4.313% | -8.255% | -17.27% | -21.39% | 28.7% | 8.713% | -4.837% | -14.36% | -18.63%
Scenario 1: Base Case with Senate Bill 6 Large Load curtailment impact | 22.1% | 34.47% | 31.7% | 26.1% | 22.46% | 28.7% | 42.23% | 39.4% | 33.61% | 29.92%
Scenario 2: High Reserve Margin Bookend with SB6 Large Load curtailment impact, lower Large Load growth, maximum TEF capacity | 22.1% | 39.22% | 39.59% | 34.02% | 32.24% | 28.7% | 47.43% | 47.99% | 42.25% | 40.57%
Scenario 3: Low Reserve Margin Bookend with SB6 Large Load curtailment impact, higher Large Load growth, TEF capacity delays | 20.96% | 21.18% | 18.25% | 13.22% | 9.607% | 27.48% | 27.37% | 24.48% | 19.2% | 15.51%
Scenario Assumption Notes
For the Texas Senate Bill 6 (SB6) Large Load curtailment assumptions, the following percentage load reductions were applied to the peak/net-peak load hour forecasts by individual Large Load category starting in summer 2027:
● Data Centers - 100% curtailable to reflect ERCOT authority to mandate curtailment during energy emergency events
● Industrial - 85% curtailable
● Hydrogen - 85% curtailable
● Crypto currency mining - price-responsive, 85% curtailable
● Oil & Gas - non-curtailable to reflect designation as "critical natural gas facility" customers by the Railroad Commission of Texas under Tex. Admin. Code § 3.65, Critical Designation of Natural Gas Infrastructure.
For the Scenario 2 resource capacity assumption, all TEF projects are assumed to be in-service as of their current reported projected Commercial Operations Dates regardless of whether all criteria for CDR planned resource eligibility are met. These criteria include a signed interconnection agreement, a written notice to the TSP to proceed with interconnection construction, sufficient financial security to fund the interconnection facilities, proof of adequate water supplies for electricity generation, and possession of necessary Texas/Federal air emission permits.
For the Scenario 3 load assumption concerning replacing ERCOT-Adjusted loads with TSP-Provided Large Loads, the increases in the load type forecasts are in proportion to the total incremental load increase. Alternately, assuming that the load type increases are in line with the TSP forecasts results in a less extreme low bookend scenario. For example, the summer "peak load" reserve margin increases an average of 3.6 percentage points for 2027-2030, while the summer "peak net load" reserve margin increases an average of 4.0 percentage points.
For the Scenario 3 resource capacity assumption, brownfield sites refer to TEF projects being developed at existing power plant sites and are therefore expected to be less likely to experience construction delays than projects at new construction sites.

## Seasonal Summary
Seasonal Summary
|  | Summer | Summer |  | Summer | Summer |  | Summer | Summer |  | Summer | Summer |  | Summer | Summer |  | Winter | Winter |  | Winter | Winter |  | Winter | Winter |  | Winter | Winter |  | Winter | Winter |  | Spring | Spring |  | Spring | Spring |  | Spring | Spring |  | Spring | Spring |  | Spring | Spring |  | Fall | Fall |  | Fall | Fall |  | Fall | Fall |  | Fall | Fall |  | Fall | Fall
|  | 2026 | 2026 |  | 2027 | 2027 |  | 2028 | 2028 |  | 2029 | 2029 |  | 2030 | 2030 |  | 2026/2027 | 2026/2027 |  | 2027/2028 | 2027/2028 |  | 2028/2029 | 2028/2029 |  | 2029/2030 | 2029/2030 |  | 2030/2031 | 2030/2031 |  | 2026 | 2026 |  | 2027 | 2027 |  | 2028 | 2028 |  | 2029 | 2029 |  | 2030 | 2030 |  | 2026 | 2026 |  | 2027 | 2027 |  | 2028 | 2028 |  | 2029 | 2029 |  | 2030 | 2030
|  | Peak Load Hour: | Peak Net Load Hour: | Difference [1] less [2] | Peak Load Hour: | Peak Net Load Hour: | Difference [4] less [5] | Peak Load Hour: | Peak Net Load Hour: | Difference [7] less [8] | Peak Load Hour: | Peak Net Load Hour: | Difference [10] less [11] | Peak Load Hour: | Peak Net Load Hour: | Difference [13] less [14] | Peak Load Hour: | Peak Net Load Hour: | Difference [16] less [17] | Peak Load Hour: | Peak Net Load Hour: | Difference [19] less [20] | Peak Load Hour: | Peak Net Load Hour: | Difference [22] less [23] | Peak Load Hour: | Peak Net Load Hour: | Difference [25] less [26] | Peak Load Hour: | Peak Net Load Hour: | Difference [28] less [29] | Peak Load Hour: | Peak Net Load Hour: | Difference [31] less [32] | Peak Load Hour: | Peak Net Load Hour: | Difference [34] less [35] | Peak Load Hour: | Peak Net Load Hour: | Difference [37] less [38] | Peak Load Hour: | Peak Net Load Hour: | Difference [40] less [41] | Peak Load Hour: | Peak Net Load Hour: | Difference [43] less [44] | Peak Load Hour: | Peak Net Load Hour: | Difference [46] less [47] | Peak Load Hour: | Peak Net Load Hour: | Difference [49] less [50] | Peak Load Hour: | Peak Net Load Hour: | Difference [52] less [53] | Peak Load Hour: | Peak Net Load Hour: | Difference [55] less [56] | Peak Load Hour: | Peak Net Load Hour: | Difference [58] less [59]
|  | 17 | 21 |  | 17 | 21 |  | 17 | 21 |  | 17 | 21 |  | 17 | 21 |  | 8 | 19 |  | 8 | 19 |  | 8 | 19 |  | 8 | 19 |  | 8 | 19 |  | 17 | 21 |  | 17 | 21 |  | 17 | 21 |  | 17 | 21 |  | 17 | 21 |  | 17 | 20 |  | 17 | 20 |  | 17 | 20 |  | 17 | 20 |  | 17 | 20
|  | [1] | [2] | [3] | [4] | [5] | [6] | [7] | [8] | [9] | [10] | [11] | [12] | [13] | [14] | [15] | [16] | [17] | [18] | [19] | [20] | [21] | [22] | [23] | [24] | [25] | [26] | [27] | [28] | [29] | [30] | [31] | [32] | [33] | [34] | [35] | [36] | [37] | [38] | [39] | [40] | [41] | [42] | [43] | [44] | [45] | [46] | [47] | [48] | [49] | [50] | [51] | [52] | [53] | [54] | [55] | [56] | [57] | [58] | [59] | [60]
Load Forecast and Adjustments, MW:
| Total Seasonal Load based on normal weather conditions* | 95419.4269 | 81472.4019 | 13947.025 | 105405.6678 | 91169.6665 | 14236.0013 | 123088.8561 | 108421.9199 | 14666.9362 | 130782.9635 | 115672.2792 | 15110.6843 | 141703.7055 | 126377.7875 | 15325.918 | 84057.2984 | 79506.1644 | 4551.134 | 99590.8913 | 95088.4066 | 4502.4847 | 114534.0674 | 109753.8203 | 4780.2471 | 126193.9904 | 121151.2639 | 5042.7265 | 133090.6559 | 127776.1584 | 5314.4976 | 81930.2985 | 65991.5714 | 15938.727 | 91202.2555 | 75262.1925 | 15940.0631 | 106682.1449 | 90621.0277 | 16061.1173 | 121491.8082 | 105401.073 | 16090.7352 | 132890.8579 | 116594.0295 | 16296.8284 | 82174.1349 | 75942.6884 | 6231.4465 | 92579.8652 | 86301.1057 | 6278.7595 | 110676.3001 | 104169.5459 | 6506.7542 | 118917.9865 | 112421.9935 | 6495.993 | 130311.7078 | 123813.9721 | 6497.7357
| less: Incremental Rooftop PV Forecast | -1260.3697 | -60.9324 | -1199.4374 | -1681.0228 | -81.4678 | -1599.5551 | -2213.7108 | -107.491 | -2106.2198 | -2877.6602 | -139.9286 | -2737.7316 | -3693.2456 | -179.7778 | -3513.4678 | -36.9405 | -9.6303 | -27.3102 | -48.9325 | -12.2007 | -36.7317 | -63.9722 | -15.3581 | -48.6141 | -82.4636 | -19.1744 | -63.2892 | -104.89 | -23.7366 | -81.1534 | -1104.2645 | -94.7442 | -1009.5203 | -1475.285 | -126.7623 | -1348.5227 | -1945.9217 | -167.3838 | -1778.5378 | -2533.5505 | -218.0977 | -2315.4528 | -3257.0364 | -280.5279 | -2976.5084 | -1203.3474 | -129.0068 | -1074.3406 | -1602.0825 | -171.1009 | -1430.9816 | -2106.1786 | -224.1615 | -1882.017 | -2732.6311 | -289.9277 | -2442.7034 | -3500.2423 | -370.3185 | -3129.9238
| less: Load Resources providing Responsive Reserves | -935 | -935 | 0 | -935 | -935 | 0 | -935 | -935 | 0 | -935 | -935 | 0 | -935 | -935 | 0 | -1498 | -1402 | -96 | -1498 | -1402 | -96 | -1498 | -1402 | -96 | -1498 | -1402 | -96 | -1498 | -1402 | -96 | -1617 | -1576 | -41 | -1617 | -1576 | -41 | -1617 | -1576 | -41 | -1617 | -1576 | -41 | -1617 | -1576 | -41 | -1280 | -1230 | -50 | -1280 | -1230 | -50 | -1280 | -1230 | -50 | -1280 | -1230 | -50 | -1280 | -1230 | -50
| less: Load Resources providing Non-Spinning Reserves | -50 | -70 | 20 | -70 | -80 | 10 | -80 | -90 | 10 | -90 | -100 | 10 | -100 | -110 | 10 | -50 | -70 | 20 | -70 | -80 | 10 | -80 | -90 | 10 | -90 | -100 | 10 | -100 | -110 | 10 | -50 | -70 | 20 | -70 | -80 | 10 | -80 | -90 | 10 | -90 | -100 | 10 | -100 | -110 | 10 | -50 | -70 | 20 | -70 | -80 | 10 | -80 | -90 | 10 | -90 | -100 | 10 | -100 | -110 | 10
| less: Load Resources providing ERCOT Contingency Reserve Service (ECRS) | -300 | -350 | 50 | -330 | -385 | 55 | -360 | -420 | 60 | -390 | -460 | 70 | -420 | -505 | 85 | -300 | -350 | 50 | -330 | -385 | 55 | -360 | -420 | 60 | -390 | -460 | 70 | -420 | -505 | 85 | -300 | -350 | 50 | -330 | -385 | 55 | -360 | -420 | 60 | -390 | -460 | 70 | -420 | -505 | 85 | -300 | -350 | 50 | -330 | -385 | 55 | -360 | -420 | 60 | -390 | -460 | 70 | -420 | -505 | 85
| less: Controllable Load Resources not included in other adjustments | -20 | -20 | 0 | -40 | -40 | 0 | -60 | -60 | 0 | -80 | -80 | 0 | -100 | -100 | 0 | -20 | -20 | 0 | -40 | -40 | 0 | -60 | -60 | 0 | -80 | -80 | 0 | -100 | -100 | 0 | -20 | -20 | 0 | -40 | -40 | 0 | -60 | -60 | 0 | -80 | -80 | 0 | -100 | -100 | 0 | -20 | -20 | 0 | -40 | -40 | 0 | -60 | -60 | 0 | -80 | -80 | 0 | -100 | -100 | 0
| less: Emergency Response Service (10- and 30-min ramp products) | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2675 | -2750 | 75 | -2675 | -2750 | 75 | -2675 | -2750 | 75 | -2675 | -2750 | 75 | -2675 | -2750 | 75 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150 | -2750 | -2600 | -150
| less: TDSP Standard Offer Load Management Programs | -303 | -303 | 0 | -303 | -303 | 0 | -303 | -303 | 0 | -303 | -303 | 0 | -303 | -303 | 0 | -74.8 | -74.8 | 0 | -74.8 | -74.8 | 0 | -74.8 | -74.8 | 0 | -74.8 | -74.8 | 0 | -74.8 | -74.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| less: Distribution Voltage Reduction | -1162 | -1162 | 0 | -1162 | -1162 | 0 | -1162 | -1162 | 0 | -1162 | -1162 | 0 | -1162 | -1162 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1279 | -1279 | 0 | -1162 | -1162 | 0 | -1162 | -1162 | 0 | -1162 | -1162 | 0 | -1162 | -1162 | 0 | -1162 | -1162 | 0
| Firm Peak Load, MW | 88639.0572 | 75971.4696 | 12667.5876 | 98134.645 | 85583.1988 | 12551.4462 | 115225.1453 | 102744.4289 | 12480.7163 | 122195.3033 | 109892.3506 | 12302.9527 | 132240.4599 | 120483.0097 | 11757.4502 | 78123.5579 | 73550.7342 | 4572.8237 | 93575.1588 | 89065.4059 | 4509.7529 | 108443.2952 | 103662.6622 | 4780.633 | 120024.7268 | 114986.2895 | 5038.4373 | 126838.966 | 121531.6218 | 5307.3442 | 74810.0339 | 60001.8272 | 14808.2067 | 83640.9705 | 69175.4302 | 14465.5404 | 98590.2233 | 84428.6438 | 14161.5794 | 112752.2577 | 99087.9752 | 13664.2825 | 123367.8215 | 110143.5016 | 13224.3199 | 75408.7875 | 70381.6816 | 5027.1059 | 85345.7826 | 80633.0048 | 4712.7779 | 102878.1215 | 98383.3844 | 4494.7371 | 110433.3554 | 106500.0658 | 3933.2896 | 120999.4655 | 117736.6536 | 3262.8119
| Energy Efficiency Program Savings Forecast, included in the Base Load Forecast | 4048.5769 | 4048.5769 |  | 4426.829 | 4426.829 |  | 4805.9274 | 4805.9274 |  | 5185.4543 | 5185.4543 |  | 5566.1918 | 5566.1918 |  | 4048.5769 | 4048.5769 |  | 4426.829 | 4426.829 |  | 4805.9274 | 4805.9274 |  | 5185.4543 | 5185.4543 |  | 5566.1918 | 5566.1918 |  | 4048.5769 | 4048.5769 |  | 4426.829 | 4426.829 |  | 4805.9274 | 4805.9274 |  | 5185.4543 | 5185.4543 |  | 5566.1918 | 5566.1918 |  | 4048.5769 | 4048.5769 |  | 4426.829 | 4426.829 |  | 4805.9274 | 4805.9274 |  | 5185.4543 | 5185.4543 |  | 5566.1918 | 5566.1918
Expected Resource Capacity Available by Period, MW:
Operational Generation Capacity
| Installed Seasonal-rated Thermal Capacity (Nuclear, Fossil, and Biomass-Fueled), excluding Switchable Units | 65430.5 | 65430.5 | 0 | 66363.1 | 66363.1 | 0 | 66363.1 | 66363.1 | 0 | 66363.1 | 66363.1 | 0 | 66433.1 | 66433.1 | 0 | 68964.8 | 68964.8 | 0 | 69897.4 | 69897.4 | 0 | 69897.4 | 69897.4 | 0 | 69897.4 | 69897.4 | 0 | 69972.4 | 69972.4 | 0 | 66675.1 | 66675.1 | 0 | 66675.1 | 66675.1 | 0 | 67607.7 | 67607.7 | 0 | 67607.7 | 67607.7 | 0 | 67607.7 | 67607.7 | 0 | 66712.5 | 66712.5 | 0 | 67645.1 | 67645.1 | 0 | 67645.1 | 67645.1 | 0 | 67645.1 | 67645.1 | 0 | 67720.1 | 67720.1 | 0
| Hydroelectric, Peak Average Capacity Contribution | 533.737 | 530.284 | 3.453 | 533.737 | 530.284 | 3.453 | 533.737 | 530.284 | 3.453 | 533.737 | 530.284 | 3.453 | 533.737 | 530.284 | 3.453 | 516.4466 | 517.8453 | -1.3987 | 516.4466 | 517.8453 | -1.3987 | 516.4466 | 517.8453 | -1.3987 | 516.4466 | 517.8453 | -1.3987 | 516.4466 | 517.8453 | -1.3987 | 489.4918 | 489.5935 | -0.10167 | 489.4918 | 489.5935 | -0.10167 | 489.4918 | 489.5935 | -0.10167 | 489.4918 | 489.5935 | -0.10167 | 489.4918 | 489.5935 | -0.10167 | 470.3158 | 466.1848 | 4.131 | 470.3158 | 466.1848 | 4.131 | 470.3158 | 466.1848 | 4.131 | 470.3158 | 466.1848 | 4.131 | 470.3158 | 466.1848 | 4.131
| Switchable Capacity | 3678 | 3678 | 0 | 3678 | 3678 | 0 | 3678 | 3678 | 0 | 3678 | 3678 | 0 | 3678 | 3678 | 0 | 4016 | 4016 | 0 | 4016 | 4016 | 0 | 4016 | 4016 | 0 | 4016 | 4016 | 0 | 4016 | 4016 | 0 | 3886 | 3886 | 0 | 3886 | 3886 | 0 | 3886 | 3886 | 0 | 3886 | 3886 | 0 | 3886 | 3886 | 0 | 3834 | 3834 | 0 | 3834 | 3834 | 0 | 3834 | 3834 | 0 | 3834 | 3834 | 0 | 3834 | 3834 | 0
| less: Switchable Capacity Unavailable to ERCOT | -2184 | -2184 | 0 | -2340 | -2340 | 0 | -2189 | -2189 | 0 | -2189 | -2189 | 0 | -1880 | -1880 | 0 | -1387 | -1387 | 0 | -1549 | -1549 | 0 | -2064 | -2064 | 0 | -2120 | -2120 | 0 | -1780 | -1780 | 0 | -628 | -628 | 0 | -1351 | -1351 | 0 | -1513 | -1513 | 0 | -1674 | -1674 | 0 | -1730 | -1730 | 0 | -1080 | -1080 | 0 | -1064 | -1064 | 0 | -1214 | -1214 | 0 | -1214 | -1214 | 0 | -1231 | -1231 | 0
| Available Mothballed Capacity (Units with reported return probabilities ≥ 75%) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity from Private Use Networks | 3431 | 3539 | -108 | 3431 | 3539 | -108 | 3431 | 3539 | -108 | 3681 | 3789 | -108 | 3681 | 3789 | -108 | 4150 | 4014 | 136 | 4150 | 4014 | 136 | 4150 | 4014 | 136 | 4400 | 4264 | 136 | 4400 | 4264 | 136 | 2947 | 2880 | 67 | 2837 | 2770 | 67 | 2837 | 2770 | 67 | 2837 | 2770 | 67 | 3087 | 3020 | 67 | 2968 | 2849 | 119 | 2968 | 2849 | 119 | 2968 | 2849 | 119 | 3218 | 3099 | 119 | 3218 | 3099 | 119
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
| Coastal Wind | 1828.5163 | 987.7138 | 840.8025 | 1855.8413 | 1007.0913 | 848.75 | 1893.2047 | 941.4231 | 951.7816 | 1903.6024 | 917.7395 | 985.8629 | 1903.6024 | 917.7395 | 985.8629 | 1717.341 | 1717.341 | 0 | 1716.2467 | 1716.2467 | 0 | 1723.8037 | 1723.8037 | 0 | 1723.8037 | 1723.8037 | 0 | 1723.8037 | 1723.8037 | 0 | 1717.341 | 1717.341 | 0 | 1716.2467 | 1716.2467 | 0 | 1723.8037 | 1723.8037 | 0 | 1723.8037 | 1723.8037 | 0 | 1723.8037 | 1723.8037 | 0 | 1838.0127 | 1838.0127 | 0 | 1898.9777 | 1898.9777 | 0 | 1905.1664 | 1905.1664 | 0 | 1905.1664 | 1905.1664 | 0 | 1905.1664 | 1905.1664 | 0
| Panhandle Wind | 1640.5104 | 886.1582 | 754.3522 | 1665.0258 | 903.5433 | 761.4825 | 1698.5476 | 844.6271 | 853.9205 | 1707.8762 | 823.3786 | 884.4976 | 1707.8762 | 823.3786 | 884.4976 | 1540.766 | 1540.766 | 0 | 1539.7841 | 1539.7841 | 0 | 1546.5641 | 1546.5641 | 0 | 1546.5641 | 1546.5641 | 0 | 1546.5641 | 1546.5641 | 0 | 1540.766 | 1540.766 | 0 | 1539.7841 | 1539.7841 | 0 | 1546.5641 | 1546.5641 | 0 | 1546.5641 | 1546.5641 | 0 | 1546.5641 | 1546.5641 | 0 | 1649.0304 | 1649.0304 | 0 | 1703.727 | 1703.727 | 0 | 1709.2793 | 1709.2793 | 0 | 1709.2793 | 1709.2793 | 0 | 1709.2793 | 1709.2793 | 0
| Other Wind | 4715.5801 | 2547.2256 | 2168.3545 | 4786.0489 | 2597.1984 | 2188.8505 | 4882.4058 | 2427.8461 | 2454.5597 | 4909.2204 | 2366.7682 | 2542.4522 | 4909.2204 | 2366.7682 | 2542.4522 | 4434.2469 | 4434.2469 | 0 | 4431.4212 | 4431.4212 | 0 | 4450.9337 | 4450.9337 | 0 | 4450.9337 | 4450.9337 | 0 | 4450.9337 | 4450.9337 | 0 | 4434.2469 | 4434.2469 | 0 | 4431.4212 | 4431.4212 | 0 | 4450.9337 | 4450.9337 | 0 | 4450.9337 | 4450.9337 | 0 | 4450.9337 | 4450.9337 | 0 | 4745.8264 | 4745.8264 | 0 | 4903.2406 | 4903.2406 | 0 | 4919.2199 | 4919.2199 | 0 | 4919.2199 | 4919.2199 | 0 | 4919.2199 | 4919.2199 | 0
| Far West Solar Utility-Scale | 1838.5473 | 296.7332 | 1541.8141 | 1549.913 | 126.2346 | 1423.6784 | 1379.0634 | 0 | 1379.0634 | 1340.0837 | 0 | 1340.0837 | 1334.8838 | 0 | 1334.8838 | 118.5445 | 118.5445 | 0 | 97.3676 | 97.3676 | 0 | 90.5647 | 90.5647 | 0 | 88.6432 | 88.6432 | 0 | 88.6432 | 88.6432 | 0 | 118.5922 | 118.5922 | 0 | 97.4068 | 97.4068 | 0 | 90.6011 | 90.6011 | 0 | 88.6789 | 88.6789 | 0 | 88.6789 | 88.6789 | 0 | 1744.9259 | 1744.9259 | 0 | 1426.4295 | 1426.4295 | 0 | 1342.5387 | 1342.5387 | 0 | 1316.5105 | 1316.5105 | 0 | 1316.5105 | 1316.5105 | 0
| West Solar Utility-Scale | 1971.475 | 318.1871 | 1653.2879 | 1661.9723 | 135.3614 | 1526.6109 | 1478.7702 | 0 | 1478.7702 | 1436.9723 | 0 | 1436.9723 | 1431.3964 | 0 | 1431.3964 | 127.1153 | 127.1153 | 0 | 104.4073 | 104.4073 | 0 | 97.1125 | 97.1125 | 0 | 95.0522 | 95.0522 | 0 | 95.0522 | 95.0522 | 0 | 127.1153 | 127.1153 | 0 | 104.4073 | 104.4073 | 0 | 97.1125 | 97.1125 | 0 | 95.0522 | 95.0522 | 0 | 95.0522 | 95.0522 | 0 | 1871.0847 | 1871.0847 | 0 | 1529.5609 | 1529.5609 | 0 | 1439.6048 | 1439.6048 | 0 | 1411.6947 | 1411.6947 | 0 | 1411.6947 | 1411.6947 | 0
| Other Solar Utility-Scale | 6121.7679 | 988.0256 | 5133.7423 | 5160.7088 | 420.3203 | 4740.3885 | 4591.835 | 0 | 4591.835 | 4462.0452 | 0 | 4462.0452 | 4444.7312 | 0 | 4444.7312 | 394.2084 | 394.2084 | 0 | 323.7868 | 323.7868 | 0 | 301.1642 | 301.1642 | 0 | 294.7746 | 294.7746 | 0 | 294.7746 | 294.7746 | 0 | 394.7147 | 394.7147 | 0 | 324.2026 | 324.2026 | 0 | 301.551 | 301.551 | 0 | 295.1532 | 295.1532 | 0 | 295.1532 | 295.1532 | 0 | 5806.625 | 5806.625 | 0 | 4746.758 | 4746.758 | 0 | 4467.5932 | 4467.5932 | 0 | 4380.9784 | 4380.9784 | 0 | 4380.9784 | 4380.9784 | 0
| Energy Storage | 9262.486 | 9262.486 | 0 | 8312.4907 | 8312.4907 | 0 | 7589.9929 | 7589.9929 | 0 | 7076.4671 | 7076.4671 | 0 | 7076.4671 | 7076.4671 | 0 | 5303.4437 | 4922.4096 | 381.0342 | 4713.2353 | 4405.8633 | 307.372 | 4347.7615 | 4053.9076 | 293.8538 | 4220.0289 | 3944.422 | 275.6069 | 4220.0289 | 3944.422 | 275.6069 | 4721.8493 | 4721.8493 | 0 | 4246.1482 | 4246.1482 | 0 | 4025.5525 | 4025.5525 | 0 | 3944.4955 | 3944.4955 | 0 | 3944.4016 | 3944.4016 | 0 | 8957.6316 | 8957.6316 | 0 | 8067.6645 | 8067.6645 | 0 | 7322.9867 | 7322.9867 | 0 | 7075.6914 | 7075.6914 | 0 | 7075.6914 | 7075.6914 | 0
| RMR Capacity to be under Contract | 412 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 412 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Capacity Pending Retirement | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational Generation Capacity, Total | 98680.1201 | 86692.3137 | 11987.8064 | 96657.8379 | 85272.6241 | 11385.2138 | 95330.6566 | 83725.2733 | 11605.3833 | 94903.1042 | 83355.7375 | 11547.3667 | 95254.0144 | 83734.7375 | 11519.2769 | 90307.9123 | 89792.2768 | 515.6355 | 89957.0956 | 89515.1224 | 441.9733 | 89073.7509 | 88645.2958 | 428.4551 | 89129.647 | 88719.4388 | 410.2082 | 89544.647 | 89134.4388 | 410.2082 | 86836.2171 | 86769.3188 | 66.8983 | 84996.2088 | 84929.3105 | 66.8983 | 85543.3104 | 85476.4121 | 66.8983 | 85290.8732 | 85223.9748 | 66.8983 | 85484.7792 | 85417.8809 | 66.8983 | 99929.9525 | 99806.8214 | 123.131 | 98129.7739 | 98006.6429 | 123.131 | 96809.805 | 96686.674 | 123.131 | 96671.9565 | 96548.8254 | 123.131 | 96729.9565 | 96606.8254 | 123.131
Non-Synchronous Ties (Based on average net import contribution during the EEA events: summer 2023 and winter 2020/2021 EEA events) |  | 817.4 | 817.4 | 0 | 817.4 | 817.4 | 0 | 817.4 | 817.4 | 0 | 817.4 | 817.4 | 0 | 817.4 | 817.4 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0 | 719.8 | 719.8 | 0
Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements
| Thermal Resources (Nuclear, Fossil, and Biomass-Fueled) | 1118.8 | 1118.8 | 0 | 1334.8 | 1334.8 | 0 | 2008.8 | 2008.8 | 0 | 3308.8 | 3308.8 | 0 | 3308.8 | 3308.8 | 0 | 1183 | 1183 | 0 | 1304.8 | 1304.8 | 0 | 3351.8 | 3351.8 | 0 | 3351.8 | 3351.8 | 0 | 3351.8 | 3351.8 | 0 | 49.8 | 49.8 | 0 | 1183 | 1183 | 0 | 2001.8 | 2001.8 | 0 | 3351.8 | 3351.8 | 0 | 3351.8 | 3351.8 | 0 | 1183 | 1183 | 0 | 1304.8 | 1304.8 | 0 | 2001.8 | 2001.8 | 0 | 3351.8 | 3351.8 | 0 | 3351.8 | 3351.8 | 0
Inverter-Based Resources, Capacity Contribution based on Effective Load Carrying Capabilities (ELCCs)
| Coastal Wind | 0 | 0 | 0 | 63.1637 | 34.2764 | 28.8873 | 110.1376 | 54.7675 | 55.3701 | 110.7425 | 53.3897 | 57.3528 | 110.7425 | 53.3897 | 57.3528 | 0 | 0 | 0 | 58.4126 | 58.4126 | 0 | 100.2827 | 100.2827 | 0 | 100.2827 | 100.2827 | 0 | 100.2827 | 100.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58.6698 | 58.6698 | 0 | 100.2827 | 100.2827 | 0 | 100.2827 | 100.2827 | 0 | 0 | 0 | 0 | 64.6319 | 64.6319 | 0 | 110.8335 | 110.8335 | 0 | 110.8335 | 110.8335 | 0 | 110.8335 | 110.8335 | 0
| Panhandle Wind | 0 | 0 | 0 | 89.3677 | 48.4963 | 40.8714 | 91.167 | 45.3341 | 45.8329 | 91.6677 | 44.1936 | 47.4741 | 91.6677 | 44.1936 | 47.4741 | 0 | 0 | 0 | 82.6456 | 82.6456 | 0 | 83.0095 | 83.0095 | 0 | 83.0095 | 83.0095 | 0 | 83.0095 | 83.0095 | 0 | 0 | 0 | 0 | 82.6456 | 82.6456 | 0 | 83.0095 | 83.0095 | 0 | 83.0095 | 83.0095 | 0 | 83.0095 | 83.0095 | 0 | 0 | 0 | 0 | 91.445 | 91.445 | 0 | 91.743 | 91.743 | 0 | 91.743 | 91.743 | 0 | 91.743 | 91.743 | 0
| Other Wind | 23.5389 | 12.7151 | 10.8238 | 141.9433 | 77.027 | 64.9163 | 649.1656 | 322.8069 | 326.3587 | 692.3624 | 333.7926 | 358.5698 | 692.3624 | 333.7926 | 358.5698 | 22.1077 | 22.1077 | 0 | 320.5658 | 320.5658 | 0 | 626.9675 | 626.9675 | 0 | 626.9675 | 626.9675 | 0 | 626.9675 | 626.9675 | 0 | 0 | 0 | 0 | 92.2602 | 92.2602 | 0 | 591.0792 | 591.0792 | 0 | 626.9675 | 626.9675 | 0 | 626.9675 | 626.9675 | 0 | 23.6611 | 23.6611 | 0 | 257.226 | 257.226 | 0 | 692.9312 | 692.9312 | 0 | 692.9312 | 692.9312 | 0 | 692.9312 | 692.9312 | 0
| Far West Solar Utility-Scale | 112.8758 | 18.2177 | 94.6582 | 252.6511 | 20.5775 | 232.0736 | 224.8009 | 0 | 224.8009 | 355.0374 | 0 | 355.0374 | 353.6598 | 0 | 353.6598 | 12.7814 | 12.7814 | 0 | 15.8719 | 15.8719 | 0 | 23.9939 | 23.9939 | 0 | 23.4848 | 23.4848 | 0 | 23.4848 | 23.4848 | 0 | 0 | 0 | 0 | 10.4981 | 10.4981 | 0 | 14.7629 | 14.7629 | 0 | 23.4848 | 23.4848 | 0 | 23.4848 | 23.4848 | 0 | 124.2749 | 124.2749 | 0 | 232.5221 | 232.5221 | 0 | 355.6879 | 355.6879 | 0 | 348.792 | 348.792 | 0 | 348.792 | 348.792 | 0
| West Solar Utility-Scale | 542.7124 | 87.5913 | 455.1211 | 1217.3937 | 99.1521 | 1118.2416 | 2151.0784 | 0 | 2151.0784 | 2470.8919 | 0 | 2470.8919 | 2461.3042 | 0 | 2461.3042 | 67.7986 | 67.7986 | 0 | 119.9531 | 119.9531 | 0 | 156.9034 | 156.9034 | 0 | 163.4434 | 163.4434 | 0 | 163.4434 | 163.4434 | 0 | 13.0656 | 13.0656 | 0 | 55.687 | 55.687 | 0 | 128.7895 | 128.7895 | 0 | 160.1602 | 160.1602 | 0 | 163.4434 | 163.4434 | 0 | 734.8249 | 734.8249 | 0 | 1757.3062 | 1757.3062 | 0 | 2325.9502 | 2325.9502 | 0 | 2427.4268 | 2427.4268 | 0 | 2427.4268 | 2427.4268 | 0
| Other Solar Utility-Scale | 509.1932 | 82.1815 | 427.0117 | 2065.8338 | 168.2544 | 1897.5794 | 2936.3872 | 0 | 2936.3872 | 3213.4901 | 0 | 3213.4901 | 3295.2761 | 0 | 3295.2761 | 67.5001 | 67.5001 | 0 | 177.0682 | 177.0682 | 0 | 206.8356 | 206.8356 | 0 | 218.8234 | 218.8234 | 0 | 218.8234 | 218.8234 | 0 | 9.3666 | 9.3666 | 0 | 85.334 | 85.334 | 0 | 185.5553 | 185.5553 | 0 | 212.5644 | 212.5644 | 0 | 218.8234 | 218.8234 | 0 | 860.5577 | 860.5577 | 0 | 2483.0009 | 2483.0009 | 0 | 3066.1502 | 3066.1502 | 0 | 3249.92 | 3249.92 | 0 | 3249.92 | 3249.92 | 0
| Energy Storage | 3045.3448 | 3045.3448 | 0 | 7129.4572 | 7129.4572 | 0 | 9793.6035 | 9793.6035 | 0 | 10506.0975 | 10506.0975 | 0 | 10506.0975 | 10506.0975 | 0 | 3007.5219 | 2791.4418 | 216.0801 | 5275.2522 | 4931.2285 | 344.0237 | 6128.1852 | 5713.9971 | 414.188 | 6265.1564 | 5855.9838 | 409.1726 | 6265.1564 | 5855.9838 | 409.1726 | 597.7028 | 597.7028 | 0 | 2792.1525 | 2792.1525 | 0 | 4811.7704 | 4811.7704 | 0 | 5770.586 | 5770.586 | 0 | 5855.9914 | 5855.9914 | 0 | 4699.3518 | 4699.3518 | 0 | 8592.0245 | 8592.0245 | 0 | 10295.1648 | 10295.1648 | 0 | 10506.784 | 10506.784 | 0 | 10506.784 | 10506.784 | 0
| Unconfirmed Planned Retirements | 0 | 0 | 0 | -420 | -420 | 0 | -420 | -420 | 0 | -1390 | -1390 | 0 | -1390 | -1390 | 0 | 0 | 0 | 0 | -420 | -420 | 0 | -980 | -980 | 0 | -1390 | -1390 | 0 | -1390 | -1390 | 0 | 0 | 0 | 0 | -420 | -420 | 0 | -420 | -420 | 0 | -1390 | -1390 | 0 | -1390 | -1390 | 0 | 0 | 0 | 0 | -420 | -420 | 0 | -420 | -420 | 0 | -1390 | -1390 | 0 | -1390 | -1390 | 0
| Planned Generation Capacity Total, Net of Unconfirmed Planned Retirements | 5352.4652 | 4364.8504 | 987.6149 | 11874.6106 | 8492.0409 | 3382.5696 | 17545.1403 | 11805.312 | 5739.8284 | 19359.0895 | 12856.2734 | 6502.8161 | 19429.9102 | 12856.2734 | 6573.6368 | 4360.7097 | 4144.6296 | 216.0801 | 6934.5694 | 6590.5457 | 344.0237 | 9697.9777 | 9283.7897 | 414.188 | 9442.9678 | 9033.7951 | 409.1726 | 9442.9678 | 9033.7951 | 409.1726 | 669.935 | 669.935 | 0 | 3881.5773 | 3881.5773 | 0 | 7455.4366 | 7455.4366 | 0 | 8938.8552 | 8938.8552 | 0 | 9033.8028 | 9033.8028 | 0 | 7625.6705 | 7625.6705 | 0 | 14362.9565 | 14362.9565 | 0 | 18520.2608 | 18520.2608 | 0 | 19390.2307 | 19390.2307 | 0 | 19390.2307 | 19390.2307 | 0
Total Capacity |  | 104849.9853 | 91874.564 | 12975.4213 | 109349.8485 | 94582.065 | 14767.7835 | 113693.1969 | 96347.9852 | 17345.2117 | 115079.5937 | 97029.4109 | 18050.1828 | 115501.3246 | 97408.4109 | 18092.9137 | 95388.422 | 94656.7064 | 731.7155 | 97611.465 | 96825.468 | 785.997 | 99491.5287 | 98648.8855 | 842.6432 | 99292.4148 | 98473.0339 | 819.3809 | 99707.4148 | 98888.0339 | 819.3809 | 88225.9521 | 88159.0538 | 66.8983 | 89597.5862 | 89530.6878 | 66.8983 | 93718.5471 | 93651.6487 | 66.8983 | 94949.5284 | 94882.63 | 66.8983 | 95238.382 | 95171.4837 | 66.8983 | 108275.423 | 108152.292 | 123.131 | 113212.5304 | 113089.3993 | 123.131 | 116049.8658 | 115926.7348 | 123.131 | 116781.9871 | 116658.8561 | 123.131 | 116839.9871 | 116716.8561 | 123.131
| Reserve Margin | 18.29% | 20.93% | -2.644% | 11.43% | 10.51% | 0.9136% | -1.33% | -6.226% | 4.896% | -5.823% | -11.71% | 5.882% | -12.66% | -19.15% | 6.494% | 22.1% | 28.7% | -6.596% | 4.313% | 8.713% | -4.399% | -8.255% | -4.837% | -3.418% | -17.27% | -14.36% | -2.912% | -21.39% | -18.63% | -2.759% | 17.93% | 46.93% | -28.99% | 7.122% | 29.43% | -22.3% | -4.941% | 10.92% | -15.87% | -15.79% | -4.244% | -11.55% | -22.8% | -13.59% | -9.208% | 43.58% | 53.67% | -10.08% | 32.65% | 40.25% | -7.6% | 12.8% | 17.83% | -5.028% | 5.749% | 9.539% | -3.79% | -3.438% | -0.8662% | -2.571%
[(Total Resources - Firm Load Forecast) / Firm Load Forecast]
*Total Load consists of the following forecast components: Base Economic, Electric Vehicle Forecast, Large Flexible Loads forecast, and ERCOT Adjustments to Transmission Service Provider (TSP) forecasts. The ERCOT adjustments to TSP-provided forecasts comprise the following: ‒ 180-Day Delay for Contracts and Officer Letter Load: ERCOT applies a 180-day delay to all contract and officer letter load forecasts provided by TSPs. ‒ All new data center load requests are reduced to 49.8% of the original request. ‒ All Officer Letter Load requests are reduced to 55.4% of the original request. The rooftop PV forecast is shown as a separate adjustment to indicate the magnitude of this Distributed Generation resource.

## Unit Details
NOTES (Acronym tab provided additional information regarding Technology, Fuel, CDR Status, CDR Resource Attribute columns) | [10 empty] | HIGH-RISK SEASON |  |  |  |  | HIGH-RISK SEASON |  |  |  |  | SHOULDER SEASON |  |  |  |  | SHOULDER SEASON
[11 empty] | Summer Capabilities, MW (As of the Season Start Date, June 1) |  |  |  |  | Winter Capabilities, MW (As of the Season Start Date, December 1) |  |  |  |  | Spring Capabilities, MW (As of the Season Start Date, March 1) |  |  |  |  | Fall Capabilities, MW (As of the Season Start Date, October 1)
UNIT NAME | INTERCONNECTION REQUEST NUMBER (INR) | UNIT CODE | TECHNOLOGY | FUEL | CDR STATUS | CDR RESOURCE ATTRIBUTE | COUNTY | ZONE | IN-SERVICE DATE | INSTALLED CAPACITY (MW) | 2026 | 2027 | 2028 | 2029 | 2030 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
COMANCHE PEAK U1 |  | CPSES_UNIT1 | ST | NUCLEAR | OPER | CONV | SOMERVELL | NORTH | 1990-08-13 | 1269 | 1205 | 1205 | 1205 | 1205 | 1205 | 1235 | 1235 | 1235 | 1235 | 1235 | 1227 | 1227 | 1227 | 1227 | 1227 | 1222 | 1222 | 1222 | 1222 | 1222
COMANCHE PEAK U2 |  | CPSES_UNIT2 | ST | NUCLEAR | OPER | CONV | SOMERVELL | NORTH | 1993-08-03 | 1269 | 1195 | 1195 | 1195 | 1195 | 1195 | 1225 | 1225 | 1225 | 1225 | 1225 | 1214 | 1214 | 1214 | 1214 | 1214 | 1209 | 1209 | 1209 | 1209 | 1209
SOUTH TEXAS U1 |  | STP_STP_G1 | ST | NUCLEAR | OPER | CONV | MATAGORDA | COASTAL | 1988-03-22 | 1365 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1293.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1353.2 | 1323.2 | 1323.2 | 1323.2 | 1323.2 | 1323.2 | 1323.2 | 1323.2 | 1323.2 | 1323.2 | 1323.2
SOUTH TEXAS U2 |  | STP_STP_G2 | ST | NUCLEAR | OPER | CONV | MATAGORDA | COASTAL | 1989-03-28 | 1365 | 1280 | 1280 | 1280 | 1280 | 1280 | 1340 | 1340 | 1340 | 1340 | 1340 | 1310 | 1310 | 1310 | 1310 | 1310 | 1310 | 1310 | 1310 | 1310 | 1310
COLETO CREEK |  | COLETO_COLETOG1 | ST | COAL | OPER-UNFC | CONV | GOLIAD | SOUTH | 1980-01-01 | 655 | 655 | 0 | 0 | 0 | 0 | 655 | 0 | 0 | 0 | 0 | 655 | 655 | 0 | 0 | 0 | 655 | 0 | 0 | 0 | 0
COLETO CREEK |  | COLETO_COLETOG1 | ST | GAS | OPER-UNFC | CONV | GOLIAD | SOUTH | 2027-07-01 | 655 | 0 | 655 | 655 | 655 | 655 | 0 | 655 | 655 | 655 | 655 | 0 | 0 | 655 | 655 | 655 | 0 | 655 | 655 | 655 | 655
FAYETTE POWER U1 |  | FPPYD1_FPP_G1 | ST | COAL | OPER | CONV | FAYETTE | SOUTH | 1979-06-16 | 615 | 604 | 604 | 604 | 604 | 604 | 603 | 603 | 603 | 603 | 603 | 608 | 608 | 608 | 608 | 608 | 603 | 603 | 603 | 603 | 603
FAYETTE POWER U2 |  | FPPYD1_FPP_G2 | ST | COAL | OPER | CONV | FAYETTE | SOUTH | 1980-05-20 | 615 | 599 | 599 | 599 | 599 | 599 | 605 | 605 | 605 | 605 | 605 | 608 | 608 | 608 | 608 | 608 | 603 | 603 | 603 | 603 | 603
FAYETTE POWER U3 |  | FPPYD2_FPP_G3 | ST | COAL | OPER | CONV | FAYETTE | SOUTH | 1988-04-29 | 460 | 437 | 437 | 437 | 437 | 437 | 449 | 449 | 449 | 449 | 449 | 448 | 448 | 448 | 448 | 448 | 444 | 444 | 444 | 444 | 444
J K SPRUCE U1 |  | CALAVERS_JKS1 | ST | COAL | OPER-UNR | CONV | BEXAR | SOUTH | 1992-11-01 | 560 | 560 | 560 | 560 | 0 | 0 | 560 | 560 | 0 | 0 | 0 | 560 | 560 | 560 | 0 | 0 | 560 | 560 | 560 | 0 | 0
J K SPRUCE U2 |  | CALAVERS_JKS2 | ST | COAL | OPER-UNFC | CONV | BEXAR | SOUTH | 2010-05-28 | 922 | 785 | 785 | 0 | 0 | 0 | 785 | 785 | 0 | 0 | 0 | 785 | 785 | 785 | 0 | 0 | 785 | 785 | 0 | 0 | 0
J K SPRUCE U2 |  | CALAVERS_JKS2 | ST | GAS | OPER-UNFC | CONV | BEXAR | SOUTH | 2028-06-01 | 922 | 0 | 0 | 785 | 785 | 785 | 0 | 0 | 785 | 785 | 785 | 0 | 0 | 0 | 785 | 785 | 0 | 0 | 785 | 785 | 785
LIMESTONE U1 |  | LEG_LEG_G1 | ST | COAL | OPER | CONV | LIMESTONE | NORTH | 1985-12-01 | 893 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831 | 831
LIMESTONE U2 |  | LEG_LEG_G2 | ST | COAL | OPER | CONV | LIMESTONE | NORTH | 1986-12-01 | 956.8 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857 | 857
MARTIN LAKE U1 |  | MLSES_UNIT1 | ST | COAL | OPER | CONV | RUSK | NORTH | 1977-05-16 | 893 | 800 | 800 | 800 | 800 | 800 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815 | 815
MARTIN LAKE U2 |  | MLSES_UNIT2 | ST | COAL | OPER | CONV | RUSK | NORTH | 1978-05-23 | 893 | 805 | 805 | 805 | 805 | 805 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
MARTIN LAKE U3 |  | MLSES_UNIT3 | ST | COAL | OPER | CONV | RUSK | NORTH | 1979-04-01 | 893 | 805 | 805 | 805 | 805 | 805 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820 | 820
OAK GROVE SES U1 |  | OGSES_UNIT1A | ST | COAL | OPER | CONV | ROBERTSON | NORTH | 2010-04-14 | 916.8 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
OAK GROVE SES U2 |  | OGSES_UNIT2 | ST | COAL | OPER | CONV | ROBERTSON | NORTH | 2011-04-19 | 916.8 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855 | 855
SAN MIGUEL U1 |  | SANMIGL_G1 | ST | COAL | OPER | CONV | ATASCOSA | SOUTH | 1982-02-07 | 430 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391 | 391
SANDY CREEK U1 |  | SCES_UNIT1 | ST | COAL | EXT-OUT | CONV | MCLENNAN | NORTH | 2013-07-17 | 1008 | 0 | 932.6 | 932.6 | 932.6 | 932.6 | 0 | 932.6 | 932.6 | 932.6 | 932.6 | 0 | 0 | 932.6 | 932.6 | 932.6 | 0 | 932.6 | 932.6 | 932.6 | 932.6
TWIN OAKS U1 |  | TNP_ONE_TNP_O_1 | ST | COAL | OPER | CONV | ROBERTSON | NORTH | 1990-06-08 | 174.6 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
TWIN OAKS U2 |  | TNP_ONE_TNP_O_2 | ST | COAL | OPER | CONV | ROBERTSON | NORTH | 1991-05-31 | 174.6 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155 | 155
W A PARISH U5 |  | WAP_WAP_G5 | ST | COAL | OPER | CONV | FORT BEND | HOUSTON | 1977-12-27 | 734.1 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664 | 664
W A PARISH U6 |  | WAP_WAP_G6 | ST | COAL | OPER | CONV | FORT BEND | HOUSTON | 1978-12-27 | 734.1 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663 | 663
W A PARISH U7 |  | WAP_WAP_G7 | ST | COAL | OPER | CONV | FORT BEND | HOUSTON | 1980-06-02 | 614.6 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577 | 577
W A PARISH U8 |  | WAP_WAP_G8 | ST | COAL | OPER | CONV | FORT BEND | HOUSTON | 1982-12-01 | 653.99 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610 | 610
ARTHUR VON ROSENBERG 1 CTG 1 |  | BRAUNIG_AVR1_CT1 | CC | GAS | OPER | CONV | BEXAR | SOUTH | 2000-06-02 | 189 | 178.2 | 178.2 | 178.2 | 178.2 | 178.2 | 176 | 176 | 176 | 176 | 176 | 178.9 | 178.9 | 178.9 | 178.9 | 178.9 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
ARTHUR VON ROSENBERG 1 CTG 2 |  | BRAUNIG_AVR1_CT2 | CC | GAS | OPER | CONV | BEXAR | SOUTH | 2000-06-02 | 189 | 178.2 | 178.2 | 178.2 | 178.2 | 178.2 | 176 | 176 | 176 | 176 | 176 | 178.9 | 178.9 | 178.9 | 178.9 | 178.9 | 179.6 | 179.6 | 179.6 | 179.6 | 179.6
ARTHUR VON ROSENBERG 1 STG |  | BRAUNIG_AVR1_ST | CC | GAS | OPER | CONV | BEXAR | SOUTH | 2000-06-02 | 222 | 197.5 | 197.5 | 197.5 | 197.5 | 197.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 199.9 | 199.9 | 199.9 | 199.9 | 199.9 | 202.7 | 202.7 | 202.7 | 202.7 | 202.7
ATKINS CTG 7 |  | ATKINS_ATKINSG7 | GT | GAS | OPER | CONV | BRAZOS | NORTH | 1973-01-01 | 21 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
BARNEY M DAVIS CTG 3 |  | B_DAVIS_B_DAVIG3 | CC | GAS | OPER | CONV | NUECES | COASTAL | 2010-03-26 | 189.55 | 157 | 157 | 157 | 157 | 157 | 165 | 165 | 165 | 165 | 165 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
BARNEY M DAVIS CTG 4 |  | B_DAVIS_B_DAVIG4 | CC | GAS | OPER | CONV | NUECES | COASTAL | 2010-03-26 | 189.55 | 157 | 157 | 157 | 157 | 157 | 165 | 165 | 165 | 165 | 165 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
BARNEY M DAVIS STG 1 |  | B_DAVIS_B_DAVIG1 | ST | GAS | OPER | CONV | NUECES | COASTAL | 1974-04-15 | 352.8 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292 | 292
BARNEY M DAVIS STG 2 |  | B_DAVIS_B_DAVIG2 | CC | GAS | OPER | CONV | NUECES | COASTAL | 1976-03-01 | 351 | 319 | 319 | 319 | 319 | 319 | 325 | 325 | 325 | 325 | 325 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322
BASTROP ENERGY CENTER CTG 1 |  | BASTEN_GTG1100 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2002-03-13 | 188 | 171 | 171 | 171 | 171 | 171 | 188 | 188 | 188 | 188 | 188 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
BASTROP ENERGY CENTER CTG 2 |  | BASTEN_GTG2100 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2002-03-13 | 188 | 171 | 171 | 171 | 171 | 171 | 188 | 188 | 188 | 188 | 188 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
BASTROP ENERGY CENTER STG |  | BASTEN_ST0100 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2002-03-13 | 242 | 233 | 233 | 233 | 233 | 233 | 234 | 234 | 234 | 234 | 234 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236 | 236
BEACHWOOD POWER STATION U1 |  | BCH_UNIT1 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BEACHWOOD POWER STATION U2 |  | BCH_UNIT2 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BEACHWOOD POWER STATION U3 |  | BCH_UNIT3 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BEACHWOOD POWER STATION U4 |  | BCH_UNIT4 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BEACHWOOD POWER STATION U5 |  | BCH_UNIT5 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BEACHWOOD POWER STATION U6 |  | BCH_UNIT6 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2022-11-09 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BEACHWOOD POWER STATION U7 |  | BCH_UNIT7 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2024-12-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
BEACHWOOD POWER STATION U8 |  | BCH_UNIT8 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2024-12-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
BOSQUE ENERGY CENTER CTG 1 |  | BOSQUESW_BSQSU_1 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2000-06-01 | 188.7 | 143 | 143 | 143 | 143 | 143 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 161.8 | 161.8 | 161.8 | 161.8 | 161.8 | 160.5 | 160.5 | 160.5 | 160.5 | 160.5
BOSQUE ENERGY CENTER CTG 2 |  | BOSQUESW_BSQSU_2 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2000-06-01 | 188.7 | 143 | 143 | 143 | 143 | 143 | 170.9 | 170.9 | 170.9 | 170.9 | 170.9 | 161.8 | 161.8 | 161.8 | 161.8 | 161.8 | 160.5 | 160.5 | 160.5 | 160.5 | 160.5
BOSQUE ENERGY CENTER CTG 3 |  | BOSQUESW_BSQSU_3 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2001-06-01 | 188.7 | 145 | 145 | 145 | 145 | 145 | 168.5 | 168.5 | 168.5 | 168.5 | 168.5 | 160.6 | 160.6 | 160.6 | 160.6 | 160.6 | 159.5 | 159.5 | 159.5 | 159.5 | 159.5
BOSQUE ENERGY CENTER STG 4 |  | BOSQUESW_BSQSU_4 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2001-06-01 | 94.95 | 79.5 | 79.5 | 79.5 | 79.5 | 79.5 | 85.2 | 85.2 | 85.2 | 85.2 | 85.2 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.3 | 83.3 | 83.3 | 83.3 | 83.3
BOSQUE ENERGY CENTER STG 5 |  | BOSQUESW_BSQSU_5 | CC | GAS | OPER | CONV | BOSQUE | NORTH | 2009-03-01 | 254.15 | 213.5 | 213.5 | 213.5 | 213.5 | 213.5 | 226.7 | 226.7 | 226.7 | 226.7 | 226.7 | 222.4 | 222.4 | 222.4 | 222.4 | 222.4 | 221.5 | 221.5 | 221.5 | 221.5 | 221.5
BRAZOS VALLEY CTG 1 |  | BVE_UNIT1 | CC | GAS | OPER | CONV | FORT BEND | HOUSTON | 2003-01-21 | 198.9 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 168 | 168 | 168 | 168 | 168 | 169 | 169 | 169 | 169 | 169 | 168 | 168 | 168 | 168 | 168
BRAZOS VALLEY CTG 2 |  | BVE_UNIT2 | CC | GAS | OPER | CONV | FORT BEND | HOUSTON | 2003-01-21 | 198.9 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 168 | 168 | 168 | 168 | 168 | 169 | 169 | 169 | 169 | 169 | 168 | 168 | 168 | 168 | 168
BRAZOS VALLEY STG 3 |  | BVE_UNIT3 | CC | GAS | OPER | CONV | FORT BEND | HOUSTON | 2003-01-21 | 275.57 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
BROTMAN POWER STATION U1 |  | BTM_UNIT1 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BROTMAN POWER STATION U2 |  | BTM_UNIT2 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BROTMAN POWER STATION U3 |  | BTM_UNIT3 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BROTMAN POWER STATION U4 |  | BTM_UNIT4 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BROTMAN POWER STATION U5 |  | BTM_UNIT5 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BROTMAN POWER STATION U6 |  | BTM_UNIT6 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-06-29 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
BROTMAN POWER STATION U7 |  | BTM_UNIT7 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-10-23 | 60.5 | 41.3 | 41.3 | 41.3 | 41.3 | 41.3 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 42 | 42 | 42 | 42 | 42 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2
BROTMAN POWER STATION U8 |  | BTM_UNIT8 | GT | GAS | OPER | CONV | BRAZORIA | COASTAL | 2023-10-23 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.2 | 45.2 | 45.2 | 45.2 | 45.2
CALENERGY-FALCON SEABOARD CTG 1 |  | FLCNS_UNIT1 | GT | GAS | OPER | CONV | HOWARD | WEST | 1987-07-20 | 75 | 62 | 62 | 62 | 62 | 62 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
CALENERGY-FALCON SEABOARD CTG 2 |  | FLCNS_UNIT2 | GT | GAS | OPER | CONV | HOWARD | WEST | 1987-07-21 | 75 | 62 | 62 | 62 | 62 | 62 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
CALHOUN (PORT COMFORT) CTG 1 |  | CALHOUN_UNIT1 | GT | GAS | OPER | CONV | CALHOUN | COASTAL | 2017-10-03 | 60.5 | 42 | 42 | 42 | 42 | 42 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
CALHOUN (PORT COMFORT) CTG 2 |  | CALHOUN_UNIT2 | GT | GAS | OPER | CONV | CALHOUN | COASTAL | 2017-10-03 | 60.5 | 42 | 42 | 42 | 42 | 42 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
CASTLEMAN CHAMON CTG 1 |  | CHAMON_CTG_0101 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2016-10-18 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
CASTLEMAN CHAMON CTG 2 |  | CHAMON_CTG_0301 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2017-10-24 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
CEDAR BAYOU 4 CTG 1 |  | CBY4_CT41 | CC | GAS | OPER | CONV | CHAMBERS | HOUSTON | 2009-03-09 | 205 | 155 | 155 | 155 | 155 | 155 | 178 | 178 | 178 | 178 | 178 | 157 | 157 | 157 | 157 | 157 | 158 | 158 | 158 | 158 | 158
CEDAR BAYOU 4 CTG 2 |  | CBY4_CT42 | CC | GAS | OPER | CONV | CHAMBERS | HOUSTON | 2009-03-09 | 205 | 155 | 155 | 155 | 155 | 155 | 178 | 178 | 178 | 178 | 178 | 157 | 157 | 157 | 157 | 157 | 158 | 158 | 158 | 158 | 158
CEDAR BAYOU 4 STG |  | CBY4_ST04 | CC | GAS | OPER | CONV | CHAMBERS | HOUSTON | 2009-03-09 | 205 | 169 | 169 | 169 | 169 | 169 | 185 | 185 | 185 | 185 | 185 | 173 | 173 | 173 | 173 | 173 | 178 | 178 | 178 | 178 | 178
CEDAR BAYOU STG 1 |  | CBY_CBY_G1 | ST | GAS | OPER | CONV | CHAMBERS | HOUSTON | 1970-12-11 | 765 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746 | 746
CEDAR BAYOU STG 2 |  | CBY_CBY_G2 | ST | GAS | OPER | CONV | CHAMBERS | HOUSTON | 1972-03-15 | 765 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749 | 749
COLORADO BEND ENERGY CENTER CTG 1 |  | CBEC_GT1 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2007-04-04 | 86.5 | 81.5 | 81.5 | 81.5 | 81.5 | 81.5 | 85 | 85 | 85 | 85 | 85 | 83.2 | 83.2 | 83.2 | 83.2 | 83.2 | 84 | 84 | 84 | 84 | 84
COLORADO BEND ENERGY CENTER CTG 2 |  | CBEC_GT2 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2007-04-04 | 86.5 | 74.8 | 74.8 | 74.8 | 74.8 | 74.8 | 79.6 | 79.6 | 79.6 | 79.6 | 79.6 | 76.2 | 76.2 | 76.2 | 76.2 | 76.2 | 76.9 | 76.9 | 76.9 | 76.9 | 76.9
COLORADO BEND ENERGY CENTER CTG 3 |  | CBEC_GT3 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2008-06-01 | 86.5 | 82.1 | 82.1 | 82.1 | 82.1 | 82.1 | 85 | 85 | 85 | 85 | 85 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 84.4 | 84.4 | 84.4 | 84.4 | 84.4
COLORADO BEND ENERGY CENTER CTG 4 |  | CBEC_GT4 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2008-06-01 | 86.5 | 75.9 | 75.9 | 75.9 | 75.9 | 75.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.9 | 77.1 | 77.1 | 77.1 | 77.1 | 77.1 | 77.8 | 77.8 | 77.8 | 77.8 | 77.8
COLORADO BEND ENERGY CENTER STG 1 |  | CBEC_STG1 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2007-04-04 | 105 | 103.2 | 103.2 | 103.2 | 103.2 | 103.2 | 105 | 105 | 105 | 105 | 105 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7 | 103.7
COLORADO BEND ENERGY CENTER STG 2 |  | CBEC_STG2 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2008-06-01 | 108.8 | 107.6 | 107.6 | 107.6 | 107.6 | 107.6 | 108 | 108 | 108 | 108 | 108 | 107.9 | 107.9 | 107.9 | 107.9 | 107.9 | 108 | 108 | 108 | 108 | 108
COLORADO BEND II CTG 7 |  | CBECII_CT7 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2017-06-23 | 360.9 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 360.2 | 360.2 | 360.2 | 360.2 | 360.2 | 332.1 | 332.1 | 332.1 | 332.1 | 332.1 | 332.5 | 332.5 | 332.5 | 332.5 | 332.5
COLORADO BEND II CTG 8 |  | CBECII_CT8 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2017-06-23 | 360.9 | 335 | 335 | 335 | 335 | 335 | 359.6 | 359.6 | 359.6 | 359.6 | 359.6 | 337.8 | 337.8 | 337.8 | 337.8 | 337.8 | 338.2 | 338.2 | 338.2 | 338.2 | 338.2
COLORADO BEND II STG 9 |  | CBECII_STG9 | CC | GAS | OPER | CONV | WHARTON | SOUTH | 2017-06-23 | 508.5 | 478.4 | 478.4 | 478.4 | 478.4 | 478.4 | 490.5 | 490.5 | 490.5 | 490.5 | 490.5 | 482.3 | 482.3 | 482.3 | 482.3 | 482.3 | 482.8 | 482.8 | 482.8 | 482.8 | 482.8
COLORADO BEND ENERGY CENTER CTG 11 |  | CBEC_GT11 | GT | GAS | OPER | CONV | WHARTON | SOUTH | 2023-05-31 | 41.65 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
COLORADO BEND ENERGY CENTER CTG 12 |  | CBEC_GT12 | GT | GAS | OPER | CONV | WHARTON | SOUTH | 2023-05-31 | 41.65 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39
CVC CHANNELVIEW CTG 1 |  | CVC_CVC_G1 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-06-30 | 192.1 | 169 | 169 | 169 | 169 | 169 | 185 | 185 | 185 | 185 | 185 | 181 | 181 | 181 | 181 | 181 | 168 | 168 | 168 | 168 | 168
CVC CHANNELVIEW CTG 2 |  | CVC_CVC_G2 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-06-30 | 192.1 | 165 | 165 | 165 | 165 | 165 | 182 | 182 | 182 | 182 | 182 | 178 | 178 | 178 | 178 | 178 | 163 | 163 | 163 | 163 | 163
CVC CHANNELVIEW CTG 3 |  | CVC_CVC_G3 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-06-30 | 192.1 | 165 | 165 | 165 | 165 | 165 | 181 | 181 | 181 | 181 | 181 | 178 | 178 | 178 | 178 | 178 | 163 | 163 | 163 | 163 | 163
CVC CHANNELVIEW STG 5 |  | CVC_CVC_G5 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-06-30 | 150 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 128 | 128 | 128 | 128 | 128
DANSBY CTG 2 |  | DANSBY_DANSBYG2 | GT | GAS | OPER | CONV | BRAZOS | NORTH | 2004-02-01 | 48 | 45 | 45 | 45 | 45 | 45 | 48 | 48 | 48 | 48 | 48 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
DANSBY CTG 3 |  | DANSBY_DANSBYG3 | GT | GAS | OPER | CONV | BRAZOS | NORTH | 2010-01-11 | 50 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 50 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5 | 48.5
DANSBY STG 1 |  | DANSBY_DANSBYG1 | ST | GAS | OPER | CONV | BRAZOS | NORTH | 1978-09-01 | 120 | 107 | 107 | 107 | 107 | 107 | 110 | 110 | 110 | 110 | 110 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5
DECKER CREEK CTG 1 |  | DECKER_DPGT_1 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 1989-01-30 | 56.7 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54 | 50 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 49 | 49
DECKER CREEK CTG 2 |  | DECKER_DPGT_2 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 1989-01-30 | 56.7 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54 | 50 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 49 | 49
DECKER CREEK CTG 3 |  | DECKER_DPGT_3 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 1989-01-30 | 56.7 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54 | 50 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 49 | 49
DECKER CREEK CTG 4 |  | DECKER_DPGT_4 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 1989-01-30 | 56.7 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54 | 50 | 50 | 50 | 50 | 50 | 49 | 49 | 49 | 49 | 49
DECORDOVA CTG 1 |  | DCSES_CT10 | GT | GAS | OPER | CONV | HOOD | NORTH | 1990-03-01 | 89.48 | 69 | 69 | 69 | 69 | 69 | 88 | 88 | 88 | 88 | 88 | 71 | 71 | 71 | 71 | 71 | 72 | 72 | 72 | 72 | 72
DECORDOVA CTG 2 |  | DCSES_CT20 | GT | GAS | OPER | CONV | HOOD | NORTH | 1990-03-01 | 89.48 | 69 | 69 | 69 | 69 | 69 | 87 | 87 | 87 | 87 | 87 | 70 | 70 | 70 | 70 | 70 | 71 | 71 | 71 | 71 | 71
DECORDOVA CTG 3 |  | DCSES_CT30 | GT | GAS | OPER | CONV | HOOD | NORTH | 1990-03-01 | 89.48 | 68 | 68 | 68 | 68 | 68 | 86 | 86 | 86 | 86 | 86 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
DECORDOVA CTG 4 |  | DCSES_CT40 | GT | GAS | OPER | CONV | HOOD | NORTH | 1990-03-01 | 89.48 | 69 | 69 | 69 | 69 | 69 | 86 | 86 | 86 | 86 | 86 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71
DEER PARK ENERGY CENTER CTG 1 |  | DDPEC_GT1 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 203 | 172 | 172 | 172 | 172 | 172 | 203 | 203 | 203 | 203 | 203 | 190 | 190 | 190 | 190 | 190 | 194 | 194 | 194 | 194 | 194
DEER PARK ENERGY CENTER CTG 2 |  | DDPEC_GT2 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 215 | 182 | 182 | 182 | 182 | 182 | 215 | 215 | 215 | 215 | 215 | 202 | 202 | 202 | 202 | 202 | 206 | 206 | 206 | 206 | 206
DEER PARK ENERGY CENTER CTG 3 |  | DDPEC_GT3 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 203 | 172 | 172 | 172 | 172 | 172 | 203 | 203 | 203 | 203 | 203 | 190 | 190 | 190 | 190 | 190 | 194 | 194 | 194 | 194 | 194
DEER PARK ENERGY CENTER CTG 4 |  | DDPEC_GT4 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 215 | 182 | 182 | 182 | 182 | 182 | 215 | 215 | 215 | 215 | 215 | 202 | 202 | 202 | 202 | 202 | 206 | 206 | 206 | 206 | 206
DEER PARK ENERGY CENTER CTG 6 |  | DDPEC_GT6 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2014-06-11 | 199 | 156 | 156 | 156 | 156 | 156 | 190 | 190 | 190 | 190 | 190 | 174 | 174 | 174 | 174 | 174 | 179 | 179 | 179 | 179 | 179
DEER PARK ENERGY CENTER STG 1 |  | DDPEC_ST1 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2002-11-10 | 290 | 287 | 287 | 287 | 287 | 287 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290
DENTON ENERGY CENTER IC A |  | DEC_AGR_A | IC | GAS | OPER | CONV | DENTON | NORTH | 2018-07-11 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
DENTON ENERGY CENTER IC B |  | DEC_AGR_B | IC | GAS | OPER | CONV | DENTON | NORTH | 2018-07-11 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
DENTON ENERGY CENTER IC C |  | DEC_AGR_C | IC | GAS | OPER | CONV | DENTON | NORTH | 2018-07-11 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
DENTON ENERGY CENTER IC D |  | DEC_AGR_D | IC | GAS | OPER | CONV | DENTON | NORTH | 2018-07-11 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5 | 56.5
ECTOR COUNTY ENERGY CTG 1 |  | ECEC_G1 | GT | GAS | OPER | CONV | ECTOR | WEST | 2015-07-25 | 181 | 181 | 181 | 181 | 181 | 181 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
ECTOR COUNTY ENERGY CTG 2 |  | ECEC_G2 | GT | GAS | OPER | CONV | ECTOR | WEST | 2015-07-25 | 181 | 181 | 181 | 181 | 181 | 181 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181 | 181
ENNIS POWER STATION CTG 2 |  | ETCCS_CT1 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2002-01-01 | 260 | 204 | 204 | 204 | 204 | 204 | 245 | 245 | 245 | 245 | 245 | 209 | 209 | 209 | 209 | 209 | 212 | 212 | 212 | 212 | 212
ENNIS POWER STATION STG 1 |  | ETCCS_UNIT1 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2002-01-01 | 140 | 115 | 115 | 115 | 115 | 115 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 117 | 117 | 117 | 117 | 117
EXTEX LAPORTE GEN STN CTG 1 |  | AZ_AZ_G1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2009-11-30 | 40 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40 | 36 | 36 | 36 | 36 | 36 | 38 | 38 | 38 | 38 | 38
EXTEX LAPORTE GEN STN CTG 2 |  | AZ_AZ_G2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2009-11-30 | 40 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40 | 36 | 36 | 36 | 36 | 36 | 38 | 38 | 38 | 38 | 38
EXTEX LAPORTE GEN STN CTG 3 |  | AZ_AZ_G3 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2009-11-30 | 40 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40 | 36 | 36 | 36 | 36 | 36 | 38 | 38 | 38 | 38 | 38
EXTEX LAPORTE GEN STN CTG 4 |  | AZ_AZ_G4 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2009-11-30 | 40 | 36 | 36 | 36 | 36 | 36 | 40 | 40 | 40 | 40 | 40 | 36 | 36 | 36 | 36 | 36 | 38 | 38 | 38 | 38 | 38
FERGUSON REPLACEMENT CTG 1 |  | FERGCC_FERGGT1 | CC | GAS | OPER | CONV | LLANO | SOUTH | 2014-08-12 | 185.3 | 169 | 169 | 169 | 169 | 169 | 180 | 180 | 180 | 180 | 180 | 176 | 176 | 176 | 176 | 176 | 173 | 173 | 173 | 173 | 173
FERGUSON REPLACEMENT CTG 2 |  | FERGCC_FERGGT2 | CC | GAS | OPER | CONV | LLANO | SOUTH | 2014-08-12 | 185.3 | 169 | 169 | 169 | 169 | 169 | 180 | 180 | 180 | 180 | 180 | 176 | 176 | 176 | 176 | 176 | 173 | 173 | 173 | 173 | 173
FERGUSON REPLACEMENT STG 1 |  | FERGCC_FERGST1 | CC | GAS | OPER | CONV | LLANO | SOUTH | 2014-08-12 | 204 | 182 | 182 | 182 | 182 | 182 | 194 | 194 | 194 | 194 | 194 | 189 | 189 | 189 | 189 | 189 | 186 | 186 | 186 | 186 | 186
FORNEY ENERGY CENTER CTG 11 |  | FRNYPP_GT11 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 165 | 165 | 165 | 165 | 165 | 195 | 195 | 195 | 195 | 195 | 167 | 167 | 167 | 167 | 167 | 169 | 169 | 169 | 169 | 169
FORNEY ENERGY CENTER CTG 12 |  | FRNYPP_GT12 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 157 | 157 | 157 | 157 | 157 | 185 | 185 | 185 | 185 | 185 | 159 | 159 | 159 | 159 | 159 | 161 | 161 | 161 | 161 | 161
FORNEY ENERGY CENTER CTG 13 |  | FRNYPP_GT13 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 157 | 157 | 157 | 157 | 157 | 185 | 185 | 185 | 185 | 185 | 159 | 159 | 159 | 159 | 159 | 161 | 161 | 161 | 161 | 161
FORNEY ENERGY CENTER CTG 21 |  | FRNYPP_GT21 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 165 | 165 | 165 | 165 | 165 | 195 | 195 | 195 | 195 | 195 | 167 | 167 | 167 | 167 | 167 | 169 | 169 | 169 | 169 | 169
FORNEY ENERGY CENTER CTG 22 |  | FRNYPP_GT22 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 157 | 157 | 157 | 157 | 157 | 185 | 185 | 185 | 185 | 185 | 159 | 159 | 159 | 159 | 159 | 161 | 161 | 161 | 161 | 161
FORNEY ENERGY CENTER CTG 23 |  | FRNYPP_GT23 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 196.7 | 157 | 157 | 157 | 157 | 157 | 185 | 185 | 185 | 185 | 185 | 159 | 159 | 159 | 159 | 159 | 161 | 161 | 161 | 161 | 161
FORNEY ENERGY CENTER STG 10 |  | FRNYPP_ST10 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 422 | 406 | 406 | 406 | 406 | 406 | 418 | 418 | 418 | 418 | 418 | 408 | 408 | 408 | 408 | 408 | 409 | 409 | 409 | 409 | 409
FORNEY ENERGY CENTER STG 20 |  | FRNYPP_ST20 | CC | GAS | OPER | CONV | KAUFMAN | NORTH | 2003-02-01 | 422 | 406 | 406 | 406 | 406 | 406 | 418 | 418 | 418 | 418 | 418 | 408 | 408 | 408 | 408 | 408 | 409 | 409 | 409 | 409 | 409
FREESTONE ENERGY CENTER CTG 1 |  | FREC_GT1 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-06-01 | 179.35 | 147 | 147 | 147 | 147 | 147 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 156.2 | 156.2 | 156.2 | 156.2 | 156.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2
FREESTONE ENERGY CENTER CTG 2 |  | FREC_GT2 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-06-01 | 179.35 | 147 | 147 | 147 | 147 | 147 | 160.7 | 160.7 | 160.7 | 160.7 | 160.7 | 156.2 | 156.2 | 156.2 | 156.2 | 156.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2
FREESTONE ENERGY CENTER CTG 4 |  | FREC_GT4 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-04-01 | 179.35 | 145 | 145 | 145 | 145 | 145 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 156.5 | 156.5 | 156.5 | 156.5 | 156.5 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4
FREESTONE ENERGY CENTER CTG 5 |  | FREC_GT5 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-04-01 | 179.35 | 145 | 145 | 145 | 145 | 145 | 161.1 | 161.1 | 161.1 | 161.1 | 161.1 | 156.5 | 156.5 | 156.5 | 156.5 | 156.5 | 155.4 | 155.4 | 155.4 | 155.4 | 155.4
FREESTONE ENERGY CENTER STG 3 |  | FREC_ST3 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-06-01 | 190.74 | 169 | 169 | 169 | 169 | 169 | 179.8 | 179.8 | 179.8 | 179.8 | 179.8 | 178 | 178 | 178 | 178 | 178 | 177.6 | 177.6 | 177.6 | 177.6 | 177.6
FREESTONE ENERGY CENTER STG 6 |  | FREC_ST6 | CC | GAS | OPER | CONV | FREESTONE | NORTH | 2002-04-01 | 190.74 | 168 | 168 | 168 | 168 | 168 | 179.7 | 179.7 | 179.7 | 179.7 | 179.7 | 177.1 | 177.1 | 177.1 | 177.1 | 177.1 | 176.5 | 176.5 | 176.5 | 176.5 | 176.5
FRIENDSWOOD G CTG 1 (FORMERLY TEJAS POWER GENERATION) |  | FEGC_UNIT1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2018-11-08 | 129 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119 | 119
FRONTERA ENERGY CENTER CTG 1 |  | FRONT_EC_CT1 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2023-08-23 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
FRONTERA ENERGY CENTER CTG 2 |  | FRONT_EC_CT2 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2023-08-23 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
FRONTERA ENERGY CENTER STG |  | FRONT_EC_ST | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2023-08-23 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5 | 184.5
GRAHAM STG 1 |  | GRSES_UNIT1 | ST | GAS | OPER | CONV | YOUNG | WEST | 1960-12-19 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239 | 239
GRAHAM STG 2 |  | GRSES_UNIT2 | ST | GAS | OPER | CONV | YOUNG | WEST | 1969-06-05 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390 | 390
GREENS BAYOU CTG 73 |  | GBY_GBYGT73 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 57 | 57 | 57 | 57 | 57 | 67 | 67 | 67 | 67 | 67 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 58
GREENS BAYOU CTG 74 |  | GBY_GBYGT74 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 53 | 53 | 53 | 53 | 53 | 68 | 68 | 68 | 68 | 68 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
GREENS BAYOU CTG 81 |  | GBY_GBYGT81 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 53 | 53 | 53 | 53 | 53 | 69 | 69 | 69 | 69 | 69 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55
GREENS BAYOU CTG 82 |  | GBY_GBYGT82 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 47 | 47 | 47 | 47 | 47 | 53 | 53 | 53 | 53 | 53 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
GREENS BAYOU CTG 83 |  | GBY_GBYGT83 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 61 | 61 | 61 | 61 | 61 | 72 | 72 | 72 | 72 | 72 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 63
GREENS BAYOU CTG 84 |  | GBY_GBYGT84 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1976-12-16 | 72 | 56 | 56 | 56 | 56 | 56 | 67 | 67 | 67 | 67 | 67 | 58 | 58 | 58 | 58 | 58 | 57 | 57 | 57 | 57 | 57
GREENVILLE IC ENGINE PLANT IC 1 |  | STEAM_ENGINE_1 | IC | GAS | OPER | CONV | HUNT | NORTH | 2010-06-01 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
GREENVILLE IC ENGINE PLANT IC 2 |  | STEAM_ENGINE_2 | IC | GAS | OPER | CONV | HUNT | NORTH | 2010-06-01 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
GREENVILLE IC ENGINE PLANT IC 3 |  | STEAM_ENGINE_3 | IC | GAS | OPER | CONV | HUNT | NORTH | 2010-06-01 | 8.44 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2 | 8.2
GREGORY POWER PARTNERS GT1 |  | LGE_LGE_GT1 | CC | GAS | OPER | CONV | SAN PATRICIO | COASTAL | 2000-07-15 | 185 | 145 | 145 | 145 | 145 | 145 | 165 | 165 | 165 | 165 | 165 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152 | 152
GREGORY POWER PARTNERS GT2 |  | LGE_LGE_GT2 | CC | GAS | OPER | CONV | SAN PATRICIO | COASTAL | 2000-07-15 | 185 | 145 | 145 | 145 | 145 | 145 | 165 | 165 | 165 | 165 | 165 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
GREGORY POWER PARTNERS STG |  | LGE_LGE_STG | CC | GAS | OPER | CONV | SAN PATRICIO | COASTAL | 2000-07-15 | 100 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
GUADALUPE ENERGY CENTER CTG 1 |  | GUADG_GAS1 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 181 | 143 | 143 | 143 | 143 | 143 | 167 | 167 | 167 | 167 | 167 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
GUADALUPE ENERGY CENTER CTG 2 |  | GUADG_GAS2 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 181 | 143 | 143 | 143 | 143 | 143 | 167 | 167 | 167 | 167 | 167 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
GUADALUPE ENERGY CENTER CTG 3 |  | GUADG_GAS3 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 181 | 141 | 141 | 141 | 141 | 141 | 167 | 167 | 167 | 167 | 167 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
GUADALUPE ENERGY CENTER CTG 4 |  | GUADG_GAS4 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 181 | 141 | 141 | 141 | 141 | 141 | 167 | 167 | 167 | 167 | 167 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
GUADALUPE ENERGY CENTER STG 5 |  | GUADG_STM5 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 204 | 198 | 198 | 198 | 198 | 198 | 203 | 203 | 203 | 203 | 203 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
GUADALUPE ENERGY CENTER STG 6 |  | GUADG_STM6 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2000-12-01 | 204 | 198 | 198 | 198 | 198 | 198 | 203 | 203 | 203 | 203 | 203 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
HANDLEY STG 3 |  | HLSES_UNIT3 | ST | GAS | OPER | CONV | TARRANT | NORTH | 1963-01-01 | 395 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 375
HANDLEY STG 4 |  | HLSES_UNIT4 | ST | GAS | OPER | CONV | TARRANT | NORTH | 1976-01-01 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HANDLEY STG 5 |  | HLSES_UNIT5 | ST | GAS | OPER | CONV | TARRANT | NORTH | 1977-01-01 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435 | 435
HAYS ENERGY FACILITY CSG 1 |  | HAYSEN_HAYSENG1 | CC | GAS | OPER | CONV | HAYS | SOUTH | 2002-05-28 | 242 | 210 | 210 | 210 | 210 | 210 | 239 | 239 | 239 | 239 | 239 | 213 | 213 | 213 | 213 | 213 | 214 | 214 | 214 | 214 | 214
HAYS ENERGY FACILITY CSG 2 |  | HAYSEN_HAYSENG2 | CC | GAS | OPER | CONV | HAYS | SOUTH | 2002-04-19 | 242 | 211 | 211 | 211 | 211 | 211 | 240 | 240 | 240 | 240 | 240 | 214 | 214 | 214 | 214 | 214 | 216 | 216 | 216 | 216 | 216
HAYS ENERGY FACILITY CSG 3 |  | HAYSEN_HAYSENG3 | CC | GAS | OPER | CONV | HAYS | SOUTH | 2002-08-16 | 252 | 210 | 210 | 210 | 210 | 210 | 242 | 242 | 242 | 242 | 242 | 213 | 213 | 213 | 213 | 213 | 215 | 215 | 215 | 215 | 215
HAYS ENERGY FACILITY CSG 4 |  | HAYSEN_HAYSENG4 | CC | GAS | OPER | CONV | HAYS | SOUTH | 2002-08-15 | 252 | 213 | 213 | 213 | 213 | 213 | 243 | 243 | 243 | 243 | 243 | 216 | 216 | 216 | 216 | 216 | 218 | 218 | 218 | 218 | 218
HIDALGO ENERGY CENTER CTG 1 |  | DUKE_DUKE_GT1 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2000-01-01 | 176.63 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 143 | 143 | 143 | 143 | 143 | 145 | 145 | 145 | 145 | 145
HIDALGO ENERGY CENTER CTG 2 |  | DUKE_DUKE_GT2 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2000-01-01 | 176.63 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 143 | 143 | 143 | 143 | 143 | 145 | 145 | 145 | 145 | 145
HIDALGO ENERGY CENTER STG 1 |  | DUKE_DUKE_ST1 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2000-01-01 | 198.05 | 168 | 168 | 168 | 168 | 168 | 176 | 176 | 176 | 176 | 176 | 172 | 172 | 172 | 172 | 172 | 173 | 173 | 173 | 173 | 173
JACK COUNTY GEN FACILITY CTG 1 |  | JACKCNTY_CT1 | CC | GAS | OPER | CONV | JACK | NORTH | 2006-02-01 | 198.9 | 150 | 150 | 150 | 150 | 150 | 165 | 165 | 165 | 165 | 165 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
JACK COUNTY GEN FACILITY CTG 2 |  | JACKCNTY_CT2 | CC | GAS | OPER | CONV | JACK | NORTH | 2006-02-01 | 198.9 | 150 | 150 | 150 | 150 | 150 | 165 | 165 | 165 | 165 | 165 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
JACK COUNTY GEN FACILITY CTG 3 |  | JCKCNTY2_CT3 | CC | GAS | OPER | CONV | JACK | NORTH | 2011-08-05 | 198.9 | 158 | 158 | 158 | 158 | 158 | 182 | 182 | 182 | 182 | 182 | 165 | 165 | 165 | 165 | 165 | 167 | 167 | 167 | 167 | 167
JACK COUNTY GEN FACILITY CTG 4 |  | JCKCNTY2_CT4 | CC | GAS | OPER | CONV | JACK | NORTH | 2011-08-05 | 198.9 | 158 | 158 | 158 | 158 | 158 | 182 | 182 | 182 | 182 | 182 | 165 | 165 | 165 | 165 | 165 | 167 | 167 | 167 | 167 | 167
JACK COUNTY GEN FACILITY STG 1 |  | JACKCNTY_STG | CC | GAS | OPER | CONV | JACK | NORTH | 2006-02-01 | 320.6 | 289 | 289 | 289 | 289 | 289 | 300 | 300 | 300 | 300 | 300 | 275 | 275 | 275 | 275 | 275 | 285 | 285 | 285 | 285 | 285
JACK COUNTY GEN FACILITY STG 2 |  | JCKCNTY2_ST2 | CC | GAS | OPER | CONV | JACK | NORTH | 2011-08-05 | 320.6 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 295 | 294 | 294 | 294 | 294 | 294 | 295 | 295 | 295 | 295 | 295
JOHNSON COUNTY GEN FACILITY CTG 1 |  | TEN_CT1 | CC | GAS | OPER | CONV | JOHNSON | NORTH | 1997-01-02 | 185 | 163 | 163 | 163 | 163 | 163 | 177 | 177 | 177 | 177 | 177 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163
JOHNSON COUNTY GEN FACILITY STG 1 |  | TEN_STG | CC | GAS | OPER | CONV | JOHNSON | NORTH | 1997-01-02 | 107 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106
LAKE HUBBARD STG 1 |  | LHSES_UNIT1 | ST | GAS | OPER | CONV | DALLAS | NORTH | 1970-06-18 | 397 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392 | 392
LAKE HUBBARD STG 2 |  | LHSES_UNIT2A | ST | GAS | OPER | CONV | DALLAS | NORTH | 1973-11-20 | 531 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523 | 523
LAMAR ENERGY CENTER CTG 11 |  | LPCCS_CT11 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 186 | 153 | 153 | 153 | 153 | 153 | 186 | 186 | 186 | 186 | 186 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
LAMAR ENERGY CENTER CTG 12 |  | LPCCS_CT12 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 186 | 145 | 145 | 145 | 145 | 145 | 178 | 178 | 178 | 178 | 178 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
LAMAR ENERGY CENTER CTG 21 |  | LPCCS_CT21 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 186 | 145 | 145 | 145 | 145 | 145 | 178 | 178 | 178 | 178 | 178 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
LAMAR ENERGY CENTER CTG 22 |  | LPCCS_CT22 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 186 | 153 | 153 | 153 | 153 | 153 | 186 | 186 | 186 | 186 | 186 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
LAMAR ENERGY CENTER STG 1 |  | LPCCS_UNIT1 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 216 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
LAMAR ENERGY CENTER STG 2 |  | LPCCS_UNIT2 | CC | GAS | OPER | CONV | LAMAR | NORTH | 2000-07-04 | 216 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 204
LAREDO CTG 4 |  | LARDVFTN_G4 | GT | GAS | OPER | CONV | WEBB | SOUTH | 2008-07-27 | 98.5 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 97.4 | 97.4 | 97.4 | 97.4 | 97.4 | 92.9 | 92.9 | 92.9 | 92.9 | 92.9 | 93 | 93 | 93 | 93 | 93
LAREDO CTG 5 |  | LARDVFTN_G5 | GT | GAS | OPER | CONV | WEBB | SOUTH | 2008-08-20 | 98.5 | 87.3 | 87.3 | 87.3 | 87.3 | 87.3 | 94.4 | 94.4 | 94.4 | 94.4 | 94.4 | 90.1 | 90.1 | 90.1 | 90.1 | 90.1 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2
LEON CREEK PEAKER CTG 1 |  | LEON_CRK_LCPCT1 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2004-03-26 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 2 |  | LEON_CRK_LCPCT2 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2004-04-08 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 3 |  | LEON_CRK_LCPCT3 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2004-04-15 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LEON CREEK PEAKER CTG 4 |  | LEON_CRK_LCPCT4 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2004-04-22 | 48 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
LIGNIN (CHAMON 2) U1 |  | LIG_UNIT1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2022-06-20 | 60.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 44 | 44 | 44 | 44 | 44 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
LIGNIN (CHAMON 2) U2 |  | LIG_UNIT2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2022-06-20 | 60.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 44 | 44 | 44 | 44 | 44 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
LOST PINES POWER CTG 1 |  | LOSTPI_LOSTPGT1 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2001-05-27 | 202.5 | 170 | 170 | 170 | 170 | 170 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 183 | 178 | 178 | 178 | 178 | 178
LOST PINES POWER CTG 2 |  | LOSTPI_LOSTPGT2 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2001-05-27 | 202.5 | 170 | 170 | 170 | 170 | 170 | 183 | 183 | 183 | 183 | 183 | 175 | 175 | 175 | 175 | 175 | 172 | 172 | 172 | 172 | 172
LOST PINES POWER STG 1 |  | LOSTPI_LOSTPST1 | CC | GAS | OPER | CONV | BASTROP | SOUTH | 2001-05-27 | 204 | 188 | 188 | 188 | 188 | 188 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 188 | 188 | 188 | 188 | 188
MAGIC VALLEY STATION CTG 1 |  | NEDIN_NEDIN_G1 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2001-07-11 | 266.9 | 215 | 215 | 215 | 215 | 215 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 213.6 | 213.6 | 213.6 | 213.6 | 213.6 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5
MAGIC VALLEY STATION CTG 2 |  | NEDIN_NEDIN_G2 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2001-07-11 | 266.9 | 215 | 215 | 215 | 215 | 215 | 218.6 | 218.6 | 218.6 | 218.6 | 218.6 | 213.6 | 213.6 | 213.6 | 213.6 | 213.6 | 212.5 | 212.5 | 212.5 | 212.5 | 212.5
MAGIC VALLEY STATION STG 3 |  | NEDIN_NEDIN_G3 | CC | GAS | OPER | CONV | HIDALGO | SOUTH | 2001-07-11 | 258.4 | 236 | 236 | 236 | 236 | 236 | 257.9 | 257.9 | 257.9 | 257.9 | 257.9 | 255.5 | 255.5 | 255.5 | 255.5 | 255.5 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9
MIDLOTHIAN ENERGY FACILITY CTG 1 |  | MDANP_CT1 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2001-03-18 | 258 | 229 | 229 | 229 | 229 | 229 | 258 | 258 | 258 | 258 | 258 | 232 | 232 | 232 | 232 | 232 | 233 | 233 | 233 | 233 | 233
MIDLOTHIAN ENERGY FACILITY CTG 2 |  | MDANP_CT2 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2001-03-15 | 256 | 227 | 227 | 227 | 227 | 227 | 256 | 256 | 256 | 256 | 256 | 230 | 230 | 230 | 230 | 230 | 231 | 231 | 231 | 231 | 231
MIDLOTHIAN ENERGY FACILITY CTG 3 |  | MDANP_CT3 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2001-01-22 | 255 | 227 | 227 | 227 | 227 | 227 | 255 | 255 | 255 | 255 | 255 | 229 | 229 | 229 | 229 | 229 | 230 | 230 | 230 | 230 | 230
MIDLOTHIAN ENERGY FACILITY CTG 4 |  | MDANP_CT4 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2001-02-08 | 258 | 227 | 227 | 227 | 227 | 227 | 258 | 258 | 258 | 258 | 258 | 232 | 232 | 232 | 232 | 232 | 233 | 233 | 233 | 233 | 233
MIDLOTHIAN ENERGY FACILITY CTG 5 |  | MDANP_CT5 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2002-06-28 | 276 | 241 | 241 | 241 | 241 | 241 | 276 | 276 | 276 | 276 | 276 | 244 | 244 | 244 | 244 | 244 | 245 | 245 | 245 | 245 | 245
MIDLOTHIAN ENERGY FACILITY CTG 6 |  | MDANP_CT6 | CC | GAS | OPER | CONV | ELLIS | NORTH | 2002-06-07 | 278 | 243 | 243 | 243 | 243 | 243 | 278 | 278 | 278 | 278 | 278 | 246 | 246 | 246 | 246 | 246 | 247 | 247 | 247 | 247 | 247
MORGAN CREEK CTG 1 |  | MGSES_CT1 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 66 | 66 | 66 | 66 | 66 | 82 | 82 | 82 | 82 | 82 | 67 | 67 | 67 | 67 | 67 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK CTG 2 |  | MGSES_CT2 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 65 | 65 | 65 | 65 | 65 | 80 | 80 | 80 | 80 | 80 | 66 | 66 | 66 | 66 | 66 | 67 | 67 | 67 | 67 | 67
MORGAN CREEK CTG 3 |  | MGSES_CT3 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 65 | 65 | 65 | 65 | 65 | 80 | 80 | 80 | 80 | 80 | 66 | 66 | 66 | 66 | 66 | 67 | 67 | 67 | 67 | 67
MORGAN CREEK CTG 4 |  | MGSES_CT4 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 67 | 67 | 67 | 67 | 67 | 81 | 81 | 81 | 81 | 81 | 67 | 67 | 67 | 67 | 67 | 68 | 68 | 68 | 68 | 68
MORGAN CREEK CTG 5 |  | MGSES_CT5 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 67 | 67 | 67 | 67 | 67 | 80 | 80 | 80 | 80 | 80 | 68 | 68 | 68 | 68 | 68 | 69 | 69 | 69 | 69 | 69
MORGAN CREEK CTG 6 |  | MGSES_CT6 | GT | GAS | OPER | CONV | MITCHELL | WEST | 1988-07-01 | 89.4 | 67 | 67 | 67 | 67 | 67 | 82 | 82 | 82 | 82 | 82 | 68 | 68 | 68 | 68 | 68 | 69 | 69 | 69 | 69 | 69
MOUNTAIN CREEK STG 6 |  | MCSES_UNIT6 | ST | GAS | OPER | CONV | DALLAS | NORTH | 1956-01-01 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122 | 122
MOUNTAIN CREEK STG 7 |  | MCSES_UNIT7 | ST | GAS | OPER | CONV | DALLAS | NORTH | 1958-01-01 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118 | 118
MOUNTAIN CREEK STG 8 |  | MCSES_UNIT8 | ST | GAS | OPER | CONV | DALLAS | NORTH | 1967-01-01 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568 | 568
NUECES BAY CTG 8 |  | NUECES_B_NUECESG8 | CC | GAS | OPER | CONV | NUECES | COASTAL | 2010-03-20 | 189.55 | 157 | 157 | 157 | 157 | 157 | 165 | 165 | 165 | 165 | 165 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
NUECES BAY CTG 9 |  | NUECES_B_NUECESG9 | CC | GAS | OPER | CONV | NUECES | COASTAL | 2010-03-20 | 189.55 | 157 | 157 | 157 | 157 | 157 | 165 | 165 | 165 | 165 | 165 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
NUECES BAY STG 7 |  | NUECES_B_NUECESG7 | CC | GAS | OPER | CONV | NUECES | COASTAL | 1972-01-01 | 351 | 319 | 319 | 319 | 319 | 319 | 325 | 325 | 325 | 325 | 325 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322 | 322
O W SOMMERS STG 1 |  | CALAVERS_OWS1 | ST | GAS | OPER-UNR | CONV | BEXAR | SOUTH | 1972-06-06 | 445 | 420 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 | 0
O W SOMMERS STG 2 |  | CALAVERS_OWS2 | ST | GAS | OPER-UNR | CONV | BEXAR | SOUTH | 1974-03-20 | 435 | 410 | 410 | 410 | 0 | 0 | 410 | 410 | 410 | 0 | 0 | 410 | 410 | 410 | 0 | 0 | 410 | 410 | 410 | 0 | 0
ODESSA-ECTOR POWER CTG 11 |  | OECCS_CT11 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 195.2 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 167.5 | 167.5 | 167.5 | 167.5 | 167.5
ODESSA-ECTOR POWER CTG 12 |  | OECCS_CT12 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 189.1 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 156.1 | 156.1 | 156.1 | 156.1 | 156.1 | 159 | 159 | 159 | 159 | 159
ODESSA-ECTOR POWER CTG 21 |  | OECCS_CT21 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 195.2 | 166.7 | 166.7 | 166.7 | 166.7 | 166.7 | 195.2 | 195.2 | 195.2 | 195.2 | 195.2 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 167.5 | 167.5 | 167.5 | 167.5 | 167.5
ODESSA-ECTOR POWER CTG 22 |  | OECCS_CT22 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 189.1 | 158.2 | 158.2 | 158.2 | 158.2 | 158.2 | 189.1 | 189.1 | 189.1 | 189.1 | 189.1 | 156.1 | 156.1 | 156.1 | 156.1 | 156.1 | 159 | 159 | 159 | 159 | 159
ODESSA-ECTOR POWER STG 1 |  | OECCS_UNIT1 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 224 | 206 | 206 | 206 | 206 | 206 | 217 | 217 | 217 | 217 | 217 | 206.4 | 206.4 | 206.4 | 206.4 | 206.4 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2
ODESSA-ECTOR POWER STG 2 |  | OECCS_UNIT2 | CC | GAS | OPER | CONV | ECTOR | WEST | 2001-06-01 | 224 | 206 | 206 | 206 | 206 | 206 | 217 | 217 | 217 | 217 | 217 | 206.4 | 206.4 | 206.4 | 206.4 | 206.4 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2
OLD BLOOMINGTON ROAD CTG 1 (VICTORIA PORT 2) |  | VICTPRT2_UNIT1 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2022-01-12 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
OLD BLOOMINGTON ROAD CTG 2 (VICTORIA PORT 2) |  | VICTPRT2_UNIT2 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2022-01-12 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
PANDA SHERMAN POWER CTG 1 |  | PANDA_S_SHER1CT1 | CC | GAS | OPER | CONV | GRAYSON | NORTH | 2014-08-01 | 232 | 199 | 199 | 199 | 199 | 199 | 224 | 224 | 224 | 224 | 224 | 218 | 218 | 218 | 218 | 218 | 217 | 217 | 217 | 217 | 217
PANDA SHERMAN POWER CTG 2 |  | PANDA_S_SHER1CT2 | CC | GAS | OPER | CONV | GRAYSON | NORTH | 2014-08-01 | 232 | 199 | 199 | 199 | 199 | 199 | 224 | 224 | 224 | 224 | 224 | 217 | 217 | 217 | 217 | 217 | 216 | 216 | 216 | 216 | 216
PANDA SHERMAN POWER STG 1 |  | PANDA_S_SHER1ST1 | CC | GAS | OPER | CONV | GRAYSON | NORTH | 2014-08-01 | 353.1 | 287 | 287 | 287 | 287 | 287 | 316 | 316 | 316 | 316 | 316 | 308 | 308 | 308 | 308 | 308 | 307 | 307 | 307 | 307 | 307
PANDA TEMPLE I POWER CTG 1 |  | PANDA_T1_TMPL1CT1 | CC | GAS | OPER | CONV | BELL | NORTH | 2014-08-01 | 232 | 223 | 223 | 223 | 223 | 223 | 222 | 222 | 222 | 222 | 222 | 220 | 220 | 220 | 220 | 220 | 219 | 219 | 219 | 219 | 219
PANDA TEMPLE I POWER CTG 2 |  | PANDA_T1_TMPL1CT2 | CC | GAS | OPER | CONV | BELL | NORTH | 2014-08-01 | 232 | 220 | 220 | 220 | 220 | 220 | 209 | 209 | 209 | 209 | 209 | 207 | 207 | 207 | 207 | 207 | 206 | 206 | 206 | 206 | 206
PANDA TEMPLE I POWER STG 1 |  | PANDA_T1_TMPL1ST1 | CC | GAS | OPER | CONV | BELL | NORTH | 2014-08-01 | 353.1 | 326 | 326 | 326 | 326 | 326 | 325 | 325 | 325 | 325 | 325 | 324 | 324 | 324 | 324 | 324 | 323 | 323 | 323 | 323 | 323
PANDA TEMPLE II POWER CTG 1 |  | PANDA_T2_TMPL2CT1 | CC | GAS | OPER | CONV | BELL | NORTH | 2015-08-01 | 232 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE II POWER CTG 2 |  | PANDA_T2_TMPL2CT2 | CC | GAS | OPER | CONV | BELL | NORTH | 2015-08-01 | 232 | 191.2 | 191.2 | 191.2 | 191.2 | 191.2 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5 | 218.5
PANDA TEMPLE II POWER STG 1 |  | PANDA_T2_TMPL2ST1 | CC | GAS | OPER | CONV | BELL | NORTH | 2015-08-01 | 353.1 | 334.7 | 334.7 | 334.7 | 334.7 | 334.7 | 333.6 | 333.6 | 333.6 | 333.6 | 333.6 | 353.1 | 353.1 | 353.1 | 353.1 | 353.1 | 353.1 | 353.1 | 353.1 | 353.1 | 353.1
PARIS ENERGY CENTER CTG 1 |  | TNSKA_GT1 | CC | GAS | OPER | CONV | LAMAR | NORTH | 1989-06-01 | 90.88 | 76 | 76 | 76 | 76 | 76 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
PARIS ENERGY CENTER CTG 2 |  | TNSKA_GT2 | CC | GAS | OPER | CONV | LAMAR | NORTH | 1989-06-01 | 90.88 | 76 | 76 | 76 | 76 | 76 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86
PARIS ENERGY CENTER STG 1 |  | TNSKA_STG | CC | GAS | OPER | CONV | LAMAR | NORTH | 1990-02-01 | 90 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79
PASADENA COGEN FACILITY CTG 2 |  | PSG_PSG_GT2 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2000-06-02 | 215.05 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 176 | 176 | 176 | 176 | 176 | 170 | 170 | 170 | 170 | 170 | 168 | 168 | 168 | 168 | 168
PASADENA COGEN FACILITY CTG 3 |  | PSG_PSG_GT3 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2000-06-02 | 215.05 | 164.5 | 164.5 | 164.5 | 164.5 | 164.5 | 176 | 176 | 176 | 176 | 176 | 170 | 170 | 170 | 170 | 170 | 168 | 168 | 168 | 168 | 168
PASADENA COGEN FACILITY STG 2 |  | PSG_PSG_ST2 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 2000-06-02 | 195.5 | 170.4 | 170.4 | 170.4 | 170.4 | 170.4 | 169 | 169 | 169 | 169 | 169 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168 | 168
PEARSALL ENGINE PLANT IC A |  | PEARSAL2_AGR_A | IC | GAS | OPER | CONV | FRIO | SOUTH | 2012-06-29 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL ENGINE PLANT IC B |  | PEARSAL2_AGR_B | IC | GAS | OPER | CONV | FRIO | SOUTH | 2012-06-29 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL ENGINE PLANT IC C |  | PEARSAL2_AGR_C | IC | GAS | OPER | CONV | FRIO | SOUTH | 2012-06-29 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PEARSALL ENGINE PLANT IC D |  | PEARSAL2_AGR_D | IC | GAS | OPER | CONV | FRIO | SOUTH | 2012-06-29 | 50.64 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6 | 50.6
PERMIAN BASIN CTG 1 |  | PB2SES_CT1 | GT | GAS | OPER | CONV | WARD | WEST | 1988-05-01 | 89.4 | 63 | 63 | 63 | 63 | 63 | 79 | 79 | 79 | 79 | 79 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
PERMIAN BASIN CTG 2 |  | PB2SES_CT2 | GT | GAS | OPER | CONV | WARD | WEST | 1988-05-01 | 89.4 | 64 | 64 | 64 | 64 | 64 | 76 | 76 | 76 | 76 | 76 | 64 | 64 | 64 | 64 | 64 | 66 | 66 | 66 | 66 | 66
PERMIAN BASIN CTG 3 |  | PB2SES_CT3 | GT | GAS | OPER | CONV | WARD | WEST | 1988-05-01 | 89.4 | 64 | 64 | 64 | 64 | 64 | 78 | 78 | 78 | 78 | 78 | 64 | 64 | 64 | 64 | 64 | 65 | 65 | 65 | 65 | 65
PERMIAN BASIN CTG 4 |  | PB2SES_CT4 | GT | GAS | OPER | CONV | WARD | WEST | 1990-02-01 | 89.4 | 64 | 64 | 64 | 64 | 64 | 75 | 75 | 75 | 75 | 75 | 64 | 64 | 64 | 64 | 64 | 65 | 65 | 65 | 65 | 65
PERMIAN BASIN CTG 5 |  | PB2SES_CT5 | GT | GAS | OPER | CONV | WARD | WEST | 1990-02-01 | 89.4 | 65 | 65 | 65 | 65 | 65 | 79 | 79 | 79 | 79 | 79 | 65 | 65 | 65 | 65 | 65 | 66 | 66 | 66 | 66 | 66
PROENERGY SOUTH 1 (PES1) CTG 1 |  | PRO_UNIT1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
PROENERGY SOUTH 1 (PES1) CTG 2 |  | PRO_UNIT2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
PROENERGY SOUTH 1 (PES1) CTG 3 |  | PRO_UNIT3 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
PROENERGY SOUTH 1 (PES1) CTG 4 |  | PRO_UNIT4 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
PROENERGY SOUTH 1 (PES1) CTG 5 |  | PRO_UNIT5 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
PROENERGY SOUTH 1 (PES1) CTG 6 |  | PRO_UNIT6 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-03-30 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
PROENERGY SOUTH 2 (PES2) CTG 7 |  | PRO_UNIT7 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-11-11 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
PROENERGY SOUTH 2 (PES2) CTG 8 |  | PRO_UNIT8 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2021-11-11 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
PHR PEAKERS (BAC) CTG 1 |  | BAC_CTG1 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 59 | 59 | 59 | 59 | 59 | 65 | 65 | 65 | 65 | 65 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
PHR PEAKERS (BAC) CTG 2 |  | BAC_CTG2 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 61 | 61 | 61 | 61 | 61 | 65 | 65 | 65 | 65 | 65 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62
PHR PEAKERS (BAC) CTG 3 |  | BAC_CTG3 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 49 | 49 | 49 | 49 | 49 | 65 | 65 | 65 | 65 | 65 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
PHR PEAKERS (BAC) CTG 4 |  | BAC_CTG4 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 54 | 54 | 54 | 54 | 54 | 65 | 65 | 65 | 65 | 65 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
PHR PEAKERS (BAC) CTG 5 |  | BAC_CTG5 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 54 | 54 | 54 | 54 | 54 | 64 | 64 | 64 | 64 | 64 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
PHR PEAKERS (BAC) CTG 6 |  | BAC_CTG6 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2018-07-11 | 65 | 52 | 52 | 52 | 52 | 52 | 65 | 65 | 65 | 65 | 65 | 54 | 54 | 54 | 54 | 54 | 55 | 55 | 55 | 55 | 55
POWERLANE PLANT STG 1 (AS OF 10/1/2022, AVAILABLE 5/1 THROUGH 9/30) |  | STEAM1A_STEAM_1 | ST | GAS | MOTH-SEA | CONV | HUNT | NORTH | 1966-08-01 | 18.75 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
POWERLANE PLANT STG 2 |  | STEAM_STEAM_2 | ST | GAS | OPER | CONV | HUNT | NORTH | 1967-01-01 | 25 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5
POWERLANE PLANT STG 3 |  | STEAM_STEAM_3 | ST | GAS | OPER | CONV | HUNT | NORTH | 1978-01-01 | 43.2 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
QUAIL RUN ENERGY CTG 1 |  | QALSW_GT1 | CC | GAS | OPER | CONV | ECTOR | WEST | 2007-04-12 | 90.6 | 74 | 74 | 74 | 74 | 74 | 84 | 84 | 84 | 84 | 84 | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 81
QUAIL RUN ENERGY CTG 2 |  | QALSW_GT2 | CC | GAS | OPER | CONV | ECTOR | WEST | 2007-04-12 | 90.6 | 74 | 74 | 74 | 74 | 74 | 86 | 86 | 86 | 86 | 86 | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 81 | 81 | 81
QUAIL RUN ENERGY CTG 3 |  | QALSW_GT3 | CC | GAS | OPER | CONV | ECTOR | WEST | 2008-05-03 | 90.6 | 72 | 72 | 72 | 72 | 72 | 81 | 81 | 81 | 81 | 81 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
QUAIL RUN ENERGY CTG 4 |  | QALSW_GT4 | CC | GAS | OPER | CONV | ECTOR | WEST | 2008-05-03 | 90.6 | 72 | 72 | 72 | 72 | 72 | 81 | 81 | 81 | 81 | 81 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
QUAIL RUN ENERGY STG 1 |  | QALSW_STG1 | CC | GAS | OPER | CONV | ECTOR | WEST | 2007-04-12 | 98.1 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
QUAIL RUN ENERGY STG 2 |  | QALSW_STG2 | CC | GAS | OPER | CONV | ECTOR | WEST | 2008-05-03 | 98.1 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
R W MILLER CTG 4 |  | MIL_MILLERG4 | GT | GAS | OPER | CONV | PALO PINTO | NORTH | 1994-07-01 | 116 | 100 | 100 | 100 | 100 | 100 | 116 | 116 | 116 | 116 | 116 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
R W MILLER CTG 5 |  | MIL_MILLERG5 | GT | GAS | OPER | CONV | PALO PINTO | NORTH | 1994-07-01 | 116 | 100 | 100 | 100 | 100 | 100 | 116 | 116 | 116 | 116 | 116 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
R W MILLER STG 1 |  | MIL_MILLERG1 | ST | GAS | EXT-OUT | CONV | PALO PINTO | NORTH | 1968-10-01 | 75 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75
R W MILLER STG 2 |  | MIL_MILLERG2 | ST | GAS | OPER | CONV | PALO PINTO | NORTH | 1972-07-01 | 120 | 118 | 118 | 118 | 118 | 118 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
R W MILLER STG 3 |  | MIL_MILLERG3 | ST | GAS | OPER | CONV | PALO PINTO | NORTH | 1975-08-01 | 216.01 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208 | 208
RAY OLINGER CTG 4 |  | OLINGR_OLING_4 | GT | GAS | OPER | CONV | COLLIN | NORTH | 2001-06-01 | 95 | 80 | 80 | 80 | 80 | 80 | 95 | 95 | 95 | 95 | 95 | 90 | 90 | 90 | 90 | 90 | 95 | 95 | 95 | 95 | 95
RAY OLINGER STG 2 |  | OLINGR_OLING_2 | ST | GAS | OPER | CONV | COLLIN | NORTH | 1971-05-01 | 113.64 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107
RAY OLINGER STG 3 |  | OLINGR_OLING_3 | ST | GAS | OPER | CONV | COLLIN | NORTH | 1975-12-01 | 156.6 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
RABBS POWER STATION U1 |  | RAB_UNIT1 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-09-12 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
RABBS POWER STATION U2 |  | RAB_UNIT2 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-07-12 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
RABBS POWER STATION U3 |  | RAB_UNIT3 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-05-02 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
RABBS POWER STATION U4 |  | RAB_UNIT4 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-05-02 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
RABBS POWER STATION U5 |  | RAB_UNIT5 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-05-02 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
RABBS POWER STATION U6 |  | RAB_UNIT6 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-06-23 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
RABBS POWER STATION U7 |  | RAB_UNIT7 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-06-23 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
RABBS POWER STATION U8 |  | RAB_UNIT8 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 2022-06-23 | 60.5 | 44.6 | 44.6 | 44.6 | 44.6 | 44.6 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.5 | 45.5 | 45.5 | 45.5 | 45.5
REDGATE IC A |  | REDGATE_AGR_A | IC | GAS | OPER | CONV | HIDALGO | SOUTH | 2016-08-10 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
REDGATE IC B |  | REDGATE_AGR_B | IC | GAS | OPER | CONV | HIDALGO | SOUTH | 2016-08-10 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
REDGATE IC C |  | REDGATE_AGR_C | IC | GAS | OPER | CONV | HIDALGO | SOUTH | 2016-08-10 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
REDGATE IC D |  | REDGATE_AGR_D | IC | GAS | OPER | CONV | HIDALGO | SOUTH | 2016-08-10 | 56.28 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3 | 56.3
REMY JADE POWER STATION U1 |  | JAD_UNIT1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
REMY JADE POWER STATION U2 |  | JAD_UNIT2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
REMY JADE POWER STATION U3 |  | JAD_UNIT3 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
REMY JADE POWER STATION U4 |  | JAD_UNIT4 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
REMY JADE POWER STATION U5 |  | JAD_UNIT5 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
REMY JADE POWER STATION U6 |  | JAD_UNIT6 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
REMY JADE POWER STATION U7 |  | JAD_UNIT7 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
REMY JADE POWER STATION U8 |  | JAD_UNIT8 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 2024-09-13 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
RIO NOGALES POWER CTG 1 |  | RIONOG_CT1 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2002-06-01 | 203 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 203 | 203 | 203 | 203 | 203 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 172.8 | 172.8 | 172.8 | 172.8 | 172.8
RIO NOGALES POWER CTG 2 |  | RIONOG_CT2 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2002-06-01 | 203 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 203 | 203 | 203 | 203 | 203 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 172.8 | 172.8 | 172.8 | 172.8 | 172.8
RIO NOGALES POWER CTG 3 |  | RIONOG_CT3 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2002-06-01 | 203 | 165.5 | 165.5 | 165.5 | 165.5 | 165.5 | 203 | 203 | 203 | 203 | 203 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 172.8 | 172.8 | 172.8 | 172.8 | 172.8
RIO NOGALES POWER STG 4 |  | RIONOG_ST1 | CC | GAS | OPER | CONV | GUADALUPE | SOUTH | 2002-06-01 | 373.16 | 303 | 303 | 303 | 303 | 303 | 319 | 319 | 319 | 319 | 319 | 306 | 306 | 306 | 306 | 306 | 307 | 307 | 307 | 307 | 307
SAM RAYBURN POWER CTG 7 |  | RAYBURN_RAYBURG7 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2003-06-24 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SAM RAYBURN POWER CTG 8 |  | RAYBURN_RAYBURG8 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2003-06-26 | 60.5 | 50 | 50 | 50 | 50 | 50 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
SAM RAYBURN POWER CTG 9 |  | RAYBURN_RAYBURG9 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2003-06-26 | 60.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SAM RAYBURN POWER STG 10 |  | RAYBURN_RAYBURG10 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2003-06-26 | 41.98 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
SAN JACINTO SES CTG 1 |  | SJS_SJS_G1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1995-04-21 | 88.23 | 80 | 80 | 80 | 80 | 80 | 87 | 87 | 87 | 87 | 87 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83
SAN JACINTO SES CTG 2 |  | SJS_SJS_G2 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1995-04-21 | 88.23 | 80 | 80 | 80 | 80 | 80 | 87 | 87 | 87 | 87 | 87 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83
SANDHILL ENERGY CENTER CTG 1 |  | SANDHSYD_SH1 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2001-06-20 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 2 |  | SANDHSYD_SH2 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2001-06-20 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 3 |  | SANDHSYD_SH3 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2001-06-20 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 4 |  | SANDHSYD_SH4 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2001-06-20 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 5A |  | SANDHSYD_SH_5A | CC | GAS | OPER | CONV | TRAVIS | SOUTH | 2004-09-01 | 198.9 | 142 | 142 | 142 | 142 | 142 | 175 | 175 | 175 | 175 | 175 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
SANDHILL ENERGY CENTER CTG 6 |  | SANDHSYD_SH6 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2010-03-22 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER CTG 7 |  | SANDHSYD_SH7 | GT | GAS | OPER | CONV | TRAVIS | SOUTH | 2010-04-09 | 60.5 | 47 | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
SANDHILL ENERGY CENTER STG 5C |  | SANDHSYD_SH_5C | CC | GAS | OPER | CONV | TRAVIS | SOUTH | 2004-09-01 | 191 | 139 | 139 | 139 | 139 | 139 | 150 | 150 | 150 | 150 | 150 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148 | 148
SILAS RAY CTG 10 |  | SILASRAY_SILAS_10 | GT | GAS | OPER | CONV | CAMERON | COASTAL | 2004-01-01 | 60.5 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
SILAS RAY POWER CTG 9 |  | SILASRAY_SILAS_9 | CC | GAS | OPER | CONV | CAMERON | COASTAL | 1996-01-01 | 50 | 38 | 38 | 38 | 38 | 38 | 49 | 49 | 49 | 49 | 49 | 40 | 40 | 40 | 40 | 40 | 38 | 38 | 38 | 38 | 38
SILAS RAY POWER STG 6 |  | SILASRAY_SILAS_6 | CC | GAS | OPER | CONV | CAMERON | COASTAL | 1962-03-02 | 25 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
SIM GIDEON STG 1 |  | GIDEON_GIDEONG1 | ST | GAS | OPER | CONV | BASTROP | SOUTH | 1965-05-15 | 136 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
SIM GIDEON STG 2 |  | GIDEON_GIDEONG2 | ST | GAS | OPER | CONV | BASTROP | SOUTH | 1968-03-01 | 136 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 133 | 133 | 133 | 133 | 133 | 135 | 135 | 135 | 135 | 135
SIM GIDEON STG 3 |  | GIDEON_GIDEONG3 | ST | GAS | OPER | CONV | BASTROP | SOUTH | 1972-05-01 | 351 | 336 | 336 | 336 | 336 | 336 | 340 | 340 | 340 | 340 | 340 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336 | 336
SKY GLOBAL POWER ONE IC A |  | SKY1_SKY1A | IC | GAS | OPER | CONV | COLORADO | SOUTH | 2016-02-10 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SKY GLOBAL POWER ONE IC B |  | SKY1_SKY1B | IC | GAS | OPER | CONV | COLORADO | SOUTH | 2016-02-10 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
SPENCER STG U4 (AS OF 10/24/2022, AVAILABLE 3/1 THROUGH 11/30) |  | SPNCER_SPNCE_4 | ST | GAS | MOTH-SEA | CONV | DENTON | NORTH | 1966-08-18 | 61 | 57 | 57 | 57 | 57 | 57 | 0 | 0 | 0 | 0 | 0 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
SPENCER STG U5 (AS OF 10/24/2022, AVAILABLE 3/1 THROUGH 11/30) |  | SPNCER_SPNCE_5 | ST | GAS | MOTH-SEA | CONV | DENTON | NORTH | 1973-05-30 | 65 | 61 | 61 | 61 | 61 | 61 | 0 | 0 | 0 | 0 | 0 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61
STRYKER CREEK STG 1 |  | SCSES_UNIT1A | ST | GAS | OPER | CONV | CHEROKEE | NORTH | 1958-06-26 | 177 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167 | 167
STRYKER CREEK STG 2 |  | SCSES_UNIT2 | ST | GAS | OPER | CONV | CHEROKEE | NORTH | 1965-12-21 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502 | 502
T H WHARTON CTG 1 |  | THW_THWGT_1 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1967-07-31 | 16.32 | 14 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
T H WHARTON POWER CTG 31 |  | THW_THWGT31 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3
T H WHARTON POWER CTG 32 |  | THW_THWGT32 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3
T H WHARTON POWER CTG 33 |  | THW_THWGT33 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3
T H WHARTON POWER CTG 34 |  | THW_THWGT34 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3
T H WHARTON POWER CTG 41 |  | THW_THWGT41 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3
T H WHARTON POWER CTG 42 |  | THW_THWGT42 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1972-07-31 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3 | 51.3
T H WHARTON POWER CTG 43 |  | THW_THWGT43 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1974-08-16 | 62 | 54 | 54 | 54 | 54 | 54 | 62 | 62 | 62 | 62 | 62 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
T H WHARTON POWER CTG 44 |  | THW_THWGT44 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1974-08-16 | 62 | 54 | 54 | 54 | 54 | 54 | 62 | 62 | 62 | 62 | 62 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
T H WHARTON POWER CTG 51 |  | THW_THWGT51 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON POWER CTG 52 |  | THW_THWGT52 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON POWER CTG 53 |  | THW_THWGT53 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON POWER CTG 54 |  | THW_THWGT54 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON POWER CTG 55 |  | THW_THWGT55 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON POWER CTG 56 |  | THW_THWGT56 | GT | GAS | OPER | CONV | HARRIS | HOUSTON | 1975-11-21 | 85 | 56 | 56 | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 65 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
T H WHARTON POWER STG 3 |  | THW_THWST_3 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1974-08-16 | 113.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 109 | 109 | 109 | 109 | 109 | 110 | 110 | 110 | 110 | 110
T H WHARTON POWER STG 4 |  | THW_THWST_4 | CC | GAS | OPER | CONV | HARRIS | HOUSTON | 1974-08-16 | 113.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 109 | 109 | 109 | 109 | 109 | 110 | 110 | 110 | 110 | 110
TEXAS CITY POWER CTG A |  | TXCTY_CTA | CC | GAS | OPER | CONV | GALVESTON | HOUSTON | 2000-01-01 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 99.1 | 99.1 | 99.1 | 99.1 | 99.1
TEXAS CITY POWER CTG B |  | TXCTY_CTB | CC | GAS | OPER | CONV | GALVESTON | HOUSTON | 2000-01-01 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 99.1 | 99.1 | 99.1 | 99.1 | 99.1
TEXAS CITY POWER CTG C |  | TXCTY_CTC | CC | GAS | OPER | CONV | GALVESTON | HOUSTON | 2000-01-01 | 129.06 | 80.3 | 80.3 | 80.3 | 80.3 | 80.3 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 100.6 | 100.6 | 100.6 | 100.6 | 100.6 | 99.1 | 99.1 | 99.1 | 99.1 | 99.1
TEXAS CITY POWER STG |  | TXCTY_ST | CC | GAS | OPER | CONV | GALVESTON | HOUSTON | 2000-01-01 | 143.65 | 124.9 | 124.9 | 124.9 | 124.9 | 124.9 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5 | 131.5
TEXAS GULF SULPHUR CTG 1 |  | TGS_GT01 | GT | GAS | OPER | CONV | WHARTON | SOUTH | 1985-04-25 | 94 | 75 | 75 | 75 | 75 | 75 | 80 | 80 | 80 | 80 | 80 | 76 | 76 | 76 | 76 | 76 | 77 | 77 | 77 | 77 | 77
TIMMERMAN POWER PLANT U1 |  | TIMPP_AGR1 | IC | GAS | OPER | CONV | CALDWELL | SOUTH | 2025-08-14 | 37.67 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
TIMMERMAN POWER PLANT U2 |  | TIMPP_AGR2 | IC | GAS | OPER | CONV | CALDWELL | SOUTH | 2025-08-14 | 56.51 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4
TIMMERMAN POWER PLANT U3 |  | TIMPP_AGR3 | IC | GAS | OPER | CONV | CALDWELL | SOUTH | 2025-08-14 | 37.67 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
TIMMERMAN POWER PLANT U4 |  | TIMPP_AGR4 | IC | GAS | OPER | CONV | CALDWELL | SOUTH | 2025-08-14 | 56.51 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4 | 56.4
TRINIDAD STG 6 |  | TRSES_UNIT6 | ST | GAS | OPER | CONV | HENDERSON | NORTH | 1965-05-26 | 239 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235 | 235
TOPAZ POWER PLANT U1 |  | TOPAZ_UNIT1 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U2 |  | TOPAZ_UNIT2 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U3 |  | TOPAZ_UNIT3 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U4 |  | TOPAZ_UNIT4 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U5 |  | TOPAZ_UNIT5 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U6 |  | TOPAZ_UNIT6 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U7 |  | TOPAZ_UNIT7 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U8 |  | TOPAZ_UNIT8 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U9 |  | TOPAZ_UNIT9 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
TOPAZ POWER PLANT U10 |  | TOPAZ_UNIT10 | GT | GAS | OPER | CONV | GALVESTON | HOUSTON | 2021-10-14 | 60.5 | 44.5 | 44.5 | 44.5 | 44.5 | 44.5 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 45.1 | 45.1 | 45.1 | 45.1 | 45.1 | 45.4 | 45.4 | 45.4 | 45.4 | 45.4
V H BRAUNIG CTG 5 |  | BRAUNIG_VHB6CT5 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2009-10-02 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 6 |  | BRAUNIG_VHB6CT6 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2009-10-02 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 7 |  | BRAUNIG_VHB6CT7 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2009-10-02 | 64.5 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
V H BRAUNIG CTG 8 |  | BRAUNIG_VHB6CT8 | GT | GAS | OPER | CONV | BEXAR | SOUTH | 2009-10-02 | 64.5 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47
VICTORIA CITY (CITYVICT) CTG 1 |  | CITYVICT_CTG01 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2020-02-06 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
VICTORIA CITY (CITYVICT) CTG 2 |  | CITYVICT_CTG02 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2020-02-06 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
VICTORIA PORT (VICTPORT) CTG 1 |  | VICTPORT_CTG01 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2019-09-30 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
VICTORIA PORT (VICTPORT) CTG 2 |  | VICTPORT_CTG02 | GT | GAS | OPER | CONV | VICTORIA | SOUTH | 2019-09-30 | 60.5 | 44 | 44 | 44 | 44 | 44 | 49.8 | 49.8 | 49.8 | 49.8 | 49.8 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.5 | 46.5 | 46.5 | 46.5 | 46.5
VICTORIA POWER CTG 6 |  | VICTORIA_VICTORG6 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2009-10-15 | 196.86 | 160 | 160 | 160 | 160 | 160 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
VICTORIA POWER STG 5 |  | VICTORIA_VICTORG5 | CC | GAS | OPER | CONV | VICTORIA | SOUTH | 2009-10-15 | 180.2 | 125 | 125 | 125 | 125 | 125 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
W A PARISH CTG 1 |  | WAP_WAPGT_1 | GT | GAS | OPER | CONV | FORT BEND | HOUSTON | 1967-07-31 | 16.32 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
W A PARISH STG 1 |  | WAP_WAP_G1 | ST | GAS | OPER | CONV | FORT BEND | HOUSTON | 1958-06-01 | 187.85 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH STG 2 |  | WAP_WAP_G2 | ST | GAS | OPER | CONV | FORT BEND | HOUSTON | 1958-12-20 | 187.85 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169 | 169
W A PARISH STG 3 |  | WAP_WAP_G3 | ST | GAS | OPER | CONV | FORT BEND | HOUSTON | 1961-03-15 | 299.2 | 240 | 240 | 240 | 240 | 240 | 258 | 258 | 258 | 258 | 258 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246 | 246
W A PARISH STG 4 |  | WAP_WAP_G4 | ST | GAS | OPER | CONV | FORT BEND | HOUSTON | 1968-06-01 | 580.5 | 527 | 527 | 527 | 527 | 527 | 552 | 552 | 552 | 552 | 552 | 536 | 536 | 536 | 536 | 536 | 536 | 536 | 536 | 536 | 536
WICHITA FALLS CTG 1 |  | WFCOGEN_UNIT1 | CC | GAS | OPER | CONV | WICHITA | WEST | 1987-06-19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
WICHITA FALLS CTG 2 |  | WFCOGEN_UNIT2 | CC | GAS | OPER | CONV | WICHITA | WEST | 1987-06-19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
WICHITA FALLS CTG 3 |  | WFCOGEN_UNIT3 | CC | GAS | OPER | CONV | WICHITA | WEST | 1987-06-19 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19
WINCHESTER POWER PARK CTG 1 |  | WIPOPA_WPP_G1 | GT | GAS | OPER | CONV | FAYETTE | SOUTH | 2009-05-31 | 60.5 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK CTG 2 |  | WIPOPA_WPP_G2 | GT | GAS | OPER | CONV | FAYETTE | SOUTH | 2009-05-31 | 60.5 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK CTG 3 |  | WIPOPA_WPP_G3 | GT | GAS | OPER | CONV | FAYETTE | SOUTH | 2009-05-31 | 60.5 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WINCHESTER POWER PARK CTG 4 |  | WIPOPA_WPP_G4 | GT | GAS | OPER | CONV | FAYETTE | SOUTH | 2009-05-31 | 60.5 | 44 | 44 | 44 | 44 | 44 | 46 | 46 | 46 | 46 | 46 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44
WISE-TRACTEBEL POWER CTG 1 |  | WCPP_CT1 | CC | GAS | OPER | CONV | WISE | NORTH | 2004-01-03 | 275 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 244.4 | 244.4 | 244.4 | 244.4 | 244.4 | 245.4 | 245.4 | 245.4 | 245.4 | 245.4
WISE-TRACTEBEL POWER CTG 2 |  | WCPP_CT2 | CC | GAS | OPER | CONV | WISE | NORTH | 2004-01-03 | 275 | 241.4 | 241.4 | 241.4 | 241.4 | 241.4 | 263.8 | 263.8 | 263.8 | 263.8 | 263.8 | 244.4 | 244.4 | 244.4 | 244.4 | 244.4 | 245.4 | 245.4 | 245.4 | 245.4 | 245.4
WISE-TRACTEBEL POWER STG 1 |  | WCPP_ST1 | CC | GAS | OPER | CONV | WISE | NORTH | 2004-01-03 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298 | 298
WOLF HOLLOW POWER CTG 1 |  | WHCCS_CT1 | CC | GAS | OPER | CONV | HOOD | NORTH | 2002-07-24 | 264.5 | 238.5 | 238.5 | 238.5 | 238.5 | 238.5 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 240.4 | 245.3 | 245.3 | 245.3 | 245.3 | 245.3
WOLF HOLLOW POWER CTG 2 |  | WHCCS_CT2 | CC | GAS | OPER | CONV | HOOD | NORTH | 2002-07-24 | 264.5 | 230.5 | 230.5 | 230.5 | 230.5 | 230.5 | 235.4 | 235.4 | 235.4 | 235.4 | 235.4 | 234.4 | 234.4 | 234.4 | 234.4 | 234.4 | 245.3 | 245.3 | 245.3 | 245.3 | 245.3
WOLF HOLLOW POWER STG |  | WHCCS_STG | CC | GAS | OPER | CONV | HOOD | NORTH | 2002-07-24 | 300 | 268 | 268 | 268 | 268 | 268 | 269 | 269 | 269 | 269 | 269 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270
WOLF HOLLOW 2 CTG 4 |  | WHCCS2_CT4 | CC | GAS | OPER | CONV | HOOD | NORTH | 2017-05-02 | 360 | 327.8 | 327.8 | 327.8 | 327.8 | 327.8 | 353.3 | 353.3 | 353.3 | 353.3 | 353.3 | 330.6 | 330.6 | 330.6 | 330.6 | 330.6 | 330.8 | 330.8 | 330.8 | 330.8 | 330.8
WOLF HOLLOW 2 CTG 5 |  | WHCCS2_CT5 | CC | GAS | OPER | CONV | HOOD | NORTH | 2017-05-02 | 360 | 329.3 | 329.3 | 329.3 | 329.3 | 329.3 | 354.6 | 354.6 | 354.6 | 354.6 | 354.6 | 331.1 | 331.1 | 331.1 | 331.1 | 331.1 | 331.3 | 331.3 | 331.3 | 331.3 | 331.3
WOLF HOLLOW 2 STG 6 |  | WHCCS2_STG6 | CC | GAS | OPER | CONV | HOOD | NORTH | 2017-05-02 | 511.2 | 446.3 | 446.3 | 446.3 | 446.3 | 446.3 | 473.1 | 473.1 | 473.1 | 473.1 | 473.1 | 456.9 | 456.9 | 456.9 | 456.9 | 456.9 | 458.8 | 458.8 | 458.8 | 458.8 | 458.8
NACOGDOCHES POWER |  | NACPW_UNIT1 | ST | BIOMASS | OPER | CONV | NACOGDOCHES | NORTH | 2012-06-22 | 116.45 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
FARMERS BRANCH LANDFILL GAS TO ENERGY |  | HBR_2UNITS | ST | BIOMASS | OPER | CONV-SODG | DENTON | NORTH | 2011-08-01 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
GRAND PRAIRIE LFG |  | TRIRA_1UNIT | ST | BIOMASS | OPER | CONV-SODG | DALLAS | NORTH | 2015-03-20 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
NELSON GARDENS LFG |  | 78252_4UNITS | ST | BIOMASS | OPER | CONV-SODG | BEXAR | SOUTH | 2013-12-31 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2
WM RENEWABLE-AUSTIN LFG |  | SPRIN_4UNITS | ST | BIOMASS | OPER | CONV-SODG | TRAVIS | SOUTH | 2007-11-21 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4 | 6.4
WM RENEWABLE-MESQUITE CREEK LFG |  | FREIH_2UNITS | ST | BIOMASS | OPER | CONV-SODG | COMAL | SOUTH | 2011-08-01 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2 | 3.2
WM RENEWABLE-WESTSIDE LFG |  | WSTHL_3UNITS | ST | BIOMASS | OPER | CONV-SODG | PARKER | NORTH | 2010-02-05 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8 | 4.8
FRIENDSWOOD G CTG 2 | 24INR0456 | FEGC_CTG2 | GT | GAS | OPER-SYN | CONV | HARRIS | HOUSTON | 2026-02-14 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9
FRIENDSWOOD G CTG 3 | 24INR0456 | FEGC_CTG3 | GT | GAS | OPER-SYN | CONV | HARRIS | HOUSTON | 2026-02-14 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9
FRIENDSWOOD G CTG 4 | 24INR0456 | FEGC_CTG4 | GT | GAS | OPER-SYN | CONV | HARRIS | HOUSTON | 2026-02-14 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9 | 47.9
OLNEY AGR1 | 24INR0647 | OLNEYTN_AGR1 | IC | DIESEL | OPER-SYN | CONV-DGR | YOUNG | WEST | 2025-12-12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
AMISTAD HYDRO 1 |  | AMISTAD_AMISTAG1 | HY | HYDRO | OPER | CONV | VAL VERDE | WEST | 1983-06-01 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AMISTAD HYDRO 2 |  | AMISTAD_AMISTAG2 | HY | HYDRO | OPER | CONV | VAL VERDE | WEST | 1983-10-01 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9 | 37.9
AUSTIN HYDRO 1 |  | AUSTPL_AUSTING1 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1940-04-01 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
AUSTIN HYDRO 2 |  | AUSTPL_AUSTING2 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1940-04-01 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
BUCHANAN HYDRO 1 |  | BUCHAN_BUCHANG1 | HY | HYDRO | OPER | CONV | LLANO | SOUTH | 1938-01-01 | 18.3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN HYDRO 2 |  | BUCHAN_BUCHANG2 | HY | HYDRO | OPER | CONV | LLANO | SOUTH | 1938-01-01 | 18.3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BUCHANAN HYDRO 3 |  | BUCHAN_BUCHANG3 | HY | HYDRO | OPER | CONV | LLANO | SOUTH | 1950-05-19 | 18.3 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
DENISON DAM 1 |  | DNDAM_DENISOG1 | HY | HYDRO | OPER | CONV | GRAYSON | NORTH | 1944-03-01 | 50.8 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
DENISON DAM 2 |  | DNDAM_DENISOG2 | HY | HYDRO | OPER | CONV | GRAYSON | NORTH | 1948-03-04 | 50.8 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5 | 49.5
EAGLE PASS HYDRO |  | EAGLE_HY_EAGLE_HY1 | HY | HYDRO | OPER | CONV-TGR | MAVERICK | SOUTH | 1928-01-01 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6 | 9.6
FALCON HYDRO 1 |  | FALCON_FALCONG1 | HY | HYDRO | OPER | CONV | STARR | SOUTH | 1954-10-11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 2 |  | FALCON_FALCONG2 | HY | HYDRO | OPER | CONV | STARR | SOUTH | 1954-10-11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
FALCON HYDRO 3 |  | FALCON_FALCONG3 | HY | HYDRO | OPER | CONV | STARR | SOUTH | 1954-10-11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
GRANITE SHOALS HYDRO 1 |  | WIRTZ_WIRTZ_G1 | HY | HYDRO | OPER | CONV | BURNET | SOUTH | 1951-06-28 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
GRANITE SHOALS HYDRO 2 |  | WIRTZ_WIRTZ_G2 | HY | HYDRO | OPER | CONV | BURNET | SOUTH | 1951-08-03 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29
GUADALUPE BLANCO RIVER AUTH-CANYON |  | CANYHY_CANYHYG1 | HY | HYDRO | OPER | CONV-TGR | COMAL | SOUTH | 1928-01-01 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6
INKS HYDRO 1 |  | INKSDA_INKS_G1 | HY | HYDRO | OPER | CONV | LLANO | SOUTH | 1938-01-01 | 15 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
MARBLE FALLS HYDRO 1 |  | MARBFA_MARBFAG1 | HY | HYDRO | OPER | CONV | BURNET | SOUTH | 1951-10-10 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
MARBLE FALLS HYDRO 2 |  | MARBFA_MARBFAG2 | HY | HYDRO | OPER | CONV | BURNET | SOUTH | 1951-09-25 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
MARSHALL FORD HYDRO 1 |  | MARSFO_MARSFOG1 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1941-01-01 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD HYDRO 2 |  | MARSFO_MARSFOG2 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1941-01-01 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
MARSHALL FORD HYDRO 3 |  | MARSFO_MARSFOG3 | HY | HYDRO | OPER | CONV | TRAVIS | SOUTH | 1941-01-01 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
WHITNEY DAM HYDRO |  | WND_WHITNEY1 | HY | HYDRO | OPER | CONV | BOSQUE | NORTH | 1953-01-01 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
WHITNEY DAM HYDRO 2 |  | WND_WHITNEY2 | HY | HYDRO | OPER | CONV | BOSQUE | NORTH | 1953-01-01 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
GUADALUPE BLANCO RIVER AUTH-MCQUEENEY |  | MCQUE_5UNITS | HY | HYDRO | OPER | CONV-SODG | GUADALUPE | SOUTH | 1928-01-01 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
GUADALUPE BLANCO RIVER AUTH-SCHUMANSVILLE |  | SCHUM_2UNITS | HY | HYDRO | OPER | CONV-SODG | GUADALUPE | SOUTH | 1928-01-01 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6 | 3.6
ANTELOPE IC 1 |  | AEEC_ANTLP_1 | IC | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 56.04 | 54 | 54 | 54 | 54 | 54 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
ANTELOPE IC 2 |  | AEEC_ANTLP_2 | IC | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 56.04 | 54 | 54 | 54 | 54 | 54 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
ANTELOPE IC 3 |  | AEEC_ANTLP_3 | IC | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 56.04 | 54 | 54 | 54 | 54 | 54 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
ELK STATION CTG 1 |  | AEEC_ELK_1 | GT | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 202 | 190 | 190 | 190 | 190 | 190 | 200 | 200 | 200 | 200 | 200 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
ELK STATION CTG 2 |  | AEEC_ELK_2 | GT | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 202 | 190 | 190 | 190 | 190 | 190 | 200 | 200 | 200 | 200 | 200 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
ELK STATION CTG 3 |  | AEEC_ELK_3 | GT | GAS | OPER | SWGR-AVA | HALE | PANHANDLE | 2016-04-01 | 202 | 190 | 190 | 190 | 190 | 190 | 200 | 200 | 200 | 200 | 200 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
TENASKA FRONTIER STATION CTG 1 |  | FTR_FTR_G1 | CC | GAS | OPER | SWGR-AVA | GRIMES | NORTH | 2000-09-17 | 185 | 160 | 160 | 160 | 160 | 160 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA FRONTIER STATION CTG 2 |  | FTR_FTR_G2 | CC | GAS | OPER | SWGR-AVA | GRIMES | NORTH | 2000-09-17 | 185 | 160 | 160 | 160 | 160 | 160 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA FRONTIER STATION CTG 3 |  | FTR_FTR_G3 | CC | GAS | OPER | SWGR-AVA | GRIMES | NORTH | 2000-09-17 | 185 | 160 | 160 | 160 | 160 | 160 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
TENASKA FRONTIER STATION STG 4 |  | FTR_FTR_G4 | CC | GAS | OPER | SWGR-AVA | GRIMES | NORTH | 2000-09-17 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400
TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1 | CC | GAS | OPER | SWGR-AVA | RUSK | NORTH | 2001-07-21 | 179 | 156 | 156 | 156 | 156 | 156 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2 | CC | GAS | OPER | SWGR-AVA | RUSK | NORTH | 2001-07-21 | 179 | 135 | 135 | 135 | 135 | 135 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179 | 179
TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3 | CC | GAS | OPER | SWGR-AVA | RUSK | NORTH | 2001-07-21 | 179 | 153 | 153 | 153 | 153 | 153 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4 | CC | GAS | OPER | SWGR-AVA | RUSK | NORTH | 2001-07-21 | 400 | 400 | 400 | 400 | 400 | 400 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389 | 389
TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101 | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 185 | 151 | 151 | 151 | 151 | 151 | 185 | 185 | 185 | 185 | 185 | 162 | 162 | 162 | 162 | 162 | 154 | 154 | 154 | 154 | 154
TENASKA KIAMICHI STATION 1CT201 |  | KMCHI_1CT201 | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 185 | 148 | 148 | 148 | 148 | 148 | 185 | 185 | 185 | 185 | 185 | 158 | 158 | 158 | 158 | 158 | 151 | 151 | 151 | 151 | 151
TENASKA KIAMICHI STATION 1ST |  | KMCHI_1ST | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 330 | 310 | 310 | 310 | 310 | 310 | 330 | 330 | 330 | 330 | 330 | 322 | 322 | 322 | 322 | 322 | 312 | 312 | 312 | 312 | 312
TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101 | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 185 | 150 | 150 | 150 | 150 | 150 | 185 | 185 | 185 | 185 | 185 | 159 | 159 | 159 | 159 | 159 | 149 | 149 | 149 | 149 | 149
TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201 | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 185 | 152 | 152 | 152 | 152 | 152 | 185 | 185 | 185 | 185 | 185 | 161 | 161 | 161 | 161 | 161 | 150 | 150 | 150 | 150 | 150
TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST | CC | GAS | OPER | SWGR-AVA | FANNIN | NORTH | 2003-04-01 | 330 | 311 | 311 | 311 | 311 | 311 | 330 | 330 | 330 | 330 | 330 | 323 | 323 | 323 | 323 | 323 | 317 | 317 | 317 | 317 | 317
ANTELOPE IC 1 |  | AEEC_ANTLP_1_UNAVAIL | IC | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -56.04 | -54 | -54 | -54 | -54 | -54 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56 | -56
ANTELOPE IC 2 |  | AEEC_ANTLP_2_UNAVAIL | IC | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -56.04 | -54 | -54 | -54 | -54 | -54 | 0 | 0 | 0 | -56 | -56 | -56 | 0 | 0 | 0 | -56 | -56 | -56 | -56 | -56 | -56
ANTELOPE IC 3 |  | AEEC_ANTLP_3_UNAVAIL | IC | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -56.04 | -54 | -54 | -54 | -54 | -54 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -56 | -56 | -56 | -56 | -56
ELK STATION CTG 1 |  | AEEC_ELK_1_UNAVAIL | GT | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -202 | -190 | -190 | -190 | -190 | -190 | -200 | -200 | -200 | -200 | -200 | 0 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195
ELK STATION CTG 2 |  | AEEC_ELK_2_UNAVAIL | GT | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -202 | -190 | -190 | -190 | -190 | -190 | -200 | -200 | -200 | -200 | -200 | 0 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195 | -195
ELK STATION CTG 3 |  | AEEC_ELK_3_UNAVAIL | GT | GAS | OPER | SWGR-UNA | HALE | PANHANDLE | 2016-04-01 | -202 | -190 | -190 | -190 | -190 | -190 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -195 | -195 | -195 | -195 | -195
TENASKA GATEWAY STATION CTG 1 |  | TGCCS_CT1_UNAVAIL | CC | GAS | OPER | SWGR-UNA | RUSK | NORTH | 2001-07-21 | -179 | 0 | -156 | -156 | -156 | 0 | 0 | -162 | -162 | -162 | 0 | 0 | 0 | -162 | -162 | -162 | 0 | -162 | -162 | -162 | 0
TENASKA GATEWAY STATION CTG 2 |  | TGCCS_CT2_UNAVAIL | CC | GAS | OPER | SWGR-UNA | RUSK | NORTH | 2001-07-21 | -179 | -135 | -135 | -135 | -135 | -135 | -179 | -179 | -179 | -179 | -179 | -179 | -179 | -179 | -179 | -179 | 0 | 0 | 0 | 0 | -179
TENASKA GATEWAY STATION CTG 3 |  | TGCCS_CT3_UNAVAIL | CC | GAS | OPER | SWGR-UNA | RUSK | NORTH | 2001-07-21 | -179 | -153 | -153 | -153 | -153 | 0 | -178 | -178 | -178 | -178 | 0 | -178 | -178 | -178 | -178 | -178 | -178 | 0 | 0 | 0 | 0
TENASKA GATEWAY STATION STG 4 |  | TGCCS_UNIT4_UNAVAIL | CC | GAS | OPER | SWGR-UNA | RUSK | NORTH | 2001-07-21 | -400 | -400 | -400 | -400 | -400 | -400 | -389 | -389 | -389 | -389 | -389 | 0 | -389 | -389 | -389 | -389 | 0 | 0 | 0 | 0 | 0
TENASKA KIAMICHI STATION 2CT101 |  | KMCHI_2CT101_UNAVAIL | CC | GAS | OPER | SWGR-UNA | FANNIN | NORTH | 2003-04-01 | -185 | -150 | -150 | -150 | -150 | -150 | -185 | -185 | -185 | -185 | -185 | -159 | -159 | -159 | -159 | -159 | -149 | -149 | -149 | -149 | -149
TENASKA KIAMICHI STATION 2CT201 |  | KMCHI_2CT201_UNAVAIL | CC | GAS | OPER | SWGR-UNA | FANNIN | NORTH | 2003-04-01 | -185 | -152 | -152 | -152 | -152 | -152 | 0 | 0 | -185 | -185 | -185 | 0 | 0 | 0 | -161 | -161 | 0 | 0 | -150 | -150 | -150
TENASKA KIAMICHI STATION 2ST |  | KMCHI_2ST_UNAVAIL | CC | GAS | OPER | SWGR-UNA | FANNIN | NORTH | 2003-04-01 | -330 | -311 | -311 | -311 | -311 | -311 | 0 | 0 | -330 | -330 | -330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TENASKA KIAMICHI STATION 1CT101 |  | KMCHI_1CT101_UNAVAIL | CC | GAS | OPER | SWGR-UNA | FANNIN | NORTH | 2003-04-01 | -185 | -151 | -151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AGUAYO WIND U1 |  | AGUAYO_UNIT1 | WT | WIND-O | OPER | CONV | MILLS | NORTH | 2023-10-17 | 193.5 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9 | 192.9
AMADEUS WIND 1 U1 |  | AMADEUS1_UNIT1 | WT | WIND-O | OPER | CONV | FISHER | WEST | 2021-04-05 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7 | 36.7
AMADEUS WIND 1 U2 |  | AMADEUS1_UNIT2 | WT | WIND-O | OPER | CONV | FISHER | WEST | 2021-04-05 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8 | 35.8
AMADEUS WIND 2 U1 |  | AMADEUS2_UNIT3 | WT | WIND-O | OPER | CONV | FISHER | WEST | 2021-04-05 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7 | 177.7
ANACACHO WIND |  | ANACACHO_ANA | WT | WIND-O | OPER | CONV | KINNEY | SOUTH | 2012-12-27 | 99.83 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
ANCHOR WIND U2 |  | ANCHOR_WIND2 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2024-04-15 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
ANCHOR WIND U3 |  | ANCHOR_WIND3 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2024-04-15 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
ANCHOR WIND U4 |  | ANCHOR_WIND4 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2024-04-15 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7 | 38.7
ANCHOR WIND U5 |  | ANCHOR_WIND5 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2024-04-15 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3 | 19.3
APOGEE WIND U1 |  | APOGEE_UNIT1 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25
APOGEE WIND U2 |  | APOGEE_UNIT2 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
APOGEE WIND U3 |  | APOGEE_UNIT3 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
APOGEE WIND U4 |  | APOGEE_UNIT4 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
APOGEE WIND U5 |  | APOGEE_UNIT5 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
APOGEE WIND U6 |  | APOGEE_UNIT6 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
APOGEE WIND U7 |  | APOGEE_UNIT7 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-19 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
APPALOOSA RUN WIND U1 |  | APPALOSA_UNIT1 | WT | WIND-O | OPER | CONV | UPTON | WEST | 2024-03-06 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9 | 157.9
APPALOOSA RUN WIND U2 |  | APPALOSA_UNIT2 | WT | WIND-O | OPER | CONV | UPTON | WEST | 2024-03-06 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
AQUILLA LAKE WIND U1 |  | AQUILLA_U1_23 | WT | WIND-O | OPER | CONV | HILL & LIMESTONE | NORTH | 2023-01-31 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
AQUILLA LAKE WIND U2 |  | AQUILLA_U1_28 | WT | WIND-O | OPER | CONV | HILL & LIMESTONE | NORTH | 2023-01-31 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4
AQUILLA LAKE 2 WIND U1 |  | AQUILLA_U2_23 | WT | WIND-O | OPER | CONV | HILL & LIMESTONE | NORTH | 2023-01-31 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7
AQUILLA LAKE 2 WIND U2 |  | AQUILLA_U2_28 | WT | WIND-O | OPER | CONV | HILL & LIMESTONE | NORTH | 2023-01-31 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8 | 143.8
AVIATOR WIND U1 |  | AVIATOR_UNIT1 | WT | WIND-O | OPER | CONV | COKE | WEST | 2021-06-22 | 180.12 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1
AVIATOR WIND U2 |  | AVIATOR_UNIT2 | WT | WIND-O | OPER | CONV | COKE | WEST | 2021-06-22 | 145.64 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6 | 145.6
AVIATOR WIND U3 |  | DEWOLF_UNIT1 | WT | WIND-O | OPER | CONV | COKE | WEST | 2021-06-22 | 199.26 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3 | 199.3
BLACKJACK CREEK WIND U1 |  | BLACKJAK_UNIT1 | WT | WIND-O | OPER | CONV | BEE | SOUTH | 2023-05-12 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BLACKJACK CREEK WIND U2 |  | BLACKJAK_UNIT2 | WT | WIND-O | OPER | CONV | BEE | SOUTH | 2023-05-12 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BAFFIN WIND UNIT1 |  | BAFFIN_UNIT1 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2016-06-24 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BAFFIN WIND UNIT2 |  | BAFFIN_UNIT2 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2016-06-24 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
BARROW RANCH (JUMBO HILL WIND) 1 |  | BARROW_UNIT1 | WT | WIND-O | OPER | CONV | ANDREWS | WEST | 2021-09-07 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2 | 90.2
BARROW RANCH (JUMBO HILL WIND) 2 |  | BARROW_UNIT2 | WT | WIND-O | OPER | CONV | ANDREWS | WEST | 2021-09-07 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5
BARTON CHAPEL WIND |  | BRTSW_BCW1 | WT | WIND-O | OPER | CONV | JACK | NORTH | 2007-12-01 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BLUE SUMMIT WIND 1 A |  | BLSUMMIT_BLSMT1_5 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2013-12-16 | 132.84 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8 | 132.8
BLUE SUMMIT WIND 1 B |  | BLSUMMIT_BLSMT1_6 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2013-12-16 | 6.96 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
BLUE SUMMIT WIND 2 A |  | BLSUMMIT_UNIT2_25 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2020-04-06 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5 | 92.5
BLUE SUMMIT WIND 2 B |  | BLSUMMIT_UNIT2_17 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2020-04-06 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9 | 6.9
BLUE SUMMIT WIND 3 A |  | BLSUMIT3_UNIT_17 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2020-05-19 | 13.7 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4 | 13.4
BLUE SUMMIT WIND 3 B |  | BLSUMIT3_UNIT_25 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2020-05-19 | 186.5 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4
BOBCAT BLUFF WIND |  | BCATWIND_WIND_1 | WT | WIND-O | OPER | CONV | ARCHER | WEST | 2020-04-17 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
BRISCOE WIND |  | BRISCOE_WIND | WT | WIND-P | OPER | CONV | BRISCOE | PANHANDLE | 2015-11-13 | 149.85 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8
BRUENNING'S BREEZE A |  | BBREEZE_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2017-12-31 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BRUENNING'S BREEZE B |  | BBREEZE_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2017-12-31 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
BUCKTHORN WIND 1 A |  | BUCKTHRN_UNIT1 | WT | WIND-O | OPER | CONV | ERATH | NORTH | 2017-12-12 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9 | 44.9
BUCKTHORN WIND 1 B |  | BUCKTHRN_UNIT2 | WT | WIND-O | OPER | CONV | ERATH | NORTH | 2017-12-12 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7 | 55.7
BUFFALO GAP WIND 1 | 26INR0622 | BUFF_GAP_UNIT1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2006-04-21 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6 | 120.6
BUFFALO GAP WIND 2_1 | 26INR0625 | BUFF_GAP_UNIT2_1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2007-07-01 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5 | 115.5
BUFFALO GAP WIND 2_2 | 26INR0625 | BUFF_GAP_UNIT2_2 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2007-07-01 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117 | 117
BUFFALO GAP WIND 3 | 26INR0626 | BUFF_GAP_UNIT3 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2008-07-30 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2 | 170.2
BULL CREEK WIND U1 |  | BULLCRK_WND1 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2009-05-14 | 89 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88
BULL CREEK WIND U2 |  | BULLCRK_WND2 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2009-05-14 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
CABEZON WIND (RIO BRAVO I WIND) 1 A |  | CABEZON_WIND1 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2019-12-17 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
CABEZON WIND (RIO BRAVO I WIND) 1 B |  | CABEZON_WIND2 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2019-12-17 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4 | 122.4
CACTUS FLATS WIND U1 |  | CFLATS_U1 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-06-13 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4
CALLAHAN WIND |  | CALLAHAN_WND1 | WT | WIND-O | OPER | CONV | CALLAHAN | WEST | 2004-12-15 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1 | 123.1
CAMERON COUNTY WIND |  | CAMWIND_UNIT1 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2016-01-27 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165 | 165
CAMP SPRINGS WIND 1 |  | CSEC_CSECG1 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2007-05-26 | 134.42 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5 | 130.5
CAMP SPRINGS WIND 2 |  | CSEC_CSECG2 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2007-11-15 | 123.6 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
CANADIAN BREAKS WIND |  | CN_BRKS_UNIT_1 | WT | WIND-P | OPER | CONV | OLDHAM | PANHANDLE | 2019-12-17 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1
CAPRICORN RIDGE WIND 1 |  | CAPRIDGE_CR1 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2007-08-01 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7 | 231.7
CAPRICORN RIDGE WIND 2 |  | CAPRIDGE_CR2 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2007-08-01 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
CAPRICORN RIDGE WIND 3 |  | CAPRIDGE_CR3 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2008-02-15 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9
CAPRICORN RIDGE WIND 4 |  | CAPRIDG4_CR4 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2008-05-22 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
CEDRO HILL WIND 1 |  | CEDROHIL_CHW1 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2010-11-23 | 79.42 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7 | 77.7
CEDRO HILL WIND 2 |  | CEDROHIL_CHW2 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2010-11-23 | 78.04 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4 | 76.4
CHALUPA WIND |  | CHALUPA_UNIT1 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2021-06-10 | 173.25 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3 | 173.3
CHAMPION WIND U1 |  | CHAMPION_UNIT1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-01-28 | 97.51 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4 | 95.4
CHAMPION WIND U2 |  | CHAMPION_UNIT2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-01-28 | 18.1 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7
CHAMPION WIND U3 |  | CHAMPION_UNIT3 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-01-28 | 8.99 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8 | 8.8
CHAPMAN RANCH WIND IA (SANTA CRUZ) |  | SANTACRU_UNIT1 | WT | WIND-C | OPER | CONV | NUECES | COASTAL | 2017-07-11 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
CHAPMAN RANCH WIND IB (SANTA CRUZ) |  | SANTACRU_UNIT2 | WT | WIND-C | OPER | CONV | NUECES | COASTAL | 2017-07-11 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4 | 98.4
COTTON PLAINS WIND |  | COTPLNS_COTTONPL | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2017-01-12 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
CRANELL WIND |  | CRANELL_UNIT1 | WT | WIND-C | OPER | CONV | REFUGIO | COASTAL | 2022-01-27 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
CRAWFISH U1 |  | CRAWFISH_UNIT1 | WT | WIND-O | OPER | CONV | WHARTON | SOUTH | 2025-05-21 | 163.2 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159
DERMOTT WIND 1_1 |  | DERMOTT_UNIT1 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2017-08-01 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
DERMOTT WIND 1_2 |  | DERMOTT_UNIT2 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2017-08-01 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
DESERT SKY WIND 1 A |  | DSKYWND1_UNIT_1A | WT | WIND-O | OPER | CONV | PECOS | WEST | 2022-02-24 | 65.79 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1 | 53.1
DESERT SKY WIND 1 B |  | DSKYWND2_UNIT_2A | WT | WIND-O | OPER | CONV | PECOS | WEST | 2022-02-24 | 65.79 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
DESERT SKY WIND 2 A |  | DSKYWND1_UNIT_1B | WT | WIND-O | OPER | CONV | PECOS | WEST | 2022-02-24 | 23.93 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7 | 18.7
DESERT SKY WIND 2 B |  | DSKYWND2_UNIT_2B | WT | WIND-O | OPER | CONV | PECOS | WEST | 2022-02-24 | 14.74 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8
DOUG COLBECK'S CORNER (CONWAY) A |  | GRANDVW1_COLA | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2016-03-15 | 100.24 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
DOUG COLBECK'S CORNER (CONWAY) B |  | GRANDVW1_COLB | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2016-03-15 | 100.24 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2 | 100.2
EAST RAYMOND WIND (EL RAYO) U1 |  | EL_RAYO_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2021-06-11 | 101.2 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
EAST RAYMOND WIND (EL RAYO) U2 |  | EL_RAYO_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2021-06-11 | 99 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
ELBOW CREEK WIND |  | ELB_ELBCREEK | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2008-11-21 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
ELECTRA WIND 1 |  | DIGBY_UNIT1 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2016-10-17 | 101.31 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
ELECTRA WIND 2 |  | DIGBY_UNIT2 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2016-10-17 | 134.29 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
EL ALGODON ALTO W U1 |  | ALGODON_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2022-05-11 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6 | 171.6
EL ALGODON ALTO W U2 |  | ALGODON_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2022-05-11 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6 | 28.6
ESPIRITU WIND |  | CHALUPA_UNIT2 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2021-06-10 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2 | 25.2
FALVEZ ASTRA WIND |  | ASTRA_UNIT1 | WT | WIND-P | OPER | CONV | RANDALL | PANHANDLE | 2017-05-24 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2 | 163.2
FLAT TOP WIND I |  | FTWIND_UNIT_1 | WT | WIND-O | OPER | CONV | MILLS | NORTH | 2018-09-07 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
FLUVANNA RENEWABLE 1 A |  | FLUVANNA_UNIT1 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2017-11-20 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8 | 79.8
FLUVANNA RENEWABLE 1 B |  | FLUVANNA_UNIT2 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2017-11-20 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6 | 75.6
FOARD CITY WIND 1 A |  | FOARDCTY_UNIT1 | WT | WIND-O | OPER | CONV | FOARD | WEST | 2019-12-05 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5
FOARD CITY WIND 1 B |  | FOARDCTY_UNIT2 | WT | WIND-O | OPER | CONV | FOARD | WEST | 2019-12-05 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8 | 163.8
FOREST CREEK WIND |  | MCDLD_FCW1 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2007-03-01 | 125.19 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2
GOAT WIND |  | GOAT_GOATWIND | WT | WIND-O | OPER | CONV | STERLING | WEST | 2008-02-21 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
GOAT WIND 2 |  | GOAT_GOATWIN2 | WT | WIND-O | OPER | CONV | STERLING | WEST | 2010-04-14 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6 | 69.6
GOLDTHWAITE WIND 1 |  | GWEC_GWEC_G1 | WT | WIND-O | OPER | CONV | MILLS | NORTH | 2014-05-29 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
GOODNIGHT WIND U1 |  | GOODNIT1_UNIT1 | WT | WIND-P | OPER | CONV | ARMSTRONG | PANHANDLE | 2024-04-08 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121 | 121
GOODNIGHT WIND U2 |  | GOODNIT1_UNIT2 | WT | WIND-P | OPER | CONV | ARMSTRONG | PANHANDLE | 2024-04-08 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1 | 137.1
GOPHER CREEK WIND 1 |  | GOPHER_UNIT1 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2020-03-09 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 82
GOPHER CREEK WIND 2 |  | GOPHER_UNIT2 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2020-03-09 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76
GRANDVIEW WIND 1 (CONWAY) GV1A |  | GRANDVW1_GV1A | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-11-01 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4 | 107.4
GRANDVIEW WIND 1 (CONWAY) GV1B |  | GRANDVW1_GV1B | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-11-01 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
GREEN MOUNTAIN WIND (BRAZOS) U1 |  | BRAZ_WND_BRAZ_WND1 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2023-07-01 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
GREEN MOUNTAIN WIND (BRAZOS) U2 |  | BRAZ_WND_BRAZ_WND2 | WT | WIND-O | OPER | CONV | SCURRY | WEST | 2023-07-01 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4 | 62.4
GREEN PASTURES WIND I |  | GPASTURE_WIND_I | WT | WIND-O | OPER | CONV | BAYLOR | WEST | 2015-11-17 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
GRIFFIN TRAIL WIND U1 |  | GRIF_TRL_UNIT1 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-10-28 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7 | 98.7
GRIFFIN TRAIL WIND U2 |  | GRIF_TRL_UNIT2 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-10-28 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9 | 126.9
GULF WIND I |  | TGW_T1 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2021-05-06 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
GULF WIND II |  | TGW_T2 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2021-05-06 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
GUNSIGHT MOUNTAIN WIND |  | GUNMTN_G1 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2016-09-28 | 119.93 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9 | 119.9
HACKBERRY WIND |  | HWF_HWFG1 | WT | WIND-O | OPER | CONV | SHACKELFORD | WEST | 2008-12-21 | 165.6 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5 | 163.5
HEREFORD WIND G |  | HRFDWIND_WIND_G | WT | WIND-P | OPER | CONV | DEAF SMITH | PANHANDLE | 2014-10-23 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9 | 99.9
HEREFORD WIND V |  | HRFDWIND_WIND_V | WT | WIND-P | OPER | CONV | DEAF SMITH | PANHANDLE | 2014-10-23 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
HICKMAN (SANTA RITA WIND) 1 |  | HICKMAN_G1 | WT | WIND-O | OPER | CONV | REAGAN | WEST | 2018-05-09 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5 | 152.5
HICKMAN (SANTA RITA WIND) 2 |  | HICKMAN_G2 | WT | WIND-O | OPER | CONV | REAGAN | WEST | 2018-05-09 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5 | 147.5
HIDALGO & STARR WIND 11 |  | MIRASOLE_MIR11 | WT | WIND-O | OPER | CONV | HIDALGO | SOUTH | 2016-12-15 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
HIDALGO & STARR WIND 12 |  | MIRASOLE_MIR12 | WT | WIND-O | OPER | CONV | HIDALGO | SOUTH | 2016-12-15 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
HIDALGO & STARR WIND 21 |  | MIRASOLE_MIR21 | WT | WIND-O | OPER | CONV | HIDALGO | SOUTH | 2016-12-15 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
HIDALGO II WIND |  | MIRASOLE_MIR13 | WT | WIND-O | OPER | CONV | HIDALGO | SOUTH | 2021-07-30 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4 | 50.4
HIGH LONESOME W 1A |  | HI_LONE_WGR1A | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46 | 46
HIGH LONESOME W 1B |  | HI_LONE_WGR1B | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52
HIGH LONESOME W 1C |  | HI_LONE_WGR1C | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3
HIGH LONESOME W 2 |  | HI_LONE_WGR2 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5 | 122.5
HIGH LONESOME W 2A |  | HI_LONE_WGR2A | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3 | 25.3
HIGH LONESOME W 3 |  | HI_LONE_WGR3 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6 | 127.6
HIGH LONESOME W 4 |  | HI_LONE_WGR4 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2021-07-01 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
HORSE CREEK WIND 1 |  | HORSECRK_UNIT1 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2017-01-23 | 134.81 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
HORSE CREEK WIND 2 |  | HORSECRK_UNIT2 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2017-01-23 | 101.69 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9 | 98.9
HORSE HOLLOW WIND 1 |  | HHGT_HHOLLOW1 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2009-10-15 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213 | 213
HORSE HOLLOW WIND 2 |  | HHGT_HHOLLOW2 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2009-10-15 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184 | 184
HORSE HOLLOW WIND 3 |  | HHGT_HHOLLOW3 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2009-10-15 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5 | 223.5
HORSE HOLLOW WIND 4 |  | HHGT_HHOLLOW4 | WT | WIND-O | OPER | CONV | TAYLOR | WEST | 2009-10-15 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115
INADALE WIND 1 |  | INDL_INADALE1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-12-18 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
INADALE WIND 2 |  | INDL_INADALE2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-12-18 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
INDIAN MESA WIND |  | INDNNWP_INDNNWP2 | WT | WIND-O | OPER | CONV | PECOS | WEST | 2001-06-01 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4 | 90.4
INERTIA WIND U1 |  | INRT_W_UNIT1 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2023-11-01 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7 | 67.7
INERTIA WIND U2 |  | INRT_W_UNIT2 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2023-11-01 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
INERTIA WIND U3 |  | INRT_W_UNIT3 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2023-11-01 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9 | 205.9
JAVELINA I WIND 18 |  | BORDAS_JAVEL18 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2015-12-23 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7 | 19.7
JAVELINA I WIND 20 |  | BORDAS_JAVEL20 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2015-12-23 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230
JAVELINA II WIND 1 |  | BORDAS2_JAVEL2_A | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2017-02-03 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
JAVELINA II WIND 2 |  | BORDAS2_JAVEL2_B | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2017-02-03 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
JAVELINA II WIND 3 |  | BORDAS2_JAVEL2_C | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2017-02-03 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
JUMBO ROAD WIND 1 |  | HRFDWIND_JRDWIND1 | WT | WIND-P | OPER | CONV | DEAF SMITH | PANHANDLE | 2015-04-09 | 146.15 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2 | 146.2
JUMBO ROAD WIND 2 |  | HRFDWIND_JRDWIND2 | WT | WIND-P | OPER | CONV | DEAF SMITH | PANHANDLE | 2015-04-09 | 153.55 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
KARANKAWA WIND 1A |  | KARAKAW1_UNIT1 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2019-12-30 | 103.32 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
KARANKAWA WIND 1B |  | KARAKAW1_UNIT2 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2019-12-30 | 103.32 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3 | 103.3
KARANKAWA WIND 2 |  | KARAKAW2_UNIT3 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2019-12-30 | 100.42 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
KEECHI WIND |  | KEECHI_U1 | WT | WIND-O | OPER | CONV | JACK | NORTH | 2014-11-15 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
KING MOUNTAIN WIND (NE) |  | KING_NE_KINGNE | WT | WIND-O | OPER | CONV | UPTON | WEST | 2001-11-08 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
KING MOUNTAIN WIND (NW) |  | KING_NW_KINGNW | WT | WIND-O | OPER | CONV | UPTON | WEST | 2001-09-21 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
KING MOUNTAIN WIND (SE) |  | KING_SE_KINGSE | WT | WIND-O | OPER | CONV | UPTON | WEST | 2001-12-01 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5 | 40.5
KING MOUNTAIN WIND (SW) |  | KING_SW_KINGSW | WT | WIND-O | OPER | CONV | UPTON | WEST | 2001-08-12 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7
LANGFORD WIND POWER |  | LGD_LANGFORD | WT | WIND-O | OPER | CONV | TOM GREEN | WEST | 2009-10-31 | 159.96 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
LACY CREEK WIND U1 |  | LACY_CRK_UNIT1 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2024-04-02 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4 | 135.4
LACY CREEK WIND U2 |  | LACY_CRK_UNIT2 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2024-04-02 | 15.12 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
LACY CREEK WIND U3 |  | LACY_CRK_UNIT3 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2024-04-02 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2 | 138.2
LACY CREEK WIND U4 |  | LACY_CRK_UNIT4 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2024-04-02 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6 | 12.6
LAS MAJADAS WIND U1 |  | LMAJADAS_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2023-07-13 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
LAS MAJADAS WIND U2 |  | LMAJADAS_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2023-07-13 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
LAS MAJADAS WIND U3 |  | LMAJADAS_UNIT3 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2023-07-13 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6 | 138.6
LOCKETT WIND FARM |  | LOCKETT_UNIT1 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2019-09-19 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7 | 183.7
LOGANS GAP WIND I U1 |  | LGW_UNIT1 | WT | WIND-O | OPER | CONV | COMANCHE | NORTH | 2015-09-30 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3 | 106.3
LOGANS GAP WIND I U2 |  | LGW_UNIT2 | WT | WIND-O | OPER | CONV | COMANCHE | NORTH | 2015-09-30 | 103.85 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
LONE STAR WIND 1 (MESQUITE) |  | LNCRK_G83 | WT | WIND-O | OPER | CONV | SHACKELFORD | WEST | 2006-11-21 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194 | 194
LONE STAR WIND 2 (POST OAK) U1 |  | LNCRK2_G871 | WT | WIND-O | OPER | CONV | SHACKELFORD | WEST | 2007-09-15 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
LONE STAR WIND 2 (POST OAK) U2 |  | LNCRK2_G872 | WT | WIND-O | OPER | CONV | SHACKELFORD | WEST | 2007-09-15 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LONGHORN WIND NORTH U1 |  | LHORN_N_UNIT1 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2015-09-21 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LONGHORN WIND NORTH U2 |  | LHORN_N_UNIT2 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2015-09-21 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LORAINE WINDPARK I |  | LONEWOLF_G1 | WT | WIND-O | OPER | CONV | MITCHELL | WEST | 2010-02-16 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
LORAINE WINDPARK II |  | LONEWOLF_G2 | WT | WIND-O | OPER | CONV | MITCHELL | WEST | 2010-02-16 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51
LORAINE WINDPARK III |  | LONEWOLF_G3 | WT | WIND-O | OPER | CONV | MITCHELL | WEST | 2011-03-01 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5 | 25.5
LORAINE WINDPARK IV |  | LONEWOLF_G4 | WT | WIND-O | OPER | CONV | MITCHELL | WEST | 2011-03-01 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24
LOS VIENTOS III WIND |  | LV3_UNIT_1 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2015-01-29 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS IV WIND |  | LV4_UNIT_1 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2016-06-06 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
LOS VIENTOS V WIND |  | LV5_UNIT_1 | WT | WIND-O | OPER | CONV | STARR | SOUTH | 2016-09-01 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
LOS VIENTOS WIND I |  | LV1_LV1A | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2013-08-30 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
LOS VIENTOS WIND II |  | LV2_LV2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2013-08-30 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MAGIC VALLEY WIND (REDFISH) 1A |  | REDFISH_MV1A | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2012-09-27 | 99.83 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8 | 99.8
MAGIC VALLEY WIND (REDFISH) 1B |  | REDFISH_MV1B | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2012-09-27 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5 | 103.5
MARIAH DEL NORTE 1 |  | MARIAH_NORTE1 | WT | WIND-P | OPER | CONV | PARMER | PANHANDLE | 2017-03-08 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
MARIAH DEL NORTE 2 |  | MARIAH_NORTE2 | WT | WIND-P | OPER | CONV | PARMER | PANHANDLE | 2017-03-08 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
MAVERICK CREEK WIND WEST U1 |  | MAVCRK_W_UNIT1 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MAVERICK CREEK WIND WEST U2 |  | MAVCRK_W_UNIT2 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1 | 11.1
MAVERICK CREEK WIND WEST U3 |  | MAVCRK_W_UNIT3 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
MAVERICK CREEK WIND WEST U4 |  | MAVCRK_W_UNIT4 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | 22.2
MAVERICK CREEK WIND EAST U1 |  | MAVCRK_E_UNIT5 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
MAVERICK CREEK WIND EAST U2 |  | MAVCRK_E_UNIT6 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3 | 33.3
MAVERICK CREEK WIND EAST U3 |  | MAVCRK_E_UNIT7 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
MAVERICK CREEK WIND EAST U4 |  | MAVCRK_E_UNIT8 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
MAVERICK CREEK WIND EAST U5 |  | MAVCRK_E_UNIT9 | WT | WIND-O | OPER | CONV | CONCHO | WEST | 2022-03-29 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8 | 76.8
MCADOO WIND |  | MWEC_G1 | WT | WIND-P | OPER | CONV | DICKENS | PANHANDLE | 2008-07-31 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
MESQUITE CREEK WIND 1 |  | MESQCRK_WND1 | WT | WIND-O | OPER | CONV | DAWSON | WEST | 2015-04-15 | 105.61 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
MESQUITE CREEK WIND 2 |  | MESQCRK_WND2 | WT | WIND-O | OPER | CONV | DAWSON | WEST | 2015-04-15 | 105.61 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6 | 105.6
MIAMI WIND G1 |  | MIAM1_G1 | WT | WIND-P | OPER | CONV | ROBERTS | PANHANDLE | 2014-12-04 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
MIAMI WIND G2 |  | MIAM1_G2 | WT | WIND-P | OPER | CONV | ROBERTS | PANHANDLE | 2014-12-04 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3 | 144.3
MIDWAY WIND |  | MIDWIND_UNIT1 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2019-08-15 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8 | 162.8
MONTGOMERY RANCH WIND U1 |  | MONT_WND_UNIT1 | WT | WIND-O | OPER | CONV | FOARD | WEST | 2024-12-13 | 106.13 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9 | 105.9
MONTGOMERY RANCH WIND U2 |  | MONT_WND_UNIT2 | WT | WIND-O | OPER | CONV | FOARD | WEST | 2024-12-13 | 92.87 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7 | 92.7
NIELS BOHR WIND A (BEARKAT WIND A) |  | NBOHR_UNIT1 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2017-12-29 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6 | 196.6
NOTREES WIND 1 |  | NWF_NWF1 | WT | WIND-O | OPER | CONV | WINKLER | WEST | 2009-04-01 | 92.61 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6 | 92.6
NOTREES WIND 2 |  | NWF_NWF2 | WT | WIND-O | OPER | CONV | WINKLER | WEST | 2009-04-01 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
OCOTILLO WIND |  | OWF_OWF | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2008-11-01 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
OLD SETTLER WIND |  | COTPLNS_OLDSETLR | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2017-01-12 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
OVEJA WIND U1 |  | OVEJA_G1 | WT | WIND-O | OPER | CONV | IRION | WEST | 2021-10-20 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
OVEJA WIND U2 |  | OVEJA_G2 | WT | WIND-O | OPER | CONV | IRION | WEST | 2021-10-20 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
PALMAS ALTAS WIND |  | PALMWIND_UNIT1 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2020-11-12 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9 | 144.9
PANHANDLE WIND 1 U1 |  | PH1_UNIT1 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-07-30 | 109.15 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
PANHANDLE WIND 1 U2 |  | PH1_UNIT2 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-07-30 | 109.15 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2 | 109.2
PANHANDLE WIND 2 U1 |  | PH2_UNIT1 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-11-11 | 94.19 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
PANHANDLE WIND 2 U2 |  | PH2_UNIT2 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2014-11-11 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
PANTHER CREEK WIND 1 |  | PC_NORTH_PANTHER1 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2008-07-18 | 149.16 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
PANTHER CREEK WIND 2 |  | PC_SOUTH_PANTHER2 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2019-12-20 | 123.25 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
PANTHER CREEK WIND 3 A |  | PC_SOUTH_PANTH31 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2022-01-05 | 106.92 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9 | 106.9
PANTHER CREEK WIND 3 B |  | PC_SOUTH_PANTH32 | WT | WIND-O | OPER | CONV | HOWARD | WEST | 2022-01-05 | 108.54 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5 | 108.5
PAPALOTE CREEK WIND |  | PAP1_PAP1 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2009-09-04 | 179.85 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9 | 179.9
PAPALOTE CREEK WIND II |  | COTTON_PAP2 | WT | WIND-C | OPER | CONV | SAN PATRICIO | COASTAL | 2010-06-01 | 200.12 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1 | 200.1
PECOS WIND 1 (WOODWARD) |  | WOODWRD1_WOODWRD1 | WT | WIND-O | OPER | CONV | PECOS | WEST | 2001-07-31 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7 | 91.7
PECOS WIND 2 (WOODWARD) |  | WOODWRD2_WOODWRD2 | WT | WIND-O | OPER | CONV | PECOS | WEST | 2001-07-31 | 86 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8 | 85.8
PENASCAL WIND 1 |  | PENA_UNIT1 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2009-04-22 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8 | 160.8
PENASCAL WIND 2 |  | PENA_UNIT2 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2009-04-22 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6 | 141.6
PENASCAL WIND 3 |  | PENA3_UNIT3 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2011-08-02 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
PEYTON CREEK WIND |  | PEY_UNIT1 | WT | WIND-C | OPER | CONV | MATAGORDA | COASTAL | 2020-06-04 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2 | 151.2
PIONEER DJ WIND U1 |  | PIONR_DJ_UNIT1 | WT | WIND-O | OPER | CONV | MIDLAND | WEST | 2025-02-28 | 124.08 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1
PIONEER DJ WIND U2 |  | PIONR_DJ_UNIT2 | WT | WIND-O | OPER | CONV | MIDLAND | WEST | 2025-02-28 | 16.24 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2 | 16.2
PYRON WIND 1 |  | PYR_PYRON1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-12-23 | 128.47 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8
PYRON WIND 2 |  | PYR_PYRON2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-12-23 | 134.9 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2 | 134.2
RANCHERO WIND U1 |  | RANCHERO_UNIT1 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2020-05-04 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RANCHERO WIND U2 |  | RANCHERO_UNIT2 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2020-05-04 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RATTLESNAKE I WIND ENERGY CENTER G1 |  | RSNAKE_G1 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2015-09-21 | 109.15 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6 | 104.6
RATTLESNAKE I WIND ENERGY CENTER G2 |  | RSNAKE_G2 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2015-09-21 | 109.15 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7
RED CANYON WIND |  | RDCANYON_RDCNY1 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2006-04-15 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6 | 89.6
RELOJ DEL SOL WIND U1 |  | RELOJ_UNIT1 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2022-08-03 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
RELOJ DEL SOL WIND U2 |  | RELOJ_UNIT2 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2022-08-03 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
RELOJ DEL SOL WIND U3 |  | RELOJ_UNIT3 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2022-08-03 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1 | 83.1
RELOJ DEL SOL WIND U4 |  | RELOJ_UNIT4 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2022-08-03 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8 | 22.8
ROADRUNNER CROSSING WIND U1 |  | RRC_WIND_UNIT1 | WT | WIND-O | OPER | CONV | EASTLAND | NORTH | 2025-08-04 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1 | 94.1
ROADRUNNER CROSSING WIND U2 |  | RRC_WIND_UNIT2 | WT | WIND-O | OPER | CONV | EASTLAND | NORTH | 2025-08-04 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7 | 28.7
ROADRUNNER CROSSING WIND U3 |  | RRC_WIND_UNIT3 | WT | WIND-O | OPER | CONV | EASTLAND | NORTH | 2025-08-04 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9
ROCK SPRINGS VAL VERDE WIND (FERMI) 1 |  | FERMI_WIND1 | WT | WIND-O | OPER | CONV | VAL VERDE | WEST | 2017-10-26 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9 | 121.9
ROCK SPRINGS VAL VERDE WIND (FERMI) 2 |  | FERMI_WIND2 | WT | WIND-O | OPER | CONV | VAL VERDE | WEST | 2017-10-26 | 27.44 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4 | 27.4
ROSCOE WIND |  | TKWSW1_ROSCOE | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-02-20 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114
ROSCOE WIND 2A |  | TKWSW1_ROSCOE2A | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-02-20 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95
ROUTE 66 WIND |  | ROUTE_66_WIND1 | WT | WIND-P | OPER | CONV | CARSON | PANHANDLE | 2015-08-11 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RTS 2 WIND (HEART OF TEXAS WIND) U1 |  | RTS2_U1 | WT | WIND-O | OPER | CONV | MCCULLOCH | SOUTH | 2021-05-14 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9
RTS 2 WIND (HEART OF TEXAS WIND) U2 |  | RTS2_U2 | WT | WIND-O | OPER | CONV | MCCULLOCH | SOUTH | 2021-05-14 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9 | 89.9
RTS WIND |  | RTS_U1 | WT | WIND-O | OPER | CONV | MCCULLOCH | SOUTH | 2018-09-07 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
SAGE DRAW WIND U1 |  | SAGEDRAW_UNIT1 | WT | WIND-O | OPER | CONV | LYNN | WEST | 2022-05-04 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
SAGE DRAW WIND U2 |  | SAGEDRAW_UNIT2 | WT | WIND-O | OPER | CONV | LYNN | WEST | 2022-05-04 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2 | 169.2
SALT FORK 1 WIND U1 |  | SALTFORK_UNIT1 | WT | WIND-P | OPER | CONV | DONLEY | PANHANDLE | 2017-06-13 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64
SALT FORK 1 WIND U2 |  | SALTFORK_UNIT2 | WT | WIND-P | OPER | CONV | DONLEY | PANHANDLE | 2017-06-13 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
SAN ROMAN WIND |  | SANROMAN_WIND_1 | WT | WIND-C | OPER | CONV | CAMERON | COASTAL | 2016-08-25 | 95.25 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
SAND BLUFF WIND U1 |  | MCDLD_SB1_2 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2025-08-15 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
SAND BLUFF WIND U2 |  | MCDLD_SB3_282 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2025-08-15 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1
SAND BLUFF WIND U3 |  | MCDLD_SB4_G87 | WT | WIND-O | OPER | CONV | GLASSCOCK | WEST | 2025-08-15 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
SENATE WIND |  | SENATEWD_UNIT1 | WT | WIND-O | OPER | CONV | JACK | NORTH | 2012-12-01 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SENDERO WIND ENERGY |  | EXGNSND_WIND_1 | WT | WIND-O | OPER | CONV | JIM HOGG | SOUTH | 2015-12-22 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78
SEYMOUR HILLS WIND (S_HILLS WIND) |  | S_HILLS_UNIT1 | WT | WIND-O | OPER | CONV | BAYLOR | WEST | 2019-08-07 | 30.24 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
SHAFFER (PATRIOT WIND/PETRONILLA) |  | SHAFFER_UNIT1 | WT | WIND-C | OPER | CONV | NUECES | COASTAL | 2021-06-08 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1 | 226.1
SHAMROCK WIND U1 |  | SHAMROCK_UNIT1 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2025-03-19 | 203.1 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203
SHAMROCK WIND U2 |  | SHAMROCK_UNIT2 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2025-03-19 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9 | 20.9
SHANNON WIND |  | SHANNONW_UNIT_1 | WT | WIND-O | OPER | CONV | CLAY | WEST | 2015-12-23 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1 | 204.1
SHEEP CREEK WIND |  | SHEEPCRK_UNIT1 | WT | WIND-O | OPER | CONV | EASTLAND | NORTH | 2024-10-01 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SHERBINO 2 WIND |  | KEO_SHRBINO2 | WT | WIND-O | OPER | CONV | PECOS | WEST | 2011-12-21 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
SILVER STAR WIND |  | FLTCK_SSI | WT | WIND-O | OPER | CONV | ERATH | NORTH | 2008-09-26 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8
SOUTH PLAINS WIND 1 U1 |  | SPLAIN1_WIND1 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2015-11-13 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102
SOUTH PLAINS WIND 1 U2 |  | SPLAIN1_WIND2 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2015-11-13 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
SOUTH PLAINS WIND 2 U1 |  | SPLAIN2_WIND21 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2016-06-08 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
SOUTH PLAINS WIND 2 U2 |  | SPLAIN2_WIND22 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2016-06-08 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8 | 151.8
SOUTH TRENT WIND |  | STWF_T1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-10-29 | 101.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2 | 98.2
SPINNING SPUR WIND TWO A |  | SSPURTWO_WIND_1 | WT | WIND-P | OPER | CONV | OLDHAM | PANHANDLE | 2014-06-19 | 160.95 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
SPINNING SPUR WIND TWO B |  | SSPURTWO_SS3WIND2 | WT | WIND-P | OPER | CONV | OLDHAM | PANHANDLE | 2015-10-13 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
SPINNING SPUR WIND TWO C |  | SSPURTWO_SS3WIND1 | WT | WIND-P | OPER | CONV | OLDHAM | PANHANDLE | 2015-10-13 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96
STANTON WIND ENERGY |  | SWEC_G1 | WT | WIND-O | OPER | CONV | MARTIN | WEST | 2008-01-28 | 123.6 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
STELLA WIND |  | STELLA_UNIT1 | WT | WIND-C | OPER | CONV | KENEDY | COASTAL | 2018-12-19 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201 | 201
STEPHENS RANCH WIND 1 |  | SRWE1_UNIT1 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2014-12-29 | 213.82 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2
STEPHENS RANCH WIND 2 |  | SRWE1_SRWE2 | WT | WIND-O | OPER | CONV | BORDEN | WEST | 2015-05-21 | 166.52 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7 | 164.7
SWEETWATER WIND 1 |  | SWEETWND_WND1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2003-11-20 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5 | 42.5
SWEETWATER WIND 2A |  | SWEETWN2_WND24 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2006-03-21 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8
SWEETWATER WIND 2B |  | SWEETWN2_WND2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2004-11-22 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8 | 110.8
SWEETWATER WIND 3A |  | SWEETWN3_WND3A | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2011-08-02 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6 | 33.6
SWEETWATER WIND 3B |  | SWEETWN3_WND3B | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2011-08-02 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6
SWEETWATER WIND 4-4A |  | SWEETWN4_WND4A | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2007-03-21 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SWEETWATER WIND 4-4B |  | SWEETWN4_WND4B | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2007-03-21 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
SWEETWATER WIND 4-5 |  | SWEETWN5_WND5 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2007-11-01 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85
TAHOKA WIND 1 |  | TAHOKA_UNIT_1 | WT | WIND-O | OPER | CONV | LYNN | WEST | 2019-03-01 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TAHOKA WIND 2 |  | TAHOKA_UNIT_2 | WT | WIND-O | OPER | CONV | LYNN | WEST | 2019-03-01 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TEXAS BIG SPRING WIND A |  | SGMTN_SIGNALMT | WT | WIND-O | OPER | CONV | HOWARD | WEST | 1999-05-27 | 27.72 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7 | 27.7
TG EAST WIND U1 |  | TRUSGILL_UNIT1 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2022-12-08 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
TG EAST WIND U2 |  | TRUSGILL_UNIT2 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2022-12-08 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8 | 44.8
TG EAST WIND U3 |  | TRUSGILL_UNIT3 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2022-12-08 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42
TG EAST WIND U4 |  | TRUSGILL_UNIT4 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2022-12-08 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2 | 207.2
TORRECILLAS WIND 1 |  | TORR_UNIT1_25 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2019-11-07 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149
TORRECILLAS WIND 2 |  | TORR_UNIT2_23 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2019-11-07 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
TORRECILLAS WIND 3 |  | TORR_UNIT2_25 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2019-11-07 | 127.98 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128 | 128
TRENT WIND 1 A |  | TRENT_TRENT | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2001-07-09 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
TRENT WIND 1 B |  | TRENT_UNIT_1B | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2018-08-01 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6 | 15.6
TRENT WIND 2 |  | TRENT_UNIT_2 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2018-08-01 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5 | 50.5
TRENT WIND 3 A |  | TRENT_UNIT_3A | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2018-08-01 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3 | 38.3
TRENT WIND 3 B |  | TRENT_UNIT_3B | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2018-08-01 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8 | 13.8
TRINITY HILLS WIND 1 |  | TRINITY_TH1_BUS1 | WT | WIND-O | OPER | CONV | ARCHER | WEST | 2012-02-03 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4 | 103.4
TRINITY HILLS WIND 2 |  | TRINITY_TH1_BUS2 | WT | WIND-O | OPER | CONV | ARCHER | WEST | 2012-02-03 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6 | 94.6
TSTC WEST TEXAS WIND |  | ROSC2_1UNIT | WT | WIND-O | OPER | CONV-SODG | NOLAN | WEST | 2008-01-01 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
TURKEY TRACK WIND |  | TTWEC_G1 | WT | WIND-O | OPER | CONV | NOLAN | WEST | 2008-11-06 | 174.6 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5 | 169.5
TYLER BLUFF WIND |  | TYLRWIND_UNIT1 | WT | WIND-O | OPER | CONV | COOKE | NORTH | 2016-10-18 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6 | 125.6
VENADO WIND U1 |  | VENADO_UNIT1 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2021-12-06 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
VENADO WIND U2 |  | VENADO_UNIT2 | WT | WIND-O | OPER | CONV | ZAPATA | SOUTH | 2021-12-06 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6 | 96.6
VERA WIND 1 |  | VERAWIND_UNIT1 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12
VERA WIND 2 |  | VERAWIND_UNIT2 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2
VERA WIND 3 |  | VERAWIND_UNIT3 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
VERA WIND 4 |  | VERAWIND_UNIT4 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
VERA WIND 5 |  | VERAWIND_UNIT5 | WT | WIND-O | OPER | CONV | KNOX | WEST | 2021-05-26 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
VERTIGO WIND (FORMERLY GREEN PASTURES WIND 2) |  | VERTIGO_WIND_I | WT | WIND-O | OPER | CONV | BAYLOR | WEST | 2015-01-26 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
VORTEX WIND U1 |  | VORTEX_WIND1 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-15 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
VORTEX WIND U2 |  | VORTEX_WIND2 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-15 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2
VORTEX WIND U3 |  | VORTEX_WIND3 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2024-04-15 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4 | 158.4
VORTEX WIND U4 |  | VORTEX_WIND4 | WT | WIND-O | OPER | CONV | THROCKMORTON | WEST | 2022-04-13 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14
WAKE WIND 1 |  | WAKEWE_G1 | WT | WIND-P | OPER | CONV | DICKENS | PANHANDLE | 2016-10-28 | 114.91 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9 | 114.9
WAKE WIND 2 |  | WAKEWE_G2 | WT | WIND-P | OPER | CONV | DICKENS | PANHANDLE | 2016-10-28 | 142.35 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3 | 142.3
WEST RAYMOND (EL TRUENO) WIND U1 |  | TRUENO_UNIT1 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2021-10-26 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6 | 116.6
WEST RAYMOND (EL TRUENO) WIND U2 |  | TRUENO_UNIT2 | WT | WIND-C | OPER | CONV | WILLACY | COASTAL | 2021-10-26 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2 | 123.2
WESTERN TRAIL WIND (AJAX WIND) U1 |  | AJAXWIND_UNIT1 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2022-01-26 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6 | 225.6
WESTERN TRAIL WIND (AJAX WIND) U2 |  | AJAXWIND_UNIT2 | WT | WIND-O | OPER | CONV | WILBARGER | WEST | 2022-01-26 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
WHIRLWIND ENERGY |  | WEC_WECG1 | WT | WIND-P | OPER | CONV | FLOYD | PANHANDLE | 2007-11-09 | 59.8 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
WHITETAIL WIND |  | EXGNWTL_WIND_1 | WT | WIND-O | OPER | CONV | WEBB | SOUTH | 2012-12-20 | 92.34 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3 | 92.3
WHITE MESA WIND U1 |  | WHMESA_UNIT1 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-01 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3 | 152.3
WHITE MESA 2 WIND U1 |  | WHMESA_UNIT2_23 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-13 | 13.92 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9 | 13.9
WHITE MESA 2 WIND U2 |  | WHMESA_UNIT2_28 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-13 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3 | 183.3
WHITE MESA 2 WIND U3 |  | WHMESA_UNIT3_23 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-13 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
WHITE MESA 2 WIND U4 |  | WHMESA_UNIT3_28 | WT | WIND-O | OPER | CONV | CROCKETT | WEST | 2022-09-13 | 132.54 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5
WILLOW SPRINGS WIND A |  | SALVTION_UNIT1 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2017-12-29 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
WILLOW SPRINGS WIND B |  | SALVTION_UNIT2 | WT | WIND-O | OPER | CONV | HASKELL | WEST | 2017-12-29 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
WILSON RANCH (INFINITY LIVE OAK WIND) |  | WL_RANCH_UNIT1 | WT | WIND-O | OPER | CONV | SCHLEICHER | WEST | 2020-04-17 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5 | 199.5
WINDTHORST 2 WIND |  | WNDTHST2_UNIT1 | WT | WIND-O | OPER | CONV | ARCHER | WEST | 2014-12-11 | 67.62 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6 | 67.6
WKN MOZART WIND |  | MOZART_WIND_1 | WT | WIND-O | OPER | CONV | KENT | WEST | 2012-12-20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
WOLF RIDGE WIND |  | WHTTAIL_WR1 | WT | WIND-O | OPER | CONV | COOKE | NORTH | 2025-09-03 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5 | 121.5
YOUNG WIND U1 |  | YNG_WND_UNIT1 | WT | WIND-O | OPER | CONV | YOUNG | WEST | 2025-05-14 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193 | 193
YOUNG WIND U2 |  | YNG_WND_UNIT2 | WT | WIND-O | OPER | CONV | YOUNG | WEST | 2025-05-14 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9 | 148.9
YOUNG WIND U3 |  | YNG_WND_UNIT3 | WT | WIND-O | OPER | CONV | YOUNG | WEST | 2025-05-14 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1 | 146.1
ANCHOR WIND U1 | 21INR0546 | ANCHOR_WIND1 | WT | WIND-O | OPER-SYN | CONV | CALLAHAN | WEST | 2025-12-29 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
BAIRD NORTH WIND U1 | 20INR0083 | BAIRDWND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | CALLAHAN | WEST | 2025-12-31 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
BAIRD NORTH WIND U2 | 20INR0083 | BAIRDWND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | CALLAHAN | WEST | 2025-12-31 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
BIG SAMPSON WIND U1 | 16INR0104 | BIGSAMWD_UNIT1 | WT | WIND-O | OPER-SYN | CONV | CROCKETT | WEST | 2025-12-31 | 132.9 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5
BIG SAMPSON WIND U2 | 16INR0104 | BIGSAMWD_UNIT2 | WT | WIND-O | OPER-SYN | CONV | CROCKETT | WEST | 2025-12-31 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5 | 132.5
BOARD CREEK WP U1 | 21INR0324 | BOARDCRK_UNIT1 | WT | WIND-O | OPER-SYN | CONV | NAVARRO | NORTH | 2026-01-30 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8 | 108.8
BOARD CREEK WP U2 | 21INR0324 | BOARDCRK_UNIT2 | WT | WIND-O | OPER-SYN | CONV | NAVARRO | NORTH | 2026-01-30 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4 | 190.4
CANYON WIND U1 | 18INR0030 | CANYONWD_UNIT1 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-11-26 | 146.64 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
CANYON WIND U2 | 18INR0030 | CANYONWD_UNIT2 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-11-26 | 2.52 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
CANYON WIND U3 | 18INR0030 | CANYONWD_UNIT3 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-11-26 | 59.22 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2 | 58.2
CANYON WIND U4 | 18INR0030 | CANYONWD_UNIT4 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-11-26 | 20.16 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8 | 19.8
CANYON WIND U5 | 18INR0030 | CANYONWD_UNIT5 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-11-26 | 67.68 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
CANYON WIND U6 | 18INR0030 | CANYONWD_UNIT6 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-11-26 | 12.6 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4 | 12.4
COYOTE WIND U1 | 17INR0027b | COYOTE_W_UNIT1 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-12-01 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
COYOTE WIND U2 | 17INR0027b | COYOTE_W_UNIT2 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-12-01 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6 | 26.6
COYOTE WIND U3 | 17INR0027b | COYOTE_W_UNIT3 | WT | WIND-O | OPER-SYN | CONV | SCURRY | WEST | 2025-12-01 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
EL SUAZ RANCH U1 | 20INR0097 | ELSAUZ_UNIT1 | WT | WIND-C | OPER-SYN | CONV | WILLACY | COASTAL | 2025-12-01 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
EL SUAZ RANCH U2 | 20INR0097 | ELSAUZ_UNIT2 | WT | WIND-C | OPER-SYN | CONV | WILLACY | COASTAL | 2025-12-01 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5 | 148.5
FOXTROT WIND U1 | 20INR0129 | FOXTROT_UNIT1 | WT | WIND-O | OPER-SYN | CONV | BEE | SOUTH | 2025-11-30 | 130.2 | 111.9 | 111.9 | 111.9 | 111.9 | 111.9 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2 | 130.2
FOXTROT WIND U2 | 20INR0129 | FOXTROT_UNIT2 | WT | WIND-O | OPER-SYN | CONV | BEE | SOUTH | 2025-11-30 | 84 | 72.2 | 72.2 | 72.2 | 72.2 | 72.2 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84
FOXTROT WIND U3 | 20INR0129 | FOXTROT_UNIT3 | WT | WIND-O | OPER-SYN | CONV | BEE | SOUTH | 2025-11-30 | 54 | 48 | 48 | 48 | 48 | 48 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54
HART WIND 2 | 24INR0116 | HART_WND_UNIT1 | WT | WIND-P | OPER-SYN | CONV | CASTRO | PANHANDLE | 2025-10-31 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4 | 163.4
HARALD (BEARKAT WIND B) | 15INR0064b | HARALD_UNIT1 | WT | WIND-O | OPER-SYN | CONV | GLASSCOCK | WEST | 2025-11-30 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
RAY GULF WIND | 22INR0517 | MAG_UNIT1 | WT | WIND-C | OPER-SYN | CONV | MATAGORDA | COASTAL | 2025-12-30 | 97.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5 | 96.5
MAGNET WING U2 (LANE CITY WIND) | 22INR0517 | MAG_UNIT2 | WT | WIND-C | OPER-SYN | CONV | MATAGORDA | COASTAL | 2025-12-30 | 102 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
MARYNEAL WINDPOWER | 18INR0031 | MARYNEAL_UNIT1 | WT | WIND-O | OPER-SYN | CONV | NOLAN | WEST | 2025-07-31 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4 | 182.4
MESTENO WIND | 16INR0081 | MESTENO_UNIT_1 | WT | WIND-O | OPER-SYN | CONV | STARR | SOUTH | 2025-06-30 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6
MONTE CRISTO 1 WIND | 19INR0054 | MONTECR1_WIND1 | WT | WIND-O | OPER-SYN | CONV | HIDALGO | SOUTH | 2025-11-15 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5 | 234.5
PEYTON CREEK WIND II | 20INR0155 | PCT_UNIT1 | WT | WIND-C | OPER-SYN | CONV | MATAGORDA | COASTAL | 2025-10-01 | 236 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1 | 234.1
PRAIRIE HILL WIND U1 | 19INR0100 | PHILLWND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | LIMESTONE | NORTH | 2026-12-15 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153 | 153
PRAIRIE HILL WIND U2 | 19INR0100 | PHILLWND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | LIMESTONE | NORTH | 2026-12-15 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147 | 147
PRIDDY WIND U1 | 16INR0085 | PRIDDY_UNIT1 | WT | WIND-O | OPER-SYN | CONV | MILLS | NORTH | 2025-12-30 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2
PRIDDY WIND U2 | 16INR0085 | PRIDDY_UNIT2 | WT | WIND-O | OPER-SYN | CONV | MILLS | NORTH | 2025-12-30 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2 | 115.2
WHITEHORSE WIND U1 | 19INR0080 | WH_WIND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | FISHER | WEST | 2024-10-31 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4 | 209.4
WHITEHORSE WIND U2 | 19INR0080 | WH_WIND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | FISHER | WEST | 2024-10-31 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5 | 209.5
WILDWIND U1 | 20INR0033 | WILDWIND_UNIT1 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2025-11-15 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4 | 18.4
WILDWIND U2 | 20INR0033 | WILDWIND_UNIT2 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2025-11-15 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48
WILDWIND U3 | 20INR0033 | WILDWIND_UNIT3 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2025-11-15 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
WILDWIND U4 | 20INR0033 | WILDWIND_UNIT4 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2025-11-15 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6 | 54.6
WILDWIND U5 | 20INR0033 | WILDWIND_UNIT5 | WT | WIND-O | OPER-SYN | CONV | COOKE | NORTH | 2025-11-15 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8 | 52.8
7V SOLAR U1 |  | 7RNCHSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | FAYETTE | SOUTH | 2025-01-30 | 139.5 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2 | 139.2
7V SOLAR U2 |  | 7RNCHSLR_UNIT2 | PV | SOLAR-O | OPER | CONV | FAYETTE | SOUTH | 2025-01-30 | 95.54 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2 | 95.2
7V SOLAR U3 |  | 7RNCHSLR_UNIT3 | PV | SOLAR-O | OPER | CONV | FAYETTE | SOUTH | 2025-01-30 | 5.57 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
ACACIA SOLAR |  | ACACIA_UNIT_1 | PV | SOLAR-FW | OPER | CONV | PRESIDIO | WEST | 2012-12-30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
AIRPORT ROAD LONEWOLFE PHASE ONE |  | AIRPRTRD_LONEWOLFE | PV | SOLAR-W | OPER | CONV-SODG | MITCHELL | WEST | 2023-06-26 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Spring Capabilities, MW (As of the Season Start Date, March 1) 2026 to Fall Capabilities, MW (As of the Season Start Date, October 1) 2030
ALEXIS SOLAR |  | ALEXIS_ALEXIS | PV | SOLAR-O | OPER | CONV-SODG | BROOKS | SOUTH | 2019-11-15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ANDROMEDA SOLAR U1 |  | ANDMDSLR_UNIT1 | PV | SOLAR-W | OPER | CONV | SCURRY | WEST | 2024-01-03 | 158.8 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
ANDROMEDA SOLAR U2 |  | ANDMDSLR_UNIT2 | PV | SOLAR-W | OPER | CONV | SCURRY | WEST | 2024-01-03 | 162.4 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
ANGELO SOLAR |  | ANG_SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | TOM GREEN | WEST | 2025-05-06 | 195.41 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
ANSON SOLAR U1 |  | ANSON1_UNIT1 | PV | SOLAR-W | OPER | CONV | JONES | WEST | 2022-01-20 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ANSON SOLAR U2 |  | ANSON1_UNIT2 | PV | SOLAR-W | OPER | CONV | JONES | WEST | 2022-01-20 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ARAGORN SOLAR |  | ARAGORN_UNIT1 | PV | SOLAR-FW | OPER | CONV | CULBERSON | WEST | 2021-12-22 | 188.2 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 187.2 | 187.2 | 187.2 | 187.2 | 187.2 | 185 | 185 | 185 | 185 | 185
ASH CREEK SOLAR U1 |  | ASCK_SLR_SOLAR1 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2025-06-11 | 206.8 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3 | 203.3
ASH CREEK SOLAR U2 |  | ASCK_SLR_SOLAR2 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2025-06-11 | 210.94 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3
AUREOLA SOLAR U1 |  | AURO_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | MILAM | SOUTH | 2024-08-12 | 201.66 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4 | 200.4
AZURE SKY SOLAR U1 |  | AZURE_SOLAR1 | PV | SOLAR-W | OPER | CONV | HASKELL | WEST | 2021-11-15 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9 | 74.9
AZURE SKY SOLAR U2 |  | AZURE_SOLAR2 | PV | SOLAR-W | OPER | CONV | HASKELL | WEST | 2021-11-15 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5 | 153.5
BECK 1 |  | CECSOLAR_BECK1 | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2016-08-09 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | bar: Spring Capabilities, MW (As of the Season Start Date, March 1) 2026 to Fall Capabilities, MW (As of the Season Start Date, October 1) 2030
BHE SOLAR PEARL PROJECT (SIRIUS 2) |  | SIRIUS_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2017-09-28 | 50 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1 | 49.1
BIG ELM SOLAR |  | BELM_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | BELL | NORTH | 2025-04-30 | 200.99 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2 | 200.2
BKVSOLAR_BKVSOLAR1 |  | BKVSOLAR_BKVSOLAR1 | PV | SOLAR-O | OPER | CONV-SODG | DENTON | NORTH | 2024-10-02 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5 | 2.5
BLUE WING 1 SOLAR |  | BROOK_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2010-08-17 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6 | 7.6
BLUE WING 2 SOLAR |  | ELMEN_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2010-09-15 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3 | 7.3
BLUEBELL SOLAR (CAPRICORN RIDGE SOLAR) |  | CAPRIDG4_BB_PV | PV | SOLAR-W | OPER | CONV | STERLING | WEST | 2019-11-07 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
BLUEBELL SOLAR II 1 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV1 | PV | SOLAR-W | OPER | CONV | STERLING | WEST | 2021-04-28 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BLUEBELL SOLAR II 2 (CAPRICORN RIDGE 4) |  | CAPRIDG4_BB2_PV2 | PV | SOLAR-W | OPER | CONV | STERLING | WEST | 2021-04-28 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
BNB LAMESA SOLAR (PHASE I) |  | LMESASLR_UNIT1 | PV | SOLAR-W | OPER | CONV | DAWSON | WEST | 2018-02-18 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
BNB LAMESA SOLAR (PHASE II) |  | LMESASLR_IVORY | PV | SOLAR-W | OPER | CONV | DAWSON | WEST | 2018-12-19 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BOVINE SOLAR LLC |  | BOVINE_BOVINE | PV | SOLAR-O | OPER | CONV-SODG | AUSTIN | SOUTH | 2018-12-26 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
BOVINE SOLAR LLC |  | BOVINE2_BOVINE2 | PV | SOLAR-O | OPER | CONV-SODG | AUSTIN | SOUTH | 2018-12-26 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
BPL FILES SOLAR |  | FILESSLR_PV1 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2023-08-29 | 146.09 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145
BRIGHTSIDE SOLAR |  | BRIGHTSD_UNIT1 | PV | SOLAR-O | OPER | CONV | BEE | SOUTH | 2022-05-16 | 53.4 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRIGHT ARROW SOLAR U1 |  | BR_ARROW_UNIT1 | PV | SOLAR-O | OPER | CONV | HOPKINS | NORTH | 2025-06-30 | 127.3 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
BRIGHT ARROW SOLAR U2 |  | BR_ARROW_UNIT2 | PV | SOLAR-O | OPER | CONV | HOPKINS | NORTH | 2025-06-30 | 173.9 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
BRONSON SOLAR I |  | BRNSN_BRNSN | PV | SOLAR-O | OPER | CONV-SODG | FORT BEND | HOUSTON | 2018-12-27 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
BRONSON SOLAR II |  | BRNSN2_BRNSN2 | PV | SOLAR-O | OPER | CONV-SODG | FORT BEND | HOUSTON | 2018-12-27 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
CASCADE SOLAR I |  | CASCADE | PV | SOLAR-O | OPER | CONV-SODG | WHARTON | SOUTH | 2018-12-14 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
CASCADE SOLAR II |  | CASCADE2 | PV | SOLAR-O | OPER | CONV-SODG | WHARTON | SOUTH | 2018-12-14 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
CASTLE GAP SOLAR |  | CASL_GAP_UNIT1 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2018-05-31 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
CATAN SOLAR |  | CS10_CATAN | PV | SOLAR-O | OPER | CONV-SODG | KARNES | SOUTH | 2020-10-31 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
CHISUM SOLAR |  | CHISUM_CHISUM | PV | SOLAR-O | OPER | CONV-SODG | LAMAR | NORTH | 2018-11-12 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
COMMERCE_SOLAR |  | X443PV1_SWRI_PV1 | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2019-05-01 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
CONIGLIO SOLAR |  | CONIGLIO_UNIT1 | PV | SOLAR-O | OPER | CONV | FANNIN | NORTH | 2021-08-09 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7 | 125.7
CORAL SOLAR U1 |  | CORALSLR_SOLAR1 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-09-24 | 97.7 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2 | 96.2
CORAL SOLAR U2 |  | CORALSLR_SOLAR2 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-09-24 | 56.3 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4 | 55.4
CORAZON SOLAR PHASE I |  | CORAZON_UNIT1 | PV | SOLAR-O | OPER | CONV | WEBB | SOUTH | 2021-10-11 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6 | 202.6
CROWN SOLAR |  | CRWN_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-01-05 | 101.3 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1
DANCIGER SOLAR U1 |  | DAG_UNIT1 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2023-01-18 | 101.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DANCIGER SOLAR U2 |  | DAG_UNIT2 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2023-01-18 | 101.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DILEO SOLAR |  | DILEOSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | BOSQUE | NORTH | 2023-11-14 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4 | 71.4
EAST BLACKLAND SOLAR (PFLUGERVILLE SOLAR) |  | E_BLACK_UNIT_1 | PV | SOLAR-O | OPER | CONV | TRAVIS | SOUTH | 2021-08-12 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
EDDY SOLAR II |  | EDDYII_EDDYII | PV | SOLAR-O | OPER | CONV-SODG | MCLENNAN | NORTH | 2018-12-13 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
EIFFEL SOLAR |  | EIFSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | LAMAR | NORTH | 2023-11-30 | 241 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
ELARA SOLAR |  | ELARA_SL_UNIT1 | PV | SOLAR-O | OPER | CONV | FRIO | SOUTH | 2022-03-17 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4 | 132.4
ELLIS SOLAR |  | ELLISSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | ELLIS | NORTH | 2023-10-24 | 81.3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
EMERALD GROVE SOLAR (PECOS SOLAR POWER I) |  | EGROVESL_UNIT1 | PV | SOLAR-FW | OPER | CONV | CRANE | WEST | 2023-03-10 | 109.5 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108
ESTONIAN SOLAR FARM U1 |  | ESTONIAN_SOLAR1 | PV | SOLAR-O | OPER | CONV | DELTA | NORTH | 2025-07-02 | 88.4 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3 | 88.3
ESTONIAN SOLAR FARM U2 |  | ESTONIAN_SOLAR2 | PV | SOLAR-O | OPER | CONV | DELTA | NORTH | 2025-07-02 | 114.4 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1 | 114.1
EUNICE SOLAR U1 |  | EUNICE_PV1 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2021-09-24 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6 | 189.6
EUNICE SOLAR U2 |  | EUNICE_PV2 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2021-09-24 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1 | 237.1
FENCE POST SOLAR U1 |  | FENCESLR_SOLAR1 | PV | SOLAR-O | OPER | CONV | NAVARRO | NORTH | 2025-02-13 | 138.88 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
FENCE POST SOLAR U2 |  | FENCESLR_SOLAR2 | PV | SOLAR-O | OPER | CONV | NAVARRO | NORTH | 2025-02-13 | 97.98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
FIFTH GENERATION SOLAR 1 |  | FIFTHGS1_FGSOLAR1 | PV | SOLAR-O | OPER | CONV-SODG | TRAVIS | SOUTH | 2016-05-31 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
FIVE WELLS SOLAR U1 |  | FIVEWSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | BELL | NORTH | 2025-03-07 | 194.42 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4 | 194.4
FIVE WELLS SOLAR U2 |  | FIVEWSLR_UNIT2 | PV | SOLAR-O | OPER | CONV | BELL | NORTH | 2025-03-07 | 126.97 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127 | 127
FOWLER RANCH |  | FWLR_SLR_UNIT1 | PV | SOLAR-FW | OPER | CONV | CRANE | WEST | 2020-08-28 | 152.5 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
FRFWS_FAIRFIELD |  | FRFWS_FAIRFIELD | PV | SOLAR-O | OPER | CONV-SODG | FREESTONE | NORTH | 2024-10-23 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
FRYE SOLAR U1 |  | FRYE_SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | SWISHER | PANHANDLE | 2024-07-03 | 250.9 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
FRYE SOLAR U2 |  | FRYE_SLR_UNIT2 | PV | SOLAR-W | OPER | CONV | SWISHER | PANHANDLE | 2024-07-03 | 251.1 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
FS BARILLA SOLAR-PECOS |  | HOVEY_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2015-01-05 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22
FS EAST PECOS SOLAR |  | BOOTLEG_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2017-01-25 | 126 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1 | 121.1
GALLOWAY 1 SOLAR |  | GALLOWAY_SOLAR1 | PV | SOLAR-W | OPER | CONV | CONCHO | WEST | 2021-10-27 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
GALLOWAY 2 SOLAR |  | GALLOWAY_SOLAR2 | PV | SOLAR-W | OPER | CONV | CONCHO | WEST | 2024-01-04 | 111.1 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
GOLD_SPIKE 1 |  | 19599_1_GOLD_SPIKE | PV | SOLAR-O | OPER | CONV-SODG | TARRANT | NORTH | 2025-05-21 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
GOLD_SPIKE 2 |  | 19599_2_GOLD_SPIKE | PV | SOLAR-O | OPER | CONV-SODG | TARRANT | NORTH | 2025-05-21 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
GOLD_SPIKE 3 |  | 19599_GOLD_SPIKE | PV | SOLAR-O | OPER | CONV-SODG | TARRANT | NORTH | 2025-05-21 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9
GOLINDA SOLAR |  | GOLINDA_UNIT1 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-02-27 | 101.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1 | 100.1
GRANSOLAR TEXAS ONE |  | GRAN_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | MILAM | SOUTH | 2025-09-12 | 50.19 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
GREASEWOOD SOLAR 1 |  | GREASWOD_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-02-09 | 126.3 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6 | 124.6
GREASEWOOD SOLAR 2 |  | GREASWOD_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-02-09 | 132.2 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4 | 130.4
GRIFFIN SOLAR |  | GRIFFIN_GRIFFIN | PV | SOLAR-O | OPER | CONV-SODG | MCLENNAN | NORTH | 2019-07-15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
GRIZZLY RIDGE SOLAR |  | GRIZZLY_SOLAR1 | PV | SOLAR-O | OPER | CONV | HAMILTON | NORTH | 2023-10-20 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
HALO SOLAR |  | HALO_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | BELL | NORTH | 2024-08-12 | 251.15 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4 | 250.4
HIGHWAY 56 |  | HWY56_HWY56 | PV | SOLAR-O | OPER | CONV-SODG | GRAYSON | NORTH | 2017-11-20 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
HM SEALY SOLAR 1 |  | SEALY_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | AUSTIN | SOUTH | 2015-12-31 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
HOLLYWOOD SOLAR U1 | 25INR0741 | HOL_UNIT1 | PV | SOLAR-O | OPER | CONV | WHARTON | SOUTH | 2024-09-06 | 178.88 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3 | 175.3
HOLLYWOOD SOLAR U2 | 25INR0741 | HOL_UNIT2 | PV | SOLAR-O | OPER | CONV | WHARTON | SOUTH | 2024-09-06 | 186.07 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1 | 178.1
HOLSTEIN SOLAR 1 |  | HOLSTEIN_SOLAR1 | PV | SOLAR-W | OPER | CONV | NOLAN | WEST | 2020-05-28 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2
HOLSTEIN SOLAR 2 |  | HOLSTEIN_SOLAR2 | PV | SOLAR-W | OPER | CONV | NOLAN | WEST | 2020-05-28 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3 | 102.3
HOPKINS SOLAR U1 |  | HOPKNSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | HOPKINS | NORTH | 2024-05-02 | 175.35 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8 | 174.8
HOPKINS SOLAR U2 |  | HOPKNSLR_UNIT2 | PV | SOLAR-O | OPER | CONV | HOPKINS | NORTH | 2024-05-02 | 76.17 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8 | 75.8
HORIZON SOLAR |  | HRZN_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | FRIO | SOUTH | 2024-03-05 | 203.5 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
HORNET SOLAR U1 |  | HRNT_SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | SWISHER | PANHANDLE | 2025-10-20 | 200.65 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
HORNET SOLAR U2 |  | HRNT_SLR_UNIT2 | PV | SOLAR-W | OPER | CONV | SWISHER | PANHANDLE | 2025-10-20 | 200.54 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
HORNET SOLAR U3 |  | HRNT_SLR_UNIT3 | PV | SOLAR-W | OPER | CONV | SWISHER | PANHANDLE | 2025-10-20 | 201.18 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
HPWHSOL_WILDHORSESOLAR |  | HPWHSOL_WILDHORSESOLAR | PV | SOLAR-W | OPER | CONV-SODG | HOWARD | WEST | 2024-06-01 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
IMPACT SOLAR |  | IMPACT_UNIT1 | PV | SOLAR-O | OPER | CONV | LAMAR | NORTH | 2021-08-20 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5 | 198.5
INFINITE PHOTON ENERGY |  | INFINITE_PHOTON_ENERGY | PV | SOLAR-W | OPER | CONV-SODG | MITCHELL | WEST | 2025-06-11 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
JADE SOLAR U1 |  | JADE_SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | SCURRY | WEST | 2024-01-02 | 158.8 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158
JADE SOLAR U2 |  | JADE_SLR_UNIT2 | PV | SOLAR-W | OPER | CONV | SCURRY | WEST | 2024-01-02 | 162.4 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162
JUNGMANN SOLAR |  | JUNG_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | MILAM | SOUTH | 2025-08-22 | 40.21 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
JUNO SOLAR PHASE I |  | JUNO_UNIT1 | PV | SOLAR-W | OPER | CONV | BORDEN | WEST | 2021-05-26 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1 | 162.1
JUNO SOLAR PHASE II |  | JUNO_UNIT2 | PV | SOLAR-W | OPER | CONV | BORDEN | WEST | 2021-08-09 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5 | 143.5
KELLAM SOLAR |  | KELAM_SL_UNIT1 | PV | SOLAR-O | OPER | CONV | VAN ZANDT | NORTH | 2020-12-24 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
LAMPWICK SOLAR |  | LAMPWICK_LAMPWICK | PV | SOLAR-W | OPER | CONV-SODG | MENARD | WEST | 2019-09-12 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
LAMPASAS_HIGHWAY183LAMPASAS |  | LAMPASAS_HIGHWAY183 | PV | SOLAR-O | OPER | CONV-SODG | BURNET | SOUTH | 2025-02-28 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
LAPETUS SOLAR |  | LAPETUS_UNIT_1 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2020-06-24 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7 | 100.7
LEON |  | LEON_LEON | PV | SOLAR-O | OPER | CONV-SODG | HUNT | NORTH | 2017-12-15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LILY SOLAR |  | LILY_SOLAR1 | PV | SOLAR-O | OPER | CONV | KAUFMAN | NORTH | 2021-10-08 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6 | 147.6
LONG DRAW SOLAR U1 |  | LGDRAW_S_UNIT1_1 | PV | SOLAR-W | OPER | CONV | BORDEN | WEST | 2021-12-14 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
LONG DRAW SOLAR U2 |  | LGDRAW_S_UNIT1_2 | PV | SOLAR-W | OPER | CONV | BORDEN | WEST | 2021-12-14 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3
LONGBOW SOLAR |  | LON_SOLAR1 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2024-04-17 | 78.2 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
MALAKOFF |  | MALAKOFF | PV | SOLAR-O | OPER | CONV-SODG | HENDERSON | NORTH | 2024-10-16 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
MANDORLA SOLAR |  | MAND_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | MILAM | SOUTH | 2024-09-19 | 251.45 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5 | 250.5
MARKUM SOLAR |  | MRKM_SLR_PV1 | PV | SOLAR-O | OPER | CONV | MCLENNAN | NORTH | 2025-09-09 | 161.5 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161 | 161
MARLIN |  | MARLIN_MARLIN | PV | SOLAR-O | OPER | CONV-SODG | FALLS | NORTH | 2017-11-27 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3 | 5.3
MARS SOLAR (DG) |  | MARS_MARS | PV | SOLAR-O | OPER | CONV-SODG | WEBB | SOUTH | 2019-03-31 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
MCLEAN (SHAKES) SOLAR |  | MCLNSLR_UNIT1 | PV | SOLAR-O | OPER | CONV | DIMMIT | SOUTH | 2023-09-01 | 207.4 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MERCURY SOLAR U1 |  | MERCURY_PV1 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2025-06-26 | 203.5 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MERCURY SOLAR U2 |  | MERCURY_PV2 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2025-06-26 | 203.5 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MEXIA_MEXIA |  | MEXIA_MEXIA | PV | SOLAR-O | OPER | CONV-SODG | LIMESTONE | NORTH | 2024-08-01 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
MEXIA1_MEXIA1 |  | MEXIA1_MEXIA1 | PV | SOLAR-O | OPER | CONV-SODG | LIMESTONE | NORTH | 2024-10-23 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
MEXIA2_MEXIA2 |  | MEXIA2_MEXIA2 | PV | SOLAR-O | OPER | CONV-SODG | LIMESTONE | NORTH | 2024-10-23 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
MISAE SOLAR U1 |  | MISAE_UNIT1 | PV | SOLAR-W | OPER | CONV | CHILDRESS | PANHANDLE | 2021-12-20 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4 | 121.4
MISAE SOLAR U2 |  | MISAE_UNIT2 | PV | SOLAR-W | OPER | CONV | CHILDRESS | PANHANDLE | 2021-12-20 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6 | 118.6
MLKF1_MALAKOFF1 |  | MLKF1_MALAKOFF1 | PV | SOLAR-O | OPER | CONV-SODG | HENDERSON | NORTH | 2024-10-23 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
MLKF2_MALAKOFF2 |  | MLKF2_MALAKOFF2 | PV | SOLAR-O | OPER | CONV-SODG | HENDERSON | NORTH | 2024-10-23 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
MUSTANG CREEK SOLAR U1 |  | MUSTNGCK_SOLAR1 | PV | SOLAR-O | OPER | CONV | JACKSON | SOUTH | 2023-10-09 | 61 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
MUSTANG CREEK SOLAR U2 |  | MUSTNGCK_SOLAR2 | PV | SOLAR-O | OPER | CONV | JACKSON | SOUTH | 2023-10-09 | 91.25 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
NEBULA SOLAR (RAYOS DEL SOL) U1 |  | NEBULA_UNIT1 | PV | SOLAR-O | OPER | CONV | CAMERON | COASTAL | 2022-10-25 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5 | 137.5
NOBLE SOLAR U1 |  | NOBLESLR_SOLAR1 | PV | SOLAR-O | OPER | CONV | DENTON | NORTH | 2022-09-19 | 148.8 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7 | 146.7
NOBLE SOLAR U2 |  | NOBLESLR_SOLAR2 | PV | SOLAR-O | OPER | CONV | DENTON | NORTH | 2022-09-19 | 130.2 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3 | 128.3
NORTH GAINESVILLE |  | NGNSVL_NGAINESV | PV | SOLAR-O | OPER | CONV-SODG | COOKE | NORTH | 2017-12-15 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.2
OBERON SOLAR |  | OBERON_UNIT_1 | PV | SOLAR-FW | OPER | CONV | ECTOR | WEST | 2020-07-13 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
OCI ALAMO 1 SOLAR |  | OCI_ALM1_UNIT1 | PV | SOLAR-O | OPER | CONV | BEXAR | SOUTH | 2013-12-13 | 39.18 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2 | 39.2
OCI ALAMO 2 SOLAR-ST. HEDWIG |  | STHWG_UNIT1 | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2014-01-20 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4 | 4.4
OCI ALAMO 3-WALZEM SOLAR |  | WALZM_UNIT1 | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2014-10-01 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
OCI ALAMO 4 SOLAR-BRACKETVILLE |  | ECLIPSE_UNIT1 | PV | SOLAR-O | OPER | CONV | KINNEY | SOUTH | 2014-08-28 | 37.62 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6 | 37.6
OCI ALAMO 5 (DOWNIE RANCH) |  | HELIOS_UNIT1 | PV | SOLAR-O | OPER | CONV | UVALDE | SOUTH | 2015-12-22 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
OCI ALAMO 6 (SIRIUS/WEST TEXAS) |  | SIRIUS_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2016-06-06 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2 | 110.2
OCI ALAMO 7 (PAINT CREEK) |  | SOLARA_UNIT1 | PV | SOLAR-W | OPER | CONV | HASKELL | WEST | 2016-07-29 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112
ORANGE GROVE SOLAR |  | OGS_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | JIM WELLS | SOUTH | 2025-06-18 | 130.6 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
OUTPOST SOLAR U1 |  | OUTP_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | WEBB | SOUTH | 2025-08-20 | 257.95 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
OUTPOST SOLAR U2 |  | OUTP_SLR_UNIT2 | PV | SOLAR-O | OPER | CONV | WEBB | SOUTH | 2025-08-20 | 259.11 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2 | 258.2
PEGASUS_PEGASUS |  | PEGASUS_PEGASUS | PV | SOLAR-FW | OPER | CONV-SODG | UPTON | WEST | 2024-07-17 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
PEREGRINE SOLAR U1 |  | PERE_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | GOLIAD | SOUTH | 2025-08-05 | 152.83 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2 | 152.2
PEREGRINE SOLAR U2 |  | PERE_SLR_UNIT2 | PV | SOLAR-O | OPER | CONV | GOLIAD | SOUTH | 2025-08-05 | 148.28 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7 | 147.7
PHOEBE SOLAR 1 |  | PHOEBE_UNIT1 | PV | SOLAR-FW | OPER | CONV | WINKLER | WEST | 2019-11-26 | 125.14 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1
PHOEBE SOLAR 2 |  | PHOEBE_UNIT2 | PV | SOLAR-FW | OPER | CONV | WINKLER | WEST | 2019-11-26 | 128.05 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1 | 128.1
PHOENIX SOLAR |  | PHOENIX_UNIT1 | PV | SOLAR-O | OPER | CONV | FANNIN | NORTH | 2021-09-01 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9 | 83.9
PISGAH RIDGE SOLAR U1 |  | PISGAH_SOLAR1 | PV | SOLAR-O | OPER | CONV | NAVARRO | NORTH | 2024-04-17 | 189.4 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5 | 186.5
PISGAH RIDGE SOLAR U2 |  | PISGAH_SOLAR2 | PV | SOLAR-O | OPER | CONV | NAVARRO | NORTH | 2024-04-17 | 64.4 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
PITTS DUDIK SOLAR U1 |  | PITTSDDK_UNIT1 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2023-11-03 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6 | 49.6
PLAINVIEW SOLAR (RAMSEY SOLAR) U1 |  | PLN_UNIT1 | PV | SOLAR-O | OPER | CONV | WHARTON | SOUTH | 2025-07-22 | 270 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
PLAINVIEW SOLAR (RAMSEY SOLAR) U2 |  | PLN_UNIT2 | PV | SOLAR-O | OPER | CONV | WHARTON | SOUTH | 2025-07-22 | 270 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257 | 257
PORTER SOLAR U1 |  | PORT_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | DENTON | NORTH | 2025-01-21 | 245.83 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245 | 245
POWERFIN KINGSBERY |  | PFK_PFKPV | PV | SOLAR-O | OPER | CONV-SODG | TRAVIS | SOUTH | 2017-12-01 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
PROSPERO SOLAR 1 U1 |  | PROSPERO_UNIT1 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2020-06-30 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
PROSPERO SOLAR 1 U2 |  | PROSPERO_UNIT2 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2020-06-30 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
PROSPERO SOLAR 2 U1 |  | PRSPERO2_UNIT1 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2021-09-23 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5 | 126.5
PROSPERO SOLAR 2 U2 |  | PRSPERO2_UNIT2 | PV | SOLAR-FW | OPER | CONV | ANDREWS | WEST | 2021-09-23 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4 | 126.4
QUEEN SOLAR U1 |  | QUEEN_SL_SOLAR1 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2020-05-04 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
QUEEN SOLAR U2 |  | QUEEN_SL_SOLAR2 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2020-05-04 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5 | 102.5
QUEEN SOLAR U3 |  | QUEEN_SL_SOLAR3 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2020-08-28 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5 | 97.5
QUEEN SOLAR U4 |  | QUEEN_SL_SOLAR4 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2020-08-28 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5 | 107.5
RADIAN SOLAR U1 |  | RADN_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | BROWN | NORTH | 2023-05-16 | 161.41 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9 | 158.9
RADIAN SOLAR U2 |  | RADN_SLR_UNIT2 | PV | SOLAR-O | OPER | CONV | BROWN | NORTH | 2023-05-16 | 166.02 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9 | 162.9
RAMBLER SOLAR |  | RAMBLER_UNIT1 | PV | SOLAR-W | OPER | CONV | TOM GREEN | WEST | 2020-10-01 | 211.19 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
RATLIFF SOLAR (CONCHO VALLEY SOLAR) |  | RATLIFF_SOLAR1 | PV | SOLAR-W | OPER | CONV | TOM GREEN | WEST | 2023-05-25 | 162.43 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8 | 159.8
RE ROSEROCK SOLAR 1 |  | REROCK_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2016-06-13 | 78.75 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
RE ROSEROCK SOLAR 2 |  | REROCK_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2016-06-13 | 78.75 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
REDBARN SOLAR 1 (RE MAPLEWOOD 2A SOLAR) |  | REDBARN_UNIT_1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-10-11 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222 | 222
REDBARN SOLAR 2 (RE MAPLEWOOD 2B SOLAR) |  | REDBARN_UNIT_2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-10-11 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
RENEWABLE ENERGY ALTERNATIVES-CCS1 |  | COSERVSS_CSS1 | PV | SOLAR-O | OPER | CONV-SODG | DENTON | NORTH | 2015-05-20 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
RIGGINS (SE BUCKTHORN WESTEX SOLAR) |  | RIGGINS_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2018-06-15 | 155.44 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RIPPEY SOLAR |  | RIPPEY_UNIT1 | PV | SOLAR-O | OPER | CONV | COOKE | NORTH | 2020-12-30 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8 | 59.8
ROWLAND SOLAR I |  | ROW_UNIT1 | PV | SOLAR-O | OPER | CONV | FORT BEND | HOUSTON | 2023-07-10 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ROWLAND SOLAR II |  | ROW_UNIT2 | PV | SOLAR-O | OPER | CONV | FORT BEND | HOUSTON | 2024-06-28 | 200.7 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
SIGNAL SOLAR |  | SIG_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | HUNT | NORTH | 2025-07-31 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SOLAIREHOLMAN 1 |  | LASSO_UNIT1 | PV | SOLAR-FW | OPER | CONV | BREWSTER | WEST | 2018-03-30 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SPARTA SOLAR U1 |  | SPARTA_UNIT1 | PV | SOLAR-O | OPER | CONV | BEE | SOUTH | 2023-10-16 | 147.5 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146 | 146
SPARTA SOLAR U2 |  | SPARTA_UNIT2 | PV | SOLAR-O | OPER | CONV | BEE | SOUTH | 2023-10-16 | 104.9 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104
SP-TX-12-PHASE B |  | SPTX12B_UNIT1 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2017-08-25 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
STERLING |  | STRLING_STRLING | PV | SOLAR-O | OPER | CONV-SODG | HUNT | NORTH | 2018-12-13 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
STRATEGIC SOLAR 1 |  | STRATEGC_UNIT1 | PV | SOLAR-O | OPER | CONV | ELLIS | NORTH | 2022-12-29 | 135 | 135 | 135 | 135 | 135 | 135 | 118.3 | 118.3 | 118.3 | 118.3 | 118.3 | 135 | 135 | 135 | 135 | 135 | 127.1 | 127.1 | 127.1 | 127.1 | 127.1
SUN VALLEY U1 |  | SUNVASLR_UNIT1 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2024-04-19 | 165.75 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8
SUN VALLEY U2 |  | SUNVASLR_UNIT2 | PV | SOLAR-O | OPER | CONV | HILL | NORTH | 2024-04-19 | 86.19 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2 | 86.2
SUNEDISON CPS3 SOMERSET 1 SOLAR |  | SOME1_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2012-04-01 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6 | 5.6
SUNEDISON RABEL ROAD SOLAR |  | VALL1_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2012-02-15 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SUNEDISON SOMERSET 2 SOLAR |  | SOME2_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2012-04-01 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
SUNEDISON VALLEY ROAD SOLAR |  | VALL2_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BEXAR | SOUTH | 2012-02-15 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SUNRAY |  | SUN_SLR_UNIT_1 | PV | SOLAR-O | OPER | CONV | UVALDE | SOUTH | 2024-08-20 | 203.5 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
TALCOWST_TALCO |  | TALCOWST_TALCO | PV | SOLAR-O | OPER | CONV-SODG | TITUS | NORTH | 2024-08-01 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
TAVENER U1 (FORT BEND SOLAR) |  | TAV_UNIT1 | PV | SOLAR-O | OPER | CONV | FORT BEND | HOUSTON | 2023-10-06 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5 | 149.5
TAVENER U2 (FORT BEND SOLAR) |  | TAV_UNIT2 | PV | SOLAR-O | OPER | CONV | FORT BEND | HOUSTON | 2023-10-06 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
TAYGETE SOLAR 1 U1 |  | TAYGETE_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-06-14 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9 | 125.9
TAYGETE SOLAR 1 U2 |  | TAYGETE_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2021-06-14 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9
TAYGETE SOLAR 2 U1 |  | TAYGETE2_UNIT1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2023-07-17 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
TAYGETE SOLAR 2 U2 |  | TAYGETE2_UNIT2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2023-07-17 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9 | 101.9
TEXAS SOLAR NOVA U1 |  | NOVA1SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | KENT | WEST | 2024-04-30 | 126.81 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
TEXAS SOLAR NOVA U2 |  | NOVA1SLR_UNIT2 | PV | SOLAR-W | OPER | CONV | KENT | WEST | 2024-04-30 | 126.7 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 126
TEXAS SOLAR NOVA 2 U1 |  | NOVA2SLR_UNIT1 | PV | SOLAR-W | OPER | CONV | KENT | WEST | 2025-10-03 | 202.37 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
TIERRA BONITA SOLAR U1 |  | TRBT_SLR_PV1 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2024-12-31 | 150 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6 | 149.6
TIERRA BONITA SOLAR U2 |  | TRBT_SLR_PV2 | PV | SOLAR-FW | OPER | CONV | PECOS | WEST | 2024-12-31 | 156.9 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3 | 156.3
TITAN SOLAR (IP TITAN) U1 |  | TI_SOLAR_UNIT1 | PV | SOLAR-FW | OPER | CONV | CULBERSON | WEST | 2021-11-22 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8 | 136.8
TITAN SOLAR (IP TITAN) U2 |  | TI_SOLAR_UNIT2 | PV | SOLAR-FW | OPER | CONV | CULBERSON | WEST | 2021-11-22 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1 | 131.1
TPE ERATH SOLAR |  | ERATH_ERATH21 | PV | SOLAR-O | OPER | CONV-SODG | ERATH | NORTH | 2021-12-24 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
TRN_TRINITYBAY |  | TRN_TRINITYBAY | PV | SOLAR-O | OPER | CONV-SODG | CHAMBERS | HOUSTON | 2024-01-10 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
TRUE NORTH SOLAR U1 |  | TNS_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-12-20 | 119.35 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8 | 118.8
TRUE NORTH SOLAR U2 |  | TNS_SLR_UNIT2 | PV | SOLAR-O | OPER | CONV | FALLS | NORTH | 2024-12-20 | 119.45 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9 | 118.9
TYSON NICK SOLAR |  | TYSN_SLR_UNIT1 | PV | SOLAR-O | OPER | CONV | LAMAR | NORTH | 2025-10-06 | 90.5 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90
VANCOURT SOLAR |  | VANCOURT_UNIT1 | PV | SOLAR-O | OPER | CONV | CAMERON | COASTAL | 2023-01-25 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7 | 45.7
VISION SOLAR 1 |  | VISION_UNIT1 | PV | SOLAR-O | OPER | CONV | NAVARRO | NORTH | 2022-12-29 | 129.2 | 127 | 127 | 127 | 127 | 127 | 112.7 | 112.7 | 112.7 | 112.7 | 112.7 | 127 | 127 | 127 | 127 | 127 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7
WAGYU SOLAR |  | WGU_UNIT1 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2021-10-04 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
WALNUT SPRINGS |  | WLNTSPRG_1UNIT | PV | SOLAR-O | OPER | CONV-SODG | BOSQUE | NORTH | 2016-07-31 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WAYMARK SOLAR |  | WAYMARK_UNIT1 | PV | SOLAR-FW | OPER | CONV | UPTON | WEST | 2018-12-20 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182 | 182
WEBBERVILLE SOLAR |  | WEBBER_S_WSP1 | PV | SOLAR-O | OPER | CONV | TRAVIS | SOUTH | 2011-11-23 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7 | 26.7
WEST MOORE II |  | WMOOREII_WMOOREII | PV | SOLAR-O | OPER | CONV-SODG | GRAYSON | NORTH | 2018-10-22 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
WEST OF PECOS SOLAR |  | W_PECOS_UNIT1 | PV | SOLAR-FW | OPER | CONV | REEVES | WEST | 2019-12-20 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
WESTORIA SOLAR U1 |  | WES_UNIT1 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2022-11-01 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
WESTORIA SOLAR U2 |  | WES_UNIT2 | PV | SOLAR-O | OPER | CONV | BRAZORIA | COASTAL | 2022-11-01 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
WHITESBORO |  | WBORO_WHTSBORO | PV | SOLAR-O | OPER | CONV-SODG | GRAYSON | NORTH | 2017-12-15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
WHITESBORO II |  | WBOROII_WHBOROII | PV | SOLAR-O | OPER | CONV-SODG | GRAYSON | NORTH | 2017-12-15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
WHITEWRIGHT |  | WHTRT_WHTRGHT | PV | SOLAR-O | OPER | CONV-SODG | FANNIN | NORTH | 2017-12-30 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WHSOLAR_WILDHORSE_SOLAR |  | WHSOLAR_WILDHORSE_SOLAR | PV | SOLAR-W | OPER | CONV-SODG | HOWARD | WEST | 2024-05-15 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
XE MURAT [ADLONG] SOLAR |  | ADL_SOLAR1 | PV | SOLAR-O | OPER | CONV | HARRIS | HOUSTON | 2025-07-03 | 60.14 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
YELLOW JACKET SOLAR |  | YLWJACKET_YLWJACKET | PV | SOLAR-O | OPER | CONV-SODG | BOSQUE | NORTH | 2018-10-15 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
ZIER SOLAR |  | ZIER_SLR_PV1 | PV | SOLAR-O | OPER | CONV | KINNEY | SOUTH | 2024-04-26 | 161.28 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
AZALEA SPRINGS SOLAR | 19INR0110 | AZSP_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | ANGELINA | NORTH | 2025-10-31 | 181 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
BAKER BRANCH SOLAR U1 | 23INR0026 | BAKE_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2026-05-31 | 234.84 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9
BAKER BRANCH SOLAR U2 | 23INR0026 | BAKE_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2026-05-31 | 234.57 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9 | 233.9
BIG STAR SOLAR U1 | 21INR0413 | BIG_STAR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | BASTROP | SOUTH | 2026-01-31 | 132.27 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130
BIG STAR SOLAR U2 | 21INR0413 | BIG_STAR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | BASTROP | SOUTH | 2026-01-31 | 70.83 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
BLEVINS SOLAR U2 | 23INR0118 | BLVN_SLR_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2025-12-20 | 132.02 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 132
BLEVINS SOLAR U3 | 23INR0118 | BLVN_SLR_SOLAR3 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2025-12-20 | 139.74 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138 | 138
BLUE JAY SOLAR I | 21INR0538 | BLUEJAY_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | GRIMES | NORTH | 2025-10-31 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69 | 69
BLUE JAY SOLAR II | 19INR0085 | BLUEJAY_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | GRIMES | NORTH | 2025-09-30 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141 | 141
BUZIOS SOLAR U1 | 24INR0399 | BUZI_SLR_UNIT1 | PV | SOLAR-W | OPER-SYN | CONV-DGR | MOTLEY | PANHANDLE | 2026-01-30 | 6.31 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3 | 6.3
BUZIOS SOLAR U2 | 24INR0399 | BUZI_SLR_UNIT2 | PV | SOLAR-W | OPER-SYN | CONV | MOTLEY | PANHANDLE | 2026-01-30 | 119.55 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7 | 118.7
BUZIOS SOLAR U3 | 24INR0399 | BUZI_SLR_UNIT3 | PV | SOLAR-W | OPER-SYN | CONV | MOTLEY | PANHANDLE | 2026-01-30 | 107.19 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5 | 106.5
BUZIOS SOLAR U4 | 24INR0399 | BUZI_SLR_UNIT4 | PV | SOLAR-W | OPER-SYN | CONV | MOTLEY | PANHANDLE | 2026-01-30 | 18.64 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5 | 18.5
BUFFALO CREEK (OLD 300 SOLAR CENTER) U1 | 21INR0406 | BCK_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | FORT BEND | HOUSTON | 2025-11-01 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5 | 217.5
BUFFALO CREEK (OLD 300 SOLAR CENTER) U2 | 21INR0406 | BCK_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | FORT BEND | HOUSTON | 2025-11-01 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3 | 221.3
CHILLINGHAM SOLAR U1 | 23INR0070 | CHIL_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | BELL | NORTH | 2026-02-28 | 174.3 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173 | 173
CHILLINGHAM SOLAR U2 | 23INR0070 | CHIL_SLR_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | BELL | NORTH | 2026-02-28 | 178.1 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177 | 177
COMPADRE SOLAR U1 | 24INR0023 | CMPD_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | HILL | NORTH | 2025-11-15 | 195.17 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5 | 194.5
COMPADRE SOLAR U2 | 24INR0023 | CMPD_SLR_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | HILL | NORTH | 2025-11-15 | 211.37 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2 | 211.2
COTTONWOOD BAYOU SOLAR I U1 | 19INR0134 | CTW_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2025-12-03 | 175.69 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
COTTONWOOD BAYOU SOLAR I U2 | 19INR0134 | CTW_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2025-12-03 | 175.71 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 175
DAMAZO (SECOND DIVISION) SOLAR | 20INR0248 | DMA_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2025-08-15 | 100.2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DANISH FIELDS SOLAR U1 | 20INR0069 | DAN_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-10-31 | 301.3 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
DANISH FIELDS SOLAR U2 | 20INR0069 | DAN_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-10-31 | 151 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2 | 150.2
DANISH FIELDS SOLAR U3 | 20INR0069 | DAN_UNIT3 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-10-31 | 150.5 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8 | 149.8
DELILAH SOLAR 1 U1 | 22INR0202 | DELILA_1_G1 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-11-28 | 153.54 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
DELILAH SOLAR 1 U2 | 22INR0202 | DELILA_1_G2 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-11-28 | 153.54 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
DELILAH SOLAR 2 U1 | 22INR0203 | DELILA_2_G1 | PV | SOLAR-O | OPER-SYN | CONV | RED RIVER | NORTH | 2025-11-10 | 107.09 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
DELILAH SOLAR 2 U2 | 22INR0203 | DELILA_2_G2 | PV | SOLAR-O | OPER-SYN | CONV | RED RIVER | NORTH | 2025-11-10 | 103.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DELILAH SOLAR 2 U3 | 22INR0203 | DELILA_2_G3 | PV | SOLAR-O | OPER-SYN | CONV | RED RIVER | NORTH | 2025-11-10 | 107.09 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105
DIVER SOLAR U1 | 25INR0105 | DIVR_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | LIMESTONE | NORTH | 2025-11-21 | 71 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8 | 69.8
DIVER SOLAR U2 | 25INR0105 | DIVR_SLR_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | LIMESTONE | NORTH | 2025-11-21 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2 | 155.2
DRY CREEK SOLAR I | 23INR0286 | DRCK_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | HENDERSON | NORTH | 2026-01-01 | 200.1 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
EASTBELL MILAM SOLAR | 21INR0203 | EBELLSLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | MILAM | SOUTH | 2025-10-31 | 244.86 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
EASTBELL MILAM SOLAR II | 24INR0208 | EBELLSL2_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | MILAM | SOUTH | 2025-10-31 | 150.6 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
ELIZA SOLAR | 21INR0368 | ELZA_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | KAUFMAN | NORTH | 2025-11-30 | 151.7 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151 | 151
FAGUS SOLAR PARK SLF U2 | 20INR0091 | FAGUSSLR_UNIT2 | PV | SOLAR-W | OPER-SYN-SLF | CONV-SLF | CHILDRESS | PANHANDLE | 2026-01-14 | 166.42 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8
FAGUS SOLAR PARK SLF U3 | 25INR0672 | FAGUSSLR_UNIT3 | PV | SOLAR-W | OPER-SYN-SLF | CONV-SLF | CHILDRESS | PANHANDLE | 2025-10-03 | 166.57 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8 | 165.8
FIGHTING JAYS SOLAR U1 | 21INR0278 | JAY_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | FORT BEND | HOUSTON | 2025-10-17 | 119.63 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3 | 119.3
FIGHTING JAYS SOLAR U2 | 21INR0278 | JAY_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | FORT BEND | HOUSTON | 2025-10-17 | 160.46 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9 | 159.9
GREYHOUND SOLAR U5 | 26INR0669 | GRYH_SLR_SOLAR5 | PV | SOLAR-FW | OPER-SYN | CONV | ECTOR | WEST | 2025-11-20 | 28.06 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8
GREYHOUND SOLAR U6 | 26INR0669 | GRYH_SLR_SOLAR6 | PV | SOLAR-FW | OPER-SYN | CONV | ECTOR | WEST | 2025-11-20 | 28.06 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8 | 27.8
GREYHOUND SOLAR U7 | 26INR0669 | GRYH_SLR_SOLAR7 | PV | SOLAR-FW | OPER-SYN | CONV | ECTOR | WEST | 2025-11-20 | 94.59 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9 | 93.9
GREYHOUND SOLAR U8 | 26INR0670 | GRYH_SLR_SOLAR8 | PV | SOLAR-FW | OPER-SYN | CONV | ECTOR | WEST | 2025-11-13 | 101.6 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8 | 100.8
GRIMES COUNTY SOLAR U1 | 23INR0160 | GRIM_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | GRIMES | NORTH | 2025-11-30 | 104.46 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8 | 103.8
GRIMES COUNTY SOLAR U2 | 23INR0160 | GRIM_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | GRIMES | NORTH | 2025-11-30 | 79.87 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4 | 79.4
GRIMES COUNTY SOLAR U3 | 23INR0160 | GRIM_SLR_UNIT3 | PV | SOLAR-O | OPER-SYN | CONV | GRIMES | NORTH | 2025-11-30 | 26.92 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8 | 26.8
HICKERSON SOLAR U1 | 21INR0359 | HKSN_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | BOSQUE | NORTH | 2025-11-21 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7 | 149.7
HICKERSON SOLAR U2 | 21INR0359 | HKSN_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | BOSQUE | NORTH | 2025-11-21 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9 | 3.9
HICKERSON SOLAR U3 | 21INR0359 | HKSN_SLR_UNIT3 | PV | SOLAR-O | OPER-SYN | CONV | BOSQUE | NORTH | 2025-11-21 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5 | 157.5
HOVEY (BARILLA SOLAR 1B) | 12INR0059b | HOVEY_UNIT2 | PV | SOLAR-FW | OPER-SYN | CONV | PECOS | WEST | 2025-12-31 | 7.41 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4 | 7.4
MIDPOINT SOLAR | 24INR0139 | MIDP_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | HILL | NORTH | 2026-02-19 | 98.3 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 98
MILLERS BRANCH SOLAR U1 | 22INR0270 | MLB_SLR_SOLAR1 | PV | SOLAR-W | OPER-SYN | CONV | HASKELL | WEST | 2025-12-01 | 201.5 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MORROW LAKE SOLAR | 19INR0155 | MROW_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | FRIO | SOUTH | 2025-11-28 | 202.2 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
MYRTLE SOLAR U1 | 19INR0041 | MYR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2025-12-31 | 171.6 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2 | 167.2
MYRTLE SOLAR U2 | 19INR0041 | MYR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2025-12-31 | 149.6 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8 | 145.8
NORTON SOLAR | 19INR0035 | NRTN_SLR_SOLAR1 | PV | SOLAR-W | OPER-SYN | CONV | RUNNELS | WEST | 2025-11-24 | 125.54 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
ORIANA SOLAR | 24INR0093 | ORIANA_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | VICTORIA | SOUTH | 2025-11-15 | 180.67 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1 | 180.1
PARLIAMENT SOLAR U1 | 23INR0044 | PAR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | WALLER | HOUSTON | 2025-11-14 | 243.2 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7
PARLIAMENT SOLAR U2 | 23INR0044 | PAR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | WALLER | HOUSTON | 2025-11-14 | 240.2 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4 | 239.4
PHOTON SOLAR U1 | 25INR0493 | PHO_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-10-31 | 129.59 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1 | 129.1
PHOTON SOLAR U2 | 25INR0493 | PHO_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-10-31 | 106.07 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7
PHOTON SOLAR U3 | 23INR0111 | PHO_SOLAR3 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-10-31 | 109.99 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6 | 109.6
PHOTON SOLAR U4 | 25INR0673 | PHO_SOLAR4 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-10-31 | 105.98 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7 | 105.7
PINE FOREST SOLAR U1 | 20INR0203 | PINEFRST_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | HOPKINS | NORTH | 2025-12-01 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7 | 242.7
PINE FOREST SOLAR U2 | 20INR0203 | PINEFRST_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | HOPKINS | NORTH | 2025-12-01 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9 | 58.9
PINNINGTON SOLAR U1 | 24INR0010 | PINN_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | JACK | NORTH | 2026-04-30 | 215.34 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2 | 214.2
PINNINGTON SOLAR U2 | 24INR0010 | PINN_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | JACK | NORTH | 2026-04-30 | 219.18 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9
PINNINGTON SOLAR U3 | 24INR0010 | PINN_SLR_UNIT3 | PV | SOLAR-O | OPER-SYN | CONV | JACK | NORTH | 2026-04-30 | 219.18 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9 | 217.9
ROSELAND SOLAR U1 | 20INR0205 | ROSELAND_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2025-11-29 | 254 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250
ROSELAND SOLAR U2 | 20INR0205 | ROSELAND_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2025-11-29 | 137.8 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6 | 135.6
ROSELAND SOLAR U3 | 22INR0506 | ROSELAND_SOLAR3 | PV | SOLAR-O | OPER-SYN | CONV | FALLS | NORTH | 2025-11-29 | 116.2 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4 | 114.4
SAMSON SOLAR 1 U1 | 21INR0221 | SAMSON_1_G1 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2026-06-30 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SAMSON SOLAR 1 U2 | 21INR0221 | SAMSON_1_G2 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2026-06-30 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SAMSON SOLAR 2 U1 | 21INR0490 | SAMSON_1_G3 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-11-28 | 101.52 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SAMSON SOLAR 2 U2 | 21INR0490 | SAMSON_1_G4 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2025-11-28 | 101.52 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SAMSON SOLAR 3 U1 | 21INR0491 | SAMSON_3_G1 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2026-06-30 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SAMSON SOLAR 3 U2 | 21INR0491 | SAMSON_3_G2 | PV | SOLAR-O | OPER-SYN | CONV | LAMAR | NORTH | 2026-06-30 | 128.42 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
SBRANCH SOLAR PROJECT | 22INR0205 | SBE_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | WHARTON | SOUTH | 2025-08-22 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5 | 233.5
STAMPEDE SOLAR U1 | 22INR0409 | STAM_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | HOPKINS | NORTH | 2025-11-30 | 77.75 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77 | 77
STAMPEDE SOLAR U2 | 22INR0409 | STAM_SLR_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | HOPKINS | NORTH | 2025-11-30 | 178.55 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
STARR SOLAR RANCH U1 | 20INR0216 | STAR_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | STARR | SOUTH | 2025-08-14 | 70.45 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
STARR SOLAR RANCH U2 | 20INR0216 | STAR_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | STARR | SOUTH | 2025-08-14 | 66.28 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66
STILLHOUSE SOLAR | 24INR0166 | STLHS_SL_PV1 | PV | SOLAR-O | OPER-SYN | CONV | BELL | NORTH | 2025-11-11 | 210.8 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210 | 210
STONERIDGE SOLAR U1 | 24INR0031 | STRG_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | MILAM | SOUTH | 2025-11-01 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1 | 184.1
STONERIDGE SOLAR U2 | 24INR0031 | STRG_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | MILAM | SOUTH | 2025-11-01 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
TANGLEWOOD SOLAR U1 | 23INR0054 | TNG_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2025-12-15 | 125.1 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
TANGLEWOOD SOLAR U2 | 23INR0054 | TNG_SOLAR2 | PV | SOLAR-O | OPER-SYN | CONV | BRAZORIA | COASTAL | 2025-12-15 | 125.1 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
TRES BAHIAS SOLAR | 20INR0266 | TREB_SLR_SOLAR1 | PV | SOLAR-O | OPER-SYN | CONV | CALHOUN | COASTAL | 2025-11-30 | 196.29 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195
TULSITA SOLAR U1 | 21INR0223 | TUL_SLR_UNIT1 | PV | SOLAR-O | OPER-SYN | CONV | GOLIAD | SOUTH | 2025-11-30 | 128.08 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8
TULSITA SOLAR U2 | 21INR0223 | TUL_SLR_UNIT2 | PV | SOLAR-O | OPER-SYN | CONV | GOLIAD | SOUTH | 2025-11-30 | 128.12 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8 | 127.8
AE-TELVIEW ESS |  | TV_BESS | BA | STORAGE | OPER | CONV-DGR | FORT BEND | HOUSTON | 2024-12-04 | 9.96 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
AL PASTOR BESS |  | ALP_BESS_BESS1 | BA | STORAGE | OPER | CONV | DAWSON | WEST | 2024-11-01 | 103.1 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3 | 100.3
ANCHOR BESS U1 |  | ANCHOR_BESS1 | BA | STORAGE | OPER | CONV | CALLAHAN | WEST | 2022-02-25 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2 | 35.2
ANCHOR BESS U2 |  | ANCHOR_BESS2 | BA | STORAGE | OPER | CONV | CALLAHAN | WEST | 2022-02-25 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3 | 36.3
ANDROMEDA STORAGE SLF U1 |  | ANDMDSLR_BESS1 | BA | STORAGE | OPER-SLF | CONV-SLF | SCURRY | WEST | 2024-09-30 | 82.04 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9
ANDROMEDA STORAGE SLF U2 |  | ANDMDSLR_BESS2 | BA | STORAGE | OPER-SLF | CONV-SLF | SCURRY | WEST | 2024-09-30 | 78.31 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1
ANEMOI ENERGY STORAGE |  | ANEM_ESS_BESS1 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2024-06-11 | 200.9 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
ANGELO STORAGE |  | ANG_SLR_BESS1 | BA | STORAGE | OPER | CONV | TOM GREEN | WEST | 2025-06-30 | 102.97 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ANGLETON BESS |  | AE_BESS | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2025-03-18 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ANOLE BESS |  | ANOL_ESS_BES1 | BA | STORAGE | OPER | CONV | DALLAS | NORTH | 2025-07-22 | 247.1 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
ANTLIA BESS |  | ANTL_ESS_BES1 | BA | STORAGE | OPER | CONV | VAL VERDE | WEST | 2025-03-31 | 72.38 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
AVILA BESS |  | AVIL_ESS_BES1 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2025-05-01 | 164.28 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160
AZURE SKY BESS |  | AZURE_BESS1 | BA | STORAGE | OPER | CONV | HASKELL | WEST | 2021-08-09 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6 | 77.6
BAT CAVE |  | BATCAVE_BES1 | BA | STORAGE | OPER | CONV | MASON | SOUTH | 2021-06-01 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
BAY CITY BESS |  | BAY_CITY_BESS | BA | STORAGE | OPER | CONV-DGR | MATAGORDA | COASTAL | 2023-07-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
BELDING TNP (TRIPLE BUTTE BATTERY) |  | BELD_BELU1 | BA | STORAGE | OPER | CONV-DGR | PECOS | WEST | 2021-04-08 | 9.18 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
BLUE JAY BESS |  | BLUEJAY_BESS1 | BA | STORAGE | OPER | CONV | GRIMES | NORTH | 2022-11-17 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BLUE SUMMIT BATTERY |  | BLSUMMIT_BATTERY | BA | STORAGE | OPER | CONV | WILBARGER | WEST | 2017-04-30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
BOCO BESS |  | BOCO_ESS_ESS1 | BA | STORAGE | OPER | CONV | BORDEN | WEST | 2024-08-12 | 154 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BOCANOVA BESS |  | BCNV_ESS_BESS1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2025-07-19 | 150.46 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
BRIGHT ARROW STORAGE U1 |  | BR_ARROW_BESS1 | BA | STORAGE | OPER | CONV | HOPKINS | NORTH | 2025-06-30 | 49.34 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3 | 48.3
BRIGHT ARROW STORAGE U2 |  | BR_ARROW_BESS2 | BA | STORAGE | OPER | CONV | HOPKINS | NORTH | 2025-06-30 | 52.77 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7 | 51.7
BRP ALVIN |  | ALVIN_UNIT1 | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2022-10-19 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP ANGLETON |  | ANGLETON_UNIT1 | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2022-10-26 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP BRAZORIA |  | BRAZORIA_UNIT1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2020-10-08 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP DICKINSON |  | DICKNSON_UNIT1 | BA | STORAGE | OPER | CONV-DGR | GALVESTON | HOUSTON | 2022-10-19 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP DICKENS BESS U1 |  | DKNS_ESS_BES1 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2024-09-16 | 50.2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP DICKENS BESS U2 |  | DKNS_ESS_BES2 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2024-09-16 | 50.2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP DICKENS BESS U3 |  | DKNS_ESS_BES3 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2024-09-16 | 50.2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP DICKENS BESS U4 |  | DKNS_ESS_BES4 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2024-09-16 | 50.2 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP HEIGHTS |  | HEIGHTTN_UNIT1 | BA | STORAGE | OPER | CONV-DGR | GALVESTON | HOUSTON | 2020-11-24 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP HYDRA BESS |  | HYDR_ESS_BES1 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2024-10-04 | 200.8 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BRP LIBRA BESS |  | LBRA_ESS_BES1 | BA | STORAGE | OPER | CONV | GUADALUPE | SOUTH | 2024-04-09 | 201.02 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BRP LOOP 463 |  | L_463S_UNIT1 | BA | STORAGE | OPER | CONV-DGR | VICTORIA | SOUTH | 2021-08-11 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP LOPENO |  | LOPENO_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ZAPATA | SOUTH | 2021-12-17 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP MAGNOLIA |  | MAGNO_TN_UNIT1 | BA | STORAGE | OPER | CONV-DGR | GALVESTON | HOUSTON | 2022-10-26 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP ODESSA SW |  | ODESW_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ECTOR | WEST | 2020-07-17 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP PALEO BESS |  | PALE_ESS_BES1 | BA | STORAGE | OPER | CONV | HALE | PANHANDLE | 2024-10-04 | 200.8 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
BRP PAVO BESS U1 |  | PAVO_ESS_BESS1 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2024-09-06 | 87.9 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5
BRP PAVO BESS U2 |  | PAVO_ESS_BESS2 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2024-09-06 | 87.9 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5 | 87.5
BRP PUEBLO I |  | PUEBLO_UNIT1 | BA | STORAGE | OPER | CONV-DGR | MAVERICK | SOUTH | 2021-06-25 | 10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP PUEBLO II |  | PUEBLO_UNIT2 | BA | STORAGE | OPER | CONV-DGR | MAVERICK | SOUTH | 2021-06-25 | 10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP RANCHTOWN |  | K0_UNIT1 | BA | STORAGE | OPER | CONV-DGR | BEXAR | SOUTH | 2021-07-19 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP SWEENY |  | SWEENY_UNIT1 | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2022-09-14 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP TORTOLAS BESS |  | TORT_ESS_BESS1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2025-01-06 | 50.3 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
BRP ZAPATA I |  | ZAPATA_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ZAPATA | SOUTH | 2021-06-30 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BRP ZAPATA II |  | ZAPATA_UNIT2 | BA | STORAGE | OPER | CONV-DGR | ZAPATA | SOUTH | 2021-06-30 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BURKSOL BESS (DONEGAL BESS) |  | BKSL_ESS_BESS1 | BA | STORAGE | OPER | CONV | DICKENS | PANHANDLE | 2025-03-31 | 103.27 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BYRD RANCH STORAGE |  | BYRDR_ES_BESS1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2022-08-01 | 55.16 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
CACHI BESS |  | CACH_ESS_BESS1 | BA | STORAGE | OPER | CONV | GUADALUPE | SOUTH | 2025-03-31 | 205.46 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
CALLISTO I ENERGY CENTER U1 |  | CLO_BESS1 | BA | STORAGE | OPER | CONV | HARRIS | HOUSTON | 2024-08-15 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CALLISTO I ENERGY CENTER U2 |  | CLO_BESS2 | BA | STORAGE | OPER | CONV | HARRIS | HOUSTON | 2024-08-15 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CAMERON STORAGE (SABAL STORAGE) |  | CAMWIND_BESS1 | BA | STORAGE | OPER | CONV | CAMERON | COASTAL | 2024-03-26 | 16.67 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4 | 16.4
CARINA BESS |  | CARN_ESS_BES1 | BA | STORAGE | OPER | CONV | NUECES | COASTAL | 2025-03-19 | 154.11 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CASTLE GAP BATTERY |  | CASL_GAP_BATTERY1 | BA | STORAGE | OPER | CONV | UPTON | WEST | 2018-12-31 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CATARINA BESS |  | CATARINA_BESS | BA | STORAGE | OPER | CONV-DGR | DIMMIT | SOUTH | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CENTURY BESS |  | CNTRY_BESS1 | BA | STORAGE | OPER | CONV-DGR | TARRANT | NORTH | 2024-12-18 | 9.88 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CEDARVALE BESS |  | CEDRVALE_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CHILLINGHAM STORAGE |  | CHIL_SL1_BESS1 | BA | STORAGE | OPER | CONV | BELL | NORTH | 2025-08-02 | 153.93 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CHISHOLM GRID |  | CHISMGRD_BES1 | BA | STORAGE | EXT-OUT | CONV | TARRANT | NORTH | 2021-07-09 | 101.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CITRUS CITY BESS |  | CITRUSCY_BESS1 | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2025-01-22 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CISCO BESS |  | CISC_BESS | BA | STORAGE | OPER | CONV-DGR | EASTLAND | NORTH | 2024-10-29 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CONTINENTAL BESS |  | CONTINEN_BESS1 | BA | STORAGE | OPER | CONV-DGR | STARR | SOUTH | 2024-07-31 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
COMMERCE ST ESS |  | X4_SWRI | BA | STORAGE | OPER | CONV-DGR | BEXAR | SOUTH | 2020-10-14 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
CONNOLLY STORAGE |  | CNLY_ESS_BESS_1 | BA | STORAGE | OPER | CONV | WISE | NORTH | 2024-11-01 | 125.41 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
CORAL STORAGE U1 |  | CORALSLR_BESS1 | BA | STORAGE | OPER | CONV | FALLS | NORTH | 2023-12-15 | 48.4 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6
CORAL STORAGE U2 |  | CORALSLR_BESS2 | BA | STORAGE | OPER | CONV | FALLS | NORTH | 2023-12-15 | 52.2 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4 | 51.4
COYOTE SPRINGS BESS |  | COYOTSPR_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CROCKETT BESS |  | CR_BESS1 | BA | STORAGE | OPER | CONV-DGR | HARRIS | HOUSTON | 2024-12-13 | 9.88 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CROSBY BESS |  | CS_BESS | BA | STORAGE | OPER | CONV-DGR | HARRIS | HOUSTON | 2025-03-13 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CROSS TRAILS STORAGE |  | CROSSTRL_BESS1 | BA | STORAGE | OPER | CONV | SCURRY | WEST | 2025-05-25 | 58.29 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57
CROSSETT POWER U1 |  | CROSSETT_BES1 | BA | STORAGE | OPER | CONV | CRANE | WEST | 2021-08-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
CROSSETT POWER U2 |  | CROSSETT_BES2 | BA | STORAGE | OPER | CONV | CRANE | WEST | 2021-08-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
DAMON STORAGE |  | DA_BESS | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2025-03-21 | 4.98 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
DANISH FIELDS STORAGE U1 |  | DAN_BESS1 | BA | STORAGE | OPER | CONV | WHARTON | SOUTH | 2025-04-30 | 77.8 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3
DANISH FIELDS STORAGE U2 |  | DAN_BESS2 | BA | STORAGE | OPER | CONV | WHARTON | SOUTH | 2025-04-30 | 75.1 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7
DECORDOVA BESS U1 |  | DCSES_BES1 | BA | STORAGE | OPER | CONV | HOOD | NORTH | 2022-05-03 | 67.3 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
DECORDOVA BESS U2 |  | DCSES_BES2 | BA | STORAGE | OPER | CONV | HOOD | NORTH | 2022-05-03 | 67.3 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5 | 66.5
DECORDOVA BESS U3 |  | DCSES_BES3 | BA | STORAGE | OPER | CONV | HOOD | NORTH | 2022-05-03 | 64.2 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
DECORDOVA BESS U4 |  | DCSES_BES4 | BA | STORAGE | OPER | CONV | HOOD | NORTH | 2022-05-03 | 64.2 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5 | 63.5
DESERT WILLOW BESS |  | DSWL_ESS_BES1 | BA | STORAGE | OPER | CONV | ELLIS | NORTH | 2025-05-12 | 154.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
DIBOLL BESS |  | DIBOL_BESS | BA | STORAGE | OPER | CONV-DGR | ANGELINA | NORTH | 2023-02-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
DOGFISH BESS |  | DGFS_ESR_BESS1 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2025-04-16 | 78.2 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75
EBONY ENERGY STORAGE |  | EBNY_ESS_BESS1 | BA | STORAGE | OPER | CONV | COMAL | SOUTH | 2024-06-12 | 201.2 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
ENDURANCE PARK STORAGE |  | ENDPARKS_ESS1 | BA | STORAGE | OPER | CONV | SCURRY | WEST | 2022-11-01 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
ELIZA STORAGE |  | ELZA_SLR_BES1 | BA | STORAGE | OPER | CONV | KAUFMAN | NORTH | 2025-06-17 | 100.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ESTONIAN ENERGY STORAGE |  | ESTONIAN_BES1 | BA | STORAGE | OPER | CONV | DELTA | NORTH | 2023-06-01 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6 | 101.6
EVELYN BATTERY ENERGY STORAGE SYSTEM |  | EVLN_ESS_BESS1 | BA | STORAGE | OPER | CONV | GALVESTON | HOUSTON | 2025-05-06 | 227.9 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
EUNICE STORAGE |  | EUNICE_BES1 | BA | STORAGE | OPER | CONV | ANDREWS | WEST | 2020-12-31 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3 | 40.3
FALFUR BESS |  | FALFUR_BESS | BA | STORAGE | OPER | CONV-DGR | BROOKS | SOUTH | 2024-09-09 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FALFURRIAS BESS |  | FALFUR1_BESS1 | BA | STORAGE | OPER | CONV-DGR | BROOKS | SOUTH | 2025-02-15 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
FARMERSVILLE BESS |  | FRMRSVLW_BESS | BA | STORAGE | OPER | CONV-DGR | COLLIN | NORTH | 2024-06-18 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FARMERSVILLE WEST BESS 2 |  | FRMRSVL1_BES2 | BA | STORAGE | OPER | CONV-DGR | COLLIN | NORTH | 2025-02-20 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FAULKNER BESS |  | FAULKNER_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-08-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FENCE POST BESS U1 |  | FENCESLR_BESS1 | BA | STORAGE | OPER | CONV | NAVARRO | NORTH | 2023-03-03 | 72.01 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70
FIVE WELLS STORAGE |  | FIVEWSLR_BESS1 | BA | STORAGE | OPER | CONV | BELL | NORTH | 2024-06-04 | 228.54 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
FLAT TOP BATTERY |  | FLAT_TOP_FLATU1 | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2020-05-05 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
FLOWER VALLEY II BATT |  | FLOWERII_BESS1 | BA | STORAGE | OPER | CONV | REEVES | WEST | 2021-08-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
FORT DUNCAN BESS |  | FTDUNCAN_BESS_GEN | BA | STORAGE | OPER | CONV | MAVERICK | SOUTH | 2025-06-01 | 101.6 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
FORT MASON BESS |  | FORTMA_BESS1 | BA | STORAGE | OPER | CONV-DGR | MASON | SOUTH | 2025-06-30 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
GAMBIT BATTERY |  | GAMBIT_BESS1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2021-06-01 | 102.4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
GARDEN CITY EAST BESS |  | GRDNE_BESS | BA | STORAGE | OPER | CONV-DGR | GLASSCOCK | WEST | 2023-10-13 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GEORGETOWN SOUTH (RABBIT HILL ESS) |  | GEORSO_ESS_1 | BA | STORAGE | OPER | CONV-DGR | WILLIAMSON | SOUTH | 2019-11-12 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GIGA TEXAS ENERGY STORAGE |  | GIGA_ESS_BESS_1 | BA | STORAGE | OPER | CONV | TRAVIS | SOUTH | 2024-08-09 | 125.31 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125
GOMEZ BESS |  | GOMZ_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2023-06-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GREAT KISKADEE STORAGE |  | GKS_BESS_BESS1 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2025-02-14 | 102.46 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
GREGORY BESS |  | GREGORY_BESS1 | BA | STORAGE | OPER | CONV-DGR | SAN PATRICIO | COASTAL | 2024-11-07 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HAMILTON BESS U1 |  | HAMILTON_BESS | BA | STORAGE | OPER | CONV-DGR | VAL VERDE | WEST | 2023-08-15 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HEARN ROAD BESS |  | HEARN_RD_BESS1 | BA | STORAGE | OPER | CONV-DGR | NUECES | COASTAL | 2025-01-15 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
HIGH LONESOME BESS |  | HI_LONEB_BESS1 | BA | STORAGE | OPER | CONV | CROCKETT | WEST | 2022-07-27 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
HOLCOMB BESS |  | HOLCOMB_BESS | BA | STORAGE | OPER | CONV-DGR | LA SALLE | SOUTH | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HOLY ESS U1 |  | HLY_BESS1 | BA | STORAGE | OPER | CONV | HARRIS | HOUSTON | 2024-12-30 | 104.66 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2
HOLY ESS U2 |  | HLY_BESS2 | BA | STORAGE | OPER | CONV | HARRIS | HOUSTON | 2024-12-30 | 104.66 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2 | 102.2
HOUSE MOUNTAIN BESS |  | HOUSEMTN_BESS1 | BA | STORAGE | OPER | CONV | BREWSTER | WEST | 2023-07-29 | 61.5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
HUMMINGBIRD STORAGE |  | HMNG_ESS_BESS1 | BA | STORAGE | OPER | CONV | DENTON | NORTH | 2024-10-11 | 100.38 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
INADALE ESS |  | INDL_ESS | BA | STORAGE | OPER | CONV | NOLAN | WEST | 2017-12-04 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
INERTIA BESS |  | INRT_W_BESS_1 | BA | STORAGE | OPER | CONV | HASKELL | WEST | 2024-05-08 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13
JOHNSON CITY BESS |  | JOHNCI_UNIT_1 | BA | STORAGE | OPER | CONV-DGR | BLANCO | SOUTH | 2020-08-05 | 2.25 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3 | 2.3
JADE STORAGE U1 |  | JADE_SLR_BESS1 | BA | STORAGE | OPER | CONV | SCURRY | WEST | 2024-09-30 | 78.53 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1
JADE STORAGE U2 |  | JADE_SLR_BESS2 | BA | STORAGE | OPER | CONV | SCURRY | WEST | 2024-09-30 | 82.27 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9
JARVIS BESS U1 |  | JAR_BES1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2025-06-12 | 149.29 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2 | 147.2
JARVIS BESS U2 |  | JAR_BES2 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2025-06-12 | 157.71 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7 | 157.7
JUDKINS BESS |  | JDKNS_BESS | BA | STORAGE | OPER | CONV-DGR | ECTOR | WEST | 2024-02-22 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
JUNCTION BESS |  | JUNCTION_BESS | BA | STORAGE | OPER | CONV-DGR | KIMBLE | SOUTH | 2023-06-14 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
JUNCTION NORTH BESS |  | JUNORTH1_BES1 | BA | STORAGE | OPER | CONV-DGR | KIMBLE | SOUTH | 2025-03-03 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
KINGSBERY ENERGY STORAGE SYSTEM |  | KB_ESS_KB_ESS | BA | STORAGE | OPER | CONV-SODG | TRAVIS | SOUTH | 2017-12-01 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
LIGGETT SWITCH BESS |  | LIGSW_BESS1 | BA | STORAGE | OPER | CONV-DGR | DALLAS | NORTH | 2025-02-08 | 9.88 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
LILY STORAGE |  | LILY_BESS1 | BA | STORAGE | OPER | CONV | KAUFMAN | NORTH | 2021-06-01 | 51.7 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
LIMOUSIN OAK STORAGE |  | LMO_BESS1 | BA | STORAGE | OPER | CONV | GRIMES | NORTH | 2024-09-11 | 100.42 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LONESTAR BESS |  | LONESTAR_BESS | BA | STORAGE | OPER | CONV-DGR | WARD | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
LONGBOW BESS |  | LON_BES1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2024-11-13 | 180.8 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174 | 174
LOWER RIO BESS |  | LOWR_ESS_BESS1 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2025-03-31 | 60.37 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
LUFKIN SOUTH BESS |  | LFSTH_BESS | BA | STORAGE | OPER | CONV-DGR | ANGELINA | NORTH | 2024-02-21 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
MADERO GRID U1 |  | MADERO_UNIT1 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2022-01-13 | 100.79 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MADERO GRID U2 (IGNACIO GRID) |  | MADERO_UNIT2 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2022-03-03 | 100.79 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
MAINLAND BESS |  | MAINLAND_BESS | BA | STORAGE | OPER | CONV-DGR | GALVESTON | HOUSTON | 2024-06-21 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MAYBERRY II BESS |  | MAYBERRY_BESS2 | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2025-01-21 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MIDWAY BESS U1 |  | MIDWY_BESS1 | BA | STORAGE | OPER | CONV-DGR | ECTOR | WEST | 2025-05-05 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
MINERAL WELLS EAST BESS |  | MNWLE_BESS | BA | STORAGE | OPER | CONV-DGR | PALO PINTO | NORTH | 2023-10-13 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MU ENERGY STORAGE SYSTEM |  | MU_ESS_MU_ESS | BA | STORAGE | OPER | CONV-SODG | TRAVIS | SOUTH | 2018-07-23 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
MUENSTER BESS |  | MUENSTER_BESS1 | BA | STORAGE | OPER | CONV-DGR | COOKE | NORTH | 2025-05-22 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MUSTANG BAYOU BESS |  | MU_BESS | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2025-06-04 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
MUSTANG CREEK STORAGE |  | MUSTNGCK_BES1 | BA | STORAGE | OPER | CONV | JACKSON | SOUTH | 2023-03-29 | 71.49 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5 | 70.5
MYRTLE STORAGE U1 |  | MYR_BES1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2025-02-28 | 76.93 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3 | 76.3
MYRTLE STORAGE U2 |  | MYR_BES2 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2025-02-28 | 74.27 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7 | 73.7
NOBLE STORAGE U1 |  | NOBLESLR_BESS1 | BA | STORAGE | OPER | CONV | DENTON | NORTH | 2022-08-01 | 63.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
NOBLE STORAGE U2 |  | NOBLESLR_BESS2 | BA | STORAGE | OPER | CONV | DENTON | NORTH | 2022-08-01 | 63.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5 | 62.5
NORTH ALAMO BESS |  | N_ALAMO_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-07-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
NORTH COLUMBIA (ROUGHNECK STORAGE) |  | NCO_ESS1 | BA | STORAGE | OPER | CONV | BRAZORIA | COASTAL | 2021-07-01 | 51.75 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
NORTH FORK |  | NF_BRP_BES1 | BA | STORAGE | OPER | CONV | WILLIAMSON | SOUTH | 2021-05-15 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5
NORTH MERCEDES BESS |  | N_MERCED_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-12-14 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
NOTREES BATTERY FACILITY |  | NWF_NBS | BA | STORAGE | OPER | CONV | WINKLER | WEST | 2012-10-01 | 36 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7 | 33.7
OLNEY BESS |  | OLNEYTN_BESS | BA | STORAGE | OPER | CONV-DGR | YOUNG | WEST | 2023-06-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PADUA GRID BESS |  | PAD1_ESS_BESS1 | BA | STORAGE | OPER | CONV | BEXAR | SOUTH | 2025-07-28 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
PAULINE BESS |  | PAULN_BESS | BA | STORAGE | OPER | CONV-DGR | HENDERSON | NORTH | 2024-02-22 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
PAVLOV BESS |  | PAVLOV_BESS | BA | STORAGE | OPER | CONV-DGR | MATAGORDA | COASTAL | 2024-10-01 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PEARSALL BESS |  | PEARSAL3_BES1 | BA | STORAGE | OPER | CONV-DGR | FRIO | SOUTH | 2025-07-09 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PHOTON STORAGE U1 |  | PHO_BES1 | BA | STORAGE | OPER | CONV | WHARTON | SOUTH | 2025-05-13 | 152.74 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
PHOTON STORAGE U2 |  | PHO_BES2 | BA | STORAGE | OPER | CONV | WHARTON | SOUTH | 2025-06-16 | 152.74 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
PORT LAVACA BATTERY |  | PRTLAVS_BESS1 | BA | STORAGE | OPER | CONV-DGR | CALHOUN | COASTAL | 2019-12-03 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PIRATE BESS |  | PIRATE1_BESS1 | BA | STORAGE | OPER | CONV-DGR | SAN PATRICIO | COASTAL | 2025-05-29 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
PRAIRIE CREEK BESS |  | PRCRK_BESS1 | BA | STORAGE | OPER | CONV-DGR | DALLAS | NORTH | 2025-09-10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PYOTE TNP (SWOOSE BATTERY) |  | PYOTE_SWOOSEU1 | BA | STORAGE | OPER | CONV-DGR | WARD | WEST | 2021-02-05 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PYRON BESS 2A |  | PYR_ESS2A | BA | STORAGE | OPER | CONV | NOLAN | WEST | 2022-12-01 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
PYRON BESS 2B |  | PYR_ESS2B | BA | STORAGE | OPER | CONV | NOLAN | WEST | 2022-12-01 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1 | 15.1
PYRON ESS |  | PYR_ESS | BA | STORAGE | OPER | CONV | NOLAN | WEST | 2017-12-08 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
QUEEN BESS |  | QUEEN_BA_BESS1 | BA | STORAGE | OPER | CONV | UPTON | WEST | 2022-05-31 | 51.1 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RATTLESNAKE BESS |  | RTLSNAKE_BESS | BA | STORAGE | OPER | CONV-DGR | WARD | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
REGIS MOORE FIELD BESS |  | MOORE_FL_BESS1 | BA | STORAGE | OPER | CONV | HIDALGO | SOUTH | 2024-10-18 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
REGIS PALACIOS BESS |  | PALACIOS_BESS1 | BA | STORAGE | OPER | CONV-DGR | MATAGORDA | COASTAL | 2024-11-19 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
REPUBLIC ROAD STORAGE |  | RPUBRDS_ESS1 | BA | STORAGE | OPER | CONV | ROBERTSON | NORTH | 2021-10-29 | 51.75 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RIO GRANDE CITY BESS 2 |  | RIO_GRAN_BESS2 | BA | STORAGE | OPER | CONV-DGR | STARR | SOUTH | 2025-01-22 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
RIVER BEND (BRAZOS BEND BESS) |  | RBN_BESS1 | BA | STORAGE | OPER | CONV | FORT BEND | HOUSTON | 2024-10-09 | 101.64 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
RIVER VALLEY STORAGE U1 |  | RVRVLYS_ESS1 | BA | STORAGE | OPER | CONV | WILLIAMSON | SOUTH | 2022-11-01 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RIVER VALLEY STORAGE U2 |  | RVRVLYS_ESS2 | BA | STORAGE | OPER | CONV | WILLIAMSON | SOUTH | 2022-11-01 | 51.5 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RODEO RANCH ENERGY STORAGE U1 |  | RRANCHES_UNIT1 | BA | STORAGE | OPER | CONV | REEVES | WEST | 2023-11-07 | 150.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
RODEO RANCH ENERGY STORAGE U2 |  | RRANCHES_UNIT2 | BA | STORAGE | OPER | CONV | REEVES | WEST | 2023-11-07 | 150.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
ROSELAND STORAGE |  | ROSELAND_BESS1 | BA | STORAGE | OPER | CONV | FALLS | NORTH | 2022-12-05 | 51.6 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
RUSSEK STREET BESS |  | RUSSEKST_BESS | BA | STORAGE | OPER | CONV-DGR | REAGAN | WEST | 2024-12-20 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SADDLEBACK BESS |  | SADLBACK_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-08-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SANDLAKE BESS |  | SANDLAK1_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2024-10-01 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
SARAGOSA BESS |  | SGSA_BESS1 | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2022-04-13 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SCREWBEAN BESS |  | SBEAN_BESS | BA | STORAGE | OPER | CONV-DGR | CULBERSON | WEST | 2022-09-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SHAMROCK ENERGY STORAGE (SLF) |  | SHAMROCK_BESS1 | BA | STORAGE | OPER-SLF | CONV-SLF | CROCKETT | WEST | 2025-07-01 | 99.33 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3 | 99.3
SHEEP CREEK STORAGE |  | SHEEPCRK_BESS1 | BA | STORAGE | OPER | CONV | EASTLAND | NORTH | 2024-07-01 | 142.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1 | 135.1
SILICON HILL STORAGE U1 |  | SLCNHLS_ESS1 | BA | STORAGE | OPER | CONV | TRAVIS | SOUTH | 2021-06-15 | 51.8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SILICON HILL STORAGE U2 |  | SLCNHLS_ESS2 | BA | STORAGE | OPER | CONV | TRAVIS | SOUTH | 2021-06-15 | 51.8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
SMT ELSA |  | ELSA_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-12-14 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT GARCENO BESS |  | GARCENO_BESS | BA | STORAGE | OPER | CONV-DGR | MATAGORDA | COASTAL | 2023-09-03 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT LOS FRESNOS |  | L_FRESNO_BESS | BA | STORAGE | OPER | CONV-DGR | CAMERON | COASTAL | 2023-11-30 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT MAYBERRY BESS |  | MAYBERRY_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2023-12-20 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT RIO GRANDE CITY BESS |  | RIO_GRAN_BESS | BA | STORAGE | OPER | CONV-DGR | STARR | SOUTH | 2023-11-30 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SMT SANTA ROSA |  | S_SNROSA_BESS | BA | STORAGE | OPER | CONV-DGR | CAMERON | COASTAL | 2023-12-14 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SNYDER |  | DPCRK_UNIT1 | BA | STORAGE | OPER | CONV-DGR | SCURRY | WEST | 2021-07-13 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
SP JAGUAR BESS U1 |  | JAG_SLR_BESS1 | BA | STORAGE | OPER | CONV | MCLENNAN | NORTH | 2025-06-30 | 157.1 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SP JAGUAR BESS U2 |  | JAG_SLR_BESS2 | BA | STORAGE | OPER | CONV | MCLENNAN | NORTH | 2025-06-30 | 157.15 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
SP TX-12B BESS |  | SPTX12B_BES1 | BA | STORAGE | OPER | CONV | UPTON | WEST | 2021-11-22 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1 | 25.1
SPENCER BESS |  | SP_BESS | BA | STORAGE | OPER | CONV-DGR | HARRIS | HOUSTON | 2025-09-30 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
STAMPEDE BESS U1 |  | STAM_SLR_BESS1 | BA | STORAGE | OPER | CONV | HOPKINS | NORTH | 2023-03-03 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 70 | 70 | 70 | 70 | 70
ST. GALL I ENERGY STORAGE |  | SGAL_BES_BESS1 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2024-03-26 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
ST. GALL II ENERGY STORAGE |  | SGAL_BES_BESS2 | BA | STORAGE | OPER | CONV | PECOS | WEST | 2025-06-01 | 102.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SUN VALLEY BESS U1 |  | SUNVASLR_BESS1 | BA | STORAGE | OPER | CONV | HILL | NORTH | 2023-12-28 | 54.08 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3 | 53.3
SUN VALLEY BESS U2 |  | SUNVASLR_BESS2 | BA | STORAGE | OPER | CONV | HILL | NORTH | 2023-12-28 | 47.32 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7 | 46.7
SWEETWATER BESS |  | SWTWR_UNIT1 | BA | STORAGE | OPER | CONV-DGR | NOLAN | WEST | 2021-04-01 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SWOOSE II |  | SWOOSEII_BESS1 | BA | STORAGE | OPER | CONV | WARD | WEST | 2021-08-01 | 101.5 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
TIMBERWOLF BESS |  | TBWF_ESS_BES1 | BA | STORAGE | OPER | CONV | CRANE | WEST | 2023-09-01 | 150.34 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
TOYAH POWER STATION |  | CHERRYCR_BESS | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2021-07-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
TIDWELL PRAIRIE STORAGE U1 |  | TDWLPR_1_BESS1 | BA | STORAGE | OPER | CONV | ROBERTSON | NORTH | 2025-06-01 | 102 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
TIDWELL PRAIRIE STORAGE U2 |  | TDWLPR_1_BESS2 | BA | STORAGE | OPER | CONV | ROBERTSON | NORTH | 2025-06-01 | 102 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
TURQUOISE STORAGE |  | TURQBESS_BESS1 | BA | STORAGE | OPER | CONV | HUNT | NORTH | 2023-02-10 | 196.2 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190
TYNAN BESS |  | TYNAN01_BESS1 | BA | STORAGE | OPER | CONV-DGR | BEE | SOUTH | 2025-05-01 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
VAL VERDE BESS |  | MV_VALV4_BESS | BA | STORAGE | OPER | CONV-DGR | HIDALGO | SOUTH | 2024-01-24 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
VORTEX BESS |  | VORTEX_BESS1 | BA | STORAGE | OPER | CONV | THROCKMORTON | WEST | 2022-04-13 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8 | 121.8
WALSTROM BESS |  | WAL_BESS_1 | BA | STORAGE | OPER | CONV | AUSTIN | SOUTH | 2025-04-15 | 205.31 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
WEST COLUMBIA (PROSPECT STORAGE) |  | WCOLLOCL_BSS_U1 | BA | STORAGE | OPER | CONV-DGR | BRAZORIA | COASTAL | 2019-12-12 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
WEST HARLINGEN BESS |  | W_HARLIN_BESS | BA | STORAGE | OPER | CONV-DGR | CAMERON | COASTAL | 2023-12-14 | 9.99 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
WESTOVER BESS |  | WOVER_UNIT1 | BA | STORAGE | OPER | CONV-DGR | ECTOR | WEST | 2021-08-01 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WEIL TRACT BESS |  | WEIL_TRC_BESS | BA | STORAGE | OPER | CONV-DGR | NUECES | COASTAL | 2023-10-13 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
WIGEON WHISTLE BESS |  | WIG_ESS_BES1 | BA | STORAGE | OPER | CONV | COLLIN | NORTH | 2024-12-20 | 122.9 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
WOLF TANK STORAGE |  | WFTANK_ESS1 | BA | STORAGE | OPER | CONV | WEBB | SOUTH | 2023-03-15 | 150.4 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
WORSHAM BATTERY |  | WORSHAM_BESS1 | BA | STORAGE | OPER | CONV-DGR | REEVES | WEST | 2019-12-30 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ZIER STORAGE U1 |  | ZIER_SLR_BES1 | BA | STORAGE | OPER | CONV | KINNEY | SOUTH | 2024-04-26 | 40.08 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40
BEXAR ESS | 23INR0381 | BEXAR_ES_BESS1 | BA | STORAGE | OPER-SYN | CONV | BEXAR | SOUTH | 2025-11-26 | 102.3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BIG STAR STORAGE | 21INR0469 | BIG_STAR_BESS | BA | STORAGE | OPER-SYN | CONV | BASTROP | SOUTH | 2026-01-31 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80
BLACK SPRINGS BESS SLF | 24INR0315 | BLACKSPR_UNIT1 | BA | STORAGE | OPER-SYN-SLF | CONV-SLF | PALO PINTO | NORTH | 2025-10-15 | 120.68 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120
BLEVINS STORAGE | 23INR0119 | BLVN_SLR_BESS1 | BA | STORAGE | OPER-SYN | CONV | FALLS | NORTH | 2025-11-12 | 188.24 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
CARRIZO SPRINGS BESS | 25INR0592 | CARRIZO_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | DIMMIT | SOUTH | 2025-10-20 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CARTWHEEL BESS 1 | 23INR0494 | CARTWHL_BESS1 | BA | STORAGE | OPER-SYN | CONV | HOPKINS | NORTH | 2025-12-23 | 154.2 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
CORAZON STORAGE | 23INR0343 | CORAZON_BESS1 | BA | STORAGE | OPER-SYN | CONV | WEBB | SOUTH | 2025-12-05 | 204.8 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
COTTONWOOD BAYOU STORAGE | 21INR0443 | CTW_BESS1 | BA | STORAGE | OPER-SYN | CONV | BRAZORIA | COASTAL | 2025-11-19 | 153.03 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
COTULLA BESS 1 | 24INR0638 | COTULLA_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | LA SALLE | SOUTH | 2025-11-27 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
EMPIRE CENTRAL BESS | 24INR0659 | EMPCT1_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | DALLAS | NORTH | 2025-10-19 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 10 | 10 | 10 | 10 | 10 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 10 | 10 | 10 | 10 | 10
GEARS BESS | 24INR0595 | GZ_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | HARRIS | HOUSTON | 2025-10-21 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GOODWIN BESS | 25INR0594 | GOODWIN_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | HIDALGO | SOUTH | 2025-10-20 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HEADCAMP ENERGY STORAGE PLANT | 23INR0401 | HEADCAMP_BESS1 | BA | STORAGE | OPER-SYN | CONV | PECOS | WEST | 2025-11-26 | 152.88 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
IEP ORCHARD BESS | 23INR0556 | OR_BESS | BA | STORAGE | OPER-SYN | CONV-DGR | FORT BEND | HOUSTON | 2025-12-20 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LAURELES BESS | 23INR0499 | LAURELES_BESS | BA | STORAGE | OPER-SYN | CONV-DGR | CAMERON | COASTAL | 2025-11-12 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
LUCKY BLUFF BESS SLF | 24INR0295 | LUCKYBLU_UNIT1 | BA | STORAGE | OPER-SYN-SLF | CONV-SLF | ERATH | NORTH | 2025-10-15 | 100.8 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
LYSSY BESS | 25INR0597 | LYSSY_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | WILSON | SOUTH | 2025-12-22 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MEDINA LAKE BESS | 24INR0499 | MEDILA_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | BANDERA | SOUTH | 2025-12-20 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MIDPOINT STORAGE | 24INR0138 | MIDP_SLR_BESS1 | BA | STORAGE | OPER-SYN | CONV | HILL | NORTH | 2026-02-19 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9
MILTON BESS | 23INR0552 | MILTON_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | KARNES | SOUTH | 2025-08-12 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
OLMITO BESS | 25INR0649 | OLMITO_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | CAMERON | COASTAL | 2025-12-05 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
PINE FOREST BESS | 22INR0526 | PINEFRST_BESS1 | BA | STORAGE | OPER-SYN | CONV | HOPKINS | NORTH | 2025-10-29 | 200.74 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200
PLATINUM STORAGE U1 | 22INR0554 | PLATINUM_BES1 | BA | STORAGE | OPER-SYN | CONV | FANNIN | NORTH | 2026-02-26 | 152.9 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3 | 148.3
PLATINUM STORAGE U2 | 22INR0554 | PLATINUM_BES2 | BA | STORAGE | OPER-SYN | CONV | FANNIN | NORTH | 2026-02-26 | 157 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7 | 151.7
POTEET BESS | 25INR0715 | POTEETS_BESS | BA | STORAGE | OPER-SYN | CONV-DGR | ATASCOSA | SOUTH | 2025-12-19 | 9.95 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
RADIAN STORAGE SLF U1 | 24INR0631 | RADN_SLR_BESS1 | BA | STORAGE | OPER-SYN-SLF | CONV-SLF | BROWN | NORTH | 2025-11-07 | 78.26 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1 | 78.1
RADIAN STORAGE SLF U2 | 24INR0631 | RADN_SLR_BESS2 | BA | STORAGE | OPER-SYN-SLF | CONV-SLF | BROWN | NORTH | 2025-11-07 | 81.99 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9 | 81.9
SEVEN FLAGS BESS | 23INR0351 | SEVNF_ES_BESS1 | BA | STORAGE | OPER-SYN | CONV | WEBB | SOUTH | 2026-01-07 | 102.7 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
STONERIDGE BESS | 25INR0389 | STRG_SLR_BESS1 | BA | STORAGE | OPER-SYN | CONV | MILAM | SOUTH | 2025-12-30 | 101.9 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
TANZANITE STORAGE U1 | 22INR0549 | TANZ_ESS_BES1 | BA | STORAGE | OPER-SYN | CONV | HENDERSON | NORTH | 2025-11-15 | 132.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9
TANZANITE STORAGE U2 | 22INR0549 | TANZ_ESS_BES2 | BA | STORAGE | OPER-SYN | CONV | HENDERSON | NORTH | 2025-11-15 | 132.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9 | 128.9
TORRECILLAS BESS | 23INR0529 | TORR_BESS1 | BA | STORAGE | OPER-SYN | CONV-TGR | WEBB | SOUTH | 2025-12-31 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
WHARTON BESS | 22INR0608 | WR_BESS1 | BA | STORAGE | OPER-SYN | CONV-DGR | WHARTON | SOUTH | 2025-12-08 | 9.96 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
WIZARD BESS | 25INR0300 | WZRD_ESS_BES1 | BA | STORAGE | OPER-SYN | CONV | GALVESTON | HOUSTON | 2025-12-18 | 150.82 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
XE MURAT [ADLONG] STORAGE | 24INR0329 | ADL1_BESS1 | BA | STORAGE | OPER-SYN | CONV | HARRIS | HOUSTON | 2025-09-24 | 60.14 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
A4 PEARSALL DGR U1 (LIFE CYCLE POWER, LCP) | 26INR0675 | A4_DGR1 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-10-10 | 35 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2
A4 PEARSALL DGR U2 (LIFE CYCLE POWER, LCP) | 26INR0675 | A4_DGR2 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-10-10 | 35 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2
K2 NACOGDOCHES DGR U1 (LIFE CYCLE POWER, LCP) | 26INR0681 | K2_DGR1 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-10-30 | 29.4 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 23.2 | 23.2 | 23.2 | 23.2 | 23.2 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5
K2 NACOGDOCHES DGR U2 (LIFE CYCLE POWER, LCP) | 26INR0681 | K2_DGR2 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-10-30 | 29.4 | 20.1 | 20.1 | 20.1 | 20.1 | 20.1 | 23.2 | 23.2 | 23.2 | 23.2 | 23.2 | 21.6 | 21.6 | 21.6 | 21.6 | 21.6 | 21.5 | 21.5 | 21.5 | 21.5 | 21.5
P2 HIGHLAND HILLS DGR U1 (LIFE CYCLE POWER, LCP) | 26INR0666 | P2_DGR1 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-09-30 | 40.9 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2
P2 HIGHLAND HILLS DGR U2 (LIFE CYCLE POWER, LCP) | 26INR0666 | P2_DGR2 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-09-30 | 40.9 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2 | 24.2
Q1 VALLEY ROAD DGR (LIFE CYCLE POWER, LCP) | 26INR0676 | Q1_DGR1 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-10-15 | 29.4 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
V H BRAUNIG STG 3 (RMR FROM 3/1/25 TO 3/1/27) |  | BRAUNIG_VHB3 | ST | GAS | RMR | CONV | BEXAR | SOUTH | 1970-08-01 | 420 | 412 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0 | 412 | 0 | 0 | 0 | 0
V2 BROOKS FIELD DGR U1 (LIFE CYCLE POWER, LCP) | 26INR0694 | V2_DGR1 | GT | DIESEL | OPER-SYN | CONV | BEXAR | SOUTH | 2025-10-31 | 32 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 26 | 26 | 26 | 26 | 26 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6
V2 BROOKS FIELD DGR U2 (LIFE CYCLE POWER, LCP) | 26INR0694 | V2_DGR2 | GT | DIESEL | OPER-SYN | CONV | BEXAR | SOUTH | 2025-10-31 | 32 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 26 | 26 | 26 | 26 | 26 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6
V2 BROOKS FIELD DGR U3 (LIFE CYCLE POWER, LCP) | 26INR0694 | V2_DGR3 | GT | DIESEL | OPER-SYN | CONV | BEXAR | SOUTH | 2025-10-31 | 32 | 21.2 | 21.2 | 21.2 | 21.2 | 21.2 | 26 | 26 | 26 | 26 | 26 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6 | 22.6
V4 PALO ALTO DGR (LIFE CYCLE POWER, LCP) | 25INR0777 | V4_DGR1 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-10-21 | 40.9 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1 | 19.1
X1 MEDINA BASE DGR (LIFE CYCLE POWER, LCP) | 26INR0674 | X1_DGR1 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-09-04 | 29.4 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5 | 17.5
Z0 BECK ROAD DGR U1 (LIFE CYCLE POWER, LCP) | 26INR0683 | Z0_DGR1 | GT | DIESEL | OPER-SYN | CONV | BEXAR | SOUTH | 2025-10-31 | 29.4 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9 | 12.9
Z0 BECK ROAD DGR U2 (LIFE CYCLE POWER, LCP) | 26INR0683 | Z0_DGR2 | GT | DIESEL | OPER-SYN | CONV | BEXAR | SOUTH | 2025-10-31 | 29.4 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8 | 16.8
Z5 SOUTHTON DGR (LIFE CYCLE POWER, LCP) | 26INR0684 | Z5_DGR1 | GT | DIESEL | OPER | CONV | BEXAR | SOUTH | 2025-09-19 | 29.4 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5 | 19.5
EAST TIE |  | DC_E | MWH | MWH | OPER | DC-TIE | FANNIN | NORTH |  | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600 | 600
NORTH TIE |  | DC_N | MWH | MWH | OPER | DC-TIE | WILBARGER | WEST |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
LAREDO VFT TIE |  | DC_L | MWH | MWH | OPER | DC-TIE | WEBB | SOUTH |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
SHARYLAND RAILROAD TIE |  | DC_R | MWH | MWH | OPER | DC-TIE | HIDALGO | SOUTH |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
BASRANCH (TEF) | 25INR0008 |  | CC | GAS | PLAN | CONV | WARD | WEST | 2028-12-01 | 1390 | 0 | 0 | 0 | 1300 | 1300 | 0 | 0 | 1350 | 1350 | 1350 | 0 | 0 | 0 | 1350 | 1350 | 0 | 0 | 0 | 1350 | 1350
CEDAR BAYOU 5 (TEF) | 23INR0029 |  | CC | GAS | PLAN | CONV | CHAMBERS | HOUSTON | 2027-12-15 | 721 | 0 | 0 | 674 | 674 | 674 | 0 | 0 | 697 | 697 | 697 | 0 | 0 | 697 | 697 | 697 | 0 | 0 | 697 | 697 | 697
CEDARVALE GAS | 25INR0710 |  | IC | GAS | PLAN | CONV-DGR | WARD | WEST | 2026-03-02 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
COYOTE SPRINGS AGR1 | 24INR0645 |  | IC | DIESEL | PLAN | CONV-DGR | REEVES | WEST | 2025-11-26 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ENCHANTED ROCK NEWPP | 22INR0546 |  | IC | GAS | PLAN | CONV | HARRIS | HOUSTON | 2026-02-28 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30
NRG THW GT 345 (TEF) | 24INR0482 |  | GT | GAS | PLAN | CONV | HARRIS | HOUSTON | 2026-05-01 | 456 | 422 | 422 | 422 | 422 | 422 | 456 | 456 | 456 | 456 | 456 | 0 | 456 | 456 | 456 | 456 | 456 | 456 | 456 | 456 | 456
PIN PEAKING ENERGY CENTER 1 (TEF) | 26INR0049 |  | GT | GAS | PLAN | CONV | FREESTONE | NORTH | 2026-05-01 | 229.5 | 206 | 206 | 206 | 206 | 206 | 218 | 218 | 218 | 218 | 218 | 0 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218
PIN PEAKING ENERGY CENTER 2 (TEF) | 26INR0109 |  | GT | GAS | PLAN | CONV | FREESTONE | NORTH | 2026-05-01 | 229.5 | 208 | 208 | 208 | 208 | 208 | 220 | 220 | 220 | 220 | 220 | 0 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220
PYOTE GAS | 25INR0718 |  | IC | GAS | PLAN | CONV-DGR | WARD | WEST | 2026-03-02 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
STAGHORN GAS | 26INR0698 |  | IC | GAS | PLAN | CONV-DGR | WARD | WEST | 2026-05-02 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ROCK ISLAND GENERATING (TEF) | 27INR0321 |  | IC | GAS | PLAN | CONV | COLORADO | SOUTH | 2027-06-01 | 121.8 | 0 | 121.8 | 121.8 | 121.8 | 121.8 | 0 | 121.8 | 121.8 | 121.8 | 121.8 | 0 | 0 | 121.8 | 121.8 | 121.8 | 0 | 121.8 | 121.8 | 121.8 | 121.8
SADDLEBACK AGR1 | 24INR0646 |  | IC | DIESEL | PLAN | CONV-DGR | REEVES | WEST | 2025-11-26 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
TIMMERMAN POWER PLANT PHASE 2 | 25INR0503 |  | IC | GAS | PLAN | CONV | CALDWELL | SOUTH | 2026-05-01 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 0 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
TIMMERMAN POWER PLANT PHASE 2B | 26INR0735 |  | IC | GAS | PLAN | CONV | CALDWELL | SOUTH | 2026-08-14 | 94.2 | 0 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 0 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2 | 94.2
AQUILLA LAKE 3 WIND | 22INR0499 |  | WT | WIND-O | PLAN | CONV | HILL | NORTH | 2027-03-01 | 297.4 | 0 | 297.4 | 297.4 | 297.4 | 297.4 | 0 | 297.4 | 297.4 | 297.4 | 297.4 | 0 | 297.4 | 297.4 | 297.4 | 297.4 | 0 | 297.4 | 297.4 | 297.4 | 297.4
BLUEBONNET PRAIRIE WIND | 25INR0247 |  | WT | WIND-O | PLAN | CONV | NAVARRO | NORTH | 2027-07-15 | 173 | 0 | 0 | 173 | 173 | 173 | 0 | 173 | 173 | 173 | 173 | 0 | 0 | 173 | 173 | 173 | 0 | 173 | 173 | 173 | 173
BOB CREEK WIND | 27INR0076 |  | WT | WIND-O | PLAN | CONV | STERLING | WEST | 2028-07-01 | 240 | 0 | 0 | 0 | 240 | 240 | 0 | 0 | 240 | 240 | 240 | 0 | 0 | 0 | 240 | 240 | 0 | 0 | 240 | 240 | 240
CASCABEL WIND 1 | 24INR0424 |  | WT | WIND-O | PLAN | CONV | ZAPATA | SOUTH | 2027-12-01 | 197.75 | 0 | 0 | 197.8 | 197.8 | 197.8 | 0 | 197.8 | 197.8 | 197.8 | 197.8 | 0 | 0 | 197.8 | 197.8 | 197.8 | 0 | 0 | 197.8 | 197.8 | 197.8
CASCABEL WIND 2 | 23INR0561 |  | WT | WIND-O | PLAN | CONV | ZAPATA | SOUTH | 2027-12-01 | 197.75 | 0 | 0 | 197.8 | 197.8 | 197.8 | 0 | 197.8 | 197.8 | 197.8 | 197.8 | 0 | 0 | 197.8 | 197.8 | 197.8 | 0 | 0 | 197.8 | 197.8 | 197.8
CORRALITOS WIND 1 | 24INR0505 |  | WT | WIND-O | PLAN | CONV | ZAPATA | SOUTH | 2027-12-01 | 196.1 | 0 | 0 | 196.1 | 196.1 | 196.1 | 0 | 196.1 | 196.1 | 196.1 | 196.1 | 0 | 0 | 196.1 | 196.1 | 196.1 | 0 | 0 | 196.1 | 196.1 | 196.1
CORRALITOS WIND 2 | 24INR0506 |  | WT | WIND-O | PLAN | CONV | ZAPATA | SOUTH | 2027-12-31 | 195.4 | 0 | 0 | 195.4 | 195.4 | 195.4 | 0 | 0 | 195.4 | 195.4 | 195.4 | 0 | 0 | 195.4 | 195.4 | 195.4 | 0 | 0 | 195.4 | 195.4 | 195.4
DUNDEE NORTH WIND | 27INR0004 |  | WT | WIND-O | PLAN | CONV | WILBARGER | WEST | 2027-12-31 | 146.44 | 0 | 0 | 146.4 | 146.4 | 146.4 | 0 | 0 | 146.4 | 146.4 | 146.4 | 0 | 0 | 146.4 | 146.4 | 146.4 | 0 | 0 | 146.4 | 146.4 | 146.4
DUNDEE SOUTH A WIND | 27INR0005 |  | WT | WIND-O | PLAN | CONV | BAYLOR | WEST | 2027-12-31 | 523.73 | 0 | 0 | 523.7 | 523.7 | 523.7 | 0 | 0 | 523.7 | 523.7 | 523.7 | 0 | 0 | 523.7 | 523.7 | 523.7 | 0 | 0 | 523.7 | 523.7 | 523.7
DUNDEE SOUTH B WIND | 27INR0011 |  | WT | WIND-O | PLAN | CONV | BAYLOR | WEST | 2027-12-31 | 261.26 | 0 | 0 | 261.3 | 261.3 | 261.3 | 0 | 0 | 261.3 | 261.3 | 261.3 | 0 | 0 | 261.3 | 261.3 | 261.3 | 0 | 0 | 261.3 | 261.3 | 261.3
GOODNIGHT WIND II | 23INR0637 |  | WT | WIND-P | PLAN | CONV | ARMSTRONG | PANHANDLE | 2027-01-09 | 259.2 | 0 | 259.2 | 259.2 | 259.2 | 259.2 | 0 | 259.2 | 259.2 | 259.2 | 259.2 | 0 | 259.2 | 259.2 | 259.2 | 259.2 | 0 | 259.2 | 259.2 | 259.2 | 259.2
HONEY MESQUITE WIND FARM | 26INR0447 |  | WT | WIND-O | PLAN | CONV | GLASSCOCK | WEST | 2026-12-15 | 173.95 | 0 | 173.9 | 173.9 | 173.9 | 173.9 | 0 | 173.9 | 173.9 | 173.9 | 173.9 | 0 | 173.9 | 173.9 | 173.9 | 173.9 | 0 | 173.9 | 173.9 | 173.9 | 173.9
HYFUELS WESTERN FARMLAND WIND | 26INR0021 |  | WT | WIND-O | PLAN | CONV | VICTORIA | SOUTH | 2027-06-30 | 281.2 | 0 | 0 | 281.2 | 281.2 | 281.2 | 0 | 281.2 | 281.2 | 281.2 | 281.2 | 0 | 0 | 281.2 | 281.2 | 281.2 | 0 | 281.2 | 281.2 | 281.2 | 281.2
LA CASA WIND | 21INR0240 |  | WT | WIND-O | PLAN | CONV | STEPHENS | NORTH | 2026-03-16 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 0 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4 | 148.4
MONTE ALTO I WIND | 19INR0022 |  | WT | WIND-C | PLAN | CONV | WILLACY | COASTAL | 2028-06-01 | 141.5 | 0 | 0 | 141.5 | 141.5 | 141.5 | 0 | 0 | 141.5 | 141.5 | 141.5 | 0 | 0 | 0 | 141.5 | 141.5 | 0 | 0 | 141.5 | 141.5 | 141.5
MONTE ALTO 2 WIND | 19INR0023 |  | WT | WIND-C | PLAN | CONV | WILLACY | COASTAL | 2027-06-01 | 199.5 | 0 | 199.5 | 199.5 | 199.5 | 199.5 | 0 | 199.5 | 199.5 | 199.5 | 199.5 | 0 | 0 | 199.5 | 199.5 | 199.5 | 0 | 199.5 | 199.5 | 199.5 | 199.5
RUBICON ALPHA WIND | 24INR0291 |  | WT | WIND-O | PLAN | CONV | HASKELL | WEST | 2027-07-31 | 225.6 | 0 | 0 | 225.6 | 225.6 | 225.6 | 0 | 225.6 | 225.6 | 225.6 | 225.6 | 0 | 0 | 225.6 | 225.6 | 225.6 | 0 | 225.6 | 225.6 | 225.6 | 225.6
SIETE | 20INR0047 |  | WT | WIND-O | PLAN | CONV | WEBB | SOUTH | 2028-01-03 | 492.8 | 0 | 0 | 492.8 | 492.8 | 492.8 | 0 | 0 | 492.8 | 492.8 | 492.8 | 0 | 0 | 492.8 | 492.8 | 492.8 | 0 | 0 | 492.8 | 492.8 | 492.8
YELLOW CAT WIND | 25INR0018 |  | WT | WIND-O | PLAN | CONV | NAVARRO | NORTH | 2027-04-01 | 262 | 0 | 262 | 262 | 262 | 262 | 0 | 262 | 262 | 262 | 262 | 0 | 0 | 262 | 262 | 262 | 0 | 262 | 262 | 262 | 262
WATER VALLEY WIND ENERGY | 20INR0247 |  | WT | WIND-O | PLAN | CONV | TOM GREEN | WEST | 2027-12-15 | 180 | 0 | 0 | 180 | 180 | 180 | 0 | 0 | 180 | 180 | 180 | 0 | 0 | 180 | 180 | 180 | 0 | 0 | 180 | 180 | 180
ALILA SOLAR | 23INR0093 |  | PV | SOLAR-O | PLAN | CONV | SAN PATRICIO | COASTAL | 2028-04-20 | 256.5 | 0 | 0 | 256.5 | 256.5 | 256.5 | 0 | 0 | 256.5 | 256.5 | 256.5 | 0 | 0 | 0 | 256.5 | 256.5 | 0 | 0 | 256.5 | 256.5 | 256.5
ANSON SOLAR 2 | 20INR0242 |  | PV | SOLAR-W | PLAN | CONV | JONES | WEST | 2026-02-06 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9 | 200.9
ARGENTA SOLAR | 25INR0060 |  | PV | SOLAR-O | PLAN | CONV | BEE | SOUTH | 2028-06-30 | 310 | 0 | 0 | 0 | 310 | 310 | 0 | 0 | 310 | 310 | 310 | 0 | 0 | 0 | 310 | 310 | 0 | 0 | 310 | 310 | 310
ARMADILLO SOLAR | 21INR0421 |  | PV | SOLAR-O | PLAN | CONV | NAVARRO | NORTH | 2026-12-31 | 200.03 | 0 | 200 | 200 | 200 | 200 | 0 | 200 | 200 | 200 | 200 | 0 | 200 | 200 | 200 | 200 | 0 | 200 | 200 | 200 | 200
ARROYO SOLAR | 20INR0086 |  | PV | SOLAR-O | PLAN | CONV | CAMERON | COASTAL | 2028-02-22 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 100
AUGUST DRAW ENERGY | 25INR0112 |  | PV | SOLAR-FW | PLAN | CONV | REEVES | WEST | 2028-06-27 | 250 | 0 | 0 | 0 | 250 | 250 | 0 | 0 | 250 | 250 | 250 | 0 | 0 | 0 | 250 | 250 | 0 | 0 | 250 | 250 | 250
AUSTIN BAYOU SOLAR | 25INR0102 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2027-06-01 | 502.48 | 0 | 502.5 | 502.5 | 502.5 | 502.5 | 0 | 502.5 | 502.5 | 502.5 | 502.5 | 0 | 0 | 502.5 | 502.5 | 502.5 | 0 | 502.5 | 502.5 | 502.5 | 502.5
BARRETT SOLAR | 24INR0477 |  | PV | SOLAR-O | PLAN | CONV | RAINS | NORTH | 2026-02-19 | 125.81 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8 | 125.8
BIGWAY SOLAR I | 27INR0127 |  | PV | SOLAR-W | PLAN | CONV | KING | WEST | 2028-12-31 | 203 | 0 | 0 | 0 | 203 | 203 | 0 | 0 | 0 | 203 | 203 | 0 | 0 | 0 | 203 | 203 | 0 | 0 | 0 | 203 | 203
BIGWAY SOLAR II | 27INR0128 |  | PV | SOLAR-W | PLAN | CONV | KING | WEST | 2028-12-31 | 203 | 0 | 0 | 0 | 203 | 203 | 0 | 0 | 0 | 203 | 203 | 0 | 0 | 0 | 203 | 203 | 0 | 0 | 0 | 203 | 203
BLUE SKY SOL | 22INR0455 |  | PV | SOLAR-W | PLAN | CONV | CROCKETT | WEST | 2027-04-23 | 101.2 | 0 | 101.2 | 101.2 | 101.2 | 101.2 | 0 | 101.2 | 101.2 | 101.2 | 101.2 | 0 | 0 | 101.2 | 101.2 | 101.2 | 0 | 101.2 | 101.2 | 101.2 | 101.2
BONHAM SOLAR 1 | 25INR0199 |  | PV | SOLAR-O | PLAN | CONV | LIMESTONE | NORTH | 2026-08-31 | 138.4 | 0 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 0 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4 | 138.4
BRIGGS SOLAR | 23INR0059 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2027-09-15 | 323.7 | 0 | 0 | 323.7 | 323.7 | 323.7 | 0 | 323.7 | 323.7 | 323.7 | 323.7 | 0 | 0 | 323.7 | 323.7 | 323.7 | 0 | 323.7 | 323.7 | 323.7 | 323.7
BYNUM SOLAR PROJECT | 24INR0181 |  | PV | SOLAR-O | PLAN | CONV | CORYELL | NORTH | 2026-01-21 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56
CACHENA SOLAR SLF | 23INR0027 |  | PV | SOLAR-O | PLAN-SLF | CONV-SLF | WILSON | SOUTH | 2027-04-29 | 600 | 0 | 600 | 600 | 600 | 600 | 0 | 600 | 600 | 600 | 600 | 0 | 0 | 600 | 600 | 600 | 0 | 600 | 600 | 600 | 600
CALICHE MOUND SOLAR | 23INR0056 |  | PV | SOLAR-W | PLAN | CONV | DEAF SMITH | PANHANDLE | 2026-10-10 | 406.6 | 0 | 406.6 | 406.6 | 406.6 | 406.6 | 406.6 | 406.6 | 406.6 | 406.6 | 406.6 | 0 | 406.6 | 406.6 | 406.6 | 406.6 | 0 | 406.6 | 406.6 | 406.6 | 406.6
CAMINO SANTIAGO SOLAR | 22INR0605 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2027-02-18 | 196.3 | 0 | 196.3 | 196.3 | 196.3 | 196.3 | 0 | 196.3 | 196.3 | 196.3 | 196.3 | 0 | 196.3 | 196.3 | 196.3 | 196.3 | 0 | 196.3 | 196.3 | 196.3 | 196.3
CANNIBAL DRAW SOLAR | 26INR0452 |  | PV | SOLAR-W | PLAN | CONV | GLASSCOCK | WEST | 2028-04-10 | 149.5 | 0 | 0 | 149.5 | 149.5 | 149.5 | 0 | 0 | 149.5 | 149.5 | 149.5 | 0 | 0 | 0 | 149.5 | 149.5 | 0 | 0 | 149.5 | 149.5 | 149.5
CANTALOUPE SOLAR | 23INR0116 |  | PV | SOLAR-FW | PLAN | CONV | REEVES | WEST | 2028-07-01 | 307 | 0 | 0 | 0 | 307 | 307 | 0 | 0 | 307 | 307 | 307 | 0 | 0 | 0 | 307 | 307 | 0 | 0 | 307 | 307 | 307
CASCADE SOLAR | 23INR0091 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2026-09-01 | 171 | 0 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 0 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171 | 171
CHARGER SOLAR | 23INR0047 |  | PV | SOLAR-O | PLAN | CONV | REFUGIO | COASTAL | 2026-08-31 | 397.15 | 0 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 0 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1 | 397.1
CIBELES SOLAR | 24INR0356 |  | PV | SOLAR-O | PLAN | CONV | MCLENNAN | NORTH | 2027-06-30 | 252.3 | 0 | 0 | 252.3 | 252.3 | 252.3 | 0 | 252.3 | 252.3 | 252.3 | 252.3 | 0 | 0 | 252.3 | 252.3 | 252.3 | 0 | 252.3 | 252.3 | 252.3 | 252.3
COSPER SOLAR | 25INR0281 |  | PV | SOLAR-O | PLAN | CONV | BELL | NORTH | 2027-11-12 | 148.16 | 0 | 0 | 148.2 | 148.2 | 148.2 | 0 | 148.2 | 148.2 | 148.2 | 148.2 | 0 | 0 | 148.2 | 148.2 | 148.2 | 0 | 0 | 148.2 | 148.2 | 148.2
CRADLE SOLAR | 23INR0150 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2027-02-22 | 200.85 | 0 | 200.9 | 200.9 | 200.9 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9
CROWDED STAR SOLAR | 20INR0241 |  | PV | SOLAR-W | PLAN | CONV | JONES | WEST | 2026-06-20 | 218.79 | 0 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 0 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8 | 218.8
CROWDED STAR SOLAR II | 22INR0274 |  | PV | SOLAR-W | PLAN | CONV | JONES | WEST | 2026-05-29 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 0 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5 | 189.5
CUCHILLAS SOLAR | 24INR0059 |  | PV | SOLAR-O | PLAN | CONV | WEBB | SOUTH | 2028-12-15 | 305.6 | 0 | 0 | 0 | 305.6 | 305.6 | 0 | 0 | 0 | 305.6 | 305.6 | 0 | 0 | 0 | 305.6 | 305.6 | 0 | 0 | 0 | 305.6 | 305.6
DIAMONDBACK SOLAR | 20INR0162 |  | PV | SOLAR-O | PLAN | CONV | STARR | SOUTH | 2027-12-31 | 203.8 | 0 | 0 | 203.8 | 203.8 | 203.8 | 0 | 0 | 203.8 | 203.8 | 203.8 | 0 | 0 | 203.8 | 203.8 | 203.8 | 0 | 0 | 203.8 | 203.8 | 203.8
DELAWARE RANCH SOLAR | 22INR0454 |  | PV | SOLAR-FW | PLAN | CONV | CULBERSON | WEST | 2026-09-16 | 36 | 0 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 0 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36
DONEGAL SOLAR | 23INR0089 |  | PV | SOLAR-W | PLAN | CONV | DICKENS | PANHANDLE | 2028-03-01 | 201.68 | 0 | 0 | 201.7 | 201.7 | 201.7 | 0 | 0 | 201.7 | 201.7 | 201.7 | 0 | 0 | 201.7 | 201.7 | 201.7 | 0 | 0 | 201.7 | 201.7 | 201.7
DORADO SOLAR | 22INR0261 |  | PV | SOLAR-W | PLAN | CONV | CALLAHAN | WEST | 2026-02-16 | 401.35 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4 | 401.4
DOVE RUN SOLAR | 21INR0326 |  | PV | SOLAR-O | PLAN | CONV | DUVAL | SOUTH | 2027-10-15 | 120.86 | 0 | 0 | 120.9 | 120.9 | 120.9 | 0 | 120.9 | 120.9 | 120.9 | 120.9 | 0 | 0 | 120.9 | 120.9 | 120.9 | 0 | 0 | 120.9 | 120.9 | 120.9
DUFFY SOLAR | 23INR0057 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2027-12-31 | 502.46 | 0 | 0 | 502.5 | 502.5 | 502.5 | 0 | 0 | 502.5 | 502.5 | 502.5 | 0 | 0 | 502.5 | 502.5 | 502.5 | 0 | 0 | 502.5 | 502.5 | 502.5
ECHOLS CREEK SOLAR | 25INR0368 |  | PV | SOLAR-O | PLAN | CONV | LAMAR | NORTH | 2027-04-03 | 201.15 | 0 | 201.1 | 201.1 | 201.1 | 201.1 | 0 | 201.1 | 201.1 | 201.1 | 201.1 | 0 | 0 | 201.1 | 201.1 | 201.1 | 0 | 201.1 | 201.1 | 201.1 | 201.1
ELDORA SOLAR | 24INR0337 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2028-07-02 | 200.94 | 0 | 0 | 0 | 200.9 | 200.9 | 0 | 0 | 200.9 | 200.9 | 200.9 | 0 | 0 | 0 | 200.9 | 200.9 | 0 | 0 | 200.9 | 200.9 | 200.9
ERATH COUNTY SOLAR | 23INR0202 |  | PV | SOLAR-O | PLAN | CONV | ERATH | NORTH | 2028-09-01 | 207.4 | 0 | 0 | 0 | 207.4 | 207.4 | 0 | 0 | 207.4 | 207.4 | 207.4 | 0 | 0 | 0 | 207.4 | 207.4 | 0 | 0 | 207.4 | 207.4 | 207.4
ERIKA SOLAR | 24INR0303 |  | PV | SOLAR-O | PLAN | CONV | KAUFMAN | NORTH | 2027-06-30 | 200.5 | 0 | 0 | 200.5 | 200.5 | 200.5 | 0 | 200.5 | 200.5 | 200.5 | 200.5 | 0 | 0 | 200.5 | 200.5 | 200.5 | 0 | 200.5 | 200.5 | 200.5 | 200.5
FAGUS SOLAR PARK SLF U1 | 26INR0524 |  | PV | SOLAR-W | PLAN-SLF | CONV-SLF | CHILDRESS | PANHANDLE | 2026-09-30 | 186.36 | 0 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 0 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4 | 186.4
FELIX EAST SOLAR | 27INR0007 |  | PV | SOLAR-W | PLAN | CONV | WILBARGER | WEST | 2027-07-31 | 301.44 | 0 | 0 | 301.4 | 301.4 | 301.4 | 0 | 301.4 | 301.4 | 301.4 | 301.4 | 0 | 0 | 301.4 | 301.4 | 301.4 | 0 | 301.4 | 301.4 | 301.4 | 301.4
FELIX NORTH SOLAR | 22INR0209 |  | PV | SOLAR-W | PLAN | CONV | WILBARGER | WEST | 2027-07-31 | 201 | 0 | 0 | 201 | 201 | 201 | 0 | 201 | 201 | 201 | 201 | 0 | 0 | 201 | 201 | 201 | 0 | 201 | 201 | 201 | 201
FELIX WEST SOLAR | 27INR0012 |  | PV | SOLAR-W | PLAN | CONV | WILBARGER | WEST | 2027-07-31 | 200.95 | 0 | 0 | 200.9 | 200.9 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9 | 0 | 0 | 200.9 | 200.9 | 200.9 | 0 | 200.9 | 200.9 | 200.9 | 200.9
FEWELL SOLAR | 23INR0367 |  | PV | SOLAR-O | PLAN | CONV | LIMESTONE | NORTH | 2027-03-15 | 203.5 | 0 | 203.5 | 203.5 | 203.5 | 203.5 | 0 | 203.5 | 203.5 | 203.5 | 203.5 | 0 | 0 | 203.5 | 203.5 | 203.5 | 0 | 203.5 | 203.5 | 203.5 | 203.5
FUNSTON SOLAR (ALTERNATIVE POI LONE STAR) | 29INR0015 |  | PV | SOLAR-W | PLAN | CONV | JONES | WEST | 2027-07-01 | 351.4 | 0 | 0 | 351.4 | 351.4 | 351.4 | 0 | 351.4 | 351.4 | 351.4 | 351.4 | 0 | 0 | 351.4 | 351.4 | 351.4 | 0 | 351.4 | 351.4 | 351.4 | 351.4
GAIA SOLAR | 24INR0141 |  | PV | SOLAR-O | PLAN | CONV | NAVARRO | NORTH | 2026-05-01 | 144.02 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 0 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144
GLASGOW SOLAR | 24INR0206 |  | PV | SOLAR-O | PLAN | CONV | NAVARRO | NORTH | 2027-03-16 | 203.5 | 0 | 203.5 | 203.5 | 203.5 | 203.5 | 0 | 203.5 | 203.5 | 203.5 | 203.5 | 0 | 0 | 203.5 | 203.5 | 203.5 | 0 | 203.5 | 203.5 | 203.5 | 203.5
GP SOLAR | 23INR0045 |  | PV | SOLAR-O | PLAN | CONV | VAN ZANDT | NORTH | 2027-06-21 | 121.04 | 0 | 0 | 121 | 121 | 121 | 0 | 121 | 121 | 121 | 121 | 0 | 0 | 121 | 121 | 121 | 0 | 121 | 121 | 121 | 121
GREATER BRYANT G SOLAR | 23INR0300 |  | PV | SOLAR-FW | PLAN | CONV | MIDLAND | WEST | 2026-09-16 | 17.7 | 0 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 0 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7 | 17.7
GREYHOUND SOLAR | 21INR0268 |  | PV | SOLAR-FW | PLAN | CONV | ECTOR | WEST | 2026-03-31 | 335.45 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 0 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5 | 335.5
HALF MOON SOLAR | 28INR0127 |  | PV | SOLAR-O | PLAN | CONV | STARR | SOUTH | 2029-07-01 | 512.5 | 0 | 0 | 0 | 0 | 512.5 | 0 | 0 | 0 | 512.5 | 512.5 | 0 | 0 | 0 | 0 | 512.5 | 0 | 0 | 0 | 512.5 | 512.5
HANSON SOLAR | 23INR0086 |  | PV | SOLAR-W | PLAN | CONV | COLEMAN | WEST | 2027-04-17 | 398.83 | 0 | 398.8 | 398.8 | 398.8 | 398.8 | 0 | 398.8 | 398.8 | 398.8 | 398.8 | 0 | 0 | 398.8 | 398.8 | 398.8 | 0 | 398.8 | 398.8 | 398.8 | 398.8
HERMES SOLAR | 23INR0344 |  | PV | SOLAR-O | PLAN | CONV | BELL | NORTH | 2026-03-01 | 100.36 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
HIGH CHAP SOLAR | 25INR0068 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2028-06-26 | 152.25 | 0 | 0 | 0 | 152.3 | 152.3 | 0 | 0 | 152.3 | 152.3 | 152.3 | 0 | 0 | 0 | 152.3 | 152.3 | 0 | 0 | 152.3 | 152.3 | 152.3
HIGH NOON SOLAR | 24INR0124 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2028-05-09 | 182 | 0 | 0 | 182 | 182 | 182 | 0 | 0 | 182 | 182 | 182 | 0 | 0 | 0 | 182 | 182 | 0 | 0 | 182 | 182 | 182
HOLLOW BRANCH CREEK SOLAR | 24INR0422 |  | PV | SOLAR-O | PLAN | CONV | LEON | NORTH | 2027-12-31 | 460 | 0 | 0 | 460 | 460 | 460 | 0 | 0 | 460 | 460 | 460 | 0 | 0 | 460 | 460 | 460 | 0 | 0 | 460 | 460 | 460
HONEYCOMB SOLAR | 22INR0559 |  | PV | SOLAR-O | PLAN | CONV | BEE | SOUTH | 2026-07-09 | 61.4 | 0 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 0 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4 | 61.4
HORNET SOLAR II SLF | 25INR0282 |  | PV | SOLAR-W | PLAN-SLF | CONV-SLF | SWISHER | PANHANDLE | 2028-03-31 | 208.95 | 0 | 0 | 208.9 | 208.9 | 208.9 | 0 | 0 | 208.9 | 208.9 | 208.9 | 0 | 0 | 208.9 | 208.9 | 208.9 | 0 | 0 | 208.9 | 208.9 | 208.9
HOYTE SOLAR | 23INR0235 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2027-04-15 | 206.75 | 0 | 206.8 | 206.8 | 206.8 | 206.8 | 0 | 206.8 | 206.8 | 206.8 | 206.8 | 0 | 0 | 206.8 | 206.8 | 206.8 | 0 | 206.8 | 206.8 | 206.8 | 206.8
INDIGO SOLAR | 21INR0031 |  | PV | SOLAR-W | PLAN | CONV | FISHER | WEST | 2026-08-17 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 0 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150
INERTIA SOLAR | 22INR0374 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2029-03-31 | 202.4 | 0 | 0 | 0 | 202.4 | 202.4 | 0 | 0 | 0 | 202.4 | 202.4 | 0 | 0 | 0 | 0 | 202.4 | 0 | 0 | 0 | 202.4 | 202.4
ISAAC SOLAR | 25INR0232 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2026-12-31 | 50.73 | 0 | 50.7 | 50.7 | 50.7 | 50.7 | 0 | 50.7 | 50.7 | 50.7 | 50.7 | 0 | 50.7 | 50.7 | 50.7 | 50.7 | 0 | 50.7 | 50.7 | 50.7 | 50.7
JAGUAR SOLAR | 24INR0038 |  | PV | SOLAR-O | PLAN | CONV | MCLENNAN | NORTH | 2027-02-11 | 300 | 0 | 300 | 300 | 300 | 300 | 0 | 300 | 300 | 300 | 300 | 0 | 300 | 300 | 300 | 300 | 0 | 300 | 300 | 300 | 300
LAMKIN SOLAR | 22INR0220 |  | PV | SOLAR-O | PLAN | CONV | COMANCHE | NORTH | 2027-08-08 | 101.5 | 0 | 0 | 101.5 | 101.5 | 101.5 | 0 | 101.5 | 101.5 | 101.5 | 101.5 | 0 | 0 | 101.5 | 101.5 | 101.5 | 0 | 101.5 | 101.5 | 101.5 | 101.5
LANGER SOLAR | 23INR0030 |  | PV | SOLAR-O | PLAN | CONV | BOSQUE | NORTH | 2027-03-01 | 249.8 | 0 | 249.8 | 249.8 | 249.8 | 249.8 | 0 | 249.8 | 249.8 | 249.8 | 249.8 | 0 | 249.8 | 249.8 | 249.8 | 249.8 | 0 | 249.8 | 249.8 | 249.8 | 249.8
LAVACA BAY SOLAR | 23INR0084 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2026-12-31 | 243.46 | 0 | 243.5 | 243.5 | 243.5 | 243.5 | 0 | 243.5 | 243.5 | 243.5 | 243.5 | 0 | 243.5 | 243.5 | 243.5 | 243.5 | 0 | 243.5 | 243.5 | 243.5 | 243.5
LEIGHTON SOLAR SLF | 24INR0298 |  | PV | SOLAR-O | PLAN-SLF | CONV-SLF | LIMESTONE | NORTH | 2027-09-01 | 183 | 0 | 0 | 183 | 183 | 183 | 0 | 183 | 183 | 183 | 183 | 0 | 0 | 183 | 183 | 183 | 0 | 183 | 183 | 183 | 183
LEON SOLAR PARK | 26INR0023 |  | PV | SOLAR-O | PLAN | CONV | LEON | NORTH | 2026-07-01 | 210.11 | 0 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 0 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1 | 210.1
LIMEWOOD SOLAR | 23INR0249 |  | PV | SOLAR-O | PLAN | CONV | BELL | NORTH | 2026-03-02 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 0 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6 | 204.6
LONG POINT SOLAR | 19INR0042 |  | PV | SOLAR-O | PLAN | CONV | BRAZORIA | COASTAL | 2026-04-07 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 0 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7
LUPINUS SOLAR 1 | 24INR0150 |  | PV | SOLAR-O | PLAN | CONV | FRANKLIN | NORTH | 2027-09-13 | 164.86 | 0 | 0 | 164.9 | 164.9 | 164.9 | 0 | 164.9 | 164.9 | 164.9 | 164.9 | 0 | 0 | 164.9 | 164.9 | 164.9 | 0 | 164.9 | 164.9 | 164.9 | 164.9
MALDIVES SOLAR (ALTERNATE POI) | 25INR0400 |  | PV | SOLAR-W | PLAN | CONV | SCURRY | WEST | 2028-07-01 | 184 | 0 | 0 | 0 | 184 | 184 | 0 | 0 | 184 | 184 | 184 | 0 | 0 | 0 | 184 | 184 | 0 | 0 | 184 | 184 | 184
MALEZA SOLAR | 21INR0220 |  | PV | SOLAR-O | PLAN | CONV | WHARTON | SOUTH | 2026-11-09 | 254.94 | 0 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 254.9 | 0 | 254.9 | 254.9 | 254.9 | 254.9 | 0 | 254.9 | 254.9 | 254.9 | 254.9
MATAGORDA SOLAR | 22INR0342 |  | PV | SOLAR-O | PLAN | CONV | MATAGORDA | COASTAL | 2027-08-25 | 101 | 0 | 0 | 101 | 101 | 101 | 0 | 101 | 101 | 101 | 101 | 0 | 0 | 101 | 101 | 101 | 0 | 101 | 101 | 101 | 101
MIDDLEBROOK SOLAR LIMITED LIABILITY COMPANY | 24INR0418 |  | PV | SOLAR-O | PLAN | CONV | NACOGDOCHES | NORTH | 2027-08-13 | 316.19 | 0 | 0 | 316.2 | 316.2 | 316.2 | 0 | 316.2 | 316.2 | 316.2 | 316.2 | 0 | 0 | 316.2 | 316.2 | 316.2 | 0 | 316.2 | 316.2 | 316.2 | 316.2
MILLERS BRANCH SOLAR II | 24INR0044 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2026-04-01 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 0 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178 | 178
MILLERS BRANCH SOLAR III | 26INR0521 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2026-07-01 | 133 | 0 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 0 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 133
MIRANDA SOLAR PROJECT | 24INR0161 |  | PV | SOLAR-O | PLAN | CONV | MCMULLEN | SOUTH | 2027-12-06 | 261.42 | 0 | 0 | 261.4 | 261.4 | 261.4 | 0 | 0 | 261.4 | 261.4 | 261.4 | 0 | 0 | 261.4 | 261.4 | 261.4 | 0 | 0 | 261.4 | 261.4 | 261.4
MOCCASIN SOLAR | 26INR0269 |  | PV | SOLAR-W | PLAN | CONV | STONEWALL | WEST | 2027-07-06 | 603.59 | 0 | 0 | 603.6 | 603.6 | 603.6 | 0 | 603.6 | 603.6 | 603.6 | 603.6 | 0 | 0 | 603.6 | 603.6 | 603.6 | 0 | 603.6 | 603.6 | 603.6 | 603.6
MRG GOODY SOLAR | 23INR0225 |  | PV | SOLAR-O | PLAN | CONV | LAMAR | NORTH | 2026-05-02 | 170.82 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 0 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8 | 170.8
NABATOTO SOLAR NORTH | 21INR0428 |  | PV | SOLAR-O | PLAN | CONV | LEON | NORTH | 2027-05-01 | 321.27 | 0 | 321.3 | 321.3 | 321.3 | 321.3 | 0 | 321.3 | 321.3 | 321.3 | 321.3 | 0 | 0 | 321.3 | 321.3 | 321.3 | 0 | 321.3 | 321.3 | 321.3 | 321.3
NAZARETH SOLAR | 16INR0049 |  | PV | SOLAR-W | PLAN | CONV | CASTRO | PANHANDLE | 2027-08-05 | 203 | 0 | 0 | 203 | 203 | 203 | 0 | 203 | 203 | 203 | 203 | 0 | 0 | 203 | 203 | 203 | 0 | 203 | 203 | 203 | 203
NEW HICKORY SOLAR | 20INR0236 |  | PV | SOLAR-O | PLAN | CONV | JACKSON | SOUTH | 2026-07-31 | 209.15 | 0 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 0 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1 | 209.1
NIGHTFALL SOLAR SLF | 21INR0334 |  | PV | SOLAR-O | PLAN-SLF | CONV-SLF | UVALDE | SOUTH | 2026-06-30 | 180.87 | 0 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 0 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9 | 180.9
NORTHINGTON SOLAR | 25INR0319 |  | PV | SOLAR-O | PLAN | CONV | WHARTON | SOUTH | 2027-07-15 | 129.81 | 0 | 0 | 129.8 | 129.8 | 129.8 | 0 | 129.8 | 129.8 | 129.8 | 129.8 | 0 | 0 | 129.8 | 129.8 | 129.8 | 0 | 129.8 | 129.8 | 129.8 | 129.8
OCI COBB CREEK SOLAR | 25INR0229 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2026-12-01 | 203.1 | 0 | 203.1 | 203.1 | 203.1 | 203.1 | 203.1 | 203.1 | 203.1 | 203.1 | 203.1 | 0 | 203.1 | 203.1 | 203.1 | 203.1 | 0 | 203.1 | 203.1 | 203.1 | 203.1
OPERATION SUNSHINE | 26INR0255 |  | PV | SOLAR-W | PLAN | CONV | CONCHO | WEST | 2028-03-12 | 603.2 | 0 | 0 | 603.2 | 603.2 | 603.2 | 0 | 0 | 603.2 | 603.2 | 603.2 | 0 | 0 | 0 | 603.2 | 603.2 | 0 | 0 | 603.2 | 603.2 | 603.2
PADRINO SOLAR | 25INR0166 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2026-07-30 | 201.4 | 0 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 0 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4
PEPPER SOLAR FARM | 26INR0380 |  | PV | SOLAR-O | PLAN | CONV | MCLENNAN | NORTH | 2027-09-20 | 120.69 | 0 | 0 | 120.7 | 120.7 | 120.7 | 0 | 120.7 | 120.7 | 120.7 | 120.7 | 0 | 0 | 120.7 | 120.7 | 120.7 | 0 | 120.7 | 120.7 | 120.7 | 120.7
PIEDRA SOLAR | 25INR0168 |  | PV | SOLAR-O | PLAN | CONV | FREESTONE | NORTH | 2026-12-22 | 281.7 | 0 | 281.7 | 281.7 | 281.7 | 281.7 | 0 | 281.7 | 281.7 | 281.7 | 281.7 | 0 | 281.7 | 281.7 | 281.7 | 281.7 | 0 | 281.7 | 281.7 | 281.7 | 281.7
PITTS DUDIK II | 24INR0364 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2026-02-27 | 30.23 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2 | 30.2
QUANTUM SOLAR | 21INR0207 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2026-03-31 | 321.66 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 0 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7 | 321.7
RENEGADE PROJECT | 20INR0255 |  | PV | SOLAR-W | PLAN | CONV | DEAF SMITH | PANHANDLE | 2027-04-17 | 515.66 | 0 | 515.7 | 515.7 | 515.7 | 515.7 | 0 | 515.7 | 515.7 | 515.7 | 515.7 | 0 | 0 | 515.7 | 515.7 | 515.7 | 0 | 515.7 | 515.7 | 515.7 | 515.7
ROCINANTE SOLAR | 23INR0231 |  | PV | SOLAR-O | PLAN | CONV | GONZALES | SOUTH | 2026-11-01 | 95.29 | 0 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 95.3 | 0 | 95.3 | 95.3 | 95.3 | 95.3 | 0 | 95.3 | 95.3 | 95.3 | 95.3
RODEO SOLAR | 19INR0103 |  | PV | SOLAR-FW | PLAN | CONV | ANDREWS | WEST | 2026-11-30 | 200 | 0 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 0 | 200 | 200 | 200 | 200 | 0 | 200 | 200 | 200 | 200
ROWDY CREEK SOLAR | 24INR0186 |  | PV | SOLAR-O | PLAN | CONV | LAMAR | NORTH | 2027-04-01 | 351.78 | 0 | 351.8 | 351.8 | 351.8 | 351.8 | 0 | 351.8 | 351.8 | 351.8 | 351.8 | 0 | 0 | 351.8 | 351.8 | 351.8 | 0 | 351.8 | 351.8 | 351.8 | 351.8
SANPAT SOLAR | 25INR0052 |  | PV | SOLAR-O | PLAN | CONV | SAN PATRICIO | COASTAL | 2027-07-22 | 256.23 | 0 | 0 | 256.2 | 256.2 | 256.2 | 0 | 256.2 | 256.2 | 256.2 | 256.2 | 0 | 0 | 256.2 | 256.2 | 256.2 | 0 | 256.2 | 256.2 | 256.2 | 256.2
SANPAT SOLAR II | 25INR0081 |  | PV | SOLAR-O | PLAN | CONV | SAN PATRICIO | COASTAL | 2027-07-08 | 308.88 | 0 | 0 | 308.9 | 308.9 | 308.9 | 0 | 308.9 | 308.9 | 308.9 | 308.9 | 0 | 0 | 308.9 | 308.9 | 308.9 | 0 | 308.9 | 308.9 | 308.9 | 308.9
SEQUOIA II SOLAR | 22INR0262 |  | PV | SOLAR-W | PLAN | CONV | CALLAHAN | WEST | 2026-11-21 | 417.47 | 0 | 417.5 | 417.5 | 417.5 | 417.5 | 417.5 | 417.5 | 417.5 | 417.5 | 417.5 | 0 | 417.5 | 417.5 | 417.5 | 417.5 | 0 | 417.5 | 417.5 | 417.5 | 417.5
SEVEN SPRINGS SOLAR | 26INR0147 |  | PV | SOLAR-O | PLAN | CONV | LAMPASAS | NORTH | 2028-05-26 | 145 | 0 | 0 | 145 | 145 | 145 | 0 | 0 | 145 | 145 | 145 | 0 | 0 | 0 | 145 | 145 | 0 | 0 | 145 | 145 | 145
SHAULA I SOLAR | 22INR0251 |  | PV | SOLAR-O | PLAN | CONV | DEWITT | SOUTH | 2026-03-31 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 0 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2
SHAULA II SOLAR | 22INR0267 |  | PV | SOLAR-O | PLAN | CONV | DEWITT | SOUTH | 2026-05-30 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 0 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2 | 205.2
SHAW SOLAR | 23INR0078 |  | PV | SOLAR-O | PLAN | CONV | BANDERA | SOUTH | 2026-04-29 | 124.65 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 0 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7 | 124.7
SHORT CREEK SOLAR | 24INR0201 |  | PV | SOLAR-W | PLAN | CONV | WICHITA | WEST | 2027-12-17 | 628.33 | 0 | 0 | 628.3 | 628.3 | 628.3 | 0 | 0 | 628.3 | 628.3 | 628.3 | 0 | 0 | 628.3 | 628.3 | 628.3 | 0 | 0 | 628.3 | 628.3 | 628.3
SISTERS SOLAR | 21INR0265 |  | PV | SOLAR-FW | PLAN | CONV | ECTOR | WEST | 2027-05-31 | 301.6 | 0 | 301.6 | 301.6 | 301.6 | 301.6 | 0 | 301.6 | 301.6 | 301.6 | 301.6 | 0 | 0 | 301.6 | 301.6 | 301.6 | 0 | 301.6 | 301.6 | 301.6 | 301.6
SOL MARINA ENERGY CENTER | 26INR0241 |  | PV | SOLAR-O | PLAN | CONV | ELLIS | NORTH | 2027-10-29 | 175.3 | 0 | 0 | 175.3 | 175.3 | 175.3 | 0 | 175.3 | 175.3 | 175.3 | 175.3 | 0 | 0 | 175.3 | 175.3 | 175.3 | 0 | 0 | 175.3 | 175.3 | 175.3
SOLACE SOLAR | 23INR0031 |  | PV | SOLAR-W | PLAN | CONV | HASKELL | WEST | 2026-03-31 | 321.64 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 0 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6 | 321.6
SPACE CITY SOLAR | 21INR0341 |  | PV | SOLAR-O | PLAN | CONV | WHARTON | SOUTH | 2027-06-01 | 366 | 0 | 366 | 366 | 366 | 366 | 0 | 366 | 366 | 366 | 366 | 0 | 0 | 366 | 366 | 366 | 0 | 366 | 366 | 366 | 366
STARLING SOLAR | 23INR0035 |  | PV | SOLAR-O | PLAN | CONV | GONZALES | SOUTH | 2028-01-28 | 144 | 0 | 0 | 144 | 144 | 144 | 0 | 0 | 144 | 144 | 144 | 0 | 0 | 144 | 144 | 144 | 0 | 0 | 144 | 144 | 144
SUGAREE SOLAR | 27INR0389 |  | PV | SOLAR-O | PLAN | CONV | MAVERICK | SOUTH | 2028-09-21 | 251.4 | 0 | 0 | 0 | 251.4 | 251.4 | 0 | 0 | 251.4 | 251.4 | 251.4 | 0 | 0 | 0 | 251.4 | 251.4 | 0 | 0 | 251.4 | 251.4 | 251.4
SUN CACTUS SOLAR | 25INR0109 |  | PV | SOLAR-O | PLAN | CONV | DUVAL | SOUTH | 2027-10-15 | 120.63 | 0 | 0 | 120.6 | 120.6 | 120.6 | 0 | 120.6 | 120.6 | 120.6 | 120.6 | 0 | 0 | 120.6 | 120.6 | 120.6 | 0 | 0 | 120.6 | 120.6 | 120.6
SUNSCAPE RENEWABLE ENERGY SOLAR SLF | 27INR0047 |  | PV | SOLAR-O | PLAN-SLF | CONV-SLF | NUECES | COASTAL | 2029-01-26 | 522.75 | 0 | 0 | 0 | 522.8 | 522.8 | 0 | 0 | 0 | 522.8 | 522.8 | 0 | 0 | 0 | 522.8 | 522.8 | 0 | 0 | 0 | 522.8 | 522.8
SYPERT BRANCH SOLAR PROJECT | 24INR0070 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2026-01-31 | 261.15 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1 | 261.1
TEHUACANA CREEK SOLAR SLF | 24INR0188 |  | PV | SOLAR-O | PLAN-SLF | CONV-SLF | NAVARRO | NORTH | 2027-03-10 | 505.43 | 0 | 505.4 | 505.4 | 505.4 | 505.4 | 0 | 505.4 | 505.4 | 505.4 | 505.4 | 0 | 505.4 | 505.4 | 505.4 | 505.4 | 0 | 505.4 | 505.4 | 505.4 | 505.4
THREE CANES SOLAR SLF | 26INR0543 |  | PV | SOLAR-O | PLAN-SLF | CONV-SLF | NAVARRO | NORTH | 2027-07-31 | 333 | 0 | 0 | 333 | 333 | 333 | 0 | 333 | 333 | 333 | 333 | 0 | 0 | 333 | 333 | 333 | 0 | 333 | 333 | 333 | 333
THREE W SOLAR | 25INR0055 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2026-06-01 | 110.89 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 0 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9 | 110.9
TIGER SOLAR | 23INR0244 |  | PV | SOLAR-W | PLAN | CONV | JONES | WEST | 2027-06-30 | 255 | 0 | 0 | 255 | 255 | 255 | 0 | 255 | 255 | 255 | 255 | 0 | 0 | 255 | 255 | 255 | 0 | 255 | 255 | 255 | 255
TOKIO SOLAR | 23INR0349 |  | PV | SOLAR-O | PLAN | CONV | MCLENNAN | NORTH | 2027-08-25 | 170.45 | 0 | 0 | 170.4 | 170.4 | 170.4 | 0 | 170.4 | 170.4 | 170.4 | 170.4 | 0 | 0 | 170.4 | 170.4 | 170.4 | 0 | 170.4 | 170.4 | 170.4 | 170.4
TORMES SOLAR | 22INR0437 |  | PV | SOLAR-O | PLAN | CONV | NAVARRO | NORTH | 2027-03-31 | 356.6 | 0 | 356.6 | 356.6 | 356.6 | 356.6 | 0 | 356.6 | 356.6 | 356.6 | 356.6 | 0 | 0 | 356.6 | 356.6 | 356.6 | 0 | 356.6 | 356.6 | 356.6 | 356.6
TROJAN SOLAR | 23INR0296 |  | PV | SOLAR-O | PLAN | CONV | COOKE | NORTH | 2026-05-05 | 150.59 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 0 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6 | 150.6
ULYSSES SOLAR | 21INR0253 |  | PV | SOLAR-W | PLAN | CONV | COKE | WEST | 2027-03-02 | 151.2 | 0 | 151.2 | 151.2 | 151.2 | 151.2 | 0 | 151.2 | 151.2 | 151.2 | 151.2 | 0 | 0 | 151.2 | 151.2 | 151.2 | 0 | 151.2 | 151.2 | 151.2 | 151.2
UVA CREEK SOLAR | 26INR0359 |  | PV | SOLAR-W | PLAN | CONV | BORDEN | WEST | 2028-08-25 | 302.16 | 0 | 0 | 0 | 302.2 | 302.2 | 0 | 0 | 302.2 | 302.2 | 302.2 | 0 | 0 | 0 | 302.2 | 302.2 | 0 | 0 | 302.2 | 302.2 | 302.2
YAUPON SOLAR SLF | 24INR0042 |  | PV | SOLAR-O | PLAN-SLF | CONV-SLF | MILAM | SOUTH | 2027-07-01 | 200.78 | 0 | 0 | 200.8 | 200.8 | 200.8 | 0 | 200.8 | 200.8 | 200.8 | 200.8 | 0 | 0 | 200.8 | 200.8 | 200.8 | 0 | 200.8 | 200.8 | 200.8 | 200.8
ZEISSEL SOLAR | 24INR0258 |  | PV | SOLAR-W | PLAN | CONV | KNOX | WEST | 2028-06-30 | 457.5 | 0 | 0 | 0 | 457.5 | 457.5 | 0 | 0 | 457.5 | 457.5 | 457.5 | 0 | 0 | 0 | 457.5 | 457.5 | 0 | 0 | 457.5 | 457.5 | 457.5
ABILENE ELMCREEK BESS | 25INR0701 |  | BA | STORAGE | PLAN | CONV-DGR | TAYLOR | WEST | 2025-12-23 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ABILENE INDUSTRIAL PARK BESS | 25INR0702 |  | BA | STORAGE | PLAN | CONV-DGR | TAYLOR | WEST | 2025-12-23 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ALAMO STREET BESS | 25INR0763 |  | BA | STORAGE | PLAN | CONV-DGR | PECOS | WEST | 2026-01-20 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ALDRIN 138 BESS | 25INR0421 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2027-07-01 | 207 | 0 | 0 | 207 | 207 | 207 | 0 | 207 | 207 | 207 | 207 | 0 | 0 | 207 | 207 | 207 | 0 | 207 | 207 | 207 | 207
ALDRIN 345 BESS | 25INR0425 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2027-12-01 | 362 | 0 | 0 | 362 | 362 | 362 | 0 | 362 | 362 | 362 | 362 | 0 | 0 | 362 | 362 | 362 | 0 | 0 | 362 | 362 | 362
ALTHEA STORAGE | 27INR0465 |  | BA | STORAGE | PLAN | CONV | MAVERICK | SOUTH | 2028-09-21 | 251.3 | 0 | 0 | 0 | 251.3 | 251.3 | 0 | 0 | 251.3 | 251.3 | 251.3 | 0 | 0 | 0 | 251.3 | 251.3 | 0 | 0 | 251.3 | 251.3 | 251.3
AMADOR STORAGE | 24INR0472 |  | BA | STORAGE | PLAN | CONV | VAN ZANDT | NORTH | 2025-12-31 | 102.41 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4 | 102.4
ANATOLE RENEWABLE ENERGY STORAGE | 24INR0355 |  | BA | STORAGE | PLAN | CONV | HENDERSON | NORTH | 2027-03-31 | 207.82 | 0 | 207.8 | 207.8 | 207.8 | 207.8 | 0 | 207.8 | 207.8 | 207.8 | 207.8 | 0 | 0 | 207.8 | 207.8 | 207.8 | 0 | 207.8 | 207.8 | 207.8 | 207.8
ANSON BAT | 22INR0457 |  | BA | STORAGE | PLAN | CONV | JONES | WEST | 2026-09-01 | 153.55 | 0 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 0 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6 | 153.6
APACHE HILL BESS | 25INR0231 |  | BA | STORAGE | PLAN | CONV | HOOD | NORTH | 2026-07-31 | 201.15 | 0 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 0 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1 | 201.1
APPLE BESS | 26INR0574 |  | BA | STORAGE | PLAN | CONV-DGR | ECTOR | WEST | 2026-05-05 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ARGENTA STORAGE | 25INR0061 |  | BA | STORAGE | PLAN | CONV | BEE | SOUTH | 2028-06-30 | 192 | 0 | 0 | 0 | 192 | 192 | 0 | 0 | 192 | 192 | 192 | 0 | 0 | 0 | 192 | 192 | 0 | 0 | 192 | 192 | 192
ARROYO STORAGE | 24INR0306 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2026-04-04 | 183.76 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 0 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8 | 183.8
BACKBONE CREEK BESS | 24INR0313 |  | BA | STORAGE | PLAN | CONV | BURNET | SOUTH | 2026-08-10 | 124.1 | 0 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 0 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1 | 124.1
BARTON BRANCH IA | 22INR0504 |  | BA | STORAGE | PLAN | CONV | ROBERTSON | NORTH | 2026-03-01 | 203.62 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6
BECK ROAD BESS1 | 25INR0717 |  | BA | STORAGE | PLAN | CONV-DGR | BEXAR | SOUTH | 2026-04-20 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
BERRY BESS1 | 25INR0743 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2025-12-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
BESS STADIUM | 25INR0696 |  | BA | STORAGE | PLAN | CONV-DGR | JIM WELLS | SOUTH | 2026-01-30 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
BIG ELM STORAGE | 23INR0469 |  | BA | STORAGE | PLAN | CONV | BELL | NORTH | 2027-11-10 | 120 | 0 | 0 | 120 | 120 | 120 | 0 | 120 | 120 | 120 | 120 | 0 | 0 | 120 | 120 | 120 | 0 | 0 | 120 | 120 | 120
BIRD DOG BESS | 22INR0467 |  | BA | STORAGE | PLAN | CONV | LIVE OAK | SOUTH | 2026-06-30 | 60.4 | 0 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 0 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4 | 60.4
BLACK & GOLD ENERGY STORAGE | 24INR0386 |  | BA | STORAGE | PLAN | CONV | MENARD | WEST | 2027-07-30 | 203.83 | 0 | 0 | 203.8 | 203.8 | 203.8 | 0 | 203.8 | 203.8 | 203.8 | 203.8 | 0 | 0 | 203.8 | 203.8 | 203.8 | 0 | 203.8 | 203.8 | 203.8 | 203.8
BLANQUILLA BESS | 24INR0528 |  | BA | STORAGE | PLAN | CONV | NUECES | COASTAL | 2027-03-29 | 200.78 | 0 | 200.8 | 200.8 | 200.8 | 200.8 | 0 | 200.8 | 200.8 | 200.8 | 200.8 | 0 | 200.8 | 200.8 | 200.8 | 200.8 | 0 | 200.8 | 200.8 | 200.8 | 200.8
BLUE SKIES BESS | 25INR0046 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2027-12-31 | 306.26 | 0 | 0 | 306.3 | 306.3 | 306.3 | 0 | 0 | 306.3 | 306.3 | 306.3 | 0 | 0 | 306.3 | 306.3 | 306.3 | 0 | 0 | 306.3 | 306.3 | 306.3
BLUE SUMMIT ENERGY STORAGE | 25INR0492 |  | BA | STORAGE | PLAN | CONV | WILBARGER | WEST | 2026-07-01 | 154 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
BOCANOVA POWER II | 25INR0706 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-06-30 | 150.46 | 0 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 0 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5 | 150.5
BORDERTOWN BESS | 23INR0354 |  | BA | STORAGE | PLAN | CONV | STARR | SOUTH | 2027-06-15 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 100 | 100 | 100 | 100 | 0 | 0 | 100 | 100 | 100 | 0 | 100 | 100 | 100 | 100
BOWSTRING BESS | 22INR0443 |  | BA | STORAGE | PLAN | CONV | SAN PATRICIO | COASTAL | 2028-09-18 | 155 | 0 | 0 | 0 | 155 | 155 | 0 | 0 | 155 | 155 | 155 | 0 | 0 | 0 | 155 | 155 | 0 | 0 | 155 | 155 | 155
BRACERO PECAN STORAGE | 26INR0034 |  | BA | STORAGE | PLAN | CONV | REEVES | WEST | 2027-07-01 | 238.21 | 0 | 0 | 238.2 | 238.2 | 238.2 | 0 | 238.2 | 238.2 | 238.2 | 238.2 | 0 | 0 | 238.2 | 238.2 | 238.2 | 0 | 238.2 | 238.2 | 238.2 | 238.2
BRIGGS STORAGE | 24INR0058 |  | BA | STORAGE | PLAN | CONV | HASKELL | WEST | 2027-09-15 | 336 | 0 | 0 | 336 | 336 | 336 | 0 | 336 | 336 | 336 | 336 | 0 | 0 | 336 | 336 | 336 | 0 | 336 | 336 | 336 | 336
BROOKVIEW ROAD BESS | 27INR0243 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2028-05-02 | 203.2 | 0 | 0 | 203.2 | 203.2 | 203.2 | 0 | 0 | 203.2 | 203.2 | 203.2 | 0 | 0 | 0 | 203.2 | 203.2 | 0 | 0 | 203.2 | 203.2 | 203.2
BROTHERTON STORAGE | 25INR0432 |  | BA | STORAGE | PLAN | CONV | ANDERSON | NORTH | 2027-05-01 | 176.13 | 0 | 176.1 | 176.1 | 176.1 | 176.1 | 0 | 176.1 | 176.1 | 176.1 | 176.1 | 0 | 0 | 176.1 | 176.1 | 176.1 | 0 | 176.1 | 176.1 | 176.1 | 176.1
BRP DIRAN BESS | 23INR0137 |  | BA | STORAGE | PLAN | CONV | WHARTON | SOUTH | 2028-01-31 | 100.63 | 0 | 0 | 100.6 | 100.6 | 100.6 | 0 | 0 | 100.6 | 100.6 | 100.6 | 0 | 0 | 100.6 | 100.6 | 100.6 | 0 | 0 | 100.6 | 100.6 | 100.6
BUDA BESS | 25INR0650 |  | BA | STORAGE | PLAN | CONV-DGR | HAYS | SOUTH | 2026-04-08 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
BUFFALO CREEK BESS | 26INR0405 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2026-03-10 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 0 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4 | 251.4
BYPASS BATTERY STORAGE | 23INR0336 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2025-12-15 | 207.89 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9 | 207.9
CALLISTO II ENERGY CENTER | 22INR0558 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2026-07-01 | 203.2 | 0 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 0 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2 | 203.2
CANNIBAL DRAW STORAGE | 26INR0453 |  | BA | STORAGE | PLAN | CONV | GLASSCOCK | WEST | 2028-04-10 | 98.6 | 0 | 0 | 98.6 | 98.6 | 98.6 | 0 | 0 | 98.6 | 98.6 | 98.6 | 0 | 0 | 0 | 98.6 | 98.6 | 0 | 0 | 98.6 | 98.6 | 98.6
CARAMBOLA BESS | 24INR0436 |  | BA | STORAGE | PLAN | CONV | HIDALGO | SOUTH | 2026-04-20 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 0 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9 | 100.9
CASTOR BESS | 23INR0358 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-03-31 | 205.39 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 0 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4 | 205.4
CITRUS FLATTS BESS | 24INR0294 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2026-05-16 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 0 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2 | 101.2
CITY BREEZE BESS | 25INR0271 |  | BA | STORAGE | PLAN | CONV | MATAGORDA | COASTAL | 2027-03-18 | 143.1 | 0 | 143.1 | 143.1 | 143.1 | 143.1 | 0 | 143.1 | 143.1 | 143.1 | 143.1 | 0 | 0 | 143.1 | 143.1 | 143.1 | 0 | 143.1 | 143.1 | 143.1 | 143.1
CONEFLOWER STORAGE PROJECT | 23INR0425 |  | BA | STORAGE | PLAN | CONV | CHAMBERS | HOUSTON | 2027-02-03 | 170.85 | 0 | 170.9 | 170.9 | 170.9 | 170.9 | 0 | 170.9 | 170.9 | 170.9 | 170.9 | 0 | 170.9 | 170.9 | 170.9 | 170.9 | 0 | 170.9 | 170.9 | 170.9 | 170.9
COUNTY ROAD BESS | 26INR0512 |  | BA | STORAGE | PLAN | CONV-DGR | REEVES | WEST | 2026-03-06 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
CROWNED HERON BESS | 24INR0405 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2025-09-30 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2
CROWNED HERON BESS 2 | 24INR0493 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2026-03-31 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 0 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2 | 154.2
CUMULUS GRID BESS | 24INR0178 |  | BA | STORAGE | PLAN | CONV | ELLIS | NORTH | 2028-01-01 | 210.74 | 0 | 0 | 210.7 | 210.7 | 210.7 | 0 | 0 | 210.7 | 210.7 | 210.7 | 0 | 0 | 210.7 | 210.7 | 210.7 | 0 | 0 | 210.7 | 210.7 | 210.7
DAMON BESS 2 | 23INR0603 |  | BA | STORAGE | PLAN | CONV-DGR | BRAZORIA | COASTAL | 2026-08-21 | 9.99 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
DAMON BESS 3 | 23INR0790 |  | BA | STORAGE | PLAN | CONV-DGR | BRAZORIA | COASTAL | 2025-12-01 | 9.96 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
DESNA BESS | 24INR0128 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-05-31 | 205.46 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 0 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5
DIOS BESS | 25INR0441 |  | BA | STORAGE | PLAN | CONV | JACKSON | SOUTH | 2027-12-31 | 201.08 | 0 | 0 | 201.1 | 201.1 | 201.1 | 0 | 0 | 201.1 | 201.1 | 201.1 | 0 | 0 | 201.1 | 201.1 | 201.1 | 0 | 0 | 201.1 | 201.1 | 201.1
DOS RIOS ENERGY STORAGE SLF | 24INR0476 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | MILAM | SOUTH | 2027-03-15 | 164.5 | 0 | 164.5 | 164.5 | 164.5 | 164.5 | 0 | 164.5 | 164.5 | 164.5 | 164.5 | 0 | 164.5 | 164.5 | 164.5 | 164.5 | 0 | 164.5 | 164.5 | 164.5 | 164.5
DOWNTOWN BESS | 25INR0764 |  | BA | STORAGE | PLAN | CONV-DGR | PECOS | WEST | 2026-01-20 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
EAST HARRISON BESS | 25INR0648 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2026-01-03 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ELDORA BESS | 24INR0338 |  | BA | STORAGE | PLAN | CONV | MATAGORDA | COASTAL | 2028-07-02 | 201.31 | 0 | 0 | 0 | 201.3 | 201.3 | 0 | 0 | 201.3 | 201.3 | 201.3 | 0 | 0 | 0 | 201.3 | 201.3 | 0 | 0 | 201.3 | 201.3 | 201.3
ELIO BESS | 25INR0103 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2027-08-05 | 317.2 | 0 | 0 | 317.2 | 317.2 | 317.2 | 0 | 317.2 | 317.2 | 317.2 | 317.2 | 0 | 0 | 317.2 | 317.2 | 317.2 | 0 | 317.2 | 317.2 | 317.2 | 317.2
ELM STREET BESS | 25INR0655 |  | BA | STORAGE | PLAN | CONV-DGR | REEVES | WEST | 2026-04-02 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
ELM STREET BESS2 | 25INR0765 |  | BA | STORAGE | PLAN | CONV-DGR | REEVES | WEST | 2026-01-20 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
ESCONDIDO BESS | 25INR0593 |  | BA | STORAGE | PLAN | CONV-DGR | MAVERICK | SOUTH | 2026-04-16 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
EVAL STORAGE | 22INR0401 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2028-12-31 | 251.85 | 0 | 0 | 0 | 251.9 | 251.9 | 0 | 0 | 0 | 251.9 | 251.9 | 0 | 0 | 0 | 251.9 | 251.9 | 0 | 0 | 0 | 251.9 | 251.9
FERDINAND GRID BESS | 22INR0422 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2026-05-01 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 0 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5 | 205.5
FIRST CAPITOL BESS | 26INR0226 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2027-05-01 | 257.48 | 0 | 257.5 | 257.5 | 257.5 | 257.5 | 0 | 257.5 | 257.5 | 257.5 | 257.5 | 0 | 0 | 257.5 | 257.5 | 257.5 | 0 | 257.5 | 257.5 | 257.5 | 257.5
GAIA STORAGE | 24INR0140 |  | BA | STORAGE | PLAN | CONV | NAVARRO | NORTH | 2026-05-01 | 78.81 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 0 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8 | 78.8
GEARS BESS2 | 25INR0742 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2025-12-15 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
GLASGOW STORAGE | 24INR0207 |  | BA | STORAGE | PLAN | CONV | NAVARRO | NORTH | 2027-03-16 | 101 | 0 | 101 | 101 | 101 | 101 | 0 | 101 | 101 | 101 | 101 | 0 | 0 | 101 | 101 | 101 | 0 | 101 | 101 | 101 | 101
GRIZZLY RIDGE BESS SLF | 22INR0596 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | HAMILTON | NORTH | 2026-07-01 | 9.95 | 0 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 0 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95 | 9.95
GUNNAR BESS | 24INR0491 |  | BA | STORAGE | PLAN | CONV | HIDALGO | SOUTH | 2026-08-31 | 154.75 | 0 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 0 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8 | 154.8
HARLINGEN #1 BESS 1 | 26INR0691 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2025-12-23 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
HERMES STORAGE | 24INR0365 |  | BA | STORAGE | PLAN | CONV | BELL | NORTH | 2026-03-01 | 100.42 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4 | 100.4
HIDDEN LAKES BESS | 23INR0617 |  | BA | STORAGE | PLAN | CONV-DGR | GALVESTON | HOUSTON | 2026-05-24 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HIDDEN VALLEY BESS | 24INR0594 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2026-02-18 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HIGH NOON STORAGE | 24INR0126 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2028-05-09 | 94 | 0 | 0 | 94 | 94 | 94 | 0 | 0 | 94 | 94 | 94 | 0 | 0 | 0 | 94 | 94 | 0 | 0 | 94 | 94 | 94
HIGHWAY 6 BESS | 26INR0520 |  | BA | STORAGE | PLAN | CONV-DGR | BRAZOS | NORTH | 2026-03-27 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
HONEYCOMB STORAGE SLF | 23INR0392 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | BEE | SOUTH | 2026-11-01 | 64.1 | 0 | 64.1 | 64.1 | 64.1 | 64.1 | 64.1 | 64.1 | 64.1 | 64.1 | 64.1 | 0 | 64.1 | 64.1 | 64.1 | 64.1 | 0 | 64.1 | 64.1 | 64.1 | 64.1
HORNET STORAGE II SLF | 25INR0283 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | SWISHER | PANHANDLE | 2028-03-31 | 207.96 | 0 | 0 | 207.96 | 207.96 | 207.96 | 0 | 0 | 207.96 | 207.96 | 207.96 | 0 | 0 | 0 | 207.96 | 207.96 | 0 | 0 | 207.96 | 207.96 | 207.96
HOUSTON IV BESS | 24INR0584 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2026-06-03 | 164.6 | 0 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 0 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6 | 164.6
IRON BELT ENERGY STORAGE | 25INR0208 |  | BA | STORAGE | PLAN | CONV | BORDEN | WEST | 2027-07-31 | 401.9 | 0 | 0 | 401.9 | 401.9 | 401.9 | 0 | 401.9 | 401.9 | 401.9 | 401.9 | 0 | 0 | 401.9 | 401.9 | 401.9 | 0 | 401.9 | 401.9 | 401.9 | 401.9
KNAPP BESS | 25INR0747 |  | BA | STORAGE | PLAN | CONV-DGR | SCURRY | WEST | 2025-12-30 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
LANGER STORAGE | 23INR0266 |  | BA | STORAGE | PLAN | CONV | BOSQUE | NORTH | 2027-03-01 | 61.53 | 0 | 61.5 | 61.5 | 61.5 | 61.5 | 0 | 61.5 | 61.5 | 61.5 | 61.5 | 0 | 61.5 | 61.5 | 61.5 | 61.5 | 0 | 61.5 | 61.5 | 61.5 | 61.5
LANTANA BESS | 25INR0647 |  | BA | STORAGE | PLAN | CONV-DGR | NUECES | COASTAL | 2026-01-03 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LAUREL STORAGE ENERGY CENTER | 27INR0080 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2027-03-28 | 200.8 | 0 | 200.8 | 200.8 | 200.8 | 200.8 | 0 | 200.8 | 200.8 | 200.8 | 200.8 | 0 | 0 | 200.8 | 200.8 | 200.8 | 0 | 200.8 | 200.8 | 200.8 | 200.8
LEOPARD BESS | 27INR0224 |  | BA | STORAGE | PLAN | CONV | VICTORIA | SOUTH | 2028-07-09 | 264.24 | 0 | 0 | 0 | 264.2 | 264.2 | 0 | 0 | 264.2 | 264.2 | 264.2 | 0 | 0 | 0 | 264.2 | 264.2 | 0 | 0 | 264.2 | 264.2 | 264.2
LIMEWOOD STORAGE | 23INR0248 |  | BA | STORAGE | PLAN | CONV | BELL | NORTH | 2028-12-29 | 50 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 50 | 50
LITTLE YORK BESS | 24INR0481 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2026-05-09 | 9.96 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
LONGFELLOW BESS I | 24INR0453 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2026-08-31 | 54.99 | 0 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55
LONGFELLOW BESS II | 24INR0455 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2026-08-31 | 105.75 | 0 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 0 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8 | 105.8
LOUISA ENERGY STORAGE | 24INR0108 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2029-03-12 | 102.77 | 0 | 0 | 0 | 102.8 | 102.8 | 0 | 0 | 0 | 102.8 | 102.8 | 0 | 0 | 0 | 0 | 102.8 | 0 | 0 | 0 | 102.8 | 102.8
LUPINUS STORAGE 3 | 24INR0490 |  | BA | STORAGE | PLAN | CONV | FRANKLIN | NORTH | 2026-09-21 | 50.9 | 0 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 0 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9 | 50.9
MALLARD BESS | 25INR0101 |  | BA | STORAGE | PLAN | CONV | COLLIN | NORTH | 2026-07-14 | 257.3 | 0 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 0 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3 | 257.3
MCCAMEY'S CASTLE BATTERY | 25INR0557 |  | BA | STORAGE | PLAN | CONV | UPTON | WEST | 2027-03-31 | 409.6 | 0 | 409.6 | 409.6 | 409.6 | 409.6 | 0 | 409.6 | 409.6 | 409.6 | 409.6 | 0 | 0 | 409.6 | 409.6 | 409.6 | 0 | 409.6 | 409.6 | 409.6 | 409.6
MEADOW PARK BESS | 26INR0699 |  | BA | STORAGE | PLAN | CONV-DGR | TARRANT | NORTH | 2026-01-26 | 9.95 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MESQUITE BESS | 25INR0697 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2026-01-28 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
MESQUITE BESS2 | 25INR0766 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2026-01-20 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
MIDDLEBROOK BESS | 25INR0215 |  | BA | STORAGE | PLAN | CONV | NACOGDOCHES | NORTH | 2027-06-30 | 158.63 | 0 | 0 | 158.6 | 158.6 | 158.6 | 0 | 158.6 | 158.6 | 158.6 | 158.6 | 0 | 0 | 158.6 | 158.6 | 158.6 | 0 | 158.6 | 158.6 | 158.6 | 158.6
MIDNIGHT SUN ENERGY STORAGE | 24INR0442 |  | BA | STORAGE | PLAN | CONV | CROCKETT | WEST | 2028-06-29 | 510 | 0 | 0 | 0 | 510 | 510 | 0 | 0 | 510 | 510 | 510 | 0 | 0 | 0 | 510 | 510 | 0 | 0 | 510 | 510 | 510
MRG GOODY STORAGE | 24INR0305 |  | BA | STORAGE | PLAN | CONV | LAMAR | NORTH | 2026-05-02 | 52.29 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 0 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3 | 52.3
NORTH EDINBURG BESS 1 | 26INR0682 |  | BA | STORAGE | PLAN | CONV-DGR | HIDALGO | SOUTH | 2026-01-27 | 9.99 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
OCI COBB CREEK ESS | 25INR0233 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2026-12-01 | 201.6 | 0 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 201.6 | 0 | 201.6 | 201.6 | 201.6 | 201.6 | 0 | 201.6 | 201.6 | 201.6 | 201.6
OPERATION SUNSHINE STORAGE | 26INR0357 |  | BA | STORAGE | PLAN | CONV | CONCHO | WEST | 2028-03-12 | 409.8 | 0 | 0 | 409.8 | 409.8 | 409.8 | 0 | 0 | 409.8 | 409.8 | 409.8 | 0 | 0 | 0 | 409.8 | 409.8 | 0 | 0 | 409.8 | 409.8 | 409.8
ORANGE GROVE BESS | 23INR0331 |  | BA | STORAGE | PLAN | CONV | JIM WELLS | SOUTH | 2027-04-30 | 61.39 | 0 | 61.4 | 61.4 | 61.4 | 61.4 | 0 | 61.4 | 61.4 | 61.4 | 61.4 | 0 | 0 | 61.4 | 61.4 | 61.4 | 0 | 61.4 | 61.4 | 61.4 | 61.4
ORIANA BESS | 24INR0109 |  | BA | STORAGE | PLAN | CONV | VICTORIA | SOUTH | 2028-10-30 | 60.3 | 0 | 0 | 0 | 60.3 | 60.3 | 0 | 0 | 60.3 | 60.3 | 60.3 | 0 | 0 | 0 | 60.3 | 60.3 | 0 | 0 | 0 | 60.3 | 60.3
PADUA GRID BESS UNIT 2 | 24INR0533 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2026-03-15 | 150.94 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 0 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9 | 150.9
PADUA GRID BESS UNIT 3 | 28INR0024 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2026-05-15 | 201.35 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 0 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4 | 201.4
PAJARITA BESS | 22INR0466 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2028-07-19 | 205.5 | 0 | 0 | 0 | 205.5 | 205.5 | 0 | 0 | 205.5 | 205.5 | 205.5 | 0 | 0 | 0 | 205.5 | 205.5 | 0 | 0 | 205.5 | 205.5 | 205.5
PALMVIEW BESS | 24INR0628 |  | BA | STORAGE | PLAN | CONV-DGR | HIDALGO | SOUTH | 2026-03-06 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
PAMELA HEIGHTS I | 28INR0154 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2026-07-01 | 101.65 | 0 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 0 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7 | 101.7
PARADISO BESS | 23INR0200 |  | BA | STORAGE | PLAN | CONV | ATASCOSA | SOUTH | 2028-03-15 | 100.92 | 0 | 0 | 100.9 | 100.9 | 100.9 | 0 | 0 | 100.9 | 100.9 | 100.9 | 0 | 0 | 0 | 100.9 | 100.9 | 0 | 0 | 100.9 | 100.9 | 100.9
PIEDRA BESS | 25INR0169 |  | BA | STORAGE | PLAN | CONV | FREESTONE | NORTH | 2026-12-22 | 103.65 | 0 | 103.7 | 103.7 | 103.7 | 103.7 | 0 | 103.7 | 103.7 | 103.7 | 103.7 | 0 | 103.7 | 103.7 | 103.7 | 103.7 | 0 | 103.7 | 103.7 | 103.7 | 103.7
PINTAIL PASS BESS | 24INR0302 |  | BA | STORAGE | PLAN | CONV | SAN PATRICIO | COASTAL | 2026-01-30 | 207.25 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3
PROJECT LYNX BESS | 25INR0329 |  | BA | STORAGE | PLAN | CONV | NUECES | COASTAL | 2026-05-01 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 0 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3 | 125.3
PURPLE SAGE BESS 1 | 25INR0391 |  | BA | STORAGE | PLAN | CONV | COLLIN | NORTH | 2027-05-30 | 156 | 0 | 156 | 156 | 156 | 156 | 0 | 156 | 156 | 156 | 156 | 0 | 0 | 156 | 156 | 156 | 0 | 156 | 156 | 156 | 156
PURPLE SAGE BESS 2 | 25INR0392 |  | BA | STORAGE | PLAN | CONV | COLLIN | NORTH | 2027-05-30 | 156 | 0 | 156 | 156 | 156 | 156 | 0 | 156 | 156 | 156 | 156 | 0 | 0 | 156 | 156 | 156 | 0 | 156 | 156 | 156 | 156
QUANTUM STORAGE | 26INR0310 |  | BA | STORAGE | PLAN | CONV | HASKELL | WEST | 2026-06-30 | 321.75 | 0 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 0 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8
RAMSEY STORAGE | 21INR0505 |  | BA | STORAGE | PLAN | CONV | WHARTON | SOUTH | 2027-12-31 | 201.1 | 0 | 0 | 201.1 | 201.1 | 201.1 | 0 | 0 | 201.1 | 201.1 | 201.1 | 0 | 0 | 201.1 | 201.1 | 201.1 | 0 | 0 | 201.1 | 201.1 | 201.1
RAVEN STORAGE | 24INR0210 |  | BA | STORAGE | PLAN | CONV | WHARTON | SOUTH | 2026-07-31 | 101.4 | 0 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 0 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4 | 101.4
RED EGRET BESS | 24INR0281 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2026-08-31 | 310.58 | 0 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 0 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6 | 310.6
RESACA OASIS STORAGE | 27INR0399 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2027-09-20 | 200.7 | 0 | 0 | 200.7 | 200.7 | 200.7 | 0 | 200.7 | 200.7 | 200.7 | 200.7 | 0 | 0 | 200.7 | 200.7 | 200.7 | 0 | 200.7 | 200.7 | 200.7 | 200.7
RHAPSODY STORAGE | 24INR0397 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2026-06-30 | 205.57 | 0 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 0 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6 | 205.6
ROADRUNNER CROSSING BESS SLF | 23INR0538 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | EASTLAND | NORTH | 2026-02-13 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4 | 150.4
ROCINANTE BESS | 23INR0232 |  | BA | STORAGE | PLAN | CONV | GONZALES | SOUTH | 2026-11-01 | 33.17 | 0 | 33.2 | 33.2 | 33.2 | 33.2 | 33.2 | 33.2 | 33.2 | 33.2 | 33.2 | 0 | 33.2 | 33.2 | 33.2 | 33.2 | 0 | 33.2 | 33.2 | 33.2 | 33.2
ROCK CREEK BESS | 26INR0407 |  | BA | STORAGE | PLAN | CONV | KENDALL | SOUTH | 2028-03-29 | 251.05 | 0 | 0 | 251.1 | 251.1 | 251.1 | 0 | 0 | 251.1 | 251.1 | 251.1 | 0 | 0 | 0 | 251.1 | 251.1 | 0 | 0 | 251.1 | 251.1 | 251.1
ROCK ROSE ENERGY BESS | 26INR0201 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2026-12-15 | 211.5 | 0 | 211.5 | 211.5 | 211.5 | 211.5 | 0 | 211.5 | 211.5 | 211.5 | 211.5 | 0 | 211.5 | 211.5 | 211.5 | 211.5 | 0 | 211.5 | 211.5 | 211.5 | 211.5
ROCKEFELLER STORAGE | 22INR0239 |  | BA | STORAGE | PLAN | CONV | SCHLEICHER | WEST | 2027-06-01 | 206.8 | 0 | 206.8 | 206.8 | 206.8 | 206.8 | 0 | 206.8 | 206.8 | 206.8 | 206.8 | 0 | 0 | 206.8 | 206.8 | 206.8 | 0 | 206.8 | 206.8 | 206.8 | 206.8
ROGERS DRAW BESS | 24INR0514 |  | BA | STORAGE | PLAN | CONV | GILLESPIE | SOUTH | 2026-06-30 | 148.61 | 0 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 0 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6 | 148.6
ROWDY CREEK BESS | 24INR0187 |  | BA | STORAGE | PLAN | CONV | LAMAR | NORTH | 2027-04-01 | 175.89 | 0 | 175.9 | 175.9 | 175.9 | 175.9 | 0 | 175.9 | 175.9 | 175.9 | 175.9 | 0 | 0 | 175.9 | 175.9 | 175.9 | 0 | 175.9 | 175.9 | 175.9 | 175.9
RUTILE BESS | 24INR0485 |  | BA | STORAGE | PLAN | CONV | RUNNELS | WEST | 2028-03-31 | 100.65 | 0 | 0 | 100.7 | 100.7 | 100.7 | 0 | 0 | 100.7 | 100.7 | 100.7 | 0 | 0 | 0 | 100.7 | 100.7 | 0 | 0 | 100.7 | 100.7 | 100.7
RYAN ENERGY STORAGE | 20INR0246 |  | BA | STORAGE | PLAN | CONV | CORYELL | NORTH | 2026-12-12 | 51.6 | 0 | 51.6 | 51.6 | 51.6 | 51.6 | 0 | 51.6 | 51.6 | 51.6 | 51.6 | 0 | 51.6 | 51.6 | 51.6 | 51.6 | 0 | 51.6 | 51.6 | 51.6 | 51.6
SAHARA BESS (SOHO BESS) | 23INR0419 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-06-01 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 0 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4 | 204.4
SAHARA II BESS (SOHO II BESS) | 25INR0162 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-06-01 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 0 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3 | 204.3
SE EDINBURG BESS | 24INR0642 |  | BA | STORAGE | PLAN | CONV-DGR | HIDALGO | SOUTH | 2026-03-06 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 0 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
SEINE BESS | 23INR0140 |  | BA | STORAGE | PLAN | CONV | FOARD | WEST | 2027-12-01 | 301.19 | 0 | 0 | 301.2 | 301.2 | 301.2 | 0 | 301.2 | 301.2 | 301.2 | 301.2 | 0 | 0 | 301.2 | 301.2 | 301.2 | 0 | 0 | 301.2 | 301.2 | 301.2
SHEPARD ENERGY STORAGE | 25INR0262 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2027-07-01 | 256.79 | 0 | 0 | 256.8 | 256.8 | 256.8 | 0 | 256.8 | 256.8 | 256.8 | 256.8 | 0 | 0 | 256.8 | 256.8 | 256.8 | 0 | 256.8 | 256.8 | 256.8 | 256.8
SHERBINO II BESS SLF | 26INR0296 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | PECOS | WEST | 2027-02-09 | 77.37 | 0 | 77.4 | 77.4 | 77.4 | 77.4 | 0 | 77.4 | 77.4 | 77.4 | 77.4 | 0 | 77.4 | 77.4 | 77.4 | 77.4 | 0 | 77.4 | 77.4 | 77.4 | 77.4
SKIPJACK ENERGY STORAGE | 26INR0189 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2028-02-28 | 154 | 0 | 0 | 154 | 154 | 154 | 0 | 0 | 154 | 154 | 154 | 0 | 0 | 154 | 154 | 154 | 0 | 0 | 154 | 154 | 154
SODA LAKE BESS 1 | 23INR0501 |  | BA | STORAGE | PLAN | CONV | CRANE | WEST | 2025-12-17 | 203.87 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9 | 203.9
SOL MARINA ENERGY CENTER BESS | 26INR0242 |  | BA | STORAGE | PLAN | CONV | ELLIS | NORTH | 2027-10-29 | 57.15 | 0 | 0 | 57.2 | 57.2 | 57.2 | 0 | 57.2 | 57.2 | 57.2 | 57.2 | 0 | 0 | 57.2 | 57.2 | 57.2 | 0 | 0 | 57.2 | 57.2 | 57.2
SOLACE STORAGE | 26INR0309 |  | BA | STORAGE | PLAN | CONV | HASKELL | WEST | 2026-03-31 | 321.79 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 0 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8 | 321.8
SOSA STORAGE | 25INR0131 |  | BA | STORAGE | PLAN | CONV | MADISON | NORTH | 2027-07-01 | 155.3 | 0 | 0 | 155.3 | 155.3 | 155.3 | 0 | 155.3 | 155.3 | 155.3 | 155.3 | 0 | 0 | 155.3 | 155.3 | 155.3 | 0 | 155.3 | 155.3 | 155.3 | 155.3
SOWERS STORAGE | 22INR0552 |  | BA | STORAGE | PLAN | CONV | KAUFMAN | NORTH | 2026-12-29 | 203.9 | 0 | 203.9 | 203.9 | 203.9 | 203.9 | 0 | 203.9 | 203.9 | 203.9 | 203.9 | 0 | 203.9 | 203.9 | 203.9 | 203.9 | 0 | 203.9 | 203.9 | 203.9 | 203.9
STARLING STORAGE | 23INR0181 |  | BA | STORAGE | PLAN | CONV | GONZALES | SOUTH | 2027-05-15 | 63.6 | 0 | 63.6 | 63.6 | 63.6 | 63.6 | 0 | 63.6 | 63.6 | 63.6 | 63.6 | 0 | 0 | 63.6 | 63.6 | 63.6 | 0 | 63.6 | 63.6 | 63.6 | 63.6
STOCKYARD GRID BATT | 21INR0492 |  | BA | STORAGE | PLAN | CONV | TARRANT | NORTH | 2026-12-31 | 150.6 | 0 | 150.6 | 150.6 | 150.6 | 150.6 | 0 | 150.6 | 150.6 | 150.6 | 150.6 | 0 | 150.6 | 150.6 | 150.6 | 150.6 | 0 | 150.6 | 150.6 | 150.6 | 150.6
SUNSCAPE RENEWABLE ENERGY STORAGE SLF | 27INR0048 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | NUECES | COASTAL | 2029-01-26 | 522.75 | 0 | 0 | 0 | 522.75 | 522.75 | 0 | 0 | 0 | 522.75 | 522.75 | 0 | 0 | 0 | 522.75 | 522.75 | 0 | 0 | 0 | 522.75 | 522.75
TAORMINA STORAGE | 23INR0479 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2029-05-26 | 231.86 | 0 | 0 | 0 | 231.9 | 231.9 | 0 | 0 | 0 | 231.9 | 231.9 | 0 | 0 | 0 | 0 | 231.9 | 0 | 0 | 0 | 231.9 | 231.9
TE SMITH STORAGE | 22INR0555 |  | BA | STORAGE | PLAN | CONV | ROCKWALL | NORTH | 2025-12-15 | 125.36 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4 | 125.4
TEHUACANA CREEK BESS SLF | 24INR0189 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | NAVARRO | NORTH | 2027-03-10 | 419 | 0 | 419 | 419 | 419 | 419 | 0 | 419 | 419 | 419 | 419 | 0 | 0 | 419 | 419 | 419 | 0 | 419 | 419 | 419 | 419
THIRD COAST BESS | 23INR0361 |  | BA | STORAGE | PLAN | CONV | JACKSON | SOUTH | 2026-11-24 | 102.82 | 0 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 102.8 | 0 | 102.8 | 102.8 | 102.8 | 102.8 | 0 | 102.8 | 102.8 | 102.8 | 102.8
THOMAS CAMERON BESS | 24INR0543 |  | BA | STORAGE | PLAN | CONV | LAMPASAS | NORTH | 2027-05-03 | 201.52 | 0 | 201.5 | 201.5 | 201.5 | 201.5 | 0 | 201.5 | 201.5 | 201.5 | 201.5 | 0 | 0 | 201.5 | 201.5 | 201.5 | 0 | 201.5 | 201.5 | 201.5 | 201.5
TIDWELL PRAIRIE STORAGE 2 | 22INR0503 |  | BA | STORAGE | PLAN | CONV | ROBERTSON | NORTH | 2026-03-01 | 203.62 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6 | 203.6
TIERRA SECA BESS | 23INR0364 |  | BA | STORAGE | PLAN | CONV | VAL VERDE | WEST | 2026-01-29 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7 | 102.7
TWO BROTHERS BATTERY ENERGY STORAGE SYSTEM | 24INR0425 |  | BA | STORAGE | PLAN | CONV | VICTORIA | SOUTH | 2027-04-07 | 152 | 0 | 152 | 152 | 152 | 152 | 0 | 152 | 152 | 152 | 152 | 0 | 0 | 152 | 152 | 152 | 0 | 152 | 152 | 152 | 152
TWO FORKS BESS | 24INR0198 |  | BA | STORAGE | PLAN | CONV | COOKE | NORTH | 2027-06-30 | 309.8 | 0 | 0 | 309.8 | 309.8 | 309.8 | 0 | 309.8 | 309.8 | 309.8 | 309.8 | 0 | 0 | 309.8 | 309.8 | 309.8 | 0 | 309.8 | 309.8 | 309.8 | 309.8
UTOPIA BESS | 24INR0501 |  | BA | STORAGE | PLAN | CONV-DGR | BANDERA | SOUTH | 2026-05-04 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 0 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8 | 9.8
VERTUS ENERGY STORAGE | 26INR0333 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2026-04-15 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 0 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3 | 207.3
VIAL BESS | 25INR0122 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2027-09-15 | 135.18 | 0 | 0 | 135.2 | 135.2 | 135.2 | 0 | 135.2 | 135.2 | 135.2 | 135.2 | 0 | 0 | 135.2 | 135.2 | 135.2 | 0 | 135.2 | 135.2 | 135.2 | 135.2
WILLIS STORAGE | 25INR0370 |  | BA | STORAGE | PLAN | CONV | RAINS | NORTH | 2027-08-13 | 176.13 | 0 | 0 | 176.1 | 176.1 | 176.1 | 0 | 176.1 | 176.1 | 176.1 | 176.1 | 0 | 0 | 176.1 | 176.1 | 176.1 | 0 | 176.1 | 176.1 | 176.1 | 176.1
ZEYA BESS | 23INR0290 |  | BA | STORAGE | PLAN | CONV | GALVESTON | HOUSTON | 2026-12-01 | 255.33 | 0 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 255.3 | 0 | 255.3 | 255.3 | 255.3 | 255.3 | 0 | 255.3 | 255.3 | 255.3 | 255.3
SMALL GENERATORS WITH SIGNED IAs AND 'MODEL READY DATES' PENDING * |  | PLANNED_SMALL_GEN_NO_MRD | BA | STORAGE | PLAN | CONV-DGR |  |  |  | 89.74 | 59.77 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 0 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74 | 89.74
BRANDON (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | BRANDON_UNIT1 | GT | GAS | MOTH-IND | CONV-DGR | LUBBOCK | PANHANDLE | 2021-06-03 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V H BRAUNIG STG 1 (INDEFINITE MOTHBALL AS OF 3/31/2025) |  | BRAUNIG_VHB1 | ST | GAS | MOTH-IND | CONV | BEXAR | SOUTH | 1966-05-03 | 225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
V H BRAUNIG STG 2 (INDEFINITE MOTHBALL AS OF 3/31/2025) |  | BRAUNIG_VHB2 | ST | GAS | MOTH-IND | CONV | BEXAR | SOUTH | 1968-05-15 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
R MASSENGALE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G6 | CC | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 2021-06-03 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
R MASSENGALE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G7 | CC | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 2021-06-03 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
R MASSENGALE STG (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | MASSENGL_G8 | CC | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 2021-06-03 | 58.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
RAY OLINGER STG 1 (INDEFINITE MOTHBALL AS OF 4/5/22) |  | OLINGR_OLING_1 | ST | GAS | MOTH-IND | CONV | COLLIN | NORTH | 1967-07-01 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TEXAS BIG SPRING WIND B (INDEFINITE MOTHBALL STATUS AS ON 1/1/24) |  | SGMTN_SIGNALM2 | WT | WIND-O | MOTH-IND | CONV | HOWARD | WEST | 1999-05-27 | 6.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TY COOKE CTG 1 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT2 | GT | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 2021-06-03 | 18.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TY COOKE CTG 2 (LP&L) (INDEFINITE MOTHBALL AS OF 10/2/2023) |  | TY_COOKE_GT3 | GT | GAS | MOTH-IND | CONV | LUBBOCK | PANHANDLE | 2021-06-03 | 26.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WICHITA FALLS STG 4 (INDEFINITE MOTHBALL STATUS AS ON 11/1/23) |  | WFCOGEN_UNIT4 | CC | GAS | MOTH-IND | CONV | WICHITA | WEST | 1987-06-19 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
WISE COUNTY POWER REPOWER (CT1, CT2) | 20INR0286 |  | CC | GAS | PLAN-RPR | CONV | WISE | NORTH | 2026-05-01 | 0 | 109 | 109 | 109 | 109 | 109 | 21 | 21 | 21 | 21 | 21 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
Note on L2: Seasonal Capabilities are based on the reported Seasonal Net Sustained Capabilities in RIOO-RS. For planned projects, if Net Sustained Capabilities are not available, then the maximum capacities reported in the RIOO-Information Services (RIOO-IS) system are used.
Note on Q2: Seasonal Capabilities are based on the reported Seasonal Net Sustained Capabilities in RIOO-RS. For planned projects, if Net Sustained Capabilities are not available, then the maximum capacities reported in the RIOO-Information Services (RIOO-IS) system are used.
Note on V2: Seasonal Capabilities are based on the reported Seasonal Net Sustained Capabilities in RIOO-RS. For planned projects, if Net Sustained Capabilities are not available, then the maximum capacities reported in the RIOO-Information Services (RIOO-IS) system are used.
Note on AA2: Seasonal Capabilities are based on the reported Seasonal Net Sustained Capabilities in RIOO-RS. For planned projects, if Net Sustained Capabilities are not available, then the maximum capacities reported in the RIOO-Information Services (RIOO-IS) system are used.
Note on J3: The capacities of planned projects that have been approved for Initial Synchronization at the time of report creation (records that have 'SYNC' in CDR Status column) are assumed to be available for the season regardless of their projected Commercial Operations Dates.
Note on K3: Installed capacity ratings are based on the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. These ratings reflect the latest information in the Resource Integration and Ongoing Operations - Resources Services (RIOO-RS) system.

## New CDR-Eligible Resources
New Planned Resources Eligible for CDR Report since the Last CDR Report, Published May 2025
5.6
The table below lists the planned resources that have met certain ERCOT Planning Guide criteria necessary for the resources to be included in this CDR report. These criteria are as follows:
Large Generators 1. For all resource types a signed Standard Generation Interconnection Agreement (SGIA) or other binding agreement (for municipally-owned utilities or electric cooperatives). 2. Air permits required by the Texas Commission on Environmental Quality (TCEQ) or notice that air permits are not required. 3. Submission of a "Declaration of Adequate Water Supplies" and proof that the resource has sufficient water supplies for electricity generation. Solar, wind, and Energy Storage Resources are exempt from this requirement. 4. Provided the required financial security for interconnection facility construction and that the TDSP has received a notice to proceed with interconnection construction. See ERCOT Planning Guide Section 6.9(1)(d)(ii)(B).
Small Generators 1. ERCOT has determined that all data submission requirements for Resource Registration have been met and the generator is added to the ERCOT Network Operations Model. These requirements are met when the Small Generator has been issued a Model Ready Date.
Notes
Year of Projected Commercial Operations: The year is based on the projected Commercial Operations Date (COD) reported by the project developer. Planned projects with a "(DGR)" suffix indicate that the resource is a Distributed Generation Resource as defined in the ERCOT Nodal Protocols (Section 2.1). Projects ending with 'SLF' represent Battery Energy Storage Systems that are Self-Limiting Facilities (SLFs), where the MW capacities are reported as zero to reflect projects for which the battery system is sized to be less than the total nameplate capacity of all registered generators at the facility. Other generators at the facility typically include one or more inverter-based resources, such as solar.
| UNIT NAME | INTERCONNECTION REQUEST NUMBER (INR) | UNIT CODE | TECHNOLOGY | FUEL | CDR STATUS | CDR RESOURCE ATTRIBUTE | COUNTY | ZONE | IN-SERVICE DATE | INSTALLED CAPACITY (MW)
| BASRANCH (TEF) | 25INR0008 |  | CC | GAS | PLAN | CONV | WARD | WEST | 2028-12-01 | 1390
| CEDARVALE GAS | 25INR0710 |  | IC | GAS | PLAN | CONV-DGR | WARD | WEST | 2026-03-02 | 9.9
| PYOTE GAS | 25INR0718 |  | IC | GAS | PLAN | CONV-DGR | WARD | WEST | 2026-03-02 | 9.9
| STAGHORN GAS | 26INR0698 |  | IC | GAS | PLAN | CONV-DGR | WARD | WEST | 2026-05-02 | 9.99
| ROCK ISLAND GENERATING (TEF) | 27INR0321 |  | IC | GAS | PLAN | CONV | COLORADO | SOUTH | 2027-06-01 | 121.8
| TIMMERMAN POWER PLANT PHASE 2 | 25INR0503 |  | IC | GAS | PLAN | CONV | CALDWELL | SOUTH | 2026-05-01 | 94.2
| TIMMERMAN POWER PLANT PHASE 2B | 26INR0735 |  | IC | GAS | PLAN | CONV | CALDWELL | SOUTH | 2026-08-14 | 94.2
| BLUEBONNET PRAIRIE WIND | 25INR0247 |  | WT | WIND-O | PLAN | CONV | NAVARRO | NORTH | 2027-07-15 | 173
| BOB CREEK WIND | 27INR0076 |  | WT | WIND-O | PLAN | CONV | STERLING | WEST | 2028-07-01 | 240
| CASCABEL WIND 1 | 24INR0424 |  | WT | WIND-O | PLAN | CONV | ZAPATA | SOUTH | 2027-12-01 | 197.75
| CASCABEL WIND 2 | 23INR0561 |  | WT | WIND-O | PLAN | CONV | ZAPATA | SOUTH | 2027-12-01 | 197.75
| CORRALITOS WIND 1 | 24INR0505 |  | WT | WIND-O | PLAN | CONV | ZAPATA | SOUTH | 2027-12-01 | 196.1
| CORRALITOS WIND 2 | 24INR0506 |  | WT | WIND-O | PLAN | CONV | ZAPATA | SOUTH | 2027-12-31 | 195.4
| HYFUELS WESTERN FARMLAND WIND | 26INR0021 |  | WT | WIND-O | PLAN | CONV | VICTORIA | SOUTH | 2027-06-30 | 281.2
| WATER VALLEY WIND ENERGY | 20INR0247 |  | WT | WIND-O | PLAN | CONV | TOM GREEN | WEST | 2027-12-15 | 180
| AUGUST DRAW ENERGY | 25INR0112 |  | PV | SOLAR-FW | PLAN | CONV | REEVES | WEST | 2028-06-27 | 250
| BONHAM SOLAR 1 | 25INR0199 |  | PV | SOLAR-O | PLAN | CONV | LIMESTONE | NORTH | 2026-08-31 | 138.4
| BYNUM SOLAR PROJECT | 24INR0181 |  | PV | SOLAR-O | PLAN | CONV | CORYELL | NORTH | 2026-01-21 | 56
| CAMINO SANTIAGO SOLAR | 22INR0605 |  | PV | SOLAR-O | PLAN | CONV | MILAM | SOUTH | 2027-02-18 | 196.3
| CIBELES SOLAR | 24INR0356 |  | PV | SOLAR-O | PLAN | CONV | MCLENNAN | NORTH | 2027-06-30 | 252.3
| COSPER SOLAR | 25INR0281 |  | PV | SOLAR-O | PLAN | CONV | BELL | NORTH | 2027-11-12 | 148.16
| ECHOLS CREEK SOLAR | 25INR0368 |  | PV | SOLAR-O | PLAN | CONV | LAMAR | NORTH | 2027-04-03 | 201.15
| ERIKA SOLAR | 24INR0303 |  | PV | SOLAR-O | PLAN | CONV | KAUFMAN | NORTH | 2027-06-30 | 200.5
| GREATER BRYANT G SOLAR | 23INR0300 |  | PV | SOLAR-FW | PLAN | CONV | MIDLAND | WEST | 2026-09-16 | 17.7
| HALF MOON SOLAR | 28INR0127 |  | PV | SOLAR-O | PLAN | CONV | STARR | SOUTH | 2029-07-01 | 512.5
| HOLLOW BRANCH CREEK SOLAR | 24INR0422 |  | PV | SOLAR-O | PLAN | CONV | LEON | NORTH | 2027-12-31 | 460
| LUPINUS SOLAR 1 | 24INR0150 |  | PV | SOLAR-O | PLAN | CONV | FRANKLIN | NORTH | 2027-09-13 | 164.86
| MIDDLEBROOK SOLAR LIMITED LIABILITY COMPANY | 24INR0418 |  | PV | SOLAR-O | PLAN | CONV | NACOGDOCHES | NORTH | 2027-08-13 | 316.19
| OCI COBB CREEK SOLAR | 25INR0229 |  | PV | SOLAR-O | PLAN | CONV | HILL | NORTH | 2026-12-01 | 203.1
| OPERATION SUNSHINE | 26INR0255 |  | PV | SOLAR-FW | PLAN | CONV | CONCHO | WEST | 2028-03-12 | 603.2
| PEPPER SOLAR FARM | 26INR0380 |  | PV | SOLAR-O | PLAN | CONV | MCLENNAN | NORTH | 2027-09-20 | 120.69
| PIEDRA SOLAR | 25INR0168 |  | PV | SOLAR-O | PLAN | CONV | FREESTONE | NORTH | 2026-12-22 | 281.7
| ROCINANTE SOLAR | 23INR0231 |  | PV | SOLAR-O | PLAN | CONV | GONZALES | SOUTH | 2026-11-01 | 95.29
| ROWDY CREEK SOLAR | 24INR0186 |  | PV | SOLAR-O | PLAN | CONV | LAMAR | NORTH | 2027-04-01 | 351.78
| SEQUOIA II SOLAR | 22INR0262 |  | PV | SOLAR-FW | PLAN | CONV | CALLAHAN | WEST | 2026-11-21 | 417.47
| SEVEN SPRINGS SOLAR | 26INR0147 |  | PV | SOLAR-O | PLAN | CONV | LAMPASAS | NORTH | 2028-05-26 | 145
| SISTERS SOLAR | 21INR0265 |  | PV | SOLAR-FW | PLAN | CONV | ECTOR | WEST | 2027-05-31 | 301.6
| SOL MARINA ENERGY CENTER | 26INR0241 |  | PV | SOLAR-O | PLAN | CONV | ELLIS | NORTH | 2027-10-29 | 175.3
| SUGAREE SOLAR | 27INR0389 |  | PV | SOLAR-O | PLAN | CONV | MAVERICK | SOUTH | 2028-09-21 | 251.4
| SUNSCAPE RENEWABLE ENERGY SOLAR SLF | 27INR0047 |  | PV | SOLAR-O | PLAN-SLF | CONV-SLF | NUECES | COASTAL | 2029-01-26 | 522.75
| ALAMO STREET BESS | 25INR0763 |  | BA | STORAGE | PLAN | CONV-DGR | PECOS | WEST | 2026-01-20 | 9.99
| ALTHEA STORAGE | 27INR0465 |  | BA | STORAGE | PLAN | CONV | MAVERICK | SOUTH | 2028-09-21 | 251.3
| APPLE BESS | 26INR0574 |  | BA | STORAGE | PLAN | CONV-DGR | ECTOR | WEST | 2026-05-05 | 9.9
| BARTON BRANCH IA | 22INR0504 |  | BA | STORAGE | PLAN | CONV | ROBERTSON | NORTH | 2026-03-01 | 203.62
| BECK ROAD BESS1 | 25INR0717 |  | BA | STORAGE | PLAN | CONV-DGR | BEXAR | SOUTH | 2026-04-20 | 9.99
| BERRY BESS1 | 25INR0743 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2025-12-15 | 9.95
| BESS STADIUM | 25INR0696 |  | BA | STORAGE | PLAN | CONV-DGR | JIM WELLS | SOUTH | 2026-01-30 | 9.9
| BOCANOVA POWER II | 25INR0706 |  | BA | STORAGE | PLAN | CONV | BRAZORIA | COASTAL | 2026-06-30 | 150.46
| BOWSTRING BESS | 22INR0443 |  | BA | STORAGE | PLAN | CONV | SAN PATRICIO | COASTAL | 2028-09-18 | 155
| BROOKVIEW ROAD BESS | 27INR0243 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2028-05-02 | 203.2
| BROTHERTON STORAGE | 25INR0432 |  | BA | STORAGE | PLAN | CONV | ANDERSON | NORTH | 2027-05-01 | 176.13
| BRP DIRAN BESS | 23INR0137 |  | BA | STORAGE | PLAN | CONV | WHARTON | SOUTH | 2028-01-31 | 100.63
| BUFFALO CREEK BESS | 26INR0405 |  | BA | STORAGE | PLAN | CONV | FORT BEND | HOUSTON | 2026-03-10 | 251.4
| COUNTY ROAD BESS | 26INR0512 |  | BA | STORAGE | PLAN | CONV-DGR | REEVES | WEST | 2026-03-06 | 9.9
| CUMULUS GRID BESS | 24INR0178 |  | BA | STORAGE | PLAN | CONV | ELLIS | NORTH | 2028-01-01 | 210.74
| DAMON BESS 3 | 23INR0790 |  | BA | STORAGE | PLAN | CONV-DGR | BRAZORIA | COASTAL | 2025-12-01 | 9.96
| DIOS BESS | 25INR0441 |  | BA | STORAGE | PLAN | CONV | JACKSON | SOUTH | 2027-12-31 | 201.08
| DOS RIOS ENERGY STORAGE SLF | 24INR0476 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | MILAM | SOUTH | 2027-03-15 | 164.5
| DOWNTOWN BESS | 25INR0764 |  | BA | STORAGE | PLAN | CONV-DGR | PECOS | WEST | 2026-01-20 | 9.99
| EAST HARRISON BESS | 25INR0648 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2026-01-03 | 9.99
| ELM STREET BESS | 25INR0655 |  | BA | STORAGE | PLAN | CONV-DGR | REEVES | WEST | 2026-04-02 | 9.9
| ELM STREET BESS2 | 25INR0765 |  | BA | STORAGE | PLAN | CONV-DGR | REEVES | WEST | 2026-01-20 | 9.99
| GEARS BESS2 | 25INR0742 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2025-12-15 | 9.95
| HARLINGEN #1 BESS 1 | 26INR0691 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2025-12-23 | 9.99
| HIGHWAY 6 BESS | 26INR0520 |  | BA | STORAGE | PLAN | CONV-DGR | BRAZOS | NORTH | 2026-03-27 | 9.9
| KNAPP BESS | 25INR0747 |  | BA | STORAGE | PLAN | CONV-DGR | SCURRY | WEST | 2025-12-30 | 9.95
| LANGER STORAGE | 23INR0266 |  | BA | STORAGE | PLAN | CONV | BOSQUE | NORTH | 2027-03-01 | 61.53
| LAUREL STORAGE ENERGY CENTER | 27INR0080 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2027-03-28 | 200.8
| LEOPARD BESS | 27INR0224 |  | BA | STORAGE | PLAN | CONV | VICTORIA | SOUTH | 2028-07-09 | 264.24
| LITTLE YORK BESS | 24INR0481 |  | BA | STORAGE | PLAN | CONV-DGR | HARRIS | HOUSTON | 2026-05-09 | 9.96
| LONGFELLOW BESS I | 24INR0453 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2026-08-31 | 54.99
| LONGFELLOW BESS II | 24INR0455 |  | BA | STORAGE | PLAN | CONV | PECOS | WEST | 2026-08-31 | 105.75
| LOUISA ENERGY STORAGE | 24INR0108 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2029-03-12 | 102.77
| LUPINUS STORAGE 3 | 24INR0490 |  | BA | STORAGE | PLAN | CONV | FRANKLIN | NORTH | 2026-09-21 | 50.9
| MALLARD BESS | 25INR0101 |  | BA | STORAGE | PLAN | CONV | COLLIN | NORTH | 2026-07-14 | 257.3
| MCCAMEY'S CASTLE BATTERY | 25INR0557 |  | BA | STORAGE | PLAN | CONV | UPTON | WEST | 2027-03-31 | 409.6
| MEADOW PARK BESS | 26INR0699 |  | BA | STORAGE | PLAN | CONV-DGR | TARRANT | NORTH | 2026-01-26 | 9.95
| MESQUITE BESS | 25INR0697 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2026-01-28 | 9.9
| MESQUITE BESS2 | 25INR0766 |  | BA | STORAGE | PLAN | CONV-DGR | CAMERON | COASTAL | 2026-01-20 | 9.99
| MIDDLEBROOK BESS | 25INR0215 |  | BA | STORAGE | PLAN | CONV | NACOGDOCHES | NORTH | 2027-06-30 | 158.63
| MIDNIGHT SUN ENERGY STORAGE | 24INR0442 |  | BA | STORAGE | PLAN | CONV | CROCKETT | WEST | 2028-06-29 | 510
| NORTH EDINBURG BESS 1 | 26INR0682 |  | BA | STORAGE | PLAN | CONV-DGR | HIDALGO | SOUTH | 2026-01-27 | 9.99
| OCI COBB CREEK ESS | 25INR0233 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2026-12-01 | 201.6
| OPERATION SUNSHINE STORAGE | 26INR0357 |  | BA | STORAGE | PLAN | CONV | CONCHO | WEST | 2028-03-12 | 409.8
| PADUA GRID BESS UNIT 2 | 24INR0533 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2026-03-15 | 150.94
| PADUA GRID BESS UNIT 3 | 28INR0024 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2026-05-15 | 201.35
| PAJARITA BESS | 22INR0466 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2028-07-19 | 205.5
| PAMELA HEIGHTS I | 28INR0154 |  | BA | STORAGE | PLAN | CONV | HARRIS | HOUSTON | 2026-07-01 | 101.65
| PARADISO BESS | 23INR0200 |  | BA | STORAGE | PLAN | CONV | ATASCOSA | SOUTH | 2028-03-15 | 100.92
| PIEDRA BESS | 25INR0169 |  | BA | STORAGE | PLAN | CONV | FREESTONE | NORTH | 2026-12-22 | 103.65
| QUANTUM STORAGE | 26INR0310 |  | BA | STORAGE | PLAN | CONV | HASKELL | WEST | 2026-06-30 | 321.75
| RAVEN STORAGE | 24INR0210 |  | BA | STORAGE | PLAN | CONV | WHARTON | SOUTH | 2026-07-31 | 101.4
| RESACA OASIS STORAGE | 27INR0399 |  | BA | STORAGE | PLAN | CONV | CAMERON | COASTAL | 2027-09-20 | 200.7
| ROADRUNNER CROSSING BESS SLF | 23INR0538 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | EASTLAND | NORTH | 2026-02-13 | 150.4
| ROCINANTE BESS | 23INR0232 |  | BA | STORAGE | PLAN | CONV | GONZALES | SOUTH | 2026-11-01 | 33.17
| ROCK CREEK BESS | 26INR0407 |  | BA | STORAGE | PLAN | CONV | KENDALL | SOUTH | 2028-03-29 | 251.05
| ROGERS DRAW BESS | 24INR0514 |  | BA | STORAGE | PLAN | CONV | GILLESPIE | SOUTH | 2026-06-30 | 148.61
| ROWDY CREEK BESS | 24INR0187 |  | BA | STORAGE | PLAN | CONV | LAMAR | NORTH | 2027-04-01 | 175.89
| RUTILE BESS | 24INR0485 |  | BA | STORAGE | PLAN | CONV | RUNNELS | WEST | 2028-03-31 | 100.65
| SEINE BESS | 23INR0140 |  | BA | STORAGE | PLAN | CONV | FOARD | WEST | 2027-12-01 | 301.19
| SOL MARINA ENERGY CENTER BESS | 26INR0242 |  | BA | STORAGE | PLAN | CONV | ELLIS | NORTH | 2027-10-29 | 57.15
| SOLACE STORAGE | 26INR0309 |  | BA | STORAGE | PLAN | CONV | HASKELL | WEST | 2026-03-31 | 321.79
| SUNSCAPE RENEWABLE ENERGY STORAGE SLF | 27INR0048 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | NUECES | COASTAL | 2029-01-26 | 522.75
| TAORMINA STORAGE | 23INR0479 |  | BA | STORAGE | PLAN | CONV | BEXAR | SOUTH | 2029-05-26 | 231.86
| TEHUACANA CREEK BESS SLF | 24INR0189 |  | BA | STORAGE | PLAN-SLF | CONV-SLF | NAVARRO | NORTH | 2027-03-10 | 419
| THOMAS CAMERON BESS | 24INR0543 |  | BA | STORAGE | PLAN | CONV | LAMPASAS | NORTH | 2027-05-03 | 201.52
| TIDWELL PRAIRIE STORAGE 2 | 22INR0503 |  | BA | STORAGE | PLAN | CONV | ROBERTSON | NORTH | 2026-03-01 | 203.62
| UTOPIA BESS | 24INR0501 |  | BA | STORAGE | PLAN | CONV-DGR | BANDERA | SOUTH | 2026-05-04 | 9.8
| VIAL BESS | 25INR0122 |  | BA | STORAGE | PLAN | CONV | HILL | NORTH | 2027-09-15 | 135.18
| WILLIS STORAGE | 25INR0370 |  | BA | STORAGE | PLAN | CONV | RAINS | NORTH | 2027-08-13 | 176.13
| TOTAL | [9 empty] | 19757.16

## ExpectedResources
Input cells (non-formulas) | Calculated cells
|  |  |  | Summer | Summer | Summer | Summer | Summer | Winter | Winter | Winter | Winter | Winter | Spring | Spring | Spring | Spring | Spring | Fall | Fall | Fall | Fall | Fall
RiskPeriod | Metric | Metric, Worksheets Precedent | Metric, Worksheets Dependent | 2026 | 2027 | 2028 | 2029 | 2030 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Peak Load Hour: | Hydroelectric, Peak Average Capacity Contribution |  | Seasonal Summary | 533.737 | 533.737 | 533.737 | 533.737 | 533.737 | 516.4466 | 516.4466 | 516.4466 | 516.4466 | 516.4466 | 489.4918 | 489.4918 | 489.4918 | 489.4918 | 489.4918 | 470.3158 | 470.3158 | 470.3158 | 470.3158 | 470.3158
Peak Net Load Hour: | Hydroelectric, Peak Average Capacity Contribution |  | Seasonal Summary | 530.284 | 530.284 | 530.284 | 530.284 | 530.284 | 517.8453 | 517.8453 | 517.8453 | 517.8453 | 517.8453 | 489.5935 | 489.5935 | 489.5935 | 489.5935 | 489.5935 | 466.1848 | 466.1848 | 466.1848 | 466.1848 | 466.1848
Peak Load Hour: | Private-Use Network Capacity Contribution (Top 20 Hours) |  |  | 3491 | 3491 | 3491 | 3491 | 3491 | 4210 | 4210 | 4210 | 4210 | 4210 | 2897 | 2897 | 2897 | 2897 | 2897 | 3028 | 3028 | 3028 | 3028 | 3028
Peak Load Hour: | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  |  | -60 | -60 | -60 | 190 | 190 | -60 | -60 | -60 | 190 | 190 | 50 | -60 | -60 | -60 | 190 | -60 | -60 | -60 | 190 | 190
Peak Load Hour: | Capacity from Private Use Networks |  | Seasonal Summary | 3431 | 3431 | 3431 | 3681 | 3681 | 4150 | 4150 | 4150 | 4400 | 4400 | 2947 | 2837 | 2837 | 2837 | 3087 | 2968 | 2968 | 2968 | 3218 | 3218
Peak Net Load Hour: | Private-Use Network Capacity Contribution (Top 20 Hours) |  |  | 3599 | 3599 | 3599 | 3599 | 3599 | 4074 | 4074 | 4074 | 4074 | 4074 | 2830 | 2830 | 2830 | 2830 | 2830 | 2909 | 2909 | 2909 | 2909 | 2909
Peak Net Load Hour: | Private-Use Network Forecast Adjustment (per Protocol 10.3.2.4) |  |  | -60 | -60 | -60 | 190 | 190 | -60 | -60 | -60 | 190 | 190 | 50 | -60 | -60 | -60 | 190 | -60 | -60 | -60 | 190 | 190
Peak Net Load Hour: | Capacity from Private Use Networks |  | Seasonal Summary | 3539 | 3539 | 3539 | 3789 | 3789 | 4014 | 4014 | 4014 | 4264 | 4264 | 2880 | 2770 | 2770 | 2770 | 3020 | 2849 | 2849 | 2849 | 3099 | 3099
Peak Load Hour: | Non-Synchronous Ties Capacity | Unit Details |  | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220
Peak Load Hour: | Non-Synchronous Ties (% Based on average net import contribution during the EEA events: summer 2023 and winter 2020/2021 EEA events) |  |  | 67% | 67% | 67% | 67% | 67% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59%
Peak Load Hour: | Non-Synchronous Ties (Based on average net import contribution during the EEA events: summer 2023 and winter 2020/2021 EEA events) |  | Seasonal Summary | 817.4 | 817.4 | 817.4 | 817.4 | 817.4 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8
Peak Net Load Hour: | Non-Synchronous Ties Capacity | Unit Details |  | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220 | 1220
Peak Net Load Hour: | Non-Synchronous Ties (% Based on average net import contribution during the EEA events: summer 2023 and winter 2020/2021 EEA events) |  |  | 67% | 67% | 67% | 67% | 67% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59% | 59%
Peak Net Load Hour: | Non-Synchronous Ties (Based on average net import contribution during the EEA events: summer 2023 and winter 2020/2021 EEA events) |  | Seasonal Summary | 817.4 | 817.4 | 817.4 | 817.4 | 817.4 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8 | 719.8
Peak Load Hour: | Unconfirmed Planned Retirements | Unit Details | Seasonal Summary | 0 | -420 | -420 | -1390 | -1390 | 0 | -420 | -980 | -1390 | -1390 | 0 | -420 | -420 | -1390 | -1390 | 0 | -420 | -420 | -1390 | -1390
Peak Net Load Hour: | Unconfirmed Planned Retirements | Unit Details | Seasonal Summary | 0 | -420 | -420 | -1390 | -1390 | 0 | -420 | -980 | -1390 | -1390 | 0 | -420 | -420 | -1390 | -1390 | 0 | -420 | -420 | -1390 | -1390
Peak Load Hour: | Operational Generation Capacity Energy Storage |  | Seasonal Summary | 9262.486 | 8312.4907 | 7589.9929 | 7076.4671 | 7076.4671 | 5303.4437 | 4713.2353 | 4347.7615 | 4220.0289 | 4220.0289 | 4721.8493 | 4246.1482 | 4025.5525 | 3944.4955 | 3944.4016 | 8957.6316 | 8067.6645 | 7322.9867 | 7075.6914 | 7075.6914
Peak Net Load Hour: | Operational Generation Capacity Energy Storage |  | Seasonal Summary | 9262.486 | 8312.4907 | 7589.9929 | 7076.4671 | 7076.4671 | 4922.4096 | 4405.8633 | 4053.9076 | 3944.422 | 3944.422 | 4721.8493 | 4246.1482 | 4025.5525 | 3944.4955 | 3944.4016 | 8957.6316 | 8067.6645 | 7322.9867 | 7075.6914 | 7075.6914
Peak Load Hour: | Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements Energy Storage |  | Seasonal Summary | 3045.3448 | 7129.4572 | 9793.6035 | 10506.0975 | 10506.0975 | 3007.5219 | 5275.2522 | 6128.1852 | 6265.1564 | 6265.1564 | 597.7028 | 2792.1525 | 4811.7704 | 5770.586 | 5855.9914 | 4699.3518 | 8592.0245 | 10295.1648 | 10506.784 | 10506.784
Peak Net Load Hour: | Planned Resource Additions (with Signed IA and Proof of Financial Commitment) and Retirements Energy Storage |  | Seasonal Summary | 3045.3448 | 7129.4572 | 9793.6035 | 10506.0975 | 10506.0975 | 2791.4418 | 4931.2285 | 5713.9971 | 5855.9838 | 5855.9838 | 597.7028 | 2792.1525 | 4811.7704 | 5770.586 | 5855.9914 | 4699.3518 | 8592.0245 | 10295.1648 | 10506.784 | 10506.784
Peak Load Hour: | Capacity Pending Retirement |  | Seasonal Summary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Net Load Hour: | Capacity Pending Retirement |  | Seasonal Summary | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## ELCCs
Input cells (non-formulas) | Calculated cells
|  | Peak Load Hour Ending | Peak Load Hour: | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 8 | 8 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
ELCC Background Info (found here) |  | Peak Net Load Hour Ending | Peak Net Load Hour: | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20
|  |  |  | Summer | Summer | Summer | Summer | Summer | Winter | Winter | Winter | Winter | Winter | Spring | Spring | Spring | Spring | Spring | Fall | Fall | Fall | Fall | Fall
Risk Period | Metric | Resource Type | Metric, Worksheets Dependent | 2026 | 2027 | 2028 | 2029 | 2030 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Peak Load Hour: | Coastal Wind | Wind - Coastal | Seasonal Summary | 31.19% | 31.66% | 32.3% | 32.48% | 32.48% | 29.3% | 29.28% | 29.41% | 29.41% | 29.41% | 29.3% | 29.28% | 29.41% | 29.41% | 29.41% | 31.36% | 32.4% | 32.5% | 32.5% | 32.5%
Peak Load Hour: | Panhandle Wind | Wind - Panhandle | Seasonal Summary | 33.97% | 34.48% | 35.17% | 35.37% | 35.37% | 31.91% | 31.88% | 32.03% | 32.03% | 32.03% | 31.91% | 31.88% | 32.03% | 32.03% | 32.03% | 34.15% | 35.28% | 35.39% | 35.39% | 35.39%
Peak Load Hour: | Other Wind | Wind - Other | Seasonal Summary | 15.86% | 16.1% | 16.42% | 16.51% | 16.51% | 14.9% | 14.89% | 14.95% | 14.95% | 14.95% | 14.9% | 14.89% | 14.95% | 14.95% | 14.95% | 15.94% | 16.47% | 16.53% | 16.53% | 16.53%
Peak Load Hour: | Far West Solar Utility-Scale | Solar - Far West | Seasonal Summary | 33.64% | 28.36% | 25.24% | 24.52% | 24.43% | 2.169% | 1.782% | 1.657% | 1.622% | 1.622% | 2.169% | 1.782% | 1.657% | 1.622% | 1.622% | 31.93% | 26.1% | 24.57% | 24.09% | 24.09%
Peak Load Hour: | West Solar Utility-Scale | Solar - West | Seasonal Summary | 33.64% | 28.36% | 25.24% | 24.52% | 24.43% | 2.169% | 1.782% | 1.657% | 1.622% | 1.622% | 2.169% | 1.782% | 1.657% | 1.622% | 1.622% | 31.93% | 26.1% | 24.57% | 24.09% | 24.09%
Peak Load Hour: | Other Solar Utility-Scale | Solar - Other | Seasonal Summary | 25.33% | 21.35% | 19% | 18.46% | 18.39% | 1.633% | 1.341% | 1.248% | 1.221% | 1.221% | 1.633% | 1.341% | 1.248% | 1.221% | 1.221% | 24.04% | 19.65% | 18.5% | 18.14% | 18.14%
Peak Load Hour: | Energy Storage - 1.0 hr | BESS - 1.0 hr | Seasonal Summary | 35.57% | 30.76% | 26.99% | 24.47% | 24.47% | 18.98% | 16.01% | 14.35% | 13.77% | 13.77% | 17.22% | 14.82% | 13.27% | 12.77% | 12.77% | 33.85% | 29.22% | 25.78% | 24.47% | 24.47%
Peak Load Hour: | Energy Storage - 2.0 hr | BESS - 2.0 hr | Seasonal Summary | 66.61% | 58.01% | 50.21% | 46.15% | 46.15% | 37.37% | 31.76% | 28.43% | 27.3% | 27.3% | 34.52% | 29.65% | 26.48% | 25.49% | 25.49% | 63.71% | 54.99% | 48.32% | 46.16% | 46.16%
Peak Load Hour: | Energy Storage - 3.0 hr | BESS - 3.0 hr | Seasonal Summary | 97.86% | 93.27% | 84.25% | 77.81% | 77.81% | 57.99% | 49.03% | 43.81% | 41.99% | 41.99% | 52.52% | 44.45% | 39.99% | 38.47% | 38.47% | 96.34% | 90.68% | 81.39% | 77.82% | 77.82%
Peak Load Hour: | Energy Storage - 4.0 hr | BESS - 4.0 hr | Seasonal Summary | 98.38% | 95.83% | 90.01% | 86.06% | 86.06% | 70.33% | 63.22% | 57.35% | 54.93% | 54.93% | 70.41% | 59.63% | 53.07% | 51.05% | 51.05% | 97.82% | 93.66% | 88.25% | 86.06% | 86.06%
Peak Load Hour: | Energy Storage - 5.0 hr | BESS - 5.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 81.18% | 70.77% | 64.97% | 63.06% | 63.06% | 86.22% | 73.47% | 66.12% | 63.67% | 63.67% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Load Hour: | Energy Storage - 6.0 hr | BESS - 6.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 90.69% | 82.49% | 73.05% | 70.72% | 70.72% | 92.88% | 84.69% | 75.55% | 73.21% | 73.21% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Load Hour: | Energy Storage - 7.0 hr | BESS - 7.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 93.11% | 84.57% | 79.32% | 77.35% | 77.35% | 93.71% | 85.4% | 79.51% | 77.53% | 77.53% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Load Hour: | Energy Storage - 8.0 hr | BESS - 8.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Load Hour: | Energy Storage - 9.0 hr | BESS - 9.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Load Hour: | Energy Storage - 10.0 hr | BESS - 10.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Load Hour: | Energy Storage - 11.0 hr | BESS - 11.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Load Hour: | Energy Storage - 12.0 hr | BESS - 12.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Net Load Hour: | Coastal Wind | Wind - Coastal | Seasonal Summary | 16.85% | 17.18% | 16.06% | 15.66% | 15.66% | 29.3% | 29.28% | 29.41% | 29.41% | 29.41% | 29.3% | 29.28% | 29.41% | 29.41% | 29.41% | 31.36% | 32.4% | 32.5% | 32.5% | 32.5%
Peak Net Load Hour: | Panhandle Wind | Wind - Panhandle | Seasonal Summary | 18.35% | 18.71% | 17.49% | 17.05% | 17.05% | 31.91% | 31.88% | 32.03% | 32.03% | 32.03% | 31.91% | 31.88% | 32.03% | 32.03% | 32.03% | 34.15% | 35.28% | 35.39% | 35.39% | 35.39%
Peak Net Load Hour: | Other Wind | Wind - Other | Seasonal Summary | 8.568% | 8.736% | 8.167% | 7.961% | 7.961% | 14.9% | 14.89% | 14.95% | 14.95% | 14.95% | 14.9% | 14.89% | 14.95% | 14.95% | 14.95% | 15.94% | 16.47% | 16.53% | 16.53% | 16.53%
Peak Net Load Hour: | Far West Solar Utility-Scale | Solar - Far West | Seasonal Summary | 5.43% | 2.31% | 0% | 0% | 0% | 2.169% | 1.782% | 1.657% | 1.622% | 1.622% | 2.169% | 1.782% | 1.657% | 1.622% | 1.622% | 31.93% | 26.1% | 24.57% | 24.09% | 24.09%
Peak Net Load Hour: | West Solar Utility-Scale | Solar - West | Seasonal Summary | 5.43% | 2.31% | 0% | 0% | 0% | 2.169% | 1.782% | 1.657% | 1.622% | 1.622% | 2.169% | 1.782% | 1.657% | 1.622% | 1.622% | 31.93% | 26.1% | 24.57% | 24.09% | 24.09%
Peak Net Load Hour: | Other Solar Utility-Scale | Solar - Other | Seasonal Summary | 4.088% | 1.739% | 0% | 0% | 0% | 1.633% | 1.341% | 1.248% | 1.221% | 1.221% | 1.633% | 1.341% | 1.248% | 1.221% | 1.221% | 24.04% | 19.65% | 18.5% | 18.14% | 18.14%
Peak Net Load Hour: | Energy Storage - 1.0 hr | BESS - 1.0 hr | Seasonal Summary | 35.57% | 30.76% | 26.99% | 24.47% | 24.47% | 17.22% | 14.82% | 13.27% | 12.77% | 12.77% | 17.22% | 14.82% | 13.27% | 12.77% | 12.77% | 33.85% | 29.22% | 25.78% | 24.47% | 24.47%
Peak Net Load Hour: | Energy Storage - 2.0 hr | BESS - 2.0 hr | Seasonal Summary | 66.61% | 58.01% | 50.21% | 46.15% | 46.15% | 34.52% | 29.65% | 26.48% | 25.49% | 25.49% | 34.52% | 29.65% | 26.48% | 25.49% | 25.49% | 63.71% | 54.99% | 48.32% | 46.16% | 46.16%
Peak Net Load Hour: | Energy Storage - 3.0 hr | BESS - 3.0 hr | Seasonal Summary | 97.86% | 93.27% | 84.25% | 77.81% | 77.81% | 52.52% | 44.45% | 39.99% | 38.47% | 38.47% | 52.52% | 44.45% | 39.99% | 38.47% | 38.47% | 96.34% | 90.68% | 81.39% | 77.82% | 77.82%
Peak Net Load Hour: | Energy Storage - 4.0 hr | BESS - 4.0 hr | Seasonal Summary | 98.38% | 95.83% | 90.01% | 86.06% | 86.06% | 70.41% | 59.63% | 53.07% | 51.05% | 51.05% | 70.41% | 59.63% | 53.07% | 51.05% | 51.05% | 97.82% | 93.66% | 88.25% | 86.06% | 86.06%
Peak Net Load Hour: | Energy Storage - 5.0 hr | BESS - 5.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 86.22% | 73.47% | 66.12% | 63.67% | 63.67% | 86.22% | 73.47% | 66.12% | 63.67% | 63.67% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Net Load Hour: | Energy Storage - 6.0 hr | BESS - 6.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 92.88% | 84.69% | 75.55% | 73.21% | 73.21% | 92.88% | 84.69% | 75.55% | 73.21% | 73.21% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Net Load Hour: | Energy Storage - 7.0 hr | BESS - 7.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 93.71% | 85.4% | 79.51% | 77.53% | 77.53% | 93.71% | 85.4% | 79.51% | 77.53% | 77.53% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Net Load Hour: | Energy Storage - 8.0 hr | BESS - 8.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Net Load Hour: | Energy Storage - 9.0 hr | BESS - 9.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Net Load Hour: | Energy Storage - 10.0 hr | BESS - 10.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Net Load Hour: | Energy Storage - 11.0 hr | BESS - 11.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%
Peak Net Load Hour: | Energy Storage - 12.0 hr | BESS - 12.0 hr | Seasonal Summary | 98.39% | 95.89% | 90.47% | 87.33% | 87.33% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 94.02% | 85.83% | 79.61% | 77.63% | 77.63% | 97.84% | 93.79% | 88.89% | 87.33% | 87.33%

## Load
Input cells (non-formulas) | Calculated cells |  | Month--> | 8 | 8 | 8 | 8 | 8 | 1 | 1 | 1 | 1 | 1 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10
|  |  |  | Summer | Summer | Summer | Summer | Summer | Winter | Winter | Winter | Winter | Winter | Spring | Spring | Spring | Spring | Spring | Fall | Fall | Fall | Fall | Fall
RiskPeriod | Metric | Metric, Worksheets Precedent | Metric, Worksheets Dependent | 2026 | 2027 | 2028 | 2029 | 2030 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Peak Load Hour: | Base Peak Demand + Rooftop PV Forecast (for Peak Load Hour) | LongTermLoadForecast |  | 86531.6631 | 87650.5351 | 88747.0227 | 89542.9286 | 90227.8022 | 71890.349 | 73974.5538 | 76107.7205 | 78328.869 | 80681.9041 | 76009.3224 | 77596.9617 | 79168.8183 | 80595.883 | 81851.1638 | 73343.3935 | 74903.6727 | 76441.9989 | 77822.9807 | 79028.8078
Peak Load Hour: | Date, HE | LongTermLoadForecast |  | 08/04/26 HE17 | 08/04/27 HE17 | 08/04/28 HE17 | 08/04/29 HE17 | 08/04/30 HE17 | 01/24/27 HE8 | 01/24/28 HE8 | 01/24/29 HE8 | 01/24/30 HE8 | 01/24/31 HE8 | 05/23/26 HE17 | 05/23/27 HE17 | 05/23/28 HE17 | 05/23/29 HE17 | 05/23/30 HE17 | 10/03/26 HE17 | 10/03/27 HE17 | 10/03/28 HE17 | 10/03/29 HE17 | 10/03/30 HE17
Peak Load Hour: | ercot_net | LongTermLoadForecast |  | 94159.0572 | 103724.645 | 120875.1453 | 127905.3033 | 138010.4599 | 84020.3579 | 99541.9588 | 114470.0952 | 126111.5268 | 132985.766 | 80826.0339 | 89726.9705 | 104736.2233 | 118958.2577 | 129633.8215 | 80970.7875 | 90977.7826 | 108570.1215 | 116185.3554 | 126811.4655
Peak Load Hour: | less: Incremental Rooftop PV Forecast | LongTermLoadForecast | Seasonal Summary | -1260.3697 | -1681.0228 | -2213.7108 | -2877.6602 | -3693.2456 | -36.9405 | -48.9325 | -63.9722 | -82.4636 | -104.89 | -1104.2645 | -1475.285 | -1945.9217 | -2533.5505 | -3257.0364 | -1203.3474 | -1602.0825 | -2106.1786 | -2732.6311 | -3500.2423
Peak Load Hour: | Total Seasonal Load based on normal weather conditions* | LongTermLoadForecast | Seasonal Summary | 95419.4269 | 105405.6678 | 123088.8561 | 130782.9635 | 141703.7055 | 84057.2984 | 99590.8913 | 114534.0674 | 126193.9904 | 133090.6559 | 81930.2985 | 91202.2555 | 106682.1449 | 121491.8082 | 132890.8579 | 82174.1349 | 92579.8652 | 110676.3001 | 118917.9865 | 130311.7078
Peak Load Hour: | Contracted Loads | LongTermLoadForecast |  | 4893.9254 | 8653.7616 | 15335.7588 | 17129.7096 | 19559.6158 | 7799.0478 | 13622.2252 | 17129.7096 | 19559.6158 | 20740.4994 | 3308.5956 | 7799.0478 | 13622.2252 | 17129.7096 | 19559.6158 | 4893.9254 | 8653.7616 | 15335.7588 | 17129.7096 | 19559.6158
Peak Load Hour: | Transmission Service Providers Officer Letter Loads | LongTermLoadForecast |  | 2733.4686 | 7420.3483 | 16792.3638 | 21232.6651 | 28223.0419 | 4330.961 | 11945.1798 | 21232.6651 | 28223.0419 | 31563.3625 | 1508.116 | 4330.961 | 11945.1798 | 21232.6651 | 28223.0419 | 2733.4686 | 7420.3483 | 16792.3638 | 21232.6651 | 28223.0419
Peak Net Load Hour: | Base Peak Demand + Rooftop PV Forecast (for Peak Net Load Hour:) | LongTermLoadForecast |  | 69408.906 | 70318.568 | 71252.2369 | 72235.9065 | 73481.2825 | 61649.3755 | 63743.4474 | 65493.8367 | 67467.1809 | 69566.309 | 57129.5782 | 58971.549 | 60481.8508 | 62392.6595 | 64102.9028 | 63973.6318 | 65634.6689 | 67361.7152 | 69314.1446 | 71205.4493
Peak Net Load Hour: | Date, HE | LongTermLoadForecast |  | 08/25/26 HE21 | 08/25/27 HE21 | 08/25/28 HE21 | 08/25/29 HE21 | 08/25/30 HE21 | 01/17/27 HE19 | 01/17/28 HE19 | 01/17/29 HE19 | 01/17/30 HE19 | 01/17/31 HE19 | 05/18/26 HE21 | 05/18/27 HE21 | 05/18/28 HE21 | 05/18/29 HE21 | 05/18/30 HE21 | 10/01/26 HE20 | 10/01/27 HE20 | 10/01/28 HE20 | 10/01/29 HE20 | 10/01/30 HE20
Peak Net Load Hour: | ercot_net | LongTermLoadForecast |  | 81411.4696 | 91088.1988 | 108314.4289 | 115532.3506 | 126198.0097 | 79496.5342 | 95076.2059 | 109738.4622 | 121132.0895 | 127752.4218 | 65896.8272 | 75135.4302 | 90453.6438 | 105182.9752 | 116313.5016 | 75813.6816 | 86130.0048 | 103945.3844 | 112132.0658 | 123443.6536
Peak Net Load Hour: | less: Incremental Rooftop PV Forecast | LongTermLoadForecast | Seasonal Summary | -60.9324 | -81.4678 | -107.491 | -139.9286 | -179.7778 | -9.6303 | -12.2007 | -15.3581 | -19.1744 | -23.7366 | -94.7442 | -126.7623 | -167.3838 | -218.0977 | -280.5279 | -129.0068 | -171.1009 | -224.1615 | -289.9277 | -370.3185
Peak Net Load Hour: | Total Seasonal Load based on normal weather conditions* | LongTermLoadForecast | Seasonal Summary | 81472.4019 | 91169.6665 | 108421.9199 | 115672.2792 | 126377.7875 | 79506.1644 | 95088.4066 | 109753.8203 | 121151.2639 | 127776.1584 | 65991.5714 | 75262.1925 | 90621.0277 | 105401.073 | 116594.0295 | 75942.6884 | 86301.1057 | 104169.5459 | 112421.9935 | 123813.9721
Peak Net Load Hour: | Contracted Loads | LongTermLoadForecast |  | 4893.9254 | 8653.7616 | 15335.7588 | 17129.7096 | 19559.6158 | 7799.0478 | 13622.2252 | 17129.7096 | 19559.6158 | 20740.4994 | 3308.5956 | 7799.0478 | 13622.2252 | 17129.7096 | 19559.6158 | 4893.9254 | 8653.7616 | 15335.7588 | 17129.7096 | 19559.6158
Peak Net Load Hour: | Transmission Service Providers Officer Letter Loads | LongTermLoadForecast |  | 2733.4686 | 7420.3483 | 16792.3638 | 21232.6651 | 28223.0419 | 4330.961 | 11945.1798 | 21232.6651 | 28223.0419 | 31563.3625 | 1508.116 | 4330.961 | 11945.1798 | 21232.6651 | 28223.0419 | 2733.4686 | 7420.3483 | 16792.3638 | 21232.6651 | 28223.0419
Peak Load Hour: | less: Load Resources providing Responsive Reserves | DemandIntegration | Seasonal Summary | -935 | -935 | -935 | -935 | -935 | -1498 | -1498 | -1498 | -1498 | -1498 | -1617 | -1617 | -1617 | -1617 | -1617 | -1280 | -1280 | -1280 | -1280 | -1280
Peak Load Hour: | less: Load Resources providing Non-Spinning Reserves | DemandIntegration | Seasonal Summary | -50 | -70 | -80 | -90 | -100 | -50 | -70 | -80 | -90 | -100 | -50 | -70 | -80 | -90 | -100 | -50 | -70 | -80 | -90 | -100
Peak Load Hour: | less: Load Resources providing ERCOT Contingency Reserve Service (ECRS) | DemandIntegration | Seasonal Summary | -300 | -330 | -360 | -390 | -420 | -300 | -330 | -360 | -390 | -420 | -300 | -330 | -360 | -390 | -420 | -300 | -330 | -360 | -390 | -420
Peak Load Hour: | less: Controllable Load Resources not included in other adjustments | DemandIntegration | Seasonal Summary | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100
Peak Load Hour: | less: Emergency Response Service (10- and 30-min ramp products) | DemandIntegration | Seasonal Summary | -2750 | -2750 | -2750 | -2750 | -2750 | -2675 | -2675 | -2675 | -2675 | -2675 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750
Peak Load Hour: | less: TDSP Standard Offer Load Management Programs |  | Seasonal Summary | -303 | -303 | -303 | -303 | -303 | -74.8 | -74.8 | -74.8 | -74.8 | -74.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Load Hour: | less: Distribution Voltage Reduction |  | Seasonal Summary | -1162 | -1162 | -1162 | -1162 | -1162 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1162 | -1162 | -1162 | -1162 | -1162
Peak Load Hour: | Energy Efficiency Program Savings Forecast, included in the Base Load Forecast |  | Seasonal Summary | 4048.5769 | 4426.829 | 4805.9274 | 5185.4543 | 5566.1918 | 4048.5769 | 4426.829 | 4805.9274 | 5185.4543 | 5566.1918 | 4048.5769 | 4426.829 | 4805.9274 | 5185.4543 | 5566.1918 | 4048.5769 | 4426.829 | 4805.9274 | 5185.4543 | 5566.1918
Peak Net Load Hour: | less: Load Resources providing Responsive Reserves | DemandIntegration | Seasonal Summary | -935 | -935 | -935 | -935 | -935 | -1402 | -1402 | -1402 | -1402 | -1402 | -1576 | -1576 | -1576 | -1576 | -1576 | -1230 | -1230 | -1230 | -1230 | -1230
Peak Net Load Hour: | less: Load Resources providing Non-Spinning Reserves | DemandIntegration | Seasonal Summary | -70 | -80 | -90 | -100 | -110 | -70 | -80 | -90 | -100 | -110 | -70 | -80 | -90 | -100 | -110 | -70 | -80 | -90 | -100 | -110
Peak Net Load Hour: | less: Load Resources providing ERCOT Contingency Reserve Service (ECRS) | DemandIntegration | Seasonal Summary | -350 | -385 | -420 | -460 | -505 | -350 | -385 | -420 | -460 | -505 | -350 | -385 | -420 | -460 | -505 | -350 | -385 | -420 | -460 | -505
Peak Net Load Hour: | less: Controllable Load Resources not included in other adjustments | DemandIntegration | Seasonal Summary | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100
Peak Net Load Hour: | less: Emergency Response Service (10- and 30-min ramp products) | DemandIntegration | Seasonal Summary | -2600 | -2600 | -2600 | -2600 | -2600 | -2750 | -2750 | -2750 | -2750 | -2750 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600
Peak Net Load Hour: | less: TDSP Standard Offer Load Management Programs |  | Seasonal Summary | -303 | -303 | -303 | -303 | -303 | -74.8 | -74.8 | -74.8 | -74.8 | -74.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Net Load Hour: | less: Distribution Voltage Reduction |  | Seasonal Summary | -1162 | -1162 | -1162 | -1162 | -1162 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1279 | -1162 | -1162 | -1162 | -1162 | -1162
Peak Net Load Hour: | Energy Efficiency Program Savings Forecast, included in the Base Load Forecast |  | Seasonal Summary | 4048.5769 | 4426.829 | 4805.9274 | 5185.4543 | 5566.1918 | 4048.5769 | 4426.829 | 4805.9274 | 5185.4543 | 5566.1918 | 4048.5769 | 4426.829 | 4805.9274 | 5185.4543 | 5566.1918 | 4048.5769 | 4426.829 | 4805.9274 | 5185.4543 | 5566.1918

## DemandIntegration
Input cells, negative values represent adjustment to Total Seasonal Load based on normal weather conditions* found on Seasonal Summary worksheet
Calculated cells
Load Resources, Controllable Load Resources, Emergency Reponse Service (ERS)
|  |  | Summer | Summer | Summer | Summer | Summer | Winter | Winter | Winter | Winter | Winter | Spring | Spring | Spring | Spring | Spring | Fall | Fall | Fall | Fall | Fall
|  |  | 2026 | 2027 | 2028 | 2029 | 2030 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
|  | Peak Load Hour: | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 8 | 8 | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17
| Risk Period | Metric
| Peak Load Hour: | less: Load Resources providing Responsive Reserves | -935 | -935 | -935 | -935 | -935 | -1498 | -1498 | -1498 | -1498 | -1498 | -1617 | -1617 | -1617 | -1617 | -1617 | -1280 | -1280 | -1280 | -1280 | -1280
| Peak Load Hour: | less: Load Resources providing Non-Spinning Reserves | -50 | -70 | -80 | -90 | -100 | -50 | -70 | -80 | -90 | -100 | -50 | -70 | -80 | -90 | -100 | -50 | -70 | -80 | -90 | -100
| Peak Load Hour: | less: Load Resources providing ERCOT Contingency Reserve Service (ECRS) | -300 | -330 | -360 | -390 | -420 | -300 | -330 | -360 | -390 | -420 | -300 | -330 | -360 | -390 | -420 | -300 | -330 | -360 | -390 | -420
| Peak Load Hour: | less: Controllable Load Resources not included in other adjustments | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100
| Peak Load Hour: | less: Emergency Response Service (10- and 30-min ramp products) | -2750 | -2750 | -2750 | -2750 | -2750 | -2675 | -2675 | -2675 | -2675 | -2675 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750 | -2750
|  | Peak Net Load Hour: | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20
| Risk Period | Metric
| Peak Net Load Hour: | less: Load Resources providing Responsive Reserves | -935 | -935 | -935 | -935 | -935 | -1402 | -1402 | -1402 | -1402 | -1402 | -1576 | -1576 | -1576 | -1576 | -1576 | -1230 | -1230 | -1230 | -1230 | -1230
| Peak Net Load Hour: | less: Load Resources providing Non-Spinning Reserves | -70 | -80 | -90 | -100 | -110 | -70 | -80 | -90 | -100 | -110 | -70 | -80 | -90 | -100 | -110 | -70 | -80 | -90 | -100 | -110
| Peak Net Load Hour: | less: Load Resources providing ERCOT Contingency Reserve Service (ECRS) | -350 | -385 | -420 | -460 | -505 | -350 | -385 | -420 | -460 | -505 | -350 | -385 | -420 | -460 | -505 | -350 | -385 | -420 | -460 | -505
| Peak Net Load Hour: | less: Controllable Load Resources not included in other adjustments | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100 | -20 | -40 | -60 | -80 | -100
| Peak Net Load Hour: | less: Emergency Response Service (10- and 30-min ramp products) | -2600 | -2600 | -2600 | -2600 | -2600 | -2750 | -2750 | -2750 | -2750 | -2750 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600 | -2600

## LoadResourceScenarios
Input cells | Calculated Cells |  | Month--> | 6 | 6 | 6 | 6 | 6 | 12 | 12 | 12 | 12 | 12
|  |  |  | Summer | Summer | Summer | Summer | Summer | Winter | Winter | Winter | Winter | Winter
RiskPeriod | Metric | Metric, Worksheets Precedent | Metric, Worksheets Dependent | 2026 | 2027 | 2028 | 2029 | 2030 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031
Peak Load Hour: | Date, HE | Load |  | 08/04/26 HE17 | 08/04/27 HE17 | 08/04/28 HE17 | 08/04/29 HE17 | 08/04/30 HE17 | 01/24/27 HE8 | 01/24/28 HE8 | 01/24/29 HE8 | 01/24/30 HE8 | 01/24/31 HE8
Peak Load Hour: | Data Centers |  |  | 2433.2268 | 6659.6851 | 13903.35 | 17995.4745 | 22175.1665 | 4307.211 | 9693.9268 | 17995.4745 | 22175.1665 | 24149.7131
Peak Load Hour: | Industrial |  |  | 5 | 310.808 | 4649.1 | 5819.44 | 7901.548 | 200.008 | 3865.128 | 5819.44 | 7901.548 | 9009.548
Peak Load Hour: | Hydrogen |  |  | 1387.4742 | 2763.2852 | 5064.179 | 5707.4586 | 7080.3056 | 2027.6482 | 3970.9166 | 5707.4586 | 7080.3056 | 7547.5852
Peak Load Hour: | Oil & Gas |  |  | 1699.1868 | 2319.7514 | 2728.5294 | 2835.4374 | 3125.2734 | 2108.7014 | 2586.8694 | 2835.4374 | 3125.2734 | 3131.0514
Peak Load Hour: | Crypto |  |  | 2102.5062 | 4020.5802 | 5782.9642 | 6004.5642 | 7500.3642 | 3486.4402 | 5450.5642 | 6004.5642 | 7500.3642 | 8465.9642
Peak Load Hour: | ERCOT Large Load Forecast Total |  |  | 7627.394 | 16074.1099 | 32128.1226 | 38362.3747 | 47782.6577 | 12130.0088 | 25567.405 | 38362.3747 | 47782.6577 | 52303.8619
Peak Load Hour: | Data Centers -100% curtailable |  |  | -2433.2268 | -6659.6851 | -13903.35 | -17995.4745 | -22175.1665 | -4307.211 | -9693.9268 | -17995.4745 | -22175.1665 | -24149.7131
Peak Load Hour: | Industrial - 85% curtailable |  |  | -4.25 | -264.1868 | -3951.735 | -4946.524 | -6716.3158 | -170.0068 | -3285.3588 | -4946.524 | -6716.3158 | -7658.1158
Peak Load Hour: | Hydrogen - 85% curtailable |  |  | -1179.353 | -2348.7924 | -4304.5521 | -4851.3398 | -6018.2597 | -1723.5009 | -3375.2791 | -4851.3398 | -6018.2597 | -6415.4474
Peak Load Hour: | Oil & Gas - non-curtailable |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Load Hour: | Crypto - 85% curtailable |  |  | -1787.1303 | -3417.4932 | -4915.5196 | -5103.8796 | -6375.3096 | -2963.4742 | -4632.9796 | -5103.8796 | -6375.3096 | -7196.0696
Peak Load Hour: | Scenario 1: Base Case with Senate Bill 6 Large Load curtailment impact |  | Load-Resource Scenarios | 0 | -12690.1575 | -27075.1567 | -32897.2178 | -41285.0516 | 0 | -20987.5443 | -32897.2178 | -41285.0516 | -45419.3459
Peak Load Hour: | Data Centers less 25% |  |  | 1824.9201 | 4994.7639 | 10427.5125 | 13496.6059 | 16631.3749 | 3230.4083 | 7270.4451 | 13496.6059 | 16631.3749 | 18112.2848
Peak Load Hour: | Industrial less 25% |  |  | 3.75 | 233.106 | 3486.825 | 4364.58 | 5926.161 | 150.006 | 2898.846 | 4364.58 | 5926.161 | 6757.161
Peak Load Hour: | Hydrogen less 25% |  |  | 1040.6056 | 2072.4639 | 3798.1342 | 4280.5939 | 5310.2292 | 1520.7361 | 2978.1874 | 4280.5939 | 5310.2292 | 5660.6889
Peak Load Hour: | Oil & Gas less 25% |  |  | 1274.3901 | 1739.8136 | 2046.3971 | 2126.5781 | 2343.955 | 1581.526 | 1940.1521 | 2126.5781 | 2343.955 | 2348.2885
Peak Load Hour: | Crypto less 25% |  |  | 1576.8797 | 3015.4352 | 4337.2232 | 4503.4232 | 5625.2732 | 2614.8302 | 4087.9232 | 4503.4232 | 5625.2732 | 6349.4732
Peak Load Hour: | ERCOT Large Load Forecast Total - less 25% |  |  | 5720.5455 | 12055.5825 | 24096.0919 | 28771.781 | 35836.9933 | 9097.5066 | 19175.5537 | 28771.781 | 35836.9933 | 39227.8964
Peak Load Hour: | Data Centers - less 25% -100% curtailable |  |  | -1824.9201 | -4994.7639 | -10427.5125 | -13496.6059 | -16631.3749 | -3230.4083 | -7270.4451 | -13496.6059 | -16631.3749 | -18112.2848
Peak Load Hour: | Industrial - less 25% - 85% curtailable |  |  | -3.1875 | -198.1401 | -2963.8012 | -3709.893 | -5037.2369 | -127.5051 | -2464.0191 | -3709.893 | -5037.2369 | -5743.5868
Peak Load Hour: | Hydrogen - less 25% - 85% curtailable |  |  | -884.5148 | -1761.5943 | -3228.4141 | -3638.5048 | -4513.6948 | -1292.6257 | -2531.4593 | -3638.5048 | -4513.6948 | -4811.5855
Peak Load Hour: | Oil & Gas - less 25% - non-curtailable |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Load Hour: | Crypto - less 25% - 85% curtailable |  |  | -1340.3477 | -2563.1199 | -3686.6397 | -3827.9097 | -4781.4822 | -2222.6057 | -3474.7347 | -3827.9097 | -4781.4822 | -5397.0522
Peak Load Hour: | Curtailment total based on 25% reduced loads |  |  | -4052.9701 | -9517.6181 | -20306.3675 | -24672.9134 | -30963.7887 | -6873.1447 | -15740.6582 | -24672.9134 | -30963.7887 | -34064.5094
Peak Load Hour: | Difference between 25% less load and protocol prescribed load |  |  | -1906.8485 | -4018.5275 | -8032.0306 | -9590.5937 | -11945.6644 | -3032.5022 | -6391.8512 | -9590.5937 | -11945.6644 | -13075.9655
Peak Load Hour: | Scenario 2: Base Case with 25% decrease in Large Load + Senate Bill 6 Large Load curtailment impact |  | Load-Resource Scenarios | 0 | -13536.1456 | -28338.3982 | -34263.5071 | -42909.4532 | 0 | -22132.5095 | -34263.5071 | -42909.4532 | -47140.4749
Peak Load Hour: | TSP Provided Large Load Forecast Total |  |  | 22008.629 | 49972.2 | 83815.977 | 106189.843 | 116852.661 | 32381.395 | 67351.537 | 83815.977 | 106189.843 | 116852.661
Peak Load Hour: | TSP Forecast Scaling Factor |  |  | 2.8855 | 3.1089 | 2.6088 | 2.7681 | 2.4455 | 2.6695 | 2.6343 | 2.1848 | 2.2224 | 2.2341
Peak Load Hour: | Data Centers, scaled by TSP Forecast Scaling Factor |  |  | 7021.0069 | 20704.0464 | 36271.1161 | 49812.7821 | 54229.4493 | 11498.2193 | 25536.4543 | 39317.3855 | 49281.0062 | 53953.1525
Peak Load Hour: | Industrial, scaled by TSP Forecast Scaling Factor |  |  | 14.4274 | 966.2594 | 12128.591 | 16108.6331 | 19323.264 | 533.9269 | 10181.8042 | 12714.5948 | 17560.0141 | 20128.3351
Peak Load Hour: | Hydrogen, scaled by TSP Forecast Scaling Factor |  |  | 4003.5173 | 8590.674 | 13211.4507 | 15798.6604 | 17314.9127 | 5412.863 | 10460.4802 | 12469.9323 | 15734.925 | 16862.147
Peak Load Hour: | Oil & Gas, scaled by TSP Forecast Scaling Factor |  |  | 4902.9553 | 7211.7885 | 7118.1986 | 7848.6969 | 7642.8673 | 5629.2369 | 6814.5215 | 6195.0012 | 6945.4548 | 6995.118
Peak Load Hour: | Crypto, scaled by TSP Forecast Scaling Factor |  |  | 6066.7221 | 12499.4317 | 15086.6206 | 16621.0705 | 18342.1677 | 9307.1489 | 14358.2768 | 13119.0632 | 16668.4429 | 18913.9083
Peak Load Hour: | ERCOT Large Load Forecast Total, scaled by TSP Forecast Scaling Factor (a.k.a. TSP LL Forecast Total) |  |  | 22008.629 | 49972.2 | 83815.977 | 106189.843 | 116852.661 | 32381.395 | 67351.537 | 83815.977 | 106189.843 | 116852.661
Peak Load Hour: | Data Centers -100% curtailable, scaled by TSP Forecast Scaling Factor |  |  | -7021.0069 | -20704.0464 | -36271.1161 | -49812.7821 | -54229.4493 | -11498.2193 | -25536.4543 | -39317.3855 | -49281.0062 | -53953.1525
Peak Load Hour: | Industrial - 85% curtailable, scaled by TSP Forecast Scaling Factor |  |  | -12.2633 | -821.3205 | -10309.3024 | -13692.3382 | -16424.7744 | -453.8379 | -8654.5336 | -10807.4056 | -14926.012 | -17109.0848
Peak Load Hour: | Hydrogen - 85% curtailable, scaled by TSP Forecast Scaling Factor |  |  | -3402.9897 | -7302.0729 | -11229.7331 | -13428.8613 | -14717.6758 | -4600.9335 | -8891.4082 | -10599.4425 | -13374.6863 | -14332.825
Peak Load Hour: | Oil & Gas - non-curtailable, scaled by TSP Forecast Scaling Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Load Hour: | Crypto - 85% curtailable, scaled by TSP Forecast Scaling Factor |  |  | -5156.7138 | -10624.517 | -12823.6276 | -14127.9099 | -15590.8425 | -7911.0766 | -12204.5353 | -11151.2037 | -14168.1765 | -16076.8221
Peak Load Hour: | Curtailment total based on TSP scaled loads |  |  | -15592.9737 | -39451.9567 | -70633.779 | -91061.8915 | -100962.742 | -24464.0673 | -55286.9314 | -71875.4373 | -91749.8809 | -101471.8844
Peak Load Hour: | Incremental Additions to Large Load (TSP - ERCOT Adjusted) |  |  | 14381.235 | 33898.0901 | 51687.8544 | 67827.4683 | 69070.0033 | 20251.3862 | 41784.132 | 45453.6023 | 58407.1853 | 64548.7991
Peak Load Hour: | Scenario 3: Base Case with TSP Provided Large Loads replacing ERCOT Adjusted Large Loads + Senate Bill 6 Large Load curtailment impact |  | Load-Resource Scenarios | 0 | -5553.8667 | -18945.9246 | -23234.4231 | -31892.7387 | 0 | -13502.7994 | -26421.8349 | -33342.6956 | -36923.0853
Peak Net Load Hour: | Date, HE | Load |  | 08/25/26 HE21 | 08/25/27 HE21 | 08/25/28 HE21 | 08/25/29 HE21 | 08/25/30 HE21 | 01/17/27 HE19 | 01/17/28 HE19 | 01/17/29 HE19 | 01/17/30 HE19 | 01/17/31 HE19
Peak Net Load Hour: | Data Centers |  |  | 2433.2268 | 6659.6851 | 13903.35 | 17995.4745 | 22175.1665 | 4307.211 | 9693.9268 | 17995.4745 | 22175.1665 | 24149.7131
Peak Net Load Hour: | Industrial |  |  | 5 | 310.808 | 4649.1 | 5819.44 | 7901.548 | 200.008 | 3865.128 | 5819.44 | 7901.548 | 9009.548
Peak Net Load Hour: | Hydrogen |  |  | 1387.4742 | 2763.2852 | 5064.179 | 5707.4586 | 7080.3056 | 2027.6482 | 3970.9166 | 5707.4586 | 7080.3056 | 7547.5852
Peak Net Load Hour: | Oil & Gas |  |  | 1699.1868 | 2319.7514 | 2728.5294 | 2835.4374 | 3125.2734 | 2108.7014 | 2586.8694 | 2835.4374 | 3125.2734 | 3131.0514
Peak Net Load Hour: | Crypto |  |  | 2102.5062 | 4020.5802 | 5782.9642 | 6004.5642 | 7500.3642 | 3486.4402 | 5450.5642 | 6004.5642 | 7500.3642 | 8465.9642
Peak Net Load Hour: | Total |  |  | 7627.394 | 16074.1099 | 32128.1226 | 38362.3747 | 47782.6577 | 12130.0088 | 25567.405 | 38362.3747 | 47782.6577 | 52303.8619
Peak Net Load Hour: | Data Centers -100% curtailable |  |  | -2433.2268 | -6659.6851 | -13903.35 | -17995.4745 | -22175.1665 | -4307.211 | -9693.9268 | -17995.4745 | -22175.1665 | -24149.7131
Peak Net Load Hour: | Industrial - 85% curtailable |  |  | -4.25 | -264.1868 | -3951.735 | -4946.524 | -6716.3158 | -170.0068 | -3285.3588 | -4946.524 | -6716.3158 | -7658.1158
Peak Net Load Hour: | Hydrogen - 85% curtailable |  |  | -1179.353 | -2348.7924 | -4304.5521 | -4851.3398 | -6018.2597 | -1723.5009 | -3375.2791 | -4851.3398 | -6018.2597 | -6415.4474
Peak Net Load Hour: | Oil & Gas - non-curtailable |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Net Load Hour: | Crypto - 85% curtailable |  |  | -1787.1303 | -3417.4932 | -4915.5196 | -5103.8796 | -6375.3096 | -2963.4742 | -4632.9796 | -5103.8796 | -6375.3096 | -7196.0696
Peak Net Load Hour: | Scenario 1: Base Case with Senate Bill 6 Large Load curtailment impact |  | Load-Resource Scenarios | 0 | -12690.1575 | -27075.1567 | -32897.2178 | -41285.0516 | 0 | -20987.5443 | -32897.2178 | -41285.0516 | -45419.3459
Peak Net Load Hour: | Data Centers less 25% |  |  | 1824.9201 | 4994.7639 | 10427.5125 | 13496.6059 | 16631.3749 | 3230.4083 | 7270.4451 | 13496.6059 | 16631.3749 | 18112.2848
Peak Net Load Hour: | Industrial less 25% |  |  | 3.75 | 233.106 | 3486.825 | 4364.58 | 5926.161 | 150.006 | 2898.846 | 4364.58 | 5926.161 | 6757.161
Peak Net Load Hour: | Hydrogen less 25% |  |  | 1040.6056 | 2072.4639 | 3798.1342 | 4280.5939 | 5310.2292 | 1520.7361 | 2978.1874 | 4280.5939 | 5310.2292 | 5660.6889
Peak Net Load Hour: | Oil & Gas less 25% |  |  | 1274.3901 | 1739.8136 | 2046.3971 | 2126.5781 | 2343.955 | 1581.526 | 1940.1521 | 2126.5781 | 2343.955 | 2348.2885
Peak Net Load Hour: | Crypto less 25% |  |  | 1576.8797 | 3015.4352 | 4337.2232 | 4503.4232 | 5625.2732 | 2614.8302 | 4087.9232 | 4503.4232 | 5625.2732 | 6349.4732
Peak Net Load Hour: | ERCOT Large Load Forecast Total - less 25% |  |  | 5720.5455 | 12055.5825 | 24096.0919 | 28771.781 | 35836.9933 | 9097.5066 | 19175.5537 | 28771.781 | 35836.9933 | 39227.8964
Peak Net Load Hour: | Data Centers - less 25% -100% curtailable |  |  | -1824.9201 | -4994.7639 | -10427.5125 | -13496.6059 | -16631.3749 | -3230.4083 | -7270.4451 | -13496.6059 | -16631.3749 | -18112.2848
Peak Net Load Hour: | Industrial - less 25% - 85% curtailable |  |  | -3.1875 | -198.1401 | -2963.8012 | -3709.893 | -5037.2369 | -127.5051 | -2464.0191 | -3709.893 | -5037.2369 | -5743.5868
Peak Net Load Hour: | Hydrogen - less 25% - 85% curtailable |  |  | -884.5148 | -1761.5943 | -3228.4141 | -3638.5048 | -4513.6948 | -1292.6257 | -2531.4593 | -3638.5048 | -4513.6948 | -4811.5855
Peak Net Load Hour: | Oil & Gas - less 25% - non-curtailable |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Net Load Hour: | Crypto - less 25% - 85% curtailable |  |  | -1340.3477 | -2563.1199 | -3686.6397 | -3827.9097 | -4781.4822 | -2222.6057 | -3474.7347 | -3827.9097 | -4781.4822 | -5397.0522
Peak Net Load Hour: | Curtailment total based on 25% reduced loads |  |  | -4052.9701 | -9517.6181 | -20306.3675 | -24672.9134 | -30963.7887 | -6873.1447 | -15740.6582 | -24672.9134 | -30963.7887 | -34064.5094
Peak Net Load Hour: | Difference between 25% less load and protocol prescribed load |  |  | -1906.8485 | -4018.5275 | -8032.0306 | -9590.5937 | -11945.6644 | -3032.5022 | -6391.8512 | -9590.5937 | -11945.6644 | -13075.9655
Peak Net Load Hour: | Scenario 2: Base Case with 25% decrease in Large Load + Senate Bill 6 Large Load curtailment impact |  | Load-Resource Scenarios | 0 | -13536.1456 | -28338.3982 | -34263.5071 | -42909.4532 | 0 | -22132.5095 | -34263.5071 | -42909.4532 | -47140.4749
Peak Net Load Hour: | TSP Provided Large Load Forecast Total |  |  | 22008.629 | 49972.2 | 83815.977 | 106189.843 | 116852.661 | 32381.395 | 67351.537 | 83815.977 | 106189.843 | 116852.661
Peak Net Load Hour: | TSP Forecast Scaling Factor |  |  | 2.8855 | 3.1089 | 2.6088 | 2.7681 | 2.4455 | 2.6695 | 2.6343 | 2.1848 | 2.2224 | 2.2341
Peak Net Load Hour: | Data Centers, scaled by TSP Forecast Scaling Factor |  |  | 7021.0069 | 20704.0464 | 36271.1161 | 49812.7821 | 54229.4493 | 11498.2193 | 25536.4543 | 39317.3855 | 49281.0062 | 53953.1525
Peak Net Load Hour: | Industrial, scaled by TSP Forecast Scaling Factor |  |  | 14.4274 | 966.2594 | 12128.591 | 16108.6331 | 19323.264 | 533.9269 | 10181.8042 | 12714.5948 | 17560.0141 | 20128.3351
Peak Net Load Hour: | Hydrogen, scaled by TSP Forecast Scaling Factor |  |  | 4003.5173 | 8590.674 | 13211.4507 | 15798.6604 | 17314.9127 | 5412.863 | 10460.4802 | 12469.9323 | 15734.925 | 16862.147
Peak Net Load Hour: | Oil & Gas, scaled by TSP Forecast Scaling Factor |  |  | 4902.9553 | 7211.7885 | 7118.1986 | 7848.6969 | 7642.8673 | 5629.2369 | 6814.5215 | 6195.0012 | 6945.4548 | 6995.118
Peak Net Load Hour: | Crypto, scaled by TSP Forecast Scaling Factor |  |  | 6066.7221 | 12499.4317 | 15086.6206 | 16621.0705 | 18342.1677 | 9307.1489 | 14358.2768 | 13119.0632 | 16668.4429 | 18913.9083
Peak Net Load Hour: | ERCOT Large Load Forecast Total, scaled by TSP Forecast Scaling Factor (a.k.a. TSP LL Forecast Total) |  |  | 22008.629 | 49972.2 | 83815.977 | 106189.843 | 116852.661 | 32381.395 | 67351.537 | 83815.977 | 106189.843 | 116852.661
Peak Net Load Hour: | Data Centers -100% curtailable, scaled by TSP Forecast Scaling Factor |  |  | -7021.0069 | -20704.0464 | -36271.1161 | -49812.7821 | -54229.4493 | -11498.2193 | -25536.4543 | -39317.3855 | -49281.0062 | -53953.1525
Peak Net Load Hour: | Industrial - 85% curtailable, scaled by TSP Forecast Scaling Factor |  |  | -12.2633 | -821.3205 | -10309.3024 | -13692.3382 | -16424.7744 | -453.8379 | -8654.5336 | -10807.4056 | -14926.012 | -17109.0848
Peak Net Load Hour: | Hydrogen - 85% curtailable, scaled by TSP Forecast Scaling Factor |  |  | -3402.9897 | -7302.0729 | -11229.7331 | -13428.8613 | -14717.6758 | -4600.9335 | -8891.4082 | -10599.4425 | -13374.6863 | -14332.825
Peak Net Load Hour: | Oil & Gas - non-curtailable, scaled by TSP Forecast Scaling Factor |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Peak Net Load Hour: | Crypto - 85% curtailable, scaled by TSP Forecast Scaling Factor |  |  | -5156.7138 | -10624.517 | -12823.6276 | -14127.9099 | -15590.8425 | -7911.0766 | -12204.5353 | -11151.2037 | -14168.1765 | -16076.8221
Peak Net Load Hour: | Curtailment total based on TSP scaled loads |  |  | -15592.9737 | -39451.9567 | -70633.779 | -91061.8915 | -100962.742 | -24464.0673 | -55286.9314 | -71875.4373 | -91749.8809 | -101471.8844
Peak Net Load Hour: | Incremental Additions to Large Load (TSP - ERCOT Adjusted) |  |  | 14381.235 | 33898.0901 | 51687.8544 | 67827.4683 | 69070.0033 | 20251.3862 | 41784.132 | 45453.6023 | 58407.1853 | 64548.7991
Peak Net Load Hour: | Scenario 3: Base Case with TSP Provided Large Loads replacing ERCOT Adjusted Large Loads + Senate Bill 6 Large Load curtailment impact |  | Load-Resource Scenarios | 0 | -5553.8667 | -18945.9246 | -23234.4231 | -31892.7387 | 0 | -13502.7994 | -26421.8349 | -33342.6956 | -36923.0853
Peak Load Hour: | TEF, CDR eligible | Unit Details |  | 836 | 957.8 | 1631.8 | 2931.8 | 2931.8 | 894 | 1015.8 | 3062.8 | 3062.8 | 3062.8
Peak Load Hour: | TEF, all projects |  |  | 836 | 2286.3 | 5236.7 | 6976.7 | 8053 | 894 | 2867.7 | 7120.7 | 7120.7 | 8748
Peak Load Hour: | Scenario 2: Includes all Texas Energy Fund projects (regardless of Planning Guide Sec. 6.9(1) milestone conditions) |  |  | 0 | 1328.5 | 3604.9 | 4044.9 | 5121.2 | 0 | 1851.9 | 4057.9 | 4057.9 | 5685.2
Peak Load Hour: | TEF, CDR eligible, non-brownfield |  |  | 414 | 535.8 | 535.8 | 1835.8 | 1835.8 | 438 | 559.8 | 1909.8 | 1909.8 | 1909.8
Peak Load Hour: | TEF, CDR eligible, non-brownfield (with delay) |  |  | 0 | 414 | 535.8 | 535.8 | 1835.8 | 0 | 438 | 559.8 | 1909.8 | 1909.8
Peak Load Hour: | Scenario 3: One-year TEF project delays for those meeting Planning Guide Sec. 6.9(1) conditions (excluding "brownfield" sites) |  |  | -836 | -543.8 | -1096 | -2396 | -1096 | -894 | -577.8 | -2503 | -1153 | -1153
Peak Net Load Hour: | TEF, CDR eligible | Unit Details |  | 836 | 957.8 | 1631.8 | 2931.8 | 2931.8 | 894 | 1015.8 | 3062.8 | 3062.8 | 3062.8
Peak Net Load Hour: | TEF, all projects |  |  | 836 | 2286.3 | 5236.7 | 6976.7 | 8053 | 894 | 2867.7 | 7120.7 | 7120.7 | 8748
Peak Net Load Hour: | Scenario 2: Includes all Texas Energy Fund projects (regardless of Planning Guide Sec. 6.9(1) milestone conditions) |  |  | 0 | 1328.5 | 3604.9 | 4044.9 | 5121.2 | 0 | 1851.9 | 4057.9 | 4057.9 | 5685.2
Peak Net Load Hour: | TEF, CDR eligible, non-brownfield |  |  | 414 | 535.8 | 535.8 | 1835.8 | 1835.8 | 438 | 559.8 | 1909.8 | 1909.8 | 1909.8
Peak Net Load Hour: | TEF, CDR eligible, non-brownfield (with delay) |  |  | 0 | 414 | 535.8 | 535.8 | 1835.8 | 0 | 438 | 559.8 | 1909.8 | 1909.8
Peak Net Load Hour: | Scenario 3: One-year TEF project delays for those meeting Planning Guide Sec. 6.9(1) conditions (excluding "brownfield" sites) |  |  | -836 | -543.8 | -1096 | -2396 | -1096 | -894 | -577.8 | -2503 | -1153 | -1153
Note on E16: accounting for Senate Bill 6 implementation period.
Note on J16: accounting for Senate Bill 6 implementation period.
Note on E30: accounting for Senate Bill 6 implementation period.
Note on J30: accounting for Senate Bill 6 implementation period.
Note on E46: accounting for Senate Bill 6 implementation period.
Note on J46: accounting for Senate Bill 6 implementation period.
Note on E59: accounting for Senate Bill 6 implementation period.
Note on J59: accounting for Senate Bill 6 implementation period.
Note on E73: accounting for Senate Bill 6 implementation period.
Note on J73: accounting for Senate Bill 6 implementation period.
Note on E89: accounting for Senate Bill 6 implementation period.
Note on J89: accounting for Senate Bill 6 implementation period.

## WindProfiles
Input cells (non-formulas)
FORECAST YEAR | Year | Month | Day | HE | Value
2026 | 2008 | 8 | 1 | 1 | 11716.7353
2026 | 2008 | 8 | 1 | 2 | 10601.6638
2026 | 2008 | 8 | 1 | 3 | 9619.4824
2026 | 2008 | 8 | 1 | 4 | 8958.3543
2026 | 2008 | 8 | 1 | 5 | 8871.2315
2026 | 2008 | 8 | 1 | 6 | 8435.8184
2026 | 2008 | 8 | 1 | 7 | 7866.0087
2026 | 2008 | 8 | 1 | 8 | 6222.0459
2026 | 2008 | 8 | 1 | 9 | 6318.634
2026 | 2008 | 8 | 1 | 10 | 5614.5953
2026 | 2008 | 8 | 1 | 11 | 3759.0014
2026 | 2008 | 8 | 1 | 12 | 4070.813
2026 | 2008 | 8 | 1 | 13 | 4753.7699
2026 | 2008 | 8 | 1 | 14 | 5980.3739
2026 | 2008 | 8 | 1 | 15 | 7665.3811
2026 | 2008 | 8 | 1 | 16 | 9309.4873
2026 | 2008 | 8 | 1 | 17 | 9938.3196
2026 | 2008 | 8 | 1 | 18 | 11401.5934
2026 | 2008 | 8 | 1 | 19 | 11120.3111
2026 | 2008 | 8 | 1 | 20 | 11208.1368
2026 | 2008 | 8 | 1 | 21 | 12282.0291
2026 | 2008 | 8 | 1 | 22 | 12513.6671
2026 | 2008 | 8 | 1 | 23 | 13220.3957
2026 | 2008 | 8 | 1 | 24 | 13481.7901
2026 | 2008 | 8 | 2 | 1 | 12691.2822
2026 | 2008 | 8 | 2 | 2 | 11831.0071
2026 | 2008 | 8 | 2 | 3 | 11736.0615
2026 | 2008 | 8 | 2 | 4 | 10888.6079
2026 | 2008 | 8 | 2 | 5 | 9873.8334
2026 | 2008 | 8 | 2 | 6 | 9494.5757
2026 | 2008 | 8 | 2 | 7 | 9072.7004
2026 | 2008 | 8 | 2 | 8 | 6891.2013
2026 | 2008 | 8 | 2 | 9 | 6714.1868
2026 | 2008 | 8 | 2 | 10 | 8257.5309
2026 | 2008 | 8 | 2 | 11 | 6654.7454
2026 | 2008 | 8 | 2 | 12 | 5738.5408
2026 | 2008 | 8 | 2 | 13 | 6470.0937
2026 | 2008 | 8 | 2 | 14 | 7890.8878
2026 | 2008 | 8 | 2 | 15 | 9459.2413
2026 | 2008 | 8 | 2 | 16 | 11036.1676
2026 | 2008 | 8 | 2 | 17 | 12813.646
2026 | 2008 | 8 | 2 | 18 | 14883.6485
2026 | 2008 | 8 | 2 | 19 | 16028.5437
2026 | 2008 | 8 | 2 | 20 | 17194.2955
2026 | 2008 | 8 | 2 | 21 | 19422.29
2026 | 2008 | 8 | 2 | 22 | 21117.2488
2026 | 2008 | 8 | 2 | 23 | 21422.378
2026 | 2008 | 8 | 2 | 24 | 20752.1735
2026 | 2008 | 8 | 3 | 1 | 19521.6182
2026 | 2008 | 8 | 3 | 2 | 19165.6255
2026 | 2008 | 8 | 3 | 3 | 19083.3875
2026 | 2008 | 8 | 3 | 4 | 18744.2442
2026 | 2008 | 8 | 3 | 5 | 18217.9774
2026 | 2008 | 8 | 3 | 6 | 16963.6838
2026 | 2008 | 8 | 3 | 7 | 16102.0057
2026 | 2008 | 8 | 3 | 8 | 11742.7912
2026 | 2008 | 8 | 3 | 9 | 10025.1466
2026 | 2008 | 8 | 3 | 10 | 11584.0688
2026 | 2008 | 8 | 3 | 11 | 10410.4014
2026 | 2008 | 8 | 3 | 12 | 10192.2493
2026 | 2008 | 8 | 3 | 13 | 11498.0009
2026 | 2008 | 8 | 3 | 14 | 11981.5794
2026 | 2008 | 8 | 3 | 15 | 12072.2124
2026 | 2008 | 8 | 3 | 16 | 12042.6792
2026 | 2008 | 8 | 3 | 17 | 12652.6106
2026 | 2008 | 8 | 3 | 18 | 13647.4688
2026 | 2008 | 8 | 3 | 19 | 14598.5498
2026 | 2008 | 8 | 3 | 20 | 16721.4402
2026 | 2008 | 8 | 3 | 21 | 19398.2139
2026 | 2008 | 8 | 3 | 22 | 21562.3946
2026 | 2008 | 8 | 3 | 23 | 22232.6065
2026 | 2008 | 8 | 3 | 24 | 22178.8741
2026 | 2008 | 8 | 4 | 1 | 20827.769
2026 | 2008 | 8 | 4 | 2 | 19726.4647
2026 | 2008 | 8 | 4 | 3 | 18937.1657
2026 | 2008 | 8 | 4 | 4 | 17156.6425
2026 | 2008 | 8 | 4 | 5 | 15323.8209
2026 | 2008 | 8 | 4 | 6 | 12685.6176
2026 | 2008 | 8 | 4 | 7 | 9793.7416
2026 | 2008 | 8 | 4 | 8 | 6149.2729
2026 | 2008 | 8 | 4 | 9 | 3815.9792
2026 | 2008 | 8 | 4 | 10 | 4551.477
2026 | 2008 | 8 | 4 | 11 | 3721.9867
2026 | 2008 | 8 | 4 | 12 | 2866.1842
2026 | 2008 | 8 | 4 | 13 | 3200.5356
2026 | 2008 | 8 | 4 | 14 | 4335.8576
2026 | 2008 | 8 | 4 | 15 | 5023.096
2026 | 2008 | 8 | 4 | 16 | 5295.3803
2026 | 2008 | 8 | 4 | 17 | 6191.2134
2026 | 2008 | 8 | 4 | 18 | 7266.5166
2026 | 2008 | 8 | 4 | 19 | 8232.9151
2026 | 2008 | 8 | 4 | 20 | 10212.4498
2026 | 2008 | 8 | 4 | 21 | 13283.7675
2026 | 2008 | 8 | 4 | 22 | 15818.89
2026 | 2008 | 8 | 4 | 23 | 15956.9243
2026 | 2008 | 8 | 4 | 24 | 14330.8913
2026 | 2008 | 8 | 5 | 1 | 12856.753
2026 | 2008 | 8 | 5 | 2 | 11524.7438
2026 | 2008 | 8 | 5 | 3 | 10275.178
2026 | 2008 | 8 | 5 | 4 | 8688.5443
2026 | 2008 | 8 | 5 | 5 | 7176.9392
2026 | 2008 | 8 | 5 | 6 | 5973.1026
2026 | 2008 | 8 | 5 | 7 | 4989.1395
2026 | 2008 | 8 | 5 | 8 | 2566.0927
2026 | 2008 | 8 | 5 | 9 | 1703.8181
2026 | 2008 | 8 | 5 | 10 | 1485.7998
2026 | 2008 | 8 | 5 | 11 | 1425.5295
2026 | 2008 | 8 | 5 | 12 | 1228.5855
2026 | 2008 | 8 | 5 | 13 | 1781.3595
2026 | 2008 | 8 | 5 | 14 | 2702.2118
2026 | 2008 | 8 | 5 | 15 | 4937.7154
2026 | 2008 | 8 | 5 | 16 | 6609.3921
2026 | 2008 | 8 | 5 | 17 | 9003.1649
2026 | 2008 | 8 | 5 | 18 | 11500.085
2026 | 2008 | 8 | 5 | 19 | 13856.8391
2026 | 2008 | 8 | 5 | 20 | 15917.1019
2026 | 2008 | 8 | 5 | 21 | 18919.4475
2026 | 2008 | 8 | 5 | 22 | 19273.9093
2026 | 2008 | 8 | 5 | 23 | 18037.3333
2026 | 2008 | 8 | 5 | 24 | 16555.8951
2026 | 2008 | 8 | 6 | 1 | 14741.6983
2026 | 2008 | 8 | 6 | 2 | 12262.9784
2026 | 2008 | 8 | 6 | 3 | 9648.9642
2026 | 2008 | 8 | 6 | 4 | 7920.2995
2026 | 2008 | 8 | 6 | 5 | 6526.0884
2026 | 2008 | 8 | 6 | 6 | 5409.2538
2026 | 2008 | 8 | 6 | 7 | 4563.6293
2026 | 2008 | 8 | 6 | 8 | 4107.9839
2026 | 2008 | 8 | 6 | 9 | 5445.969
2026 | 2008 | 8 | 6 | 10 | 7181.3182
2026 | 2008 | 8 | 6 | 11 | 7921.6606
2026 | 2008 | 8 | 6 | 12 | 9004.5475
2026 | 2008 | 8 | 6 | 13 | 10742.8746
2026 | 2008 | 8 | 6 | 14 | 11553.6985
2026 | 2008 | 8 | 6 | 15 | 12335.6295
2026 | 2008 | 8 | 6 | 16 | 12174.7603
2026 | 2008 | 8 | 6 | 17 | 13190.6546
2026 | 2008 | 8 | 6 | 18 | 13746.7884
2026 | 2008 | 8 | 6 | 19 | 13931.2215
2026 | 2008 | 8 | 6 | 20 | 13842.4113
2026 | 2008 | 8 | 6 | 21 | 14489.1568
2026 | 2008 | 8 | 6 | 22 | 14537.831
2026 | 2008 | 8 | 6 | 23 | 14154.7936
2026 | 2008 | 8 | 6 | 24 | 13373.9409
2026 | 2008 | 8 | 7 | 1 | 12081.3632
2026 | 2008 | 8 | 7 | 2 | 10716.7196
2026 | 2008 | 8 | 7 | 3 | 10251.7468
2026 | 2008 | 8 | 7 | 4 | 9527.8181
2026 | 2008 | 8 | 7 | 5 | 8592.8317
2026 | 2008 | 8 | 7 | 6 | 7513.7616
2026 | 2008 | 8 | 7 | 7 | 6818.0642
2026 | 2008 | 8 | 7 | 8 | 5760.3818
2026 | 2008 | 8 | 7 | 9 | 6461.943
2026 | 2008 | 8 | 7 | 10 | 6776.0184
2026 | 2008 | 8 | 7 | 11 | 6624.5366
2026 | 2008 | 8 | 7 | 12 | 6598.5997
2026 | 2008 | 8 | 7 | 13 | 6923.3615
2026 | 2008 | 8 | 7 | 14 | 7606.291
2026 | 2008 | 8 | 7 | 15 | 8510.5064
2026 | 2008 | 8 | 7 | 16 | 8678.6659
2026 | 2008 | 8 | 7 | 17 | 9517.7703
2026 | 2008 | 8 | 7 | 18 | 10320.9327
2026 | 2008 | 8 | 7 | 19 | 10867.7198
2026 | 2008 | 8 | 7 | 20 | 10798.4911
2026 | 2008 | 8 | 7 | 21 | 11260.8838
2026 | 2008 | 8 | 7 | 22 | 12133.8025
2026 | 2008 | 8 | 7 | 23 | 12380.8182
2026 | 2008 | 8 | 7 | 24 | 12918.1513
2026 | 2008 | 8 | 8 | 1 | 12841.7455
2026 | 2008 | 8 | 8 | 2 | 12534.7314
2026 | 2008 | 8 | 8 | 3 | 12128.7297
2026 | 2008 | 8 | 8 | 4 | 11008.8942
2026 | 2008 | 8 | 8 | 5 | 10231.8788
2026 | 2008 | 8 | 8 | 6 | 9695.6934
2026 | 2008 | 8 | 8 | 7 | 8809.7901
2026 | 2008 | 8 | 8 | 8 | 5778.7004
2026 | 2008 | 8 | 8 | 9 | 4785.023
2026 | 2008 | 8 | 8 | 10 | 5508.707
2026 | 2008 | 8 | 8 | 11 | 4586.032
2026 | 2008 | 8 | 8 | 12 | 3771.6095
2026 | 2008 | 8 | 8 | 13 | 4201.6571
2026 | 2008 | 8 | 8 | 14 | 5682.5077
2026 | 2008 | 8 | 8 | 15 | 7510.7077
2026 | 2008 | 8 | 8 | 16 | 9335.7911
2026 | 2008 | 8 | 8 | 17 | 10530.9184
2026 | 2008 | 8 | 8 | 18 | 11344.2285
2026 | 2008 | 8 | 8 | 19 | 12165.5159
2026 | 2008 | 8 | 8 | 20 | 13594.7719
2026 | 2008 | 8 | 8 | 21 | 16172.4057
2026 | 2008 | 8 | 8 | 22 | 18190.6
2026 | 2008 | 8 | 8 | 23 | 19750.4832
2026 | 2008 | 8 | 8 | 24 | 19921.1603
2026 | 2008 | 8 | 9 | 1 | 18928.8566
2026 | 2008 | 8 | 9 | 2 | 18087.0857
2026 | 2008 | 8 | 9 | 3 | 17341.1772
2026 | 2008 | 8 | 9 | 4 | 16873.3792
2026 | 2008 | 8 | 9 | 5 | 16592.4468
2026 | 2008 | 8 | 9 | 6 | 16711.2047
2026 | 2008 | 8 | 9 | 7 | 16713.1907
2026 | 2008 | 8 | 9 | 8 | 13047.2461
2026 | 2008 | 8 | 9 | 9 | 11739.2079
2026 | 2008 | 8 | 9 | 10 | 13117.546
2026 | 2008 | 8 | 9 | 11 | 12589.6304
2026 | 2008 | 8 | 9 | 12 | 12754.3806
2026 | 2008 | 8 | 9 | 13 | 14715.2086
2026 | 2008 | 8 | 9 | 14 | 16099.5372
2026 | 2008 | 8 | 9 | 15 | 17409.4262
2026 | 2008 | 8 | 9 | 16 | 17795.3651
2026 | 2008 | 8 | 9 | 17 | 19310.6587
2026 | 2008 | 8 | 9 | 18 | 21052.5682
2026 | 2008 | 8 | 9 | 19 | 21661.8768
2026 | 2008 | 8 | 9 | 20 | 22482.6912
2026 | 2008 | 8 | 9 | 21 | 23893.2983
2026 | 2008 | 8 | 9 | 22 | 25625.4238
2026 | 2008 | 8 | 9 | 23 | 26371.8398
2026 | 2008 | 8 | 9 | 24 | 26819.2721
2026 | 2008 | 8 | 10 | 1 | 26146.9427
2026 | 2008 | 8 | 10 | 2 | 26299.9864
2026 | 2008 | 8 | 10 | 3 | 26672.0889
2026 | 2008 | 8 | 10 | 4 | 26767.9846
2026 | 2008 | 8 | 10 | 5 | 26561.0284
2026 | 2008 | 8 | 10 | 6 | 26501.618
2026 | 2008 | 8 | 10 | 7 | 24516.3081
2026 | 2008 | 8 | 10 | 8 | 22120.3507
2026 | 2008 | 8 | 10 | 9 | 23516.3001
2026 | 2008 | 8 | 10 | 10 | 22814.7672
2026 | 2008 | 8 | 10 | 11 | 18724.0177
2026 | 2008 | 8 | 10 | 12 | 15768.1264
2026 | 2008 | 8 | 10 | 13 | 14127.5999
2026 | 2008 | 8 | 10 | 14 | 13299.3027
2026 | 2008 | 8 | 10 | 15 | 12397.1557
2026 | 2008 | 8 | 10 | 16 | 12739.9762
2026 | 2008 | 8 | 10 | 17 | 14791.2173
2026 | 2008 | 8 | 10 | 18 | 18104.7786
2026 | 2008 | 8 | 10 | 19 | 20066.0966
2026 | 2008 | 8 | 10 | 20 | 19377.4405
2026 | 2008 | 8 | 10 | 21 | 19222.8432
2026 | 2008 | 8 | 10 | 22 | 18456.3556
2026 | 2008 | 8 | 10 | 23 | 18195.4763
2026 | 2008 | 8 | 10 | 24 | 16076.2718
2026 | 2008 | 8 | 11 | 1 | 14599.0048
2026 | 2008 | 8 | 11 | 2 | 14461.2862
2026 | 2008 | 8 | 11 | 3 | 14161.619
2026 | 2008 | 8 | 11 | 4 | 13500.0809
2026 | 2008 | 8 | 11 | 5 | 12615.753
2026 | 2008 | 8 | 11 | 6 | 11967.3921
2026 | 2008 | 8 | 11 | 7 | 11161.9777
2026 | 2008 | 8 | 11 | 8 | 10423.2722
2026 | 2008 | 8 | 11 | 9 | 13178.1165
2026 | 2008 | 8 | 11 | 10 | 13287.9311
2026 | 2008 | 8 | 11 | 11 | 12555.1488
2026 | 2008 | 8 | 11 | 12 | 12184.7958
2026 | 2008 | 8 | 11 | 13 | 11913.2853
2026 | 2008 | 8 | 11 | 14 | 12064.2542
2026 | 2008 | 8 | 11 | 15 | 11543.4735
2026 | 2008 | 8 | 11 | 16 | 11013.6753
2026 | 2008 | 8 | 11 | 17 | 11637.421
2026 | 2008 | 8 | 11 | 18 | 11539.0473
2026 | 2008 | 8 | 11 | 19 | 12090.8674
2026 | 2008 | 8 | 11 | 20 | 11876.9385
2026 | 2008 | 8 | 11 | 21 | 11921.4472
2026 | 2008 | 8 | 11 | 22 | 10305.7942
2026 | 2008 | 8 | 11 | 23 | 9519.5082
2026 | 2008 | 8 | 11 | 24 | 8768.0515
2026 | 2008 | 8 | 12 | 1 | 8439.595
2026 | 2008 | 8 | 12 | 2 | 8660.8979
2026 | 2008 | 8 | 12 | 3 | 8356.763
2026 | 2008 | 8 | 12 | 4 | 8148.0289
2026 | 2008 | 8 | 12 | 5 | 7512.0325
2026 | 2008 | 8 | 12 | 6 | 7153.3331
2026 | 2008 | 8 | 12 | 7 | 6427.4373
2026 | 2008 | 8 | 12 | 8 | 5168.4247
2026 | 2008 | 8 | 12 | 9 | 6211.1102
2026 | 2008 | 8 | 12 | 10 | 6554.1144
2026 | 2008 | 8 | 12 | 11 | 6077.911
2026 | 2008 | 8 | 12 | 12 | 5366.6478
2026 | 2008 | 8 | 12 | 13 | 6385.2771
2026 | 2008 | 8 | 12 | 14 | 7333.173
2026 | 2008 | 8 | 12 | 15 | 8050.6292
2026 | 2008 | 8 | 12 | 16 | 8533.2229
2026 | 2008 | 8 | 12 | 17 | 9069.9364
2026 | 2008 | 8 | 12 | 18 | 9919.5693
2026 | 2008 | 8 | 12 | 19 | 10454.0992
2026 | 2008 | 8 | 12 | 20 | 9732.9619
2026 | 2008 | 8 | 12 | 21 | 9610.0502
2026 | 2008 | 8 | 12 | 22 | 9372.5553
2026 | 2008 | 8 | 12 | 23 | 8956.7828
2026 | 2008 | 8 | 12 | 24 | 8178.5888
2026 | 2008 | 8 | 13 | 1 | 7046.0518
2026 | 2008 | 8 | 13 | 2 | 6471.7294
2026 | 2008 | 8 | 13 | 3 | 6242.9569
2026 | 2008 | 8 | 13 | 4 | 6086.583
2026 | 2008 | 8 | 13 | 5 | 5259.2938
2026 | 2008 | 8 | 13 | 6 | 4378.8279
2026 | 2008 | 8 | 13 | 7 | 3320.9289
2026 | 2008 | 8 | 13 | 8 | 2081.1419
2026 | 2008 | 8 | 13 | 9 | 2413.2554
2026 | 2008 | 8 | 13 | 10 | 2548.7175
2026 | 2008 | 8 | 13 | 11 | 2144.3754
2026 | 2008 | 8 | 13 | 12 | 2188.0004
2026 | 2008 | 8 | 13 | 13 | 2214.5428
2026 | 2008 | 8 | 13 | 14 | 2628.9222
2026 | 2008 | 8 | 13 | 15 | 3603.4737
2026 | 2008 | 8 | 13 | 16 | 4425.0702
2026 | 2008 | 8 | 13 | 17 | 5682.8623
2026 | 2008 | 8 | 13 | 18 | 7617.27
2026 | 2008 | 8 | 13 | 19 | 8579.686
2026 | 2008 | 8 | 13 | 20 | 9290.6543
2026 | 2008 | 8 | 13 | 21 | 10663.494
2026 | 2008 | 8 | 13 | 22 | 11156.5993
2026 | 2008 | 8 | 13 | 23 | 10377.8395
2026 | 2008 | 8 | 13 | 24 | 9295.8325
2026 | 2008 | 8 | 14 | 1 | 8432.5234
2026 | 2008 | 8 | 14 | 2 | 8152.8616
2026 | 2008 | 8 | 14 | 3 | 7943.2457
2026 | 2008 | 8 | 14 | 4 | 7876.2083
2026 | 2008 | 8 | 14 | 5 | 7140.9112
2026 | 2008 | 8 | 14 | 6 | 6553.405
2026 | 2008 | 8 | 14 | 7 | 5834.556
2026 | 2008 | 8 | 14 | 8 | 3995.6826
2026 | 2008 | 8 | 14 | 9 | 3485.4652
2026 | 2008 | 8 | 14 | 10 | 3675.4278
2026 | 2008 | 8 | 14 | 11 | 4472.6902
2026 | 2008 | 8 | 14 | 12 | 4669.6813
2026 | 2008 | 8 | 14 | 13 | 6201.2429
2026 | 2008 | 8 | 14 | 14 | 7412.0205
2026 | 2008 | 8 | 14 | 15 | 8390.5628
2026 | 2008 | 8 | 14 | 16 | 9107.5178
2026 | 2008 | 8 | 14 | 17 | 9915.9729
2026 | 2008 | 8 | 14 | 18 | 10959.0548
2026 | 2008 | 8 | 14 | 19 | 12218.2394
2026 | 2008 | 8 | 14 | 20 | 13149.1514
2026 | 2008 | 8 | 14 | 21 | 15082.2085
2026 | 2008 | 8 | 14 | 22 | 18150.5957
2026 | 2008 | 8 | 14 | 23 | 21712.9565
2026 | 2008 | 8 | 14 | 24 | 22483.6235
2026 | 2008 | 8 | 15 | 1 | 21420.0172
2026 | 2008 | 8 | 15 | 2 | 19792.757
2026 | 2008 | 8 | 15 | 3 | 18065.0646
2026 | 2008 | 8 | 15 | 4 | 15812.935
2026 | 2008 | 8 | 15 | 5 | 11781.6397
2026 | 2008 | 8 | 15 | 6 | 9253.4505
2026 | 2008 | 8 | 15 | 7 | 7166.6072
2026 | 2008 | 8 | 15 | 8 | 4702.5808
2026 | 2008 | 8 | 15 | 9 | 4207.5308
2026 | 2008 | 8 | 15 | 10 | 5281.1377
2026 | 2008 | 8 | 15 | 11 | 5820.948
2026 | 2008 | 8 | 15 | 12 | 6279.4509
2026 | 2008 | 8 | 15 | 13 | 7156.5534
2026 | 2008 | 8 | 15 | 14 | 7711.9082
2026 | 2008 | 8 | 15 | 15 | 7733.656
2026 | 2008 | 8 | 15 | 16 | 7998.4371
2026 | 2008 | 8 | 15 | 17 | 8635.1773
2026 | 2008 | 8 | 15 | 18 | 10079.7187
2026 | 2008 | 8 | 15 | 19 | 11093.9539
2026 | 2008 | 8 | 15 | 20 | 12701.2512
2026 | 2008 | 8 | 15 | 21 | 15131.2849
2026 | 2008 | 8 | 15 | 22 | 16958.1875
2026 | 2008 | 8 | 15 | 23 | 17144.9636
2026 | 2008 | 8 | 15 | 24 | 16772.7472
2026 | 2008 | 8 | 16 | 1 | 15798.7765
2026 | 2008 | 8 | 16 | 2 | 14763.8488
2026 | 2008 | 8 | 16 | 3 | 12516.7777
2026 | 2008 | 8 | 16 | 4 | 10598.2472
2026 | 2008 | 8 | 16 | 5 | 8511.4666
2026 | 2008 | 8 | 16 | 6 | 6912.6815
2026 | 2008 | 8 | 16 | 7 | 5494.9579
2026 | 2008 | 8 | 16 | 8 | 4395.8464
2026 | 2008 | 8 | 16 | 9 | 4930.0367
2026 | 2008 | 8 | 16 | 10 | 6382.0256
2026 | 2008 | 8 | 16 | 11 | 7078.3215
2026 | 2008 | 8 | 16 | 12 | 7882.3555
2026 | 2008 | 8 | 16 | 13 | 9481.7571
2026 | 2008 | 8 | 16 | 14 | 12344.5068
2026 | 2008 | 8 | 16 | 15 | 13446.5507
2026 | 2008 | 8 | 16 | 16 | 14454.1894
2026 | 2008 | 8 | 16 | 17 | 15722.4121
2026 | 2008 | 8 | 16 | 18 | 16221.7499
2026 | 2008 | 8 | 16 | 19 | 15759.7956
2026 | 2008 | 8 | 16 | 20 | 14153.6205
2026 | 2008 | 8 | 16 | 21 | 13140.7486
2026 | 2008 | 8 | 16 | 22 | 11227.1902
2026 | 2008 | 8 | 16 | 23 | 9292.8048
2026 | 2008 | 8 | 16 | 24 | 7207.763
2026 | 2008 | 8 | 17 | 1 | 5396.9335
2026 | 2008 | 8 | 17 | 2 | 4388.3783
2026 | 2008 | 8 | 17 | 3 | 4058.3772
2026 | 2008 | 8 | 17 | 4 | 3891.0134
2026 | 2008 | 8 | 17 | 5 | 3957.2947
2026 | 2008 | 8 | 17 | 6 | 4365.7549
2026 | 2008 | 8 | 17 | 7 | 4394.2322
2026 | 2008 | 8 | 17 | 8 | 4699.6651
2026 | 2008 | 8 | 17 | 9 | 6198.2531
2026 | 2008 | 8 | 17 | 10 | 7622.1647
2026 | 2008 | 8 | 17 | 11 | 7812.2229
2026 | 2008 | 8 | 17 | 12 | 7932.5975
2026 | 2008 | 8 | 17 | 13 | 7798.4164
2026 | 2008 | 8 | 17 | 14 | 7525.25
2026 | 2008 | 8 | 17 | 15 | 6734.0893
2026 | 2008 | 8 | 17 | 16 | 6897.725
2026 | 2008 | 8 | 17 | 17 | 8249.9838
2026 | 2008 | 8 | 17 | 18 | 9863.2478
2026 | 2008 | 8 | 17 | 19 | 10944.7063
2026 | 2008 | 8 | 17 | 20 | 10625.7584
2026 | 2008 | 8 | 17 | 21 | 11226.7019
2026 | 2008 | 8 | 17 | 22 | 11524.5033
2026 | 2008 | 8 | 17 | 23 | 11536.1921
2026 | 2008 | 8 | 17 | 24 | 11366.2403
2026 | 2008 | 8 | 18 | 1 | 10608.866
2026 | 2008 | 8 | 18 | 2 | 10061.9281
2026 | 2008 | 8 | 18 | 3 | 9483.629
2026 | 2008 | 8 | 18 | 4 | 9610.4269
2026 | 2008 | 8 | 18 | 5 | 9588.5802
2026 | 2008 | 8 | 18 | 6 | 9798.1375
2026 | 2008 | 8 | 18 | 7 | 8975.951
2026 | 2008 | 8 | 18 | 8 | 8089.3934
2026 | 2008 | 8 | 18 | 9 | 9710.4298
2026 | 2008 | 8 | 18 | 10 | 10730.3795
2026 | 2008 | 8 | 18 | 11 | 10451.8705
2026 | 2008 | 8 | 18 | 12 | 10376.4697
2026 | 2008 | 8 | 18 | 13 | 10801.5819
2026 | 2008 | 8 | 18 | 14 | 11223.9479
2026 | 2008 | 8 | 18 | 15 | 11809.9865
2026 | 2008 | 8 | 18 | 16 | 12100.1217
2026 | 2008 | 8 | 18 | 17 | 13468.9797
2026 | 2008 | 8 | 18 | 18 | 13800.5298
2026 | 2008 | 8 | 18 | 19 | 13652.2574
2026 | 2008 | 8 | 18 | 20 | 12955.1806
2026 | 2008 | 8 | 18 | 21 | 12903.6021
2026 | 2008 | 8 | 18 | 22 | 12594.7123
2026 | 2008 | 8 | 18 | 23 | 11490.9077
2026 | 2008 | 8 | 18 | 24 | 10591.4047
2026 | 2008 | 8 | 19 | 1 | 10063.145
2026 | 2008 | 8 | 19 | 2 | 9809.269
2026 | 2008 | 8 | 19 | 3 | 10768.8963
2026 | 2008 | 8 | 19 | 4 | 11655.9213
2026 | 2008 | 8 | 19 | 5 | 12284.808
2026 | 2008 | 8 | 19 | 6 | 13071.8756
2026 | 2008 | 8 | 19 | 7 | 13289.0252
2026 | 2008 | 8 | 19 | 8 | 12171.7172
2026 | 2008 | 8 | 19 | 9 | 14323.9693
2026 | 2008 | 8 | 19 | 10 | 13362.496
2026 | 2008 | 8 | 19 | 11 | 10934.4004
2026 | 2008 | 8 | 19 | 12 | 10307.8433
2026 | 2008 | 8 | 19 | 13 | 10984.0506
2026 | 2008 | 8 | 19 | 14 | 11710.363
2026 | 2008 | 8 | 19 | 15 | 13228.6699
2026 | 2008 | 8 | 19 | 16 | 14278.7795
2026 | 2008 | 8 | 19 | 17 | 15533.2473
2026 | 2008 | 8 | 19 | 18 | 15318.2472
2026 | 2008 | 8 | 19 | 19 | 15132.3097
2026 | 2008 | 8 | 19 | 20 | 13996.0395
2026 | 2008 | 8 | 19 | 21 | 13353.9276
2026 | 2008 | 8 | 19 | 22 | 11791.5954
2026 | 2008 | 8 | 19 | 23 | 9435.1824
2026 | 2008 | 8 | 19 | 24 | 7728.011
2026 | 2008 | 8 | 20 | 1 | 6175.8613
2026 | 2008 | 8 | 20 | 2 | 5369.9683
2026 | 2008 | 8 | 20 | 3 | 5274.5512
2026 | 2008 | 8 | 20 | 4 | 5230.2542
2026 | 2008 | 8 | 20 | 5 | 4960.6496
2026 | 2008 | 8 | 20 | 6 | 4795.4363
2026 | 2008 | 8 | 20 | 7 | 4707.8077
2026 | 2008 | 8 | 20 | 8 | 4076.083
2026 | 2008 | 8 | 20 | 9 | 4850.5517
2026 | 2008 | 8 | 20 | 10 | 4757.255
2026 | 2008 | 8 | 20 | 11 | 4318.8134
2026 | 2008 | 8 | 20 | 12 | 4271.4168
2026 | 2008 | 8 | 20 | 13 | 4847.2006
2026 | 2008 | 8 | 20 | 14 | 5620.7714
2026 | 2008 | 8 | 20 | 15 | 6178.9952
2026 | 2008 | 8 | 20 | 16 | 6570.6466
2026 | 2008 | 8 | 20 | 17 | 6200.2936
2026 | 2008 | 8 | 20 | 18 | 5487.6062
2026 | 2008 | 8 | 20 | 19 | 4755.3385
2026 | 2008 | 8 | 20 | 20 | 4675.4112
2026 | 2008 | 8 | 20 | 21 | 5362.1814
2026 | 2008 | 8 | 20 | 22 | 6565.7194
2026 | 2008 | 8 | 20 | 23 | 7175.7097
2026 | 2008 | 8 | 20 | 24 | 7529.1474
2026 | 2008 | 8 | 21 | 1 | 7983.814
2026 | 2008 | 8 | 21 | 2 | 7838.1369
2026 | 2008 | 8 | 21 | 3 | 7266.9035
2026 | 2008 | 8 | 21 | 4 | 6900.1575
2026 | 2008 | 8 | 21 | 5 | 6421.6413
2026 | 2008 | 8 | 21 | 6 | 6187.5792
2026 | 2008 | 8 | 21 | 7 | 5747.8917
2026 | 2008 | 8 | 21 | 8 | 4237.7887
2026 | 2008 | 8 | 21 | 9 | 4282.9756
2026 | 2008 | 8 | 21 | 10 | 5303.7022
2026 | 2008 | 8 | 21 | 11 | 6112.9235
2026 | 2008 | 8 | 21 | 12 | 6977.2438
2026 | 2008 | 8 | 21 | 13 | 7844.8458
2026 | 2008 | 8 | 21 | 14 | 9180.2421
2026 | 2008 | 8 | 21 | 15 | 9718.2377
2026 | 2008 | 8 | 21 | 16 | 9469.6693
2026 | 2008 | 8 | 21 | 17 | 10232.6621
2026 | 2008 | 8 | 21 | 18 | 11338.4631
2026 | 2008 | 8 | 21 | 19 | 12739.8133
2026 | 2008 | 8 | 21 | 20 | 14597.6901
2026 | 2008 | 8 | 21 | 21 | 18098.2206
2026 | 2008 | 8 | 21 | 22 | 20651.1918
2026 | 2008 | 8 | 21 | 23 | 21818.6662
2026 | 2008 | 8 | 21 | 24 | 21961.7578
2026 | 2008 | 8 | 22 | 1 | 21261.5468
2026 | 2008 | 8 | 22 | 2 | 20534.629
2026 | 2008 | 8 | 22 | 3 | 20394.6112
2026 | 2008 | 8 | 22 | 4 | 20635.261
2026 | 2008 | 8 | 22 | 5 | 20687.5779
2026 | 2008 | 8 | 22 | 6 | 21458.1541
2026 | 2008 | 8 | 22 | 7 | 21595.8304
2026 | 2008 | 8 | 22 | 8 | 19363.0027
2026 | 2008 | 8 | 22 | 9 | 20415.9908
2026 | 2008 | 8 | 22 | 10 | 21485.0168
2026 | 2008 | 8 | 22 | 11 | 19450.6483
2026 | 2008 | 8 | 22 | 12 | 18464.8713
2026 | 2008 | 8 | 22 | 13 | 19796.0571
2026 | 2008 | 8 | 22 | 14 | 20192.8286
2026 | 2008 | 8 | 22 | 15 | 19619.4214
2026 | 2008 | 8 | 22 | 16 | 18181.3885
2026 | 2008 | 8 | 22 | 17 | 17416.4671
2026 | 2008 | 8 | 22 | 18 | 17445.4989
2026 | 2008 | 8 | 22 | 19 | 17235.0504
2026 | 2008 | 8 | 22 | 20 | 18519.3993
2026 | 2008 | 8 | 22 | 21 | 19972.7779
2026 | 2008 | 8 | 22 | 22 | 20753.995
2026 | 2008 | 8 | 22 | 23 | 20181.6331
2026 | 2008 | 8 | 22 | 24 | 18817.8582
2026 | 2008 | 8 | 23 | 1 | 16166.093
2026 | 2008 | 8 | 23 | 2 | 14009.8703
2026 | 2008 | 8 | 23 | 3 | 12036.5042
2026 | 2008 | 8 | 23 | 4 | 9862.2211
2026 | 2008 | 8 | 23 | 5 | 7998.4
2026 | 2008 | 8 | 23 | 6 | 6097.8619
2026 | 2008 | 8 | 23 | 7 | 4629.6099
2026 | 2008 | 8 | 23 | 8 | 3358.6597
2026 | 2008 | 8 | 23 | 9 | 4123.8033
2026 | 2008 | 8 | 23 | 10 | 4389.8356
2026 | 2008 | 8 | 23 | 11 | 3998.7864
2026 | 2008 | 8 | 23 | 12 | 3740.1456
2026 | 2008 | 8 | 23 | 13 | 4583.0705
2026 | 2008 | 8 | 23 | 14 | 5604.8967
2026 | 2008 | 8 | 23 | 15 | 6583.4874
2026 | 2008 | 8 | 23 | 16 | 7031.1539
2026 | 2008 | 8 | 23 | 17 | 7706.1186
2026 | 2008 | 8 | 23 | 18 | 7790.9966
2026 | 2008 | 8 | 23 | 19 | 7011.2354
2026 | 2008 | 8 | 23 | 20 | 5930.7992
2026 | 2008 | 8 | 23 | 21 | 5514.3867
2026 | 2008 | 8 | 23 | 22 | 4481.4481
2026 | 2008 | 8 | 23 | 23 | 3346.323
2026 | 2008 | 8 | 23 | 24 | 2548.9277
2026 | 2008 | 8 | 24 | 1 | 1956.4509
2026 | 2008 | 8 | 24 | 2 | 1272.6041
2026 | 2008 | 8 | 24 | 3 | 922.7103
2026 | 2008 | 8 | 24 | 4 | 714.0967
2026 | 2008 | 8 | 24 | 5 | 619.8907
2026 | 2008 | 8 | 24 | 6 | 564.5803
2026 | 2008 | 8 | 24 | 7 | 650.737
2026 | 2008 | 8 | 24 | 8 | 528.7573
2026 | 2008 | 8 | 24 | 9 | 834.5647
2026 | 2008 | 8 | 24 | 10 | 941.339
2026 | 2008 | 8 | 24 | 11 | 1437.254
2026 | 2008 | 8 | 24 | 12 | 2001.4343
2026 | 2008 | 8 | 24 | 13 | 2772.9087
2026 | 2008 | 8 | 24 | 14 | 2899.9177
2026 | 2008 | 8 | 24 | 15 | 3535.6855
2026 | 2008 | 8 | 24 | 16 | 4039.3567
2026 | 2008 | 8 | 24 | 17 | 4402.5498
2026 | 2008 | 8 | 24 | 18 | 4837.2153
2026 | 2008 | 8 | 24 | 19 | 4619.5269
2026 | 2008 | 8 | 24 | 20 | 3996.7903
2026 | 2008 | 8 | 24 | 21 | 3840.4679
2026 | 2008 | 8 | 24 | 22 | 3754.6062
2026 | 2008 | 8 | 24 | 23 | 3339.0819
2026 | 2008 | 8 | 24 | 24 | 2999.9757
2026 | 2008 | 8 | 25 | 1 | 2839.7936
2026 | 2008 | 8 | 25 | 2 | 2723.0398
2026 | 2008 | 8 | 25 | 3 | 2859.0822
2026 | 2008 | 8 | 25 | 4 | 2905.6143
2026 | 2008 | 8 | 25 | 5 | 2842.1736
2026 | 2008 | 8 | 25 | 6 | 2709.9754
2026 | 2008 | 8 | 25 | 7 | 2357.8514
2026 | 2008 | 8 | 25 | 8 | 1683.8606
2026 | 2008 | 8 | 25 | 9 | 1626.7826
2026 | 2008 | 8 | 25 | 10 | 1311.5047
2026 | 2008 | 8 | 25 | 11 | 925.8061
2026 | 2008 | 8 | 25 | 12 | 819.9384
2026 | 2008 | 8 | 25 | 13 | 1085.0447
2026 | 2008 | 8 | 25 | 14 | 1594.9975
2026 | 2008 | 8 | 25 | 15 | 2137.7764
2026 | 2008 | 8 | 25 | 16 | 2422.2565
2026 | 2008 | 8 | 25 | 17 | 2834.6164
2026 | 2008 | 8 | 25 | 18 | 3230.5023
2026 | 2008 | 8 | 25 | 19 | 3775.1822
2026 | 2008 | 8 | 25 | 20 | 3635.6711
2026 | 2008 | 8 | 25 | 21 | 4375.1695
2026 | 2008 | 8 | 25 | 22 | 4765.4044
2026 | 2008 | 8 | 25 | 23 | 4889.8972
2026 | 2008 | 8 | 25 | 24 | 4774.8075
2026 | 2008 | 8 | 26 | 1 | 4492.9555
2026 | 2008 | 8 | 26 | 2 | 4509.8446
2026 | 2008 | 8 | 26 | 3 | 4419.425
2026 | 2008 | 8 | 26 | 4 | 4244.3221
2026 | 2008 | 8 | 26 | 5 | 4153.4496
2026 | 2008 | 8 | 26 | 6 | 3982.217
2026 | 2008 | 8 | 26 | 7 | 3357.5459
2026 | 2008 | 8 | 26 | 8 | 2215.6246
2026 | 2008 | 8 | 26 | 9 | 1812.1125
2026 | 2008 | 8 | 26 | 10 | 2433.2665
2026 | 2008 | 8 | 26 | 11 | 2794.7966
2026 | 2008 | 8 | 26 | 12 | 3069.362
2026 | 2008 | 8 | 26 | 13 | 3436.9168
2026 | 2008 | 8 | 26 | 14 | 3747.3672
2026 | 2008 | 8 | 26 | 15 | 4545.2135
2026 | 2008 | 8 | 26 | 16 | 5082.9247
2026 | 2008 | 8 | 26 | 17 | 6545.054
2026 | 2008 | 8 | 26 | 18 | 8321.509
2026 | 2008 | 8 | 26 | 19 | 9539.8641
2026 | 2008 | 8 | 26 | 20 | 11018.6702
2026 | 2008 | 8 | 26 | 21 | 13198.2881
2026 | 2008 | 8 | 26 | 22 | 14740.3255
2026 | 2008 | 8 | 26 | 23 | 15045.4949
2026 | 2008 | 8 | 26 | 24 | 14845.8949
2026 | 2008 | 8 | 27 | 1 | 13763.7935
2026 | 2008 | 8 | 27 | 2 | 12956.4075
2026 | 2008 | 8 | 27 | 3 | 12069.6025
2026 | 2008 | 8 | 27 | 4 | 10966.3752
2026 | 2008 | 8 | 27 | 5 | 10423.5994
2026 | 2008 | 8 | 27 | 6 | 10234.5138
2026 | 2008 | 8 | 27 | 7 | 9866.4042
2026 | 2008 | 8 | 27 | 8 | 7412.2021
2026 | 2008 | 8 | 27 | 9 | 6918.8983
2026 | 2008 | 8 | 27 | 10 | 6679.568
2026 | 2008 | 8 | 27 | 11 | 8129.3774
2026 | 2008 | 8 | 27 | 12 | 9640.2237
2026 | 2008 | 8 | 27 | 13 | 10702.2787
2026 | 2008 | 8 | 27 | 14 | 11647.0855
2026 | 2008 | 8 | 27 | 15 | 11846.3228
2026 | 2008 | 8 | 27 | 16 | 11285.7781
2026 | 2008 | 8 | 27 | 17 | 11901.8148
2026 | 2008 | 8 | 27 | 18 | 12797.2916
2026 | 2008 | 8 | 27 | 19 | 12934.2041
2026 | 2008 | 8 | 27 | 20 | 13569.4496
2026 | 2008 | 8 | 27 | 21 | 15042.0701
2026 | 2008 | 8 | 27 | 22 | 16148.3779
2026 | 2008 | 8 | 27 | 23 | 16045.3454
2026 | 2008 | 8 | 27 | 24 | 15587.2889
2026 | 2008 | 8 | 28 | 1 | 14827.4716
2026 | 2008 | 8 | 28 | 2 | 14224.1674
2026 | 2008 | 8 | 28 | 3 | 13625.7271
2026 | 2008 | 8 | 28 | 4 | 13242.6535
2026 | 2008 | 8 | 28 | 5 | 13027.2932
2026 | 2008 | 8 | 28 | 6 | 12643.2569
2026 | 2008 | 8 | 28 | 7 | 11992.1832
2026 | 2008 | 8 | 28 | 8 | 9538.7469
2026 | 2008 | 8 | 28 | 9 | 9425.2863
2026 | 2008 | 8 | 28 | 10 | 8055.2881
2026 | 2008 | 8 | 28 | 11 | 7567.7598
2026 | 2008 | 8 | 28 | 12 | 8048.7312
2026 | 2008 | 8 | 28 | 13 | 9202.1502
2026 | 2008 | 8 | 28 | 14 | 10713.4916
2026 | 2008 | 8 | 28 | 15 | 11507.4665
2026 | 2008 | 8 | 28 | 16 | 12029.1996
2026 | 2008 | 8 | 28 | 17 | 12779.265
2026 | 2008 | 8 | 28 | 18 | 13879.7586
2026 | 2008 | 8 | 28 | 19 | 13577.7515
2026 | 2008 | 8 | 28 | 20 | 12928.796
2026 | 2008 | 8 | 28 | 21 | 12809.2771
2026 | 2008 | 8 | 28 | 22 | 12754.89
2026 | 2008 | 8 | 28 | 23 | 12129.1878
2026 | 2008 | 8 | 28 | 24 | 10704.8529
2026 | 2008 | 8 | 29 | 1 | 9458.8648
2026 | 2008 | 8 | 29 | 2 | 8212.7757
2026 | 2008 | 8 | 29 | 3 | 6892.2514
2026 | 2008 | 8 | 29 | 4 | 5092.745
2026 | 2008 | 8 | 29 | 5 | 3507.8047
2026 | 2008 | 8 | 29 | 6 | 2796.9018
2026 | 2008 | 8 | 29 | 7 | 2568.4024
2026 | 2008 | 8 | 29 | 8 | 2577.4472
2026 | 2008 | 8 | 29 | 9 | 4034.2636
2026 | 2008 | 8 | 29 | 10 | 4661.0182
2026 | 2008 | 8 | 29 | 11 | 4689.531
2026 | 2008 | 8 | 29 | 12 | 5263.1819
2026 | 2008 | 8 | 29 | 13 | 7469.2416
2026 | 2008 | 8 | 29 | 14 | 9361.2738
2026 | 2008 | 8 | 29 | 15 | 11334.5814
2026 | 2008 | 8 | 29 | 16 | 11647.7724
2026 | 2008 | 8 | 29 | 17 | 11651.1209
2026 | 2008 | 8 | 29 | 18 | 11364.2883
2026 | 2008 | 8 | 29 | 19 | 10798.9395
2026 | 2008 | 8 | 29 | 20 | 9755.0295
2026 | 2008 | 8 | 29 | 21 | 9387.4848
2026 | 2008 | 8 | 29 | 22 | 8717.0717
2026 | 2008 | 8 | 29 | 23 | 7644.9823
2026 | 2008 | 8 | 29 | 24 | 6175.3832
2026 | 2008 | 8 | 30 | 1 | 4638.3558
2026 | 2008 | 8 | 30 | 2 | 3186.547
2026 | 2008 | 8 | 30 | 3 | 2637.1166
2026 | 2008 | 8 | 30 | 4 | 2179.6244
2026 | 2008 | 8 | 30 | 5 | 1890.6364
2026 | 2008 | 8 | 30 | 6 | 1609.4506
2026 | 2008 | 8 | 30 | 7 | 1856.8771
2026 | 2008 | 8 | 30 | 8 | 1906.0756
2026 | 2008 | 8 | 30 | 9 | 2911.8828
2026 | 2008 | 8 | 30 | 10 | 3954.3056
2026 | 2008 | 8 | 30 | 11 | 6339.4907
2026 | 2008 | 8 | 30 | 12 | 9109.4749
2026 | 2008 | 8 | 30 | 13 | 12567.0134
2026 | 2008 | 8 | 30 | 14 | 15364.5703
2026 | 2008 | 8 | 30 | 15 | 16867.6008
2026 | 2008 | 8 | 30 | 16 | 17046.3002
2026 | 2008 | 8 | 30 | 17 | 17196.5321
2026 | 2008 | 8 | 30 | 18 | 17153.1196
2026 | 2008 | 8 | 30 | 19 | 15314.7653
2026 | 2008 | 8 | 30 | 20 | 13006.574
2026 | 2008 | 8 | 30 | 21 | 11510.9433
2026 | 2008 | 8 | 30 | 22 | 10064.5464
2026 | 2008 | 8 | 30 | 23 | 9190.3572
2026 | 2008 | 8 | 30 | 24 | 8912.3035
2026 | 2008 | 8 | 31 | 1 | 8805.9483
2026 | 2008 | 8 | 31 | 2 | 8393.6366
2026 | 2008 | 8 | 31 | 3 | 8214.4514
2026 | 2008 | 8 | 31 | 4 | 7684.8865
2026 | 2008 | 8 | 31 | 5 | 7140.788
2026 | 2008 | 8 | 31 | 6 | 7218.829
2026 | 2008 | 8 | 31 | 7 | 7213.7678
2026 | 2008 | 8 | 31 | 8 | 5779.9654
2026 | 2008 | 8 | 31 | 9 | 5444.7676
2026 | 2008 | 8 | 31 | 10 | 7238.5956
2026 | 2008 | 8 | 31 | 11 | 9088.471
2026 | 2008 | 8 | 31 | 12 | 9430.1919
2026 | 2008 | 8 | 31 | 13 | 10169.5387
2026 | 2008 | 8 | 31 | 14 | 10767.0417
2026 | 2008 | 8 | 31 | 15 | 10840.426
2026 | 2008 | 8 | 31 | 16 | 11537.7675
2026 | 2008 | 8 | 31 | 17 | 12562.066
2026 | 2008 | 8 | 31 | 18 | 14119.8094
2026 | 2008 | 8 | 31 | 19 | 12314.5991
2026 | 2008 | 8 | 31 | 20 | 12384.2621
2026 | 2008 | 8 | 31 | 21 | 13197.7898
2026 | 2008 | 8 | 31 | 22 | 13921.1674
2026 | 2008 | 8 | 31 | 23 | 14318.646
2026 | 2008 | 8 | 31 | 24 | 14809.6636
2027 | 2008 | 8 | 1 | 1 | 12732.8344
2027 | 2008 | 8 | 1 | 2 | 11757.9342
2027 | 2008 | 8 | 1 | 3 | 10727.9733
2027 | 2008 | 8 | 1 | 4 | 9929.5838
2027 | 2008 | 8 | 1 | 5 | 9668.554
2027 | 2008 | 8 | 1 | 6 | 9086.0479
2027 | 2008 | 8 | 1 | 7 | 8389.6718
2027 | 2008 | 8 | 1 | 8 | 6625.4394
2027 | 2008 | 8 | 1 | 9 | 6763.9018
2027 | 2008 | 8 | 1 | 10 | 6039.7024
2027 | 2008 | 8 | 1 | 11 | 4069.0354
2027 | 2008 | 8 | 1 | 12 | 4374.3917
2027 | 2008 | 8 | 1 | 13 | 5060.9006
2027 | 2008 | 8 | 1 | 14 | 6390.1914
2027 | 2008 | 8 | 1 | 15 | 8032.9635
2027 | 2008 | 8 | 1 | 16 | 9793.3366
2027 | 2008 | 8 | 1 | 17 | 10626.8353
2027 | 2008 | 8 | 1 | 18 | 12073.7932
2027 | 2008 | 8 | 1 | 19 | 11912.7583
2027 | 2008 | 8 | 1 | 20 | 12085.0152
2027 | 2008 | 8 | 1 | 21 | 13280.6746
2027 | 2008 | 8 | 1 | 22 | 13600.7351
2027 | 2008 | 8 | 1 | 23 | 14381.7032
2027 | 2008 | 8 | 1 | 24 | 14513.5262
2027 | 2008 | 8 | 2 | 1 | 13934.4879
2027 | 2008 | 8 | 2 | 2 | 13226.0639
2027 | 2008 | 8 | 2 | 3 | 13134.3125
2027 | 2008 | 8 | 2 | 4 | 12058.7305
2027 | 2008 | 8 | 2 | 5 | 10854.6002
2027 | 2008 | 8 | 2 | 6 | 10484.3105
2027 | 2008 | 8 | 2 | 7 | 10064.1363
2027 | 2008 | 8 | 2 | 8 | 7514.4573
2027 | 2008 | 8 | 2 | 9 | 7279.0437
2027 | 2008 | 8 | 2 | 10 | 8993.1193
2027 | 2008 | 8 | 2 | 11 | 7305.1522
2027 | 2008 | 8 | 2 | 12 | 6372.7653
2027 | 2008 | 8 | 2 | 13 | 7156.3984
2027 | 2008 | 8 | 2 | 14 | 8592.1156
2027 | 2008 | 8 | 2 | 15 | 10325.7305
2027 | 2008 | 8 | 2 | 16 | 11639.5797
2027 | 2008 | 8 | 2 | 17 | 13627.8428
2027 | 2008 | 8 | 2 | 18 | 15921.078
2027 | 2008 | 8 | 2 | 19 | 17087.4612
2027 | 2008 | 8 | 2 | 20 | 18329.1976
2027 | 2008 | 8 | 2 | 21 | 20608.5069
2027 | 2008 | 8 | 2 | 22 | 22341.7493
2027 | 2008 | 8 | 2 | 23 | 22776.1867
2027 | 2008 | 8 | 2 | 24 | 22038.8678
2027 | 2008 | 8 | 3 | 1 | 20823.0245
2027 | 2008 | 8 | 3 | 2 | 20430.8027
2027 | 2008 | 8 | 3 | 3 | 20696.6714
2027 | 2008 | 8 | 3 | 4 | 20365.1004
2027 | 2008 | 8 | 3 | 5 | 19725.009
2027 | 2008 | 8 | 3 | 6 | 18296.9859
2027 | 2008 | 8 | 3 | 7 | 17276.8869
2027 | 2008 | 8 | 3 | 8 | 12742.7861
2027 | 2008 | 8 | 3 | 9 | 10890.9152
2027 | 2008 | 8 | 3 | 10 | 12576.4021
2027 | 2008 | 8 | 3 | 11 | 11286.7901
2027 | 2008 | 8 | 3 | 12 | 10948.4375
2027 | 2008 | 8 | 3 | 13 | 12175.7277
2027 | 2008 | 8 | 3 | 14 | 12719.5392
2027 | 2008 | 8 | 3 | 15 | 12871.7594
2027 | 2008 | 8 | 3 | 16 | 12789.6465
2027 | 2008 | 8 | 3 | 17 | 13456.7176
2027 | 2008 | 8 | 3 | 18 | 14503.0237
2027 | 2008 | 8 | 3 | 19 | 15414.1092
2027 | 2008 | 8 | 3 | 20 | 17796.8663
2027 | 2008 | 8 | 3 | 21 | 20832.1755
2027 | 2008 | 8 | 3 | 22 | 22952.3507
2027 | 2008 | 8 | 3 | 23 | 23559.8335
2027 | 2008 | 8 | 3 | 24 | 23309.6428
2027 | 2008 | 8 | 4 | 1 | 21912.9897
2027 | 2008 | 8 | 4 | 2 | 20865.6431
2027 | 2008 | 8 | 4 | 3 | 20035.5148
2027 | 2008 | 8 | 4 | 4 | 18283.5483
2027 | 2008 | 8 | 4 | 5 | 16255.7133
2027 | 2008 | 8 | 4 | 6 | 13339.9131
2027 | 2008 | 8 | 4 | 7 | 10273.7128
2027 | 2008 | 8 | 4 | 8 | 6571.2706
2027 | 2008 | 8 | 4 | 9 | 4202.7404
2027 | 2008 | 8 | 4 | 10 | 5005.9894
2027 | 2008 | 8 | 4 | 11 | 4266.6344
2027 | 2008 | 8 | 4 | 12 | 3419.6366
2027 | 2008 | 8 | 4 | 13 | 3827.1977
2027 | 2008 | 8 | 4 | 14 | 5025.259
2027 | 2008 | 8 | 4 | 15 | 5647.1337
2027 | 2008 | 8 | 4 | 16 | 5808.8897
2027 | 2008 | 8 | 4 | 17 | 6895.9229
2027 | 2008 | 8 | 4 | 18 | 7893.8986
2027 | 2008 | 8 | 4 | 19 | 8932.0234
2027 | 2008 | 8 | 4 | 20 | 10937.2922
2027 | 2008 | 8 | 4 | 21 | 14155.8132
2027 | 2008 | 8 | 4 | 22 | 16836.4267
2027 | 2008 | 8 | 4 | 23 | 17019.7248
2027 | 2008 | 8 | 4 | 24 | 15126.1395
2027 | 2008 | 8 | 5 | 1 | 13628.5296
2027 | 2008 | 8 | 5 | 2 | 12355.905
2027 | 2008 | 8 | 5 | 3 | 11106.0872
2027 | 2008 | 8 | 5 | 4 | 9393.0998
2027 | 2008 | 8 | 5 | 5 | 7870.6901
2027 | 2008 | 8 | 5 | 6 | 6654.6725
2027 | 2008 | 8 | 5 | 7 | 5592.6005
2027 | 2008 | 8 | 5 | 8 | 3007.1269
2027 | 2008 | 8 | 5 | 9 | 2064.5121
2027 | 2008 | 8 | 5 | 10 | 1702.119
2027 | 2008 | 8 | 5 | 11 | 1759.7242
2027 | 2008 | 8 | 5 | 12 | 1602.2944
2027 | 2008 | 8 | 5 | 13 | 2455.5387
2027 | 2008 | 8 | 5 | 14 | 3490.4252
2027 | 2008 | 8 | 5 | 15 | 5862.1656
2027 | 2008 | 8 | 5 | 16 | 7567.1346
2027 | 2008 | 8 | 5 | 17 | 10070.7737
2027 | 2008 | 8 | 5 | 18 | 12670.0439
2027 | 2008 | 8 | 5 | 19 | 14973.8798
2027 | 2008 | 8 | 5 | 20 | 17287.2284
2027 | 2008 | 8 | 5 | 21 | 20436.8997
2027 | 2008 | 8 | 5 | 22 | 21003.7102
2027 | 2008 | 8 | 5 | 23 | 19666.4181
2027 | 2008 | 8 | 5 | 24 | 18182.4632
2027 | 2008 | 8 | 6 | 1 | 16329.1232
2027 | 2008 | 8 | 6 | 2 | 13674.7714
2027 | 2008 | 8 | 6 | 3 | 10877.9871
2027 | 2008 | 8 | 6 | 4 | 9031.5644
2027 | 2008 | 8 | 6 | 5 | 7631.8334
2027 | 2008 | 8 | 6 | 6 | 6512.814
2027 | 2008 | 8 | 6 | 7 | 5586.1424
2027 | 2008 | 8 | 6 | 8 | 4990.5337
2027 | 2008 | 8 | 6 | 9 | 6312.1584
2027 | 2008 | 8 | 6 | 10 | 8086.3659
2027 | 2008 | 8 | 6 | 11 | 8883.2352
2027 | 2008 | 8 | 6 | 12 | 9912.6629
2027 | 2008 | 8 | 6 | 13 | 11496.5164
2027 | 2008 | 8 | 6 | 14 | 12309.2037
2027 | 2008 | 8 | 6 | 15 | 13128.935
2027 | 2008 | 8 | 6 | 16 | 12890.1707
2027 | 2008 | 8 | 6 | 17 | 13957.1584
2027 | 2008 | 8 | 6 | 18 | 14520.2012
2027 | 2008 | 8 | 6 | 19 | 14786.4423
2027 | 2008 | 8 | 6 | 20 | 14773.4752
2027 | 2008 | 8 | 6 | 21 | 15648.6089
2027 | 2008 | 8 | 6 | 22 | 15911.7687
2027 | 2008 | 8 | 6 | 23 | 15203.8788
2027 | 2008 | 8 | 6 | 24 | 14301.2911
2027 | 2008 | 8 | 7 | 1 | 12990.3114
2027 | 2008 | 8 | 7 | 2 | 11712.8042
2027 | 2008 | 8 | 7 | 3 | 11276.8128
2027 | 2008 | 8 | 7 | 4 | 10556.5836
2027 | 2008 | 8 | 7 | 5 | 9428.764
2027 | 2008 | 8 | 7 | 6 | 8389.7636
2027 | 2008 | 8 | 7 | 7 | 7849.1521
2027 | 2008 | 8 | 7 | 8 | 6643.1136
2027 | 2008 | 8 | 7 | 9 | 7268.3582
2027 | 2008 | 8 | 7 | 10 | 7230.1068
2027 | 2008 | 8 | 7 | 11 | 6973.5894
2027 | 2008 | 8 | 7 | 12 | 6935.1024
2027 | 2008 | 8 | 7 | 13 | 7313.8213
2027 | 2008 | 8 | 7 | 14 | 8041.1992
2027 | 2008 | 8 | 7 | 15 | 8947.4896
2027 | 2008 | 8 | 7 | 16 | 9068.9186
2027 | 2008 | 8 | 7 | 17 | 9967.2409
2027 | 2008 | 8 | 7 | 18 | 10781.0946
2027 | 2008 | 8 | 7 | 19 | 11386.9013
2027 | 2008 | 8 | 7 | 20 | 11414.1821
2027 | 2008 | 8 | 7 | 21 | 12021.9759
2027 | 2008 | 8 | 7 | 22 | 12978.3461
2027 | 2008 | 8 | 7 | 23 | 13149.9002
2027 | 2008 | 8 | 7 | 24 | 13948.2393
2027 | 2008 | 8 | 8 | 1 | 14027.9222
2027 | 2008 | 8 | 8 | 2 | 13864.4965
2027 | 2008 | 8 | 8 | 3 | 13434.8261
2027 | 2008 | 8 | 8 | 4 | 12165.3196
2027 | 2008 | 8 | 8 | 5 | 11057.3872
2027 | 2008 | 8 | 8 | 6 | 10485.9389
2027 | 2008 | 8 | 8 | 7 | 9663.2411
2027 | 2008 | 8 | 8 | 8 | 6394.2844
2027 | 2008 | 8 | 8 | 9 | 5329.0556
2027 | 2008 | 8 | 8 | 10 | 6059.2799
2027 | 2008 | 8 | 8 | 11 | 5148.8463
2027 | 2008 | 8 | 8 | 12 | 4288.4104
2027 | 2008 | 8 | 8 | 13 | 4740.4067
2027 | 2008 | 8 | 8 | 14 | 6254.3586
2027 | 2008 | 8 | 8 | 15 | 8205.7758
2027 | 2008 | 8 | 8 | 16 | 9960.214
2027 | 2008 | 8 | 8 | 17 | 11199.0347
2027 | 2008 | 8 | 8 | 18 | 12047.7327
2027 | 2008 | 8 | 8 | 19 | 13394.112
2027 | 2008 | 8 | 8 | 20 | 14723.1276
2027 | 2008 | 8 | 8 | 21 | 17331.8
2027 | 2008 | 8 | 8 | 22 | 19377.7237
2027 | 2008 | 8 | 8 | 23 | 21049.2022
2027 | 2008 | 8 | 8 | 24 | 21055.4767
2027 | 2008 | 8 | 9 | 1 | 19931.6342
2027 | 2008 | 8 | 9 | 2 | 19143.3033
2027 | 2008 | 8 | 9 | 3 | 18407.4937
2027 | 2008 | 8 | 9 | 4 | 17968.4309
2027 | 2008 | 8 | 9 | 5 | 17647.4135
2027 | 2008 | 8 | 9 | 6 | 17873.9256
2027 | 2008 | 8 | 9 | 7 | 17810.2597
2027 | 2008 | 8 | 9 | 8 | 14010.2205
2027 | 2008 | 8 | 9 | 9 | 12617.6612
2027 | 2008 | 8 | 9 | 10 | 14044.0206
2027 | 2008 | 8 | 9 | 11 | 13324.5869
2027 | 2008 | 8 | 9 | 12 | 13373.6735
2027 | 2008 | 8 | 9 | 13 | 15499.446
2027 | 2008 | 8 | 9 | 14 | 16886.2674
2027 | 2008 | 8 | 9 | 15 | 18362.0352
2027 | 2008 | 8 | 9 | 16 | 18617.5551
2027 | 2008 | 8 | 9 | 17 | 20066.4535
2027 | 2008 | 8 | 9 | 18 | 22015.5278
2027 | 2008 | 8 | 9 | 19 | 22695.9382
2027 | 2008 | 8 | 9 | 20 | 23845.7094
2027 | 2008 | 8 | 9 | 21 | 25498.6853
2027 | 2008 | 8 | 9 | 22 | 27316.1779
2027 | 2008 | 8 | 9 | 23 | 28086.8381
2027 | 2008 | 8 | 9 | 24 | 28567.2438
2027 | 2008 | 8 | 10 | 1 | 27822.0641
2027 | 2008 | 8 | 10 | 2 | 27860.554
2027 | 2008 | 8 | 10 | 3 | 28453.1224
2027 | 2008 | 8 | 10 | 4 | 28460.2599
2027 | 2008 | 8 | 10 | 5 | 28265.3503
2027 | 2008 | 8 | 10 | 6 | 28107.8124
2027 | 2008 | 8 | 10 | 7 | 26136.0646
2027 | 2008 | 8 | 10 | 8 | 23499.6592
2027 | 2008 | 8 | 10 | 9 | 24879.811
2027 | 2008 | 8 | 10 | 10 | 24241.5397
2027 | 2008 | 8 | 10 | 11 | 19961.3042
2027 | 2008 | 8 | 10 | 12 | 17017.0807
2027 | 2008 | 8 | 10 | 13 | 15265.251
2027 | 2008 | 8 | 10 | 14 | 14502.3915
2027 | 2008 | 8 | 10 | 15 | 13475.7888
2027 | 2008 | 8 | 10 | 16 | 13630.448
2027 | 2008 | 8 | 10 | 17 | 15671.6396
2027 | 2008 | 8 | 10 | 18 | 19235.7663
2027 | 2008 | 8 | 10 | 19 | 21461.2948
2027 | 2008 | 8 | 10 | 20 | 20666.2286
2027 | 2008 | 8 | 10 | 21 | 20431.0657
2027 | 2008 | 8 | 10 | 22 | 19602.1364
2027 | 2008 | 8 | 10 | 23 | 19512.5534
2027 | 2008 | 8 | 10 | 24 | 17408.2162
2027 | 2008 | 8 | 11 | 1 | 15954.3933
2027 | 2008 | 8 | 11 | 2 | 15860.5311
2027 | 2008 | 8 | 11 | 3 | 15542.3339
2027 | 2008 | 8 | 11 | 4 | 14763.1619
2027 | 2008 | 8 | 11 | 5 | 13839.2129
2027 | 2008 | 8 | 11 | 6 | 13228.0442
2027 | 2008 | 8 | 11 | 7 | 12365.6264
2027 | 2008 | 8 | 11 | 8 | 11495.52
2027 | 2008 | 8 | 11 | 9 | 14227.1016
2027 | 2008 | 8 | 11 | 10 | 14297.6358
2027 | 2008 | 8 | 11 | 11 | 13536.702
2027 | 2008 | 8 | 11 | 12 | 13171.5395
2027 | 2008 | 8 | 11 | 13 | 12983.8906
2027 | 2008 | 8 | 11 | 14 | 13175.9748
2027 | 2008 | 8 | 11 | 15 | 12662.0647
2027 | 2008 | 8 | 11 | 16 | 12111.8288
2027 | 2008 | 8 | 11 | 17 | 12852.6687
2027 | 2008 | 8 | 11 | 18 | 12829.2325
2027 | 2008 | 8 | 11 | 19 | 13350.8869
2027 | 2008 | 8 | 11 | 20 | 12699.8513
2027 | 2008 | 8 | 11 | 21 | 12661.1819
2027 | 2008 | 8 | 11 | 22 | 11041.0874
2027 | 2008 | 8 | 11 | 23 | 10277.7312
2027 | 2008 | 8 | 11 | 24 | 9565.3576
2027 | 2008 | 8 | 12 | 1 | 9478.312
2027 | 2008 | 8 | 12 | 2 | 9636.9966
2027 | 2008 | 8 | 12 | 3 | 9443.4991
2027 | 2008 | 8 | 12 | 4 | 9188.8428
2027 | 2008 | 8 | 12 | 5 | 8287.8467
2027 | 2008 | 8 | 12 | 6 | 7932.5899
2027 | 2008 | 8 | 12 | 7 | 7328.1227
2027 | 2008 | 8 | 12 | 8 | 5986.6891
2027 | 2008 | 8 | 12 | 9 | 7116.739
2027 | 2008 | 8 | 12 | 10 | 7448.9613
2027 | 2008 | 8 | 12 | 11 | 6938.9339
2027 | 2008 | 8 | 12 | 12 | 6273.3333
2027 | 2008 | 8 | 12 | 13 | 7226.0257
2027 | 2008 | 8 | 12 | 14 | 8187.8425
2027 | 2008 | 8 | 12 | 15 | 8949.8211
2027 | 2008 | 8 | 12 | 16 | 9495.9266
2027 | 2008 | 8 | 12 | 17 | 9933.0745
2027 | 2008 | 8 | 12 | 18 | 10666.3858
2027 | 2008 | 8 | 12 | 19 | 11280.9623
2027 | 2008 | 8 | 12 | 20 | 10483.5921
2027 | 2008 | 8 | 12 | 21 | 10402.8777
2027 | 2008 | 8 | 12 | 22 | 10302.4459
2027 | 2008 | 8 | 12 | 23 | 9824.6299
2027 | 2008 | 8 | 12 | 24 | 8872.3853
2027 | 2008 | 8 | 13 | 1 | 7613.4513
2027 | 2008 | 8 | 13 | 2 | 7005.4213
2027 | 2008 | 8 | 13 | 3 | 6767.9657
2027 | 2008 | 8 | 13 | 4 | 6563.3036
2027 | 2008 | 8 | 13 | 5 | 5689.7373
2027 | 2008 | 8 | 13 | 6 | 4701.3623
2027 | 2008 | 8 | 13 | 7 | 3597.6354
2027 | 2008 | 8 | 13 | 8 | 2306.3459
2027 | 2008 | 8 | 13 | 9 | 2668.033
2027 | 2008 | 8 | 13 | 10 | 2780.6166
2027 | 2008 | 8 | 13 | 11 | 2353.6731
2027 | 2008 | 8 | 13 | 12 | 2388.6082
2027 | 2008 | 8 | 13 | 13 | 2391.9347
2027 | 2008 | 8 | 13 | 14 | 2874.7937
2027 | 2008 | 8 | 13 | 15 | 3881.1691
2027 | 2008 | 8 | 13 | 16 | 4650.4295
2027 | 2008 | 8 | 13 | 17 | 5996.0653
2027 | 2008 | 8 | 13 | 18 | 7990.8645
2027 | 2008 | 8 | 13 | 19 | 9097.8331
2027 | 2008 | 8 | 13 | 20 | 9983.2335
2027 | 2008 | 8 | 13 | 21 | 11541.6033
2027 | 2008 | 8 | 13 | 22 | 12047.2468
2027 | 2008 | 8 | 13 | 23 | 11258.085
2027 | 2008 | 8 | 13 | 24 | 10112.3045
2027 | 2008 | 8 | 14 | 1 | 9270.022
2027 | 2008 | 8 | 14 | 2 | 8913.0801
2027 | 2008 | 8 | 14 | 3 | 8691.5032
2027 | 2008 | 8 | 14 | 4 | 8566.4792
2027 | 2008 | 8 | 14 | 5 | 7683.0444
2027 | 2008 | 8 | 14 | 6 | 6926.0849
2027 | 2008 | 8 | 14 | 7 | 5980.2397
2027 | 2008 | 8 | 14 | 8 | 4099.152
2027 | 2008 | 8 | 14 | 9 | 3612.0862
2027 | 2008 | 8 | 14 | 10 | 3763.5293
2027 | 2008 | 8 | 14 | 11 | 4678.6476
2027 | 2008 | 8 | 14 | 12 | 4878.9171
2027 | 2008 | 8 | 14 | 13 | 6531.6879
2027 | 2008 | 8 | 14 | 14 | 7795.8431
2027 | 2008 | 8 | 14 | 15 | 8800.5162
2027 | 2008 | 8 | 14 | 16 | 9529.14
2027 | 2008 | 8 | 14 | 17 | 10319.1393
2027 | 2008 | 8 | 14 | 18 | 11406.1079
2027 | 2008 | 8 | 14 | 19 | 12840.9232
2027 | 2008 | 8 | 14 | 20 | 13772.5076
2027 | 2008 | 8 | 14 | 21 | 15808.017
2027 | 2008 | 8 | 14 | 22 | 19184.2889
2027 | 2008 | 8 | 14 | 23 | 22743.2736
2027 | 2008 | 8 | 14 | 24 | 23606.8363
2027 | 2008 | 8 | 15 | 1 | 22534.0205
2027 | 2008 | 8 | 15 | 2 | 20918.9387
2027 | 2008 | 8 | 15 | 3 | 19240.9087
2027 | 2008 | 8 | 15 | 4 | 16901.4612
2027 | 2008 | 8 | 15 | 5 | 12769.4138
2027 | 2008 | 8 | 15 | 6 | 9959.076
2027 | 2008 | 8 | 15 | 7 | 7919.2648
2027 | 2008 | 8 | 15 | 8 | 5263.8779
2027 | 2008 | 8 | 15 | 9 | 4840.5561
2027 | 2008 | 8 | 15 | 10 | 5855.1783
2027 | 2008 | 8 | 15 | 11 | 6487.4144
2027 | 2008 | 8 | 15 | 12 | 6995.2276
2027 | 2008 | 8 | 15 | 13 | 8144.3283
2027 | 2008 | 8 | 15 | 14 | 8679.8221
2027 | 2008 | 8 | 15 | 15 | 8610.6636
2027 | 2008 | 8 | 15 | 16 | 8625.0089
2027 | 2008 | 8 | 15 | 17 | 9303.7045
2027 | 2008 | 8 | 15 | 18 | 10865.2948
2027 | 2008 | 8 | 15 | 19 | 11763.1276
2027 | 2008 | 8 | 15 | 20 | 13648.3657
2027 | 2008 | 8 | 15 | 21 | 16287.8959
2027 | 2008 | 8 | 15 | 22 | 18333.5505
2027 | 2008 | 8 | 15 | 23 | 18342.752
2027 | 2008 | 8 | 15 | 24 | 17909.669
2027 | 2008 | 8 | 16 | 1 | 16892.0072
2027 | 2008 | 8 | 16 | 2 | 15752.5752
2027 | 2008 | 8 | 16 | 3 | 13389.9474
2027 | 2008 | 8 | 16 | 4 | 11329.0146
2027 | 2008 | 8 | 16 | 5 | 9105.491
2027 | 2008 | 8 | 16 | 6 | 7379.0214
2027 | 2008 | 8 | 16 | 7 | 5884.6316
2027 | 2008 | 8 | 16 | 8 | 4827.159
2027 | 2008 | 8 | 16 | 9 | 5578.5056
2027 | 2008 | 8 | 16 | 10 | 7396.0362
2027 | 2008 | 8 | 16 | 11 | 7997.3078
2027 | 2008 | 8 | 16 | 12 | 8665.436
2027 | 2008 | 8 | 16 | 13 | 10347.7254
2027 | 2008 | 8 | 16 | 14 | 13107.8297
2027 | 2008 | 8 | 16 | 15 | 13929.9917
2027 | 2008 | 8 | 16 | 16 | 14975.1417
2027 | 2008 | 8 | 16 | 17 | 16287.2208
2027 | 2008 | 8 | 16 | 18 | 16862.0046
2027 | 2008 | 8 | 16 | 19 | 16764.3698
2027 | 2008 | 8 | 16 | 20 | 15210.7068
2027 | 2008 | 8 | 16 | 21 | 14197.9883
2027 | 2008 | 8 | 16 | 22 | 12186.9661
2027 | 2008 | 8 | 16 | 23 | 10114.7729
2027 | 2008 | 8 | 16 | 24 | 7881.2659
2027 | 2008 | 8 | 17 | 1 | 5909.8861
2027 | 2008 | 8 | 17 | 2 | 4778.4974
2027 | 2008 | 8 | 17 | 3 | 4354.3003
2027 | 2008 | 8 | 17 | 4 | 4325.5853
2027 | 2008 | 8 | 17 | 5 | 4418.2605
2027 | 2008 | 8 | 17 | 6 | 4995.8248
2027 | 2008 | 8 | 17 | 7 | 4866.9844
2027 | 2008 | 8 | 17 | 8 | 5073.2007
2027 | 2008 | 8 | 17 | 9 | 6577.5661
2027 | 2008 | 8 | 17 | 10 | 8243.6763
2027 | 2008 | 8 | 17 | 11 | 8406.2254
2027 | 2008 | 8 | 17 | 12 | 8565.6234
2027 | 2008 | 8 | 17 | 13 | 8345.1568
2027 | 2008 | 8 | 17 | 14 | 8050.1455
2027 | 2008 | 8 | 17 | 15 | 7038.9236
2027 | 2008 | 8 | 17 | 16 | 7114.9109
2027 | 2008 | 8 | 17 | 17 | 8541.1217
2027 | 2008 | 8 | 17 | 18 | 10229.5479
2027 | 2008 | 8 | 17 | 19 | 11496.6201
2027 | 2008 | 8 | 17 | 20 | 11155.748
2027 | 2008 | 8 | 17 | 21 | 11770.3213
2027 | 2008 | 8 | 17 | 22 | 12015.1036
2027 | 2008 | 8 | 17 | 23 | 12029.9154
2027 | 2008 | 8 | 17 | 24 | 11950.3209
2027 | 2008 | 8 | 18 | 1 | 11188.3581
2027 | 2008 | 8 | 18 | 2 | 10683.6673
2027 | 2008 | 8 | 18 | 3 | 10125.4984
2027 | 2008 | 8 | 18 | 4 | 10338.6211
2027 | 2008 | 8 | 18 | 5 | 10171.8277
2027 | 2008 | 8 | 18 | 6 | 10248.1805
2027 | 2008 | 8 | 18 | 7 | 9352.2315
2027 | 2008 | 8 | 18 | 8 | 8439.7614
2027 | 2008 | 8 | 18 | 9 | 10128.571
2027 | 2008 | 8 | 18 | 10 | 11129.6954
2027 | 2008 | 8 | 18 | 11 | 10863.7677
2027 | 2008 | 8 | 18 | 12 | 10822.0609
2027 | 2008 | 8 | 18 | 13 | 11370.4708
2027 | 2008 | 8 | 18 | 14 | 11807.4196
2027 | 2008 | 8 | 18 | 15 | 12520.7278
2027 | 2008 | 8 | 18 | 16 | 12720.3847
2027 | 2008 | 8 | 18 | 17 | 14311.8291
2027 | 2008 | 8 | 18 | 18 | 14803.604
2027 | 2008 | 8 | 18 | 19 | 14675.551
2027 | 2008 | 8 | 18 | 20 | 13893.0331
2027 | 2008 | 8 | 18 | 21 | 13841.6242
2027 | 2008 | 8 | 18 | 22 | 13573.3693
2027 | 2008 | 8 | 18 | 23 | 12495.3015
2027 | 2008 | 8 | 18 | 24 | 11446.3146
2027 | 2008 | 8 | 19 | 1 | 10835.6238
2027 | 2008 | 8 | 19 | 2 | 10566.3069
2027 | 2008 | 8 | 19 | 3 | 11295.4226
2027 | 2008 | 8 | 19 | 4 | 12218.9157
2027 | 2008 | 8 | 19 | 5 | 12937
2027 | 2008 | 8 | 19 | 6 | 13617.389
2027 | 2008 | 8 | 19 | 7 | 13829.1467
2027 | 2008 | 8 | 19 | 8 | 12648.3559
2027 | 2008 | 8 | 19 | 9 | 14936.2111
2027 | 2008 | 8 | 19 | 10 | 14094.1261
2027 | 2008 | 8 | 19 | 11 | 11505.0889
2027 | 2008 | 8 | 19 | 12 | 11054.3943
2027 | 2008 | 8 | 19 | 13 | 11714.832
2027 | 2008 | 8 | 19 | 14 | 12532.8985
2027 | 2008 | 8 | 19 | 15 | 14090.7726
2027 | 2008 | 8 | 19 | 16 | 14885.119
2027 | 2008 | 8 | 19 | 17 | 16094.1264
2027 | 2008 | 8 | 19 | 18 | 16045.7466
2027 | 2008 | 8 | 19 | 19 | 16096.1526
2027 | 2008 | 8 | 19 | 20 | 14877.5081
2027 | 2008 | 8 | 19 | 21 | 14261.2898
2027 | 2008 | 8 | 19 | 22 | 12725.1063
2027 | 2008 | 8 | 19 | 23 | 10247.107
2027 | 2008 | 8 | 19 | 24 | 8446.4135
2027 | 2008 | 8 | 20 | 1 | 6744.4011
2027 | 2008 | 8 | 20 | 2 | 5799.5343
2027 | 2008 | 8 | 20 | 3 | 5754.6221
2027 | 2008 | 8 | 20 | 4 | 5625.3243
2027 | 2008 | 8 | 20 | 5 | 5357.4296
2027 | 2008 | 8 | 20 | 6 | 5097.5079
2027 | 2008 | 8 | 20 | 7 | 4910.7285
2027 | 2008 | 8 | 20 | 8 | 4253.1733
2027 | 2008 | 8 | 20 | 9 | 5109.7249
2027 | 2008 | 8 | 20 | 10 | 5115.2329
2027 | 2008 | 8 | 20 | 11 | 4677.381
2027 | 2008 | 8 | 20 | 12 | 4599.6695
2027 | 2008 | 8 | 20 | 13 | 5227.2012
2027 | 2008 | 8 | 20 | 14 | 5974.1484
2027 | 2008 | 8 | 20 | 15 | 6539.6362
2027 | 2008 | 8 | 20 | 16 | 6856.8881
2027 | 2008 | 8 | 20 | 17 | 6459.346
2027 | 2008 | 8 | 20 | 18 | 5728.0337
2027 | 2008 | 8 | 20 | 19 | 4965.0634
2027 | 2008 | 8 | 20 | 20 | 4932.6381
2027 | 2008 | 8 | 20 | 21 | 5851.5556
2027 | 2008 | 8 | 20 | 22 | 7160.7413
2027 | 2008 | 8 | 20 | 23 | 7960.5886
2027 | 2008 | 8 | 20 | 24 | 8277.5336
2027 | 2008 | 8 | 21 | 1 | 8763.8997
2027 | 2008 | 8 | 21 | 2 | 8756.4432
2027 | 2008 | 8 | 21 | 3 | 8141.6957
2027 | 2008 | 8 | 21 | 4 | 7742.716
2027 | 2008 | 8 | 21 | 5 | 7170.6069
2027 | 2008 | 8 | 21 | 6 | 6846.5133
2027 | 2008 | 8 | 21 | 7 | 6345.9102
2027 | 2008 | 8 | 21 | 8 | 4688.0712
2027 | 2008 | 8 | 21 | 9 | 4788.0493
2027 | 2008 | 8 | 21 | 10 | 5855.9892
2027 | 2008 | 8 | 21 | 11 | 6840.042
2027 | 2008 | 8 | 21 | 12 | 7716.4386
2027 | 2008 | 8 | 21 | 13 | 8675.6221
2027 | 2008 | 8 | 21 | 14 | 9880.4017
2027 | 2008 | 8 | 21 | 15 | 10374.1208
2027 | 2008 | 8 | 21 | 16 | 9960.4242
2027 | 2008 | 8 | 21 | 17 | 10672.4081
2027 | 2008 | 8 | 21 | 18 | 11903.0607
2027 | 2008 | 8 | 21 | 19 | 13297.0159
2027 | 2008 | 8 | 21 | 20 | 15413.8986
2027 | 2008 | 8 | 21 | 21 | 19224.2523
2027 | 2008 | 8 | 21 | 22 | 21819.0663
2027 | 2008 | 8 | 21 | 23 | 22880.9152
2027 | 2008 | 8 | 21 | 24 | 23098.6256
2027 | 2008 | 8 | 22 | 1 | 22390.4632
2027 | 2008 | 8 | 22 | 2 | 21785.8855
2027 | 2008 | 8 | 22 | 3 | 21813.4183
2027 | 2008 | 8 | 22 | 4 | 21992.1995
2027 | 2008 | 8 | 22 | 5 | 22056.6117
2027 | 2008 | 8 | 22 | 6 | 22834.733
2027 | 2008 | 8 | 22 | 7 | 22955.4069
2027 | 2008 | 8 | 22 | 8 | 20650.6366
2027 | 2008 | 8 | 22 | 9 | 21839.5263
2027 | 2008 | 8 | 22 | 10 | 22871.0966
2027 | 2008 | 8 | 22 | 11 | 20767.2443
2027 | 2008 | 8 | 22 | 12 | 19752.3361
2027 | 2008 | 8 | 22 | 13 | 21024.6941
2027 | 2008 | 8 | 22 | 14 | 21340.8754
2027 | 2008 | 8 | 22 | 15 | 20728.9611
2027 | 2008 | 8 | 22 | 16 | 19189.4288
2027 | 2008 | 8 | 22 | 17 | 18247.9277
2027 | 2008 | 8 | 22 | 18 | 18352.3383
2027 | 2008 | 8 | 22 | 19 | 18107.6183
2027 | 2008 | 8 | 22 | 20 | 19461.5906
2027 | 2008 | 8 | 22 | 21 | 20925.8388
2027 | 2008 | 8 | 22 | 22 | 22016.4655
2027 | 2008 | 8 | 22 | 23 | 21525.8451
2027 | 2008 | 8 | 22 | 24 | 20027.7874
2027 | 2008 | 8 | 23 | 1 | 16942.1111
2027 | 2008 | 8 | 23 | 2 | 14683.3385
2027 | 2008 | 8 | 23 | 3 | 12579.4388
2027 | 2008 | 8 | 23 | 4 | 10325.1894
2027 | 2008 | 8 | 23 | 5 | 8352.3227
2027 | 2008 | 8 | 23 | 6 | 6387.8562
2027 | 2008 | 8 | 23 | 7 | 5010.9546
2027 | 2008 | 8 | 23 | 8 | 3605.9177
2027 | 2008 | 8 | 23 | 9 | 4406.3069
2027 | 2008 | 8 | 23 | 10 | 4998.276
2027 | 2008 | 8 | 23 | 11 | 4608.1215
2027 | 2008 | 8 | 23 | 12 | 4374.5428
2027 | 2008 | 8 | 23 | 13 | 5269.3473
2027 | 2008 | 8 | 23 | 14 | 6220.1799
2027 | 2008 | 8 | 23 | 15 | 7123.2093
2027 | 2008 | 8 | 23 | 16 | 7604.7162
2027 | 2008 | 8 | 23 | 17 | 8217.1677
2027 | 2008 | 8 | 23 | 18 | 8331.7083
2027 | 2008 | 8 | 23 | 19 | 7581.9554
2027 | 2008 | 8 | 23 | 20 | 6385.3799
2027 | 2008 | 8 | 23 | 21 | 5936.4437
2027 | 2008 | 8 | 23 | 22 | 4837.8757
2027 | 2008 | 8 | 23 | 23 | 3625.6458
2027 | 2008 | 8 | 23 | 24 | 2794.8654
2027 | 2008 | 8 | 24 | 1 | 2130.9762
2027 | 2008 | 8 | 24 | 2 | 1372.8689
2027 | 2008 | 8 | 24 | 3 | 994.4368
2027 | 2008 | 8 | 24 | 4 | 797.0001
2027 | 2008 | 8 | 24 | 5 | 732.0977
2027 | 2008 | 8 | 24 | 6 | 718.0919
2027 | 2008 | 8 | 24 | 7 | 804.9423
2027 | 2008 | 8 | 24 | 8 | 580.033
2027 | 2008 | 8 | 24 | 9 | 902.439
2027 | 2008 | 8 | 24 | 10 | 1040.8085
2027 | 2008 | 8 | 24 | 11 | 1563.2405
2027 | 2008 | 8 | 24 | 12 | 2161.3874
2027 | 2008 | 8 | 24 | 13 | 3062.9702
2027 | 2008 | 8 | 24 | 14 | 3142.7413
2027 | 2008 | 8 | 24 | 15 | 3867.8967
2027 | 2008 | 8 | 24 | 16 | 4249.1273
2027 | 2008 | 8 | 24 | 17 | 4605.5961
2027 | 2008 | 8 | 24 | 18 | 5096.2085
2027 | 2008 | 8 | 24 | 19 | 4958.0894
2027 | 2008 | 8 | 24 | 20 | 4284.6864
2027 | 2008 | 8 | 24 | 21 | 4161.1117
2027 | 2008 | 8 | 24 | 22 | 4061.459
2027 | 2008 | 8 | 24 | 23 | 3631.7214
2027 | 2008 | 8 | 24 | 24 | 3272.8646
2027 | 2008 | 8 | 25 | 1 | 3119.9054
2027 | 2008 | 8 | 25 | 2 | 3069.6691
2027 | 2008 | 8 | 25 | 3 | 3187.3782
2027 | 2008 | 8 | 25 | 4 | 3262.7707
2027 | 2008 | 8 | 25 | 5 | 3287.957
2027 | 2008 | 8 | 25 | 6 | 3067.3383
2027 | 2008 | 8 | 25 | 7 | 2749.2386
2027 | 2008 | 8 | 25 | 8 | 1985.9452
2027 | 2008 | 8 | 25 | 9 | 1871.1258
2027 | 2008 | 8 | 25 | 10 | 1618.967
2027 | 2008 | 8 | 25 | 11 | 1163.4833
2027 | 2008 | 8 | 25 | 12 | 1018.2211
2027 | 2008 | 8 | 25 | 13 | 1381.8128
2027 | 2008 | 8 | 25 | 14 | 1949.1322
2027 | 2008 | 8 | 25 | 15 | 2517.5873
2027 | 2008 | 8 | 25 | 16 | 2727.4135
2027 | 2008 | 8 | 25 | 17 | 3094.172
2027 | 2008 | 8 | 25 | 18 | 3510.9559
2027 | 2008 | 8 | 25 | 19 | 3985.8281
2027 | 2008 | 8 | 25 | 20 | 3907.3627
2027 | 2008 | 8 | 25 | 21 | 4695.5208
2027 | 2008 | 8 | 25 | 22 | 5146.13
2027 | 2008 | 8 | 25 | 23 | 5333.4538
2027 | 2008 | 8 | 25 | 24 | 5197.3346
2027 | 2008 | 8 | 26 | 1 | 4867.7253
2027 | 2008 | 8 | 26 | 2 | 4793.6158
2027 | 2008 | 8 | 26 | 3 | 4678.3412
2027 | 2008 | 8 | 26 | 4 | 4473.4762
2027 | 2008 | 8 | 26 | 5 | 4403.4853
2027 | 2008 | 8 | 26 | 6 | 4252.3683
2027 | 2008 | 8 | 26 | 7 | 3550.0556
2027 | 2008 | 8 | 26 | 8 | 2323.3855
2027 | 2008 | 8 | 26 | 9 | 1926.3657
2027 | 2008 | 8 | 26 | 10 | 2580.5658
2027 | 2008 | 8 | 26 | 11 | 3026.5626
2027 | 2008 | 8 | 26 | 12 | 3339.2904
2027 | 2008 | 8 | 26 | 13 | 3719.452
2027 | 2008 | 8 | 26 | 14 | 3989.3775
2027 | 2008 | 8 | 26 | 15 | 4805.4512
2027 | 2008 | 8 | 26 | 16 | 5283.9699
2027 | 2008 | 8 | 26 | 17 | 6862.0759
2027 | 2008 | 8 | 26 | 18 | 8637.6067
2027 | 2008 | 8 | 26 | 19 | 9937.5964
2027 | 2008 | 8 | 26 | 20 | 11595.6385
2027 | 2008 | 8 | 26 | 21 | 14032.4589
2027 | 2008 | 8 | 26 | 22 | 15825.1681
2027 | 2008 | 8 | 26 | 23 | 16219.1714
2027 | 2008 | 8 | 26 | 24 | 15938.1874
2027 | 2008 | 8 | 27 | 1 | 14840.3028
2027 | 2008 | 8 | 27 | 2 | 14018.3279
2027 | 2008 | 8 | 27 | 3 | 13044.7966
2027 | 2008 | 8 | 27 | 4 | 11870.4782
2027 | 2008 | 8 | 27 | 5 | 11241.0644
2027 | 2008 | 8 | 27 | 6 | 11050.4974
2027 | 2008 | 8 | 27 | 7 | 10835.0889
2027 | 2008 | 8 | 27 | 8 | 8256.5181
2027 | 2008 | 8 | 27 | 9 | 7835.384
2027 | 2008 | 8 | 27 | 10 | 7491.2729
2027 | 2008 | 8 | 27 | 11 | 8986.7053
2027 | 2008 | 8 | 27 | 12 | 10454.9555
2027 | 2008 | 8 | 27 | 13 | 11530.7791
2027 | 2008 | 8 | 27 | 14 | 12523.1238
2027 | 2008 | 8 | 27 | 15 | 12688.7722
2027 | 2008 | 8 | 27 | 16 | 11957.5296
2027 | 2008 | 8 | 27 | 17 | 12658.0514
2027 | 2008 | 8 | 27 | 18 | 13550.3764
2027 | 2008 | 8 | 27 | 19 | 13819.324
2027 | 2008 | 8 | 27 | 20 | 14531.3801
2027 | 2008 | 8 | 27 | 21 | 16073.0612
2027 | 2008 | 8 | 27 | 22 | 17020.3565
2027 | 2008 | 8 | 27 | 23 | 16945.3791
2027 | 2008 | 8 | 27 | 24 | 16604.6653
2027 | 2008 | 8 | 28 | 1 | 15921.1688
2027 | 2008 | 8 | 28 | 2 | 15336.265
2027 | 2008 | 8 | 28 | 3 | 14761.6083
2027 | 2008 | 8 | 28 | 4 | 14444.9586
2027 | 2008 | 8 | 28 | 5 | 13997.6791
2027 | 2008 | 8 | 28 | 6 | 13513.887
2027 | 2008 | 8 | 28 | 7 | 12718.098
2027 | 2008 | 8 | 28 | 8 | 10090.5288
2027 | 2008 | 8 | 28 | 9 | 9991.1641
2027 | 2008 | 8 | 28 | 10 | 8705.3837
2027 | 2008 | 8 | 28 | 11 | 8082.207
2027 | 2008 | 8 | 28 | 12 | 8670.3398
2027 | 2008 | 8 | 28 | 13 | 9759.6616
2027 | 2008 | 8 | 28 | 14 | 11314.2633
2027 | 2008 | 8 | 28 | 15 | 12173.1648
2027 | 2008 | 8 | 28 | 16 | 12554.741
2027 | 2008 | 8 | 28 | 17 | 13466.6284
2027 | 2008 | 8 | 28 | 18 | 14588.4091
2027 | 2008 | 8 | 28 | 19 | 14404.8515
2027 | 2008 | 8 | 28 | 20 | 13811.5482
2027 | 2008 | 8 | 28 | 21 | 13777.6356
2027 | 2008 | 8 | 28 | 22 | 13823.2398
2027 | 2008 | 8 | 28 | 23 | 13234.7755
2027 | 2008 | 8 | 28 | 24 | 11591.7984
2027 | 2008 | 8 | 29 | 1 | 10151.0377
2027 | 2008 | 8 | 29 | 2 | 8851.1032
2027 | 2008 | 8 | 29 | 3 | 7463.2406
2027 | 2008 | 8 | 29 | 4 | 5598.1131
2027 | 2008 | 8 | 29 | 5 | 3858.3892
2027 | 2008 | 8 | 29 | 6 | 3125.9032
2027 | 2008 | 8 | 29 | 7 | 2870.5256
2027 | 2008 | 8 | 29 | 8 | 2898.0309
2027 | 2008 | 8 | 29 | 9 | 4413.6133
2027 | 2008 | 8 | 29 | 10 | 5123.7638
2027 | 2008 | 8 | 29 | 11 | 5166.54
2027 | 2008 | 8 | 29 | 12 | 5772.5564
2027 | 2008 | 8 | 29 | 13 | 8297.3625
2027 | 2008 | 8 | 29 | 14 | 10232.4953
2027 | 2008 | 8 | 29 | 15 | 12280.7179
2027 | 2008 | 8 | 29 | 16 | 12569.5497
2027 | 2008 | 8 | 29 | 17 | 12435.5572
2027 | 2008 | 8 | 29 | 18 | 12006.4633
2027 | 2008 | 8 | 29 | 19 | 11446.1942
2027 | 2008 | 8 | 29 | 20 | 10395.4622
2027 | 2008 | 8 | 29 | 21 | 10064.1753
2027 | 2008 | 8 | 29 | 22 | 9325.9886
2027 | 2008 | 8 | 29 | 23 | 8229.9786
2027 | 2008 | 8 | 29 | 24 | 6594.7913
2027 | 2008 | 8 | 30 | 1 | 4884.8935
2027 | 2008 | 8 | 30 | 2 | 3418.2284
2027 | 2008 | 8 | 30 | 3 | 2820.0363
2027 | 2008 | 8 | 30 | 4 | 2410.0331
2027 | 2008 | 8 | 30 | 5 | 2170.736
2027 | 2008 | 8 | 30 | 6 | 1891.5933
2027 | 2008 | 8 | 30 | 7 | 2297.3667
2027 | 2008 | 8 | 30 | 8 | 2331.6706
2027 | 2008 | 8 | 30 | 9 | 3404.5799
2027 | 2008 | 8 | 30 | 10 | 4570.868
2027 | 2008 | 8 | 30 | 11 | 7186.0807
2027 | 2008 | 8 | 30 | 12 | 10093.8974
2027 | 2008 | 8 | 30 | 13 | 13651.0704
2027 | 2008 | 8 | 30 | 14 | 16499.6545
2027 | 2008 | 8 | 30 | 15 | 18084.5887
2027 | 2008 | 8 | 30 | 16 | 18131.0223
2027 | 2008 | 8 | 30 | 17 | 18232.3407
2027 | 2008 | 8 | 30 | 18 | 18287.8619
2027 | 2008 | 8 | 30 | 19 | 16375.4915
2027 | 2008 | 8 | 30 | 20 | 14088.6115
2027 | 2008 | 8 | 30 | 21 | 12544.7017
2027 | 2008 | 8 | 30 | 22 | 10997.6883
2027 | 2008 | 8 | 30 | 23 | 10013.3003
2027 | 2008 | 8 | 30 | 24 | 9630.1031
2027 | 2008 | 8 | 31 | 1 | 9503.4901
2027 | 2008 | 8 | 31 | 2 | 9046.6579
2027 | 2008 | 8 | 31 | 3 | 8932.422
2027 | 2008 | 8 | 31 | 4 | 8382.3268
2027 | 2008 | 8 | 31 | 5 | 7812.2886
2027 | 2008 | 8 | 31 | 6 | 7761.7412
2027 | 2008 | 8 | 31 | 7 | 7791.2907
2027 | 2008 | 8 | 31 | 8 | 6345.6858
2027 | 2008 | 8 | 31 | 9 | 6138.5564
2027 | 2008 | 8 | 31 | 10 | 8221.6481
2027 | 2008 | 8 | 31 | 11 | 10055.5307
2027 | 2008 | 8 | 31 | 12 | 10394.7746
2027 | 2008 | 8 | 31 | 13 | 11180.4849
2027 | 2008 | 8 | 31 | 14 | 11869.4044
2027 | 2008 | 8 | 31 | 15 | 11850.7134
2027 | 2008 | 8 | 31 | 16 | 12457.2162
2027 | 2008 | 8 | 31 | 17 | 13555.6699
2027 | 2008 | 8 | 31 | 18 | 15193.2986
2027 | 2008 | 8 | 31 | 19 | 13189.998
2027 | 2008 | 8 | 31 | 20 | 13325.2188
2027 | 2008 | 8 | 31 | 21 | 14282.3186
2027 | 2008 | 8 | 31 | 22 | 15041.5025
2027 | 2008 | 8 | 31 | 23 | 15463.3533
2027 | 2008 | 8 | 31 | 24 | 15955.1185
2028 | 2008 | 8 | 1 | 1 | 13245.2873
2028 | 2008 | 8 | 1 | 2 | 12269.9683
2028 | 2008 | 8 | 1 | 3 | 11108.413
2028 | 2008 | 8 | 1 | 4 | 10200.383
2028 | 2008 | 8 | 1 | 5 | 9823.1042
2028 | 2008 | 8 | 1 | 6 | 9156.5714
2028 | 2008 | 8 | 1 | 7 | 8436.465
2028 | 2008 | 8 | 1 | 8 | 6644.8091
2028 | 2008 | 8 | 1 | 9 | 6781.3632
2028 | 2008 | 8 | 1 | 10 | 6065.2681
2028 | 2008 | 8 | 1 | 11 | 4077.5093
2028 | 2008 | 8 | 1 | 12 | 4442.3165
2028 | 2008 | 8 | 1 | 13 | 5129.6779
2028 | 2008 | 8 | 1 | 14 | 6531.7815
2028 | 2008 | 8 | 1 | 15 | 8268.8489
2028 | 2008 | 8 | 1 | 16 | 10044.1409
2028 | 2008 | 8 | 1 | 17 | 10882.1117
2028 | 2008 | 8 | 1 | 18 | 12495.7116
2028 | 2008 | 8 | 1 | 19 | 12390.1082
2028 | 2008 | 8 | 1 | 20 | 12447.6483
2028 | 2008 | 8 | 1 | 21 | 13558.5595
2028 | 2008 | 8 | 1 | 22 | 13907.5372
2028 | 2008 | 8 | 1 | 23 | 14700.4284
2028 | 2008 | 8 | 1 | 24 | 14790.1276
2028 | 2008 | 8 | 2 | 1 | 14273.2273
2028 | 2008 | 8 | 2 | 2 | 13549.9667
2028 | 2008 | 8 | 2 | 3 | 13382.1539
2028 | 2008 | 8 | 2 | 4 | 12432.7118
2028 | 2008 | 8 | 2 | 5 | 11258.6825
2028 | 2008 | 8 | 2 | 6 | 11002.6092
2028 | 2008 | 8 | 2 | 7 | 10764.4251
2028 | 2008 | 8 | 2 | 8 | 8086.2954
2028 | 2008 | 8 | 2 | 9 | 7742.1121
2028 | 2008 | 8 | 2 | 10 | 9760.1325
2028 | 2008 | 8 | 2 | 11 | 7818.3673
2028 | 2008 | 8 | 2 | 12 | 6737.6261
2028 | 2008 | 8 | 2 | 13 | 7414.2273
2028 | 2008 | 8 | 2 | 14 | 8799.7205
2028 | 2008 | 8 | 2 | 15 | 10478.477
2028 | 2008 | 8 | 2 | 16 | 11893.1919
2028 | 2008 | 8 | 2 | 17 | 13924.3331
2028 | 2008 | 8 | 2 | 18 | 16550.4149
2028 | 2008 | 8 | 2 | 19 | 17751.9109
2028 | 2008 | 8 | 2 | 20 | 19191.3117
2028 | 2008 | 8 | 2 | 21 | 21548.8192
2028 | 2008 | 8 | 2 | 22 | 23370.2518
2028 | 2008 | 8 | 2 | 23 | 23837.6552
2028 | 2008 | 8 | 2 | 24 | 23124.815
2028 | 2008 | 8 | 3 | 1 | 21866.2245
2028 | 2008 | 8 | 3 | 2 | 21490.8059
2028 | 2008 | 8 | 3 | 3 | 21664.5976
2028 | 2008 | 8 | 3 | 4 | 21410.5348
2028 | 2008 | 8 | 3 | 5 | 20738.8983
2028 | 2008 | 8 | 3 | 6 | 19220.0932
2028 | 2008 | 8 | 3 | 7 | 18122.6412
2028 | 2008 | 8 | 3 | 8 | 13333.8116
2028 | 2008 | 8 | 3 | 9 | 11371.0336
2028 | 2008 | 8 | 3 | 10 | 13247.3994
2028 | 2008 | 8 | 3 | 11 | 11801.5553
2028 | 2008 | 8 | 3 | 12 | 11456.636
2028 | 2008 | 8 | 3 | 13 | 12817.048
2028 | 2008 | 8 | 3 | 14 | 13345.8497
2028 | 2008 | 8 | 3 | 15 | 13488.6958
2028 | 2008 | 8 | 3 | 16 | 13207.7831
2028 | 2008 | 8 | 3 | 17 | 13780.1038
2028 | 2008 | 8 | 3 | 18 | 14985.1405
2028 | 2008 | 8 | 3 | 19 | 16215.0643
2028 | 2008 | 8 | 3 | 20 | 18744.4324
2028 | 2008 | 8 | 3 | 21 | 21822.3532
2028 | 2008 | 8 | 3 | 22 | 23937.8055
2028 | 2008 | 8 | 3 | 23 | 24554.224
2028 | 2008 | 8 | 3 | 24 | 24305.3665
2028 | 2008 | 8 | 4 | 1 | 22918.5394
2028 | 2008 | 8 | 4 | 2 | 21766.7739
2028 | 2008 | 8 | 4 | 3 | 21088.3728
2028 | 2008 | 8 | 4 | 4 | 19329.642
2028 | 2008 | 8 | 4 | 5 | 17254.3711
2028 | 2008 | 8 | 4 | 6 | 14245.6996
2028 | 2008 | 8 | 4 | 7 | 11119.1449
2028 | 2008 | 8 | 4 | 8 | 6979.3084
2028 | 2008 | 8 | 4 | 9 | 4423.6583
2028 | 2008 | 8 | 4 | 10 | 5293.8563
2028 | 2008 | 8 | 4 | 11 | 4524.7369
2028 | 2008 | 8 | 4 | 12 | 3595.0066
2028 | 2008 | 8 | 4 | 13 | 4004.304
2028 | 2008 | 8 | 4 | 14 | 5272.6379
2028 | 2008 | 8 | 4 | 15 | 5951.2626
2028 | 2008 | 8 | 4 | 16 | 6015.4396
2028 | 2008 | 8 | 4 | 17 | 7095.4784
2028 | 2008 | 8 | 4 | 18 | 8136.1262
2028 | 2008 | 8 | 4 | 19 | 9337.3359
2028 | 2008 | 8 | 4 | 20 | 11525.0642
2028 | 2008 | 8 | 4 | 21 | 14987.8047
2028 | 2008 | 8 | 4 | 22 | 17870.4671
2028 | 2008 | 8 | 4 | 23 | 17998.1292
2028 | 2008 | 8 | 4 | 24 | 16147.4949
2028 | 2008 | 8 | 5 | 1 | 14354.6054
2028 | 2008 | 8 | 5 | 2 | 12945.1011
2028 | 2008 | 8 | 5 | 3 | 11679.0102
2028 | 2008 | 8 | 5 | 4 | 9745.3863
2028 | 2008 | 8 | 5 | 5 | 8191.0339
2028 | 2008 | 8 | 5 | 6 | 6952.2099
2028 | 2008 | 8 | 5 | 7 | 5842.7884
2028 | 2008 | 8 | 5 | 8 | 3197.948
2028 | 2008 | 8 | 5 | 9 | 2205.6368
2028 | 2008 | 8 | 5 | 10 | 1808.7148
2028 | 2008 | 8 | 5 | 11 | 1880.9622
2028 | 2008 | 8 | 5 | 12 | 1695.101
2028 | 2008 | 8 | 5 | 13 | 2573.4914
2028 | 2008 | 8 | 5 | 14 | 3726.8465
2028 | 2008 | 8 | 5 | 15 | 6165.1015
2028 | 2008 | 8 | 5 | 16 | 7879.8679
2028 | 2008 | 8 | 5 | 17 | 10517.1725
2028 | 2008 | 8 | 5 | 18 | 13388.1785
2028 | 2008 | 8 | 5 | 19 | 15775.2951
2028 | 2008 | 8 | 5 | 20 | 18295.0202
2028 | 2008 | 8 | 5 | 21 | 21441.4784
2028 | 2008 | 8 | 5 | 22 | 21993.7957
2028 | 2008 | 8 | 5 | 23 | 20587.4773
2028 | 2008 | 8 | 5 | 24 | 19045.9941
2028 | 2008 | 8 | 6 | 1 | 17078.5641
2028 | 2008 | 8 | 6 | 2 | 14279.451
2028 | 2008 | 8 | 6 | 3 | 11294.6877
2028 | 2008 | 8 | 6 | 4 | 9312.5035
2028 | 2008 | 8 | 6 | 5 | 7862.5506
2028 | 2008 | 8 | 6 | 6 | 6738.1769
2028 | 2008 | 8 | 6 | 7 | 5743.8457
2028 | 2008 | 8 | 6 | 8 | 5194.8046
2028 | 2008 | 8 | 6 | 9 | 6570.5837
2028 | 2008 | 8 | 6 | 10 | 8526.039
2028 | 2008 | 8 | 6 | 11 | 9474.414
2028 | 2008 | 8 | 6 | 12 | 10500.1518
2028 | 2008 | 8 | 6 | 13 | 12271.5864
2028 | 2008 | 8 | 6 | 14 | 12830.0447
2028 | 2008 | 8 | 6 | 15 | 13834.0306
2028 | 2008 | 8 | 6 | 16 | 13454.8797
2028 | 2008 | 8 | 6 | 17 | 14439.5679
2028 | 2008 | 8 | 6 | 18 | 14941.6708
2028 | 2008 | 8 | 6 | 19 | 15302.2028
2028 | 2008 | 8 | 6 | 20 | 15217.5527
2028 | 2008 | 8 | 6 | 21 | 16135.0085
2028 | 2008 | 8 | 6 | 22 | 16283.7616
2028 | 2008 | 8 | 6 | 23 | 15464.1272
2028 | 2008 | 8 | 6 | 24 | 14611.6856
2028 | 2008 | 8 | 7 | 1 | 13341.3702
2028 | 2008 | 8 | 7 | 2 | 11932.7156
2028 | 2008 | 8 | 7 | 3 | 11409.468
2028 | 2008 | 8 | 7 | 4 | 10668.3534
2028 | 2008 | 8 | 7 | 5 | 9534.1937
2028 | 2008 | 8 | 7 | 6 | 8477.8846
2028 | 2008 | 8 | 7 | 7 | 7925.95
2028 | 2008 | 8 | 7 | 8 | 6700.3332
2028 | 2008 | 8 | 7 | 9 | 7378.3653
2028 | 2008 | 8 | 7 | 10 | 7384.087
2028 | 2008 | 8 | 7 | 11 | 7137.1827
2028 | 2008 | 8 | 7 | 12 | 7070.0939
2028 | 2008 | 8 | 7 | 13 | 7456.8912
2028 | 2008 | 8 | 7 | 14 | 8163.1847
2028 | 2008 | 8 | 7 | 15 | 9113.7163
2028 | 2008 | 8 | 7 | 16 | 9164.5088
2028 | 2008 | 8 | 7 | 17 | 10045.4853
2028 | 2008 | 8 | 7 | 18 | 10946.7451
2028 | 2008 | 8 | 7 | 19 | 11613.8187
2028 | 2008 | 8 | 7 | 20 | 11566.0471
2028 | 2008 | 8 | 7 | 21 | 12168.7744
2028 | 2008 | 8 | 7 | 22 | 13195.3011
2028 | 2008 | 8 | 7 | 23 | 13437.819
2028 | 2008 | 8 | 7 | 24 | 14267.0334
2028 | 2008 | 8 | 8 | 1 | 14486.5834
2028 | 2008 | 8 | 8 | 2 | 14404.2054
2028 | 2008 | 8 | 8 | 3 | 13940.5245
2028 | 2008 | 8 | 8 | 4 | 12579.1836
2028 | 2008 | 8 | 8 | 5 | 11428.9016
2028 | 2008 | 8 | 8 | 6 | 10811.2804
2028 | 2008 | 8 | 8 | 7 | 10013.125
2028 | 2008 | 8 | 8 | 8 | 6651.6008
2028 | 2008 | 8 | 8 | 9 | 5469.096
2028 | 2008 | 8 | 8 | 10 | 6249.1754
2028 | 2008 | 8 | 8 | 11 | 5327.2741
2028 | 2008 | 8 | 8 | 12 | 4411.2291
2028 | 2008 | 8 | 8 | 13 | 4805.327
2028 | 2008 | 8 | 8 | 14 | 6268.537
2028 | 2008 | 8 | 8 | 15 | 8222.7779
2028 | 2008 | 8 | 8 | 16 | 9986.3634
2028 | 2008 | 8 | 8 | 17 | 11252.2243
2028 | 2008 | 8 | 8 | 18 | 12139.5837
2028 | 2008 | 8 | 8 | 19 | 13797.8974
2028 | 2008 | 8 | 8 | 20 | 15296.8209
2028 | 2008 | 8 | 8 | 21 | 18076.6646
2028 | 2008 | 8 | 8 | 22 | 20271.8016
2028 | 2008 | 8 | 8 | 23 | 21989.4409
2028 | 2008 | 8 | 8 | 24 | 21872.43
2028 | 2008 | 8 | 9 | 1 | 20666.2857
2028 | 2008 | 8 | 9 | 2 | 20005.0524
2028 | 2008 | 8 | 9 | 3 | 19156.8932
2028 | 2008 | 8 | 9 | 4 | 18785.8625
2028 | 2008 | 8 | 9 | 5 | 18557.4229
2028 | 2008 | 8 | 9 | 6 | 18825.314
2028 | 2008 | 8 | 9 | 7 | 18554.862
2028 | 2008 | 8 | 9 | 8 | 14770.151
2028 | 2008 | 8 | 9 | 9 | 13265.3466
2028 | 2008 | 8 | 9 | 10 | 14897.5745
2028 | 2008 | 8 | 9 | 11 | 14149.0374
2028 | 2008 | 8 | 9 | 12 | 14258.1066
2028 | 2008 | 8 | 9 | 13 | 16465.2671
2028 | 2008 | 8 | 9 | 14 | 17888.5455
2028 | 2008 | 8 | 9 | 15 | 19367.4111
2028 | 2008 | 8 | 9 | 16 | 19562.9103
2028 | 2008 | 8 | 9 | 17 | 21022.4613
2028 | 2008 | 8 | 9 | 18 | 22966.5302
2028 | 2008 | 8 | 9 | 19 | 23465.7517
2028 | 2008 | 8 | 9 | 20 | 24713.3958
2028 | 2008 | 8 | 9 | 21 | 26500.3117
2028 | 2008 | 8 | 9 | 22 | 28335.9214
2028 | 2008 | 8 | 9 | 23 | 29124.8881
2028 | 2008 | 8 | 9 | 24 | 29620.8386
2028 | 2008 | 8 | 10 | 1 | 28891.6511
2028 | 2008 | 8 | 10 | 2 | 28947.8788
2028 | 2008 | 8 | 10 | 3 | 29557.782
2028 | 2008 | 8 | 10 | 4 | 29572.7041
2028 | 2008 | 8 | 10 | 5 | 29385.8551
2028 | 2008 | 8 | 10 | 6 | 29223.5092
2028 | 2008 | 8 | 10 | 7 | 27240.6233
2028 | 2008 | 8 | 10 | 8 | 24502.6477
2028 | 2008 | 8 | 10 | 9 | 25867.7834
2028 | 2008 | 8 | 10 | 10 | 25228.2076
2028 | 2008 | 8 | 10 | 11 | 20721.5638
2028 | 2008 | 8 | 10 | 12 | 17688.8033
2028 | 2008 | 8 | 10 | 13 | 15761.349
2028 | 2008 | 8 | 10 | 14 | 14926.0587
2028 | 2008 | 8 | 10 | 15 | 13895.8159
2028 | 2008 | 8 | 10 | 16 | 13990.2578
2028 | 2008 | 8 | 10 | 17 | 15957.1377
2028 | 2008 | 8 | 10 | 18 | 19644.4929
2028 | 2008 | 8 | 10 | 19 | 21977.0954
2028 | 2008 | 8 | 10 | 20 | 21254.1206
2028 | 2008 | 8 | 10 | 21 | 21020.1521
2028 | 2008 | 8 | 10 | 22 | 20170.4333
2028 | 2008 | 8 | 10 | 23 | 20263.9167
2028 | 2008 | 8 | 10 | 24 | 18041.897
2028 | 2008 | 8 | 11 | 1 | 16483.399
2028 | 2008 | 8 | 11 | 2 | 16257.7918
2028 | 2008 | 8 | 11 | 3 | 15882.3758
2028 | 2008 | 8 | 11 | 4 | 15064.2089
2028 | 2008 | 8 | 11 | 5 | 13966.5397
2028 | 2008 | 8 | 11 | 6 | 13340.6151
2028 | 2008 | 8 | 11 | 7 | 12476.6479
2028 | 2008 | 8 | 11 | 8 | 11562.2326
2028 | 2008 | 8 | 11 | 9 | 14366.6066
2028 | 2008 | 8 | 11 | 10 | 14588.5603
2028 | 2008 | 8 | 11 | 11 | 13732.5445
2028 | 2008 | 8 | 11 | 12 | 13457.7308
2028 | 2008 | 8 | 11 | 13 | 13270.7397
2028 | 2008 | 8 | 11 | 14 | 13353.6898
2028 | 2008 | 8 | 11 | 15 | 12940.1908
2028 | 2008 | 8 | 11 | 16 | 12691.8561
2028 | 2008 | 8 | 11 | 17 | 13207.5727
2028 | 2008 | 8 | 11 | 18 | 13092.8149
2028 | 2008 | 8 | 11 | 19 | 13601.3089
2028 | 2008 | 8 | 11 | 20 | 12919.599
2028 | 2008 | 8 | 11 | 21 | 12848.6015
2028 | 2008 | 8 | 11 | 22 | 11253.7721
2028 | 2008 | 8 | 11 | 23 | 10515.0667
2028 | 2008 | 8 | 11 | 24 | 9934.2472
2028 | 2008 | 8 | 12 | 1 | 9891.111
2028 | 2008 | 8 | 12 | 2 | 10043.0903
2028 | 2008 | 8 | 12 | 3 | 9826.5142
2028 | 2008 | 8 | 12 | 4 | 9630.5543
2028 | 2008 | 8 | 12 | 5 | 8721.8338
2028 | 2008 | 8 | 12 | 6 | 8241.9611
2028 | 2008 | 8 | 12 | 7 | 7572.964
2028 | 2008 | 8 | 12 | 8 | 6200.0084
2028 | 2008 | 8 | 12 | 9 | 7370.4751
2028 | 2008 | 8 | 12 | 10 | 7658.9772
2028 | 2008 | 8 | 12 | 11 | 7194.4374
2028 | 2008 | 8 | 12 | 12 | 6614.8785
2028 | 2008 | 8 | 12 | 13 | 7683.1165
2028 | 2008 | 8 | 12 | 14 | 8755.8996
2028 | 2008 | 8 | 12 | 15 | 9528.0468
2028 | 2008 | 8 | 12 | 16 | 9991.0744
2028 | 2008 | 8 | 12 | 17 | 10353.1192
2028 | 2008 | 8 | 12 | 18 | 11066.0909
2028 | 2008 | 8 | 12 | 19 | 11625.0904
2028 | 2008 | 8 | 12 | 20 | 10864.3927
2028 | 2008 | 8 | 12 | 21 | 10776.2549
2028 | 2008 | 8 | 12 | 22 | 10622.0344
2028 | 2008 | 8 | 12 | 23 | 10074.7138
2028 | 2008 | 8 | 12 | 24 | 9147.7716
2028 | 2008 | 8 | 13 | 1 | 7886.3838
2028 | 2008 | 8 | 13 | 2 | 7261.8015
2028 | 2008 | 8 | 13 | 3 | 7035.8994
2028 | 2008 | 8 | 13 | 4 | 6800.2882
2028 | 2008 | 8 | 13 | 5 | 5849.3338
2028 | 2008 | 8 | 13 | 6 | 4801.1515
2028 | 2008 | 8 | 13 | 7 | 3648.6645
2028 | 2008 | 8 | 13 | 8 | 2314.3648
2028 | 2008 | 8 | 13 | 9 | 2668.5531
2028 | 2008 | 8 | 13 | 10 | 2785.4192
2028 | 2008 | 8 | 13 | 11 | 2361.3902
2028 | 2008 | 8 | 13 | 12 | 2402.9416
2028 | 2008 | 8 | 13 | 13 | 2408.4356
2028 | 2008 | 8 | 13 | 14 | 2890.0843
2028 | 2008 | 8 | 13 | 15 | 3910.7273
2028 | 2008 | 8 | 13 | 16 | 4692.8144
2028 | 2008 | 8 | 13 | 17 | 6086.2869
2028 | 2008 | 8 | 13 | 18 | 8136.6004
2028 | 2008 | 8 | 13 | 19 | 9277.9722
2028 | 2008 | 8 | 13 | 20 | 10201.3988
2028 | 2008 | 8 | 13 | 21 | 11830.0102
2028 | 2008 | 8 | 13 | 22 | 12204.1146
2028 | 2008 | 8 | 13 | 23 | 11399.8912
2028 | 2008 | 8 | 13 | 24 | 10285.5766
2028 | 2008 | 8 | 14 | 1 | 9501.7821
2028 | 2008 | 8 | 14 | 2 | 9213.9941
2028 | 2008 | 8 | 14 | 3 | 8909.3423
2028 | 2008 | 8 | 14 | 4 | 8774.6439
2028 | 2008 | 8 | 14 | 5 | 7923.2554
2028 | 2008 | 8 | 14 | 6 | 7278.1137
2028 | 2008 | 8 | 14 | 7 | 6311.2421
2028 | 2008 | 8 | 14 | 8 | 4294.0664
2028 | 2008 | 8 | 14 | 9 | 3876.9818
2028 | 2008 | 8 | 14 | 10 | 4065.6397
2028 | 2008 | 8 | 14 | 11 | 5092.447
2028 | 2008 | 8 | 14 | 12 | 5361.2601
2028 | 2008 | 8 | 14 | 13 | 7080.3021
2028 | 2008 | 8 | 14 | 14 | 8357.0215
2028 | 2008 | 8 | 14 | 15 | 9468.0216
2028 | 2008 | 8 | 14 | 16 | 10052.6006
2028 | 2008 | 8 | 14 | 17 | 10838.6032
2028 | 2008 | 8 | 14 | 18 | 11885.3726
2028 | 2008 | 8 | 14 | 19 | 13269.875
2028 | 2008 | 8 | 14 | 20 | 14400.7022
2028 | 2008 | 8 | 14 | 21 | 16465.5953
2028 | 2008 | 8 | 14 | 22 | 20097.5321
2028 | 2008 | 8 | 14 | 23 | 23704.5471
2028 | 2008 | 8 | 14 | 24 | 24577.1633
2028 | 2008 | 8 | 15 | 1 | 23462.6477
2028 | 2008 | 8 | 15 | 2 | 21912.2964
2028 | 2008 | 8 | 15 | 3 | 20233.5977
2028 | 2008 | 8 | 15 | 4 | 17546.3564
2028 | 2008 | 8 | 15 | 5 | 13385.478
2028 | 2008 | 8 | 15 | 6 | 10487.5418
2028 | 2008 | 8 | 15 | 7 | 8240.8292
2028 | 2008 | 8 | 15 | 8 | 5407.9523
2028 | 2008 | 8 | 15 | 9 | 4928.389
2028 | 2008 | 8 | 15 | 10 | 6019.9552
2028 | 2008 | 8 | 15 | 11 | 6767.1297
2028 | 2008 | 8 | 15 | 12 | 7251.9658
2028 | 2008 | 8 | 15 | 13 | 8381.6646
2028 | 2008 | 8 | 15 | 14 | 8900.4389
2028 | 2008 | 8 | 15 | 15 | 8795.2569
2028 | 2008 | 8 | 15 | 16 | 8735.2268
2028 | 2008 | 8 | 15 | 17 | 9390.0178
2028 | 2008 | 8 | 15 | 18 | 10960.3451
2028 | 2008 | 8 | 15 | 19 | 11860.5992
2028 | 2008 | 8 | 15 | 20 | 13895.6101
2028 | 2008 | 8 | 15 | 21 | 16667.6423
2028 | 2008 | 8 | 15 | 22 | 18801.6876
2028 | 2008 | 8 | 15 | 23 | 18918.8931
2028 | 2008 | 8 | 15 | 24 | 18666.9593
2028 | 2008 | 8 | 16 | 1 | 17753.251
2028 | 2008 | 8 | 16 | 2 | 16606.7119
2028 | 2008 | 8 | 16 | 3 | 14144.5907
2028 | 2008 | 8 | 16 | 4 | 11827.0562
2028 | 2008 | 8 | 16 | 5 | 9612.0874
2028 | 2008 | 8 | 16 | 6 | 7810.1278
2028 | 2008 | 8 | 16 | 7 | 6030.7219
2028 | 2008 | 8 | 16 | 8 | 4997.5692
2028 | 2008 | 8 | 16 | 9 | 5786.557
2028 | 2008 | 8 | 16 | 10 | 7881.3724
2028 | 2008 | 8 | 16 | 11 | 8585.1221
2028 | 2008 | 8 | 16 | 12 | 9384.918
2028 | 2008 | 8 | 16 | 13 | 11163.8451
2028 | 2008 | 8 | 16 | 14 | 13908.3411
2028 | 2008 | 8 | 16 | 15 | 14761.1828
2028 | 2008 | 8 | 16 | 16 | 15701.752
2028 | 2008 | 8 | 16 | 17 | 17124.0495
2028 | 2008 | 8 | 16 | 18 | 17725.5019
2028 | 2008 | 8 | 16 | 19 | 17495.6419
2028 | 2008 | 8 | 16 | 20 | 15905.177
2028 | 2008 | 8 | 16 | 21 | 14846.6815
2028 | 2008 | 8 | 16 | 22 | 12691.8128
2028 | 2008 | 8 | 16 | 23 | 10438.929
2028 | 2008 | 8 | 16 | 24 | 8158.4526
2028 | 2008 | 8 | 17 | 1 | 6147.5693
2028 | 2008 | 8 | 17 | 2 | 4955.7394
2028 | 2008 | 8 | 17 | 3 | 4513.4601
2028 | 2008 | 8 | 17 | 4 | 4475.2908
2028 | 2008 | 8 | 17 | 5 | 4591.1501
2028 | 2008 | 8 | 17 | 6 | 5243.5151
2028 | 2008 | 8 | 17 | 7 | 5223.3057
2028 | 2008 | 8 | 17 | 8 | 5566.014
2028 | 2008 | 8 | 17 | 9 | 7117.0612
2028 | 2008 | 8 | 17 | 10 | 8990.4288
2028 | 2008 | 8 | 17 | 11 | 9226.5375
2028 | 2008 | 8 | 17 | 12 | 9548.1685
2028 | 2008 | 8 | 17 | 13 | 9102.5641
2028 | 2008 | 8 | 17 | 14 | 8749.6146
2028 | 2008 | 8 | 17 | 15 | 7640.5099
2028 | 2008 | 8 | 17 | 16 | 7611.7835
2028 | 2008 | 8 | 17 | 17 | 9047.7787
2028 | 2008 | 8 | 17 | 18 | 10647.5876
2028 | 2008 | 8 | 17 | 19 | 11888.7131
2028 | 2008 | 8 | 17 | 20 | 11427.5987
2028 | 2008 | 8 | 17 | 21 | 12139.3241
2028 | 2008 | 8 | 17 | 22 | 12479.7372
2028 | 2008 | 8 | 17 | 23 | 12567.3606
2028 | 2008 | 8 | 17 | 24 | 12485.5363
2028 | 2008 | 8 | 18 | 1 | 11688.5522
2028 | 2008 | 8 | 18 | 2 | 11154.2058
2028 | 2008 | 8 | 18 | 3 | 10599.4392
2028 | 2008 | 8 | 18 | 4 | 10818.9767
2028 | 2008 | 8 | 18 | 5 | 10681.0168
2028 | 2008 | 8 | 18 | 6 | 10855.721
2028 | 2008 | 8 | 18 | 7 | 10099.0627
2028 | 2008 | 8 | 18 | 8 | 9324.6156
2028 | 2008 | 8 | 18 | 9 | 11144.7247
2028 | 2008 | 8 | 18 | 10 | 12136.5629
2028 | 2008 | 8 | 18 | 11 | 11777.4155
2028 | 2008 | 8 | 18 | 12 | 11640.7103
2028 | 2008 | 8 | 18 | 13 | 12124.0914
2028 | 2008 | 8 | 18 | 14 | 12669.0478
2028 | 2008 | 8 | 18 | 15 | 13414.8827
2028 | 2008 | 8 | 18 | 16 | 13515.4236
2028 | 2008 | 8 | 18 | 17 | 15061.1701
2028 | 2008 | 8 | 18 | 18 | 15497.4562
2028 | 2008 | 8 | 18 | 19 | 15396.7128
2028 | 2008 | 8 | 18 | 20 | 14483.4361
2028 | 2008 | 8 | 18 | 21 | 14458.9057
2028 | 2008 | 8 | 18 | 22 | 14181.3848
2028 | 2008 | 8 | 18 | 23 | 13115.7577
2028 | 2008 | 8 | 18 | 24 | 12022.3009
2028 | 2008 | 8 | 19 | 1 | 11341.5912
2028 | 2008 | 8 | 19 | 2 | 11040.7591
2028 | 2008 | 8 | 19 | 3 | 11830.854
2028 | 2008 | 8 | 19 | 4 | 13141.6804
2028 | 2008 | 8 | 19 | 5 | 13828.1592
2028 | 2008 | 8 | 19 | 6 | 14478.5744
2028 | 2008 | 8 | 19 | 7 | 14682.2313
2028 | 2008 | 8 | 19 | 8 | 13396.0397
2028 | 2008 | 8 | 19 | 9 | 15670.1488
2028 | 2008 | 8 | 19 | 10 | 14761.6477
2028 | 2008 | 8 | 19 | 11 | 11815.1435
2028 | 2008 | 8 | 19 | 12 | 11386.4355
2028 | 2008 | 8 | 19 | 13 | 12069.4269
2028 | 2008 | 8 | 19 | 14 | 12969.2013
2028 | 2008 | 8 | 19 | 15 | 14563.4832
2028 | 2008 | 8 | 19 | 16 | 15551.6385
2028 | 2008 | 8 | 19 | 17 | 17094.1289
2028 | 2008 | 8 | 19 | 18 | 17079.2959
2028 | 2008 | 8 | 19 | 19 | 17021.5952
2028 | 2008 | 8 | 19 | 20 | 15736.3503
2028 | 2008 | 8 | 19 | 21 | 14980.6587
2028 | 2008 | 8 | 19 | 22 | 13330.1685
2028 | 2008 | 8 | 19 | 23 | 10721.9899
2028 | 2008 | 8 | 19 | 24 | 8794.9274
2028 | 2008 | 8 | 20 | 1 | 7009.9237
2028 | 2008 | 8 | 20 | 2 | 6007.5706
2028 | 2008 | 8 | 20 | 3 | 5974.8107
2028 | 2008 | 8 | 20 | 4 | 5848.7962
2028 | 2008 | 8 | 20 | 5 | 5590.5983
2028 | 2008 | 8 | 20 | 6 | 5405.8263
2028 | 2008 | 8 | 20 | 7 | 5419.4519
2028 | 2008 | 8 | 20 | 8 | 4714.2609
2028 | 2008 | 8 | 20 | 9 | 5642.9186
2028 | 2008 | 8 | 20 | 10 | 5702.2472
2028 | 2008 | 8 | 20 | 11 | 5119.5593
2028 | 2008 | 8 | 20 | 12 | 5072.6529
2028 | 2008 | 8 | 20 | 13 | 5658.1756
2028 | 2008 | 8 | 20 | 14 | 6465.439
2028 | 2008 | 8 | 20 | 15 | 6997.5467
2028 | 2008 | 8 | 20 | 16 | 7168.0141
2028 | 2008 | 8 | 20 | 17 | 6690.5688
2028 | 2008 | 8 | 20 | 18 | 5934.5425
2028 | 2008 | 8 | 20 | 19 | 5138.6168
2028 | 2008 | 8 | 20 | 20 | 5054.67
2028 | 2008 | 8 | 20 | 21 | 5966.8249
2028 | 2008 | 8 | 20 | 22 | 7279.8179
2028 | 2008 | 8 | 20 | 23 | 8103.94
2028 | 2008 | 8 | 20 | 24 | 8418.603
2028 | 2008 | 8 | 21 | 1 | 8905.4733
2028 | 2008 | 8 | 21 | 2 | 8929.0516
2028 | 2008 | 8 | 21 | 3 | 8262.4865
2028 | 2008 | 8 | 21 | 4 | 7861.0787
2028 | 2008 | 8 | 21 | 5 | 7260.0672
2028 | 2008 | 8 | 21 | 6 | 6941.6464
2028 | 2008 | 8 | 21 | 7 | 6408.047
2028 | 2008 | 8 | 21 | 8 | 4730.476
2028 | 2008 | 8 | 21 | 9 | 4822.9254
2028 | 2008 | 8 | 21 | 10 | 5898.759
2028 | 2008 | 8 | 21 | 11 | 6937.995
2028 | 2008 | 8 | 21 | 12 | 7816.4429
2028 | 2008 | 8 | 21 | 13 | 8811.7711
2028 | 2008 | 8 | 21 | 14 | 10029.1719
2028 | 2008 | 8 | 21 | 15 | 10522.1492
2028 | 2008 | 8 | 21 | 16 | 10086.7013
2028 | 2008 | 8 | 21 | 17 | 10797.9069
2028 | 2008 | 8 | 21 | 18 | 12094.751
2028 | 2008 | 8 | 21 | 19 | 13709.1684
2028 | 2008 | 8 | 21 | 20 | 15944.0701
2028 | 2008 | 8 | 21 | 21 | 20025.5124
2028 | 2008 | 8 | 21 | 22 | 22808.0162
2028 | 2008 | 8 | 21 | 23 | 23923.0156
2028 | 2008 | 8 | 21 | 24 | 24144.7725
2028 | 2008 | 8 | 22 | 1 | 23380.1385
2028 | 2008 | 8 | 22 | 2 | 22799.7879
2028 | 2008 | 8 | 22 | 3 | 22860.7976
2028 | 2008 | 8 | 22 | 4 | 23073.7
2028 | 2008 | 8 | 22 | 5 | 23048.298
2028 | 2008 | 8 | 22 | 6 | 23710.0594
2028 | 2008 | 8 | 22 | 7 | 23997.846
2028 | 2008 | 8 | 22 | 8 | 21624.0668
2028 | 2008 | 8 | 22 | 9 | 22705.3572
2028 | 2008 | 8 | 22 | 10 | 23849.1294
2028 | 2008 | 8 | 22 | 11 | 21745.7246
2028 | 2008 | 8 | 22 | 12 | 20749.9502
2028 | 2008 | 8 | 22 | 13 | 22057.7959
2028 | 2008 | 8 | 22 | 14 | 22382.2785
2028 | 2008 | 8 | 22 | 15 | 21670.2038
2028 | 2008 | 8 | 22 | 16 | 19863.587
2028 | 2008 | 8 | 22 | 17 | 18795.667
2028 | 2008 | 8 | 22 | 18 | 19045.6784
2028 | 2008 | 8 | 22 | 19 | 18865.039
2028 | 2008 | 8 | 22 | 20 | 20374.6193
2028 | 2008 | 8 | 22 | 21 | 21882.002
2028 | 2008 | 8 | 22 | 22 | 23021.0768
2028 | 2008 | 8 | 22 | 23 | 22492.3452
2028 | 2008 | 8 | 22 | 24 | 20978.6646
2028 | 2008 | 8 | 23 | 1 | 17845.4606
2028 | 2008 | 8 | 23 | 2 | 15542.7666
2028 | 2008 | 8 | 23 | 3 | 13115.2883
2028 | 2008 | 8 | 23 | 4 | 10893.5452
2028 | 2008 | 8 | 23 | 5 | 8837.0859
2028 | 2008 | 8 | 23 | 6 | 6712.8748
2028 | 2008 | 8 | 23 | 7 | 5206.634
2028 | 2008 | 8 | 23 | 8 | 3698.7739
2028 | 2008 | 8 | 23 | 9 | 4457.8076
2028 | 2008 | 8 | 23 | 10 | 5010.5544
2028 | 2008 | 8 | 23 | 11 | 4636.8199
2028 | 2008 | 8 | 23 | 12 | 4387.1996
2028 | 2008 | 8 | 23 | 13 | 5285.2604
2028 | 2008 | 8 | 23 | 14 | 6280.6376
2028 | 2008 | 8 | 23 | 15 | 7167.7875
2028 | 2008 | 8 | 23 | 16 | 7643.8332
2028 | 2008 | 8 | 23 | 17 | 8291.1334
2028 | 2008 | 8 | 23 | 18 | 8438.5906
2028 | 2008 | 8 | 23 | 19 | 7732.2839
2028 | 2008 | 8 | 23 | 20 | 6514.3841
2028 | 2008 | 8 | 23 | 21 | 6044.7968
2028 | 2008 | 8 | 23 | 22 | 5025.602
2028 | 2008 | 8 | 23 | 23 | 3625.6458
2028 | 2008 | 8 | 23 | 24 | 2868.0901
2028 | 2008 | 8 | 24 | 1 | 2264.7679
2028 | 2008 | 8 | 24 | 2 | 1514.4573
2028 | 2008 | 8 | 24 | 3 | 1126.6933
2028 | 2008 | 8 | 24 | 4 | 864.3561
2028 | 2008 | 8 | 24 | 5 | 810.7621
2028 | 2008 | 8 | 24 | 6 | 768.6248
2028 | 2008 | 8 | 24 | 7 | 874.3706
2028 | 2008 | 8 | 24 | 8 | 590.5288
2028 | 2008 | 8 | 24 | 9 | 906.8839
2028 | 2008 | 8 | 24 | 10 | 1054.3108
2028 | 2008 | 8 | 24 | 11 | 1577.7493
2028 | 2008 | 8 | 24 | 12 | 2218.767
2028 | 2008 | 8 | 24 | 13 | 3200.8714
2028 | 2008 | 8 | 24 | 14 | 3321.1256
2028 | 2008 | 8 | 24 | 15 | 4137.9828
2028 | 2008 | 8 | 24 | 16 | 4497.518
2028 | 2008 | 8 | 24 | 17 | 4921.7547
2028 | 2008 | 8 | 24 | 18 | 5354.4504
2028 | 2008 | 8 | 24 | 19 | 5257.8269
2028 | 2008 | 8 | 24 | 20 | 4506.6665
2028 | 2008 | 8 | 24 | 21 | 4372.8768
2028 | 2008 | 8 | 24 | 22 | 4270.8209
2028 | 2008 | 8 | 24 | 23 | 3848.4425
2028 | 2008 | 8 | 24 | 24 | 3517.0326
2028 | 2008 | 8 | 25 | 1 | 3370.5043
2028 | 2008 | 8 | 25 | 2 | 3346.8259
2028 | 2008 | 8 | 25 | 3 | 3452.7518
2028 | 2008 | 8 | 25 | 4 | 3519.5599
2028 | 2008 | 8 | 25 | 5 | 3667.2501
2028 | 2008 | 8 | 25 | 6 | 3558.5899
2028 | 2008 | 8 | 25 | 7 | 3252.8197
2028 | 2008 | 8 | 25 | 8 | 2387.7161
2028 | 2008 | 8 | 25 | 9 | 2209.2703
2028 | 2008 | 8 | 25 | 10 | 1928.0274
2028 | 2008 | 8 | 25 | 11 | 1369.5184
2028 | 2008 | 8 | 25 | 12 | 1220.3985
2028 | 2008 | 8 | 25 | 13 | 1659.7827
2028 | 2008 | 8 | 25 | 14 | 2288.1808
2028 | 2008 | 8 | 25 | 15 | 2834.9708
2028 | 2008 | 8 | 25 | 16 | 3015.0414
2028 | 2008 | 8 | 25 | 17 | 3376.1983
2028 | 2008 | 8 | 25 | 18 | 3774.4771
2028 | 2008 | 8 | 25 | 19 | 4232.7927
2028 | 2008 | 8 | 25 | 20 | 4120.0063
2028 | 2008 | 8 | 25 | 21 | 4934.0695
2028 | 2008 | 8 | 25 | 22 | 5456.8336
2028 | 2008 | 8 | 25 | 23 | 5662.3132
2028 | 2008 | 8 | 25 | 24 | 5468.1893
2028 | 2008 | 8 | 26 | 1 | 5109.7205
2028 | 2008 | 8 | 26 | 2 | 5088.2164
2028 | 2008 | 8 | 26 | 3 | 5029.2189
2028 | 2008 | 8 | 26 | 4 | 4868.1473
2028 | 2008 | 8 | 26 | 5 | 4853.2034
2028 | 2008 | 8 | 26 | 6 | 4649.9917
2028 | 2008 | 8 | 26 | 7 | 3840.3562
2028 | 2008 | 8 | 26 | 8 | 2431.7077
2028 | 2008 | 8 | 26 | 9 | 1974.5839
2028 | 2008 | 8 | 26 | 10 | 2633.5597
2028 | 2008 | 8 | 26 | 11 | 3049.219
2028 | 2008 | 8 | 26 | 12 | 3356.6361
2028 | 2008 | 8 | 26 | 13 | 3726.5428
2028 | 2008 | 8 | 26 | 14 | 4004.074
2028 | 2008 | 8 | 26 | 15 | 4829.5723
2028 | 2008 | 8 | 26 | 16 | 5334.3592
2028 | 2008 | 8 | 26 | 17 | 6909.9643
2028 | 2008 | 8 | 26 | 18 | 8773.4647
2028 | 2008 | 8 | 26 | 19 | 10123.3448
2028 | 2008 | 8 | 26 | 20 | 11896.2504
2028 | 2008 | 8 | 26 | 21 | 14505.8856
2028 | 2008 | 8 | 26 | 22 | 16343.9094
2028 | 2008 | 8 | 26 | 23 | 16865.9557
2028 | 2008 | 8 | 26 | 24 | 16554.6687
2028 | 2008 | 8 | 27 | 1 | 15456.6927
2028 | 2008 | 8 | 27 | 2 | 14564.8495
2028 | 2008 | 8 | 27 | 3 | 13538.8998
2028 | 2008 | 8 | 27 | 4 | 12404.3787
2028 | 2008 | 8 | 27 | 5 | 11693.5136
2028 | 2008 | 8 | 27 | 6 | 11519.3137
2028 | 2008 | 8 | 27 | 7 | 11387.9423
2028 | 2008 | 8 | 27 | 8 | 8543.4074
2028 | 2008 | 8 | 27 | 9 | 7974.3519
2028 | 2008 | 8 | 27 | 10 | 7591.0263
2028 | 2008 | 8 | 27 | 11 | 9120.152
2028 | 2008 | 8 | 27 | 12 | 10704.2218
2028 | 2008 | 8 | 27 | 13 | 11870.0019
2028 | 2008 | 8 | 27 | 14 | 12780.5008
2028 | 2008 | 8 | 27 | 15 | 12905.2538
2028 | 2008 | 8 | 27 | 16 | 12189.8338
2028 | 2008 | 8 | 27 | 17 | 12907.7737
2028 | 2008 | 8 | 27 | 18 | 13855.4256
2028 | 2008 | 8 | 27 | 19 | 14182.8999
2028 | 2008 | 8 | 27 | 20 | 15016.4383
2028 | 2008 | 8 | 27 | 21 | 16722.3202
2028 | 2008 | 8 | 27 | 22 | 17895.3863
2028 | 2008 | 8 | 27 | 23 | 17773.7528
2028 | 2008 | 8 | 27 | 24 | 17407.4719
2028 | 2008 | 8 | 28 | 1 | 16571.2919
2028 | 2008 | 8 | 28 | 2 | 15743.5692
2028 | 2008 | 8 | 28 | 3 | 15344.8967
2028 | 2008 | 8 | 28 | 4 | 15247.5362
2028 | 2008 | 8 | 28 | 5 | 14812.731
2028 | 2008 | 8 | 28 | 6 | 14295.2569
2028 | 2008 | 8 | 28 | 7 | 13517.8111
2028 | 2008 | 8 | 28 | 8 | 10706.8901
2028 | 2008 | 8 | 28 | 9 | 10400.4426
2028 | 2008 | 8 | 28 | 10 | 8921.1891
2028 | 2008 | 8 | 28 | 11 | 8279.4842
2028 | 2008 | 8 | 28 | 12 | 8871.6988
2028 | 2008 | 8 | 28 | 13 | 9990.2507
2028 | 2008 | 8 | 28 | 14 | 11533.1041
2028 | 2008 | 8 | 28 | 15 | 12528.9775
2028 | 2008 | 8 | 28 | 16 | 12816.8522
2028 | 2008 | 8 | 28 | 17 | 13759.8679
2028 | 2008 | 8 | 28 | 18 | 15010.4306
2028 | 2008 | 8 | 28 | 19 | 14782.7508
2028 | 2008 | 8 | 28 | 20 | 14172.9621
2028 | 2008 | 8 | 28 | 21 | 14109.3173
2028 | 2008 | 8 | 28 | 22 | 14120.3756
2028 | 2008 | 8 | 28 | 23 | 13467.666
2028 | 2008 | 8 | 28 | 24 | 11857.0433
2028 | 2008 | 8 | 29 | 1 | 10448.7517
2028 | 2008 | 8 | 29 | 2 | 9055.2921
2028 | 2008 | 8 | 29 | 3 | 7560.8181
2028 | 2008 | 8 | 29 | 4 | 5659.0208
2028 | 2008 | 8 | 29 | 5 | 3876.8952
2028 | 2008 | 8 | 29 | 6 | 3142.5529
2028 | 2008 | 8 | 29 | 7 | 2878.4401
2028 | 2008 | 8 | 29 | 8 | 2901.1602
2028 | 2008 | 8 | 29 | 9 | 4414.4722
2028 | 2008 | 8 | 29 | 10 | 5123.873
2028 | 2008 | 8 | 29 | 11 | 5166.54
2028 | 2008 | 8 | 29 | 12 | 5772.6173
2028 | 2008 | 8 | 29 | 13 | 8303.8376
2028 | 2008 | 8 | 29 | 14 | 10276.852
2028 | 2008 | 8 | 29 | 15 | 12473.9049
2028 | 2008 | 8 | 29 | 16 | 12795.4191
2028 | 2008 | 8 | 29 | 17 | 12630.5531
2028 | 2008 | 8 | 29 | 18 | 12331.4686
2028 | 2008 | 8 | 29 | 19 | 11711.963
2028 | 2008 | 8 | 29 | 20 | 10663.5284
2028 | 2008 | 8 | 29 | 21 | 10331.0636
2028 | 2008 | 8 | 29 | 22 | 9642.4042
2028 | 2008 | 8 | 29 | 23 | 8475.2084
2028 | 2008 | 8 | 29 | 24 | 6752.8096
2028 | 2008 | 8 | 30 | 1 | 4999.9772
2028 | 2008 | 8 | 30 | 2 | 3479.3004
2028 | 2008 | 8 | 30 | 3 | 2844.1008
2028 | 2008 | 8 | 30 | 4 | 2417.0932
2028 | 2008 | 8 | 30 | 5 | 2174.9037
2028 | 2008 | 8 | 30 | 6 | 1902.0325
2028 | 2008 | 8 | 30 | 7 | 2311.7313
2028 | 2008 | 8 | 30 | 8 | 2354.9331
2028 | 2008 | 8 | 30 | 9 | 3452.4149
2028 | 2008 | 8 | 30 | 10 | 4662.9459
2028 | 2008 | 8 | 30 | 11 | 7359.8489
2028 | 2008 | 8 | 30 | 12 | 10451.4332
2028 | 2008 | 8 | 30 | 13 | 14165.0704
2028 | 2008 | 8 | 30 | 14 | 17124.6334
2028 | 2008 | 8 | 30 | 15 | 18786.4966
2028 | 2008 | 8 | 30 | 16 | 18815.7553
2028 | 2008 | 8 | 30 | 17 | 19057.0319
2028 | 2008 | 8 | 30 | 18 | 18958.5118
2028 | 2008 | 8 | 30 | 19 | 16998.2838
2028 | 2008 | 8 | 30 | 20 | 14551.6028
2028 | 2008 | 8 | 30 | 21 | 12925.6786
2028 | 2008 | 8 | 30 | 22 | 11194.353
2028 | 2008 | 8 | 30 | 23 | 10306.1449
2028 | 2008 | 8 | 30 | 24 | 10102.9553
2028 | 2008 | 8 | 31 | 1 | 9854.9215
2028 | 2008 | 8 | 31 | 2 | 9316.3494
2028 | 2008 | 8 | 31 | 3 | 9233.7884
2028 | 2008 | 8 | 31 | 4 | 8560.6776
2028 | 2008 | 8 | 31 | 5 | 8040.5764
2028 | 2008 | 8 | 31 | 6 | 8069.2586
2028 | 2008 | 8 | 31 | 7 | 8085.4519
2028 | 2008 | 8 | 31 | 8 | 6566.7229
2028 | 2008 | 8 | 31 | 9 | 6368.7502
2028 | 2008 | 8 | 31 | 10 | 8494.7444
2028 | 2008 | 8 | 31 | 11 | 10444.1016
2028 | 2008 | 8 | 31 | 12 | 10777.1879
2028 | 2008 | 8 | 31 | 13 | 11593.7903
2028 | 2008 | 8 | 31 | 14 | 12349.8171
2028 | 2008 | 8 | 31 | 15 | 12325.5233
2028 | 2008 | 8 | 31 | 16 | 12841.7804
2028 | 2008 | 8 | 31 | 17 | 14033.9976
2028 | 2008 | 8 | 31 | 18 | 15760.4218
2028 | 2008 | 8 | 31 | 19 | 13700.3825
2028 | 2008 | 8 | 31 | 20 | 14070.3741
2028 | 2008 | 8 | 31 | 21 | 15207.8369
2028 | 2008 | 8 | 31 | 22 | 15893.9066
2028 | 2008 | 8 | 31 | 23 | 16227.2537
2028 | 2008 | 8 | 31 | 24 | 16795.0575
2029 | 2008 | 8 | 1 | 1 | 13245.2873
2029 | 2008 | 8 | 1 | 2 | 12269.9683
2029 | 2008 | 8 | 1 | 3 | 11108.413
2029 | 2008 | 8 | 1 | 4 | 10200.383
2029 | 2008 | 8 | 1 | 5 | 9823.1042
2029 | 2008 | 8 | 1 | 6 | 9156.5714
2029 | 2008 | 8 | 1 | 7 | 8436.465
2029 | 2008 | 8 | 1 | 8 | 6644.8091
2029 | 2008 | 8 | 1 | 9 | 6781.3632
2029 | 2008 | 8 | 1 | 10 | 6065.2681
2029 | 2008 | 8 | 1 | 11 | 4077.5093
2029 | 2008 | 8 | 1 | 12 | 4442.3165
2029 | 2008 | 8 | 1 | 13 | 5129.6779
2029 | 2008 | 8 | 1 | 14 | 6531.7815
2029 | 2008 | 8 | 1 | 15 | 8268.8489
2029 | 2008 | 8 | 1 | 16 | 10044.1409
2029 | 2008 | 8 | 1 | 17 | 10882.1117
2029 | 2008 | 8 | 1 | 18 | 12495.7116
2029 | 2008 | 8 | 1 | 19 | 12390.1082
2029 | 2008 | 8 | 1 | 20 | 12447.6483
2029 | 2008 | 8 | 1 | 21 | 13558.5595
2029 | 2008 | 8 | 1 | 22 | 13907.5372
2029 | 2008 | 8 | 1 | 23 | 14700.4284
2029 | 2008 | 8 | 1 | 24 | 14790.1276
2029 | 2008 | 8 | 2 | 1 | 14273.2273
2029 | 2008 | 8 | 2 | 2 | 13549.9667
2029 | 2008 | 8 | 2 | 3 | 13382.1539
2029 | 2008 | 8 | 2 | 4 | 12432.7118
2029 | 2008 | 8 | 2 | 5 | 11258.6825
2029 | 2008 | 8 | 2 | 6 | 11002.6092
2029 | 2008 | 8 | 2 | 7 | 10764.4251
2029 | 2008 | 8 | 2 | 8 | 8086.2954
2029 | 2008 | 8 | 2 | 9 | 7742.1121
2029 | 2008 | 8 | 2 | 10 | 9760.1325
2029 | 2008 | 8 | 2 | 11 | 7818.3673
2029 | 2008 | 8 | 2 | 12 | 6737.6261
2029 | 2008 | 8 | 2 | 13 | 7414.2273
2029 | 2008 | 8 | 2 | 14 | 8799.7205
2029 | 2008 | 8 | 2 | 15 | 10478.477
2029 | 2008 | 8 | 2 | 16 | 11893.1919
2029 | 2008 | 8 | 2 | 17 | 13924.3331
2029 | 2008 | 8 | 2 | 18 | 16550.4149
2029 | 2008 | 8 | 2 | 19 | 17751.9109
2029 | 2008 | 8 | 2 | 20 | 19191.3117
2029 | 2008 | 8 | 2 | 21 | 21548.8192
2029 | 2008 | 8 | 2 | 22 | 23370.2518
2029 | 2008 | 8 | 2 | 23 | 23837.6552
2029 | 2008 | 8 | 2 | 24 | 23124.815
2029 | 2008 | 8 | 3 | 1 | 21866.2245
2029 | 2008 | 8 | 3 | 2 | 21490.8059
2029 | 2008 | 8 | 3 | 3 | 21664.5976
2029 | 2008 | 8 | 3 | 4 | 21410.5348
2029 | 2008 | 8 | 3 | 5 | 20738.8983
2029 | 2008 | 8 | 3 | 6 | 19220.0932
2029 | 2008 | 8 | 3 | 7 | 18122.6412
2029 | 2008 | 8 | 3 | 8 | 13333.8116
2029 | 2008 | 8 | 3 | 9 | 11371.0336
2029 | 2008 | 8 | 3 | 10 | 13247.3994
2029 | 2008 | 8 | 3 | 11 | 11801.5553
2029 | 2008 | 8 | 3 | 12 | 11456.636
2029 | 2008 | 8 | 3 | 13 | 12817.048
2029 | 2008 | 8 | 3 | 14 | 13345.8497
2029 | 2008 | 8 | 3 | 15 | 13488.6958
2029 | 2008 | 8 | 3 | 16 | 13207.7831
2029 | 2008 | 8 | 3 | 17 | 13780.1038
2029 | 2008 | 8 | 3 | 18 | 14985.1405
2029 | 2008 | 8 | 3 | 19 | 16215.0643
2029 | 2008 | 8 | 3 | 20 | 18744.4324
2029 | 2008 | 8 | 3 | 21 | 21822.3532
2029 | 2008 | 8 | 3 | 22 | 23937.8055
2029 | 2008 | 8 | 3 | 23 | 24554.224
2029 | 2008 | 8 | 3 | 24 | 24305.3665
2029 | 2008 | 8 | 4 | 1 | 22918.5394
2029 | 2008 | 8 | 4 | 2 | 21766.7739
2029 | 2008 | 8 | 4 | 3 | 21088.3728
2029 | 2008 | 8 | 4 | 4 | 19329.642
2029 | 2008 | 8 | 4 | 5 | 17254.3711
2029 | 2008 | 8 | 4 | 6 | 14245.6996
2029 | 2008 | 8 | 4 | 7 | 11119.1449
2029 | 2008 | 8 | 4 | 8 | 6979.3084
2029 | 2008 | 8 | 4 | 9 | 4423.6583
2029 | 2008 | 8 | 4 | 10 | 5293.8563
2029 | 2008 | 8 | 4 | 11 | 4524.7369
2029 | 2008 | 8 | 4 | 12 | 3595.0066
2029 | 2008 | 8 | 4 | 13 | 4004.304
2029 | 2008 | 8 | 4 | 14 | 5272.6379
2029 | 2008 | 8 | 4 | 15 | 5951.2626
2029 | 2008 | 8 | 4 | 16 | 6015.4396
2029 | 2008 | 8 | 4 | 17 | 7095.4784
2029 | 2008 | 8 | 4 | 18 | 8136.1262
2029 | 2008 | 8 | 4 | 19 | 9337.3359
2029 | 2008 | 8 | 4 | 20 | 11525.0642
2029 | 2008 | 8 | 4 | 21 | 14987.8047
2029 | 2008 | 8 | 4 | 22 | 17870.4671
2029 | 2008 | 8 | 4 | 23 | 17998.1292
2029 | 2008 | 8 | 4 | 24 | 16147.4949
2029 | 2008 | 8 | 5 | 1 | 14354.6054
2029 | 2008 | 8 | 5 | 2 | 12945.1011
2029 | 2008 | 8 | 5 | 3 | 11679.0102
2029 | 2008 | 8 | 5 | 4 | 9745.3863
2029 | 2008 | 8 | 5 | 5 | 8191.0339
2029 | 2008 | 8 | 5 | 6 | 6952.2099
2029 | 2008 | 8 | 5 | 7 | 5842.7884
2029 | 2008 | 8 | 5 | 8 | 3197.948
2029 | 2008 | 8 | 5 | 9 | 2205.6368
2029 | 2008 | 8 | 5 | 10 | 1808.7148
2029 | 2008 | 8 | 5 | 11 | 1880.9622
2029 | 2008 | 8 | 5 | 12 | 1695.101
2029 | 2008 | 8 | 5 | 13 | 2573.4914
2029 | 2008 | 8 | 5 | 14 | 3726.8465
2029 | 2008 | 8 | 5 | 15 | 6165.1015
2029 | 2008 | 8 | 5 | 16 | 7879.8679
2029 | 2008 | 8 | 5 | 17 | 10517.1725
2029 | 2008 | 8 | 5 | 18 | 13388.1785
2029 | 2008 | 8 | 5 | 19 | 15775.2951
2029 | 2008 | 8 | 5 | 20 | 18295.0202
2029 | 2008 | 8 | 5 | 21 | 21441.4784
2029 | 2008 | 8 | 5 | 22 | 21993.7957
2029 | 2008 | 8 | 5 | 23 | 20587.4773
2029 | 2008 | 8 | 5 | 24 | 19045.9941
2029 | 2008 | 8 | 6 | 1 | 17078.5641
2029 | 2008 | 8 | 6 | 2 | 14279.451
2029 | 2008 | 8 | 6 | 3 | 11294.6877
2029 | 2008 | 8 | 6 | 4 | 9312.5035
2029 | 2008 | 8 | 6 | 5 | 7862.5506
2029 | 2008 | 8 | 6 | 6 | 6738.1769
2029 | 2008 | 8 | 6 | 7 | 5743.8457
2029 | 2008 | 8 | 6 | 8 | 5194.8046
2029 | 2008 | 8 | 6 | 9 | 6570.5837
2029 | 2008 | 8 | 6 | 10 | 8526.039
2029 | 2008 | 8 | 6 | 11 | 9474.414
2029 | 2008 | 8 | 6 | 12 | 10500.1518
2029 | 2008 | 8 | 6 | 13 | 12271.5864
2029 | 2008 | 8 | 6 | 14 | 12830.0447
2029 | 2008 | 8 | 6 | 15 | 13834.0306
2029 | 2008 | 8 | 6 | 16 | 13454.8797
2029 | 2008 | 8 | 6 | 17 | 14439.5679
2029 | 2008 | 8 | 6 | 18 | 14941.6708
2029 | 2008 | 8 | 6 | 19 | 15302.2028
2029 | 2008 | 8 | 6 | 20 | 15217.5527
2029 | 2008 | 8 | 6 | 21 | 16135.0085
2029 | 2008 | 8 | 6 | 22 | 16283.7616
2029 | 2008 | 8 | 6 | 23 | 15464.1272
2029 | 2008 | 8 | 6 | 24 | 14611.6856
2029 | 2008 | 8 | 7 | 1 | 13341.3702
2029 | 2008 | 8 | 7 | 2 | 11932.7156
2029 | 2008 | 8 | 7 | 3 | 11409.468
2029 | 2008 | 8 | 7 | 4 | 10668.3534
2029 | 2008 | 8 | 7 | 5 | 9534.1937
2029 | 2008 | 8 | 7 | 6 | 8477.8846
2029 | 2008 | 8 | 7 | 7 | 7925.95
2029 | 2008 | 8 | 7 | 8 | 6700.3332
2029 | 2008 | 8 | 7 | 9 | 7378.3653
2029 | 2008 | 8 | 7 | 10 | 7384.087
2029 | 2008 | 8 | 7 | 11 | 7137.1827
2029 | 2008 | 8 | 7 | 12 | 7070.0939
2029 | 2008 | 8 | 7 | 13 | 7456.8912
2029 | 2008 | 8 | 7 | 14 | 8163.1847
2029 | 2008 | 8 | 7 | 15 | 9113.7163
2029 | 2008 | 8 | 7 | 16 | 9164.5088
2029 | 2008 | 8 | 7 | 17 | 10045.4853
2029 | 2008 | 8 | 7 | 18 | 10946.7451
2029 | 2008 | 8 | 7 | 19 | 11613.8187
2029 | 2008 | 8 | 7 | 20 | 11566.0471
2029 | 2008 | 8 | 7 | 21 | 12168.7744
2029 | 2008 | 8 | 7 | 22 | 13195.3011
2029 | 2008 | 8 | 7 | 23 | 13437.819
2029 | 2008 | 8 | 7 | 24 | 14267.0334
2029 | 2008 | 8 | 8 | 1 | 14486.5834
2029 | 2008 | 8 | 8 | 2 | 14404.2054
2029 | 2008 | 8 | 8 | 3 | 13940.5245
2029 | 2008 | 8 | 8 | 4 | 12579.1836
2029 | 2008 | 8 | 8 | 5 | 11428.9016
2029 | 2008 | 8 | 8 | 6 | 10811.2804
2029 | 2008 | 8 | 8 | 7 | 10013.125
2029 | 2008 | 8 | 8 | 8 | 6651.6008
2029 | 2008 | 8 | 8 | 9 | 5469.096
2029 | 2008 | 8 | 8 | 10 | 6249.1754
2029 | 2008 | 8 | 8 | 11 | 5327.2741
2029 | 2008 | 8 | 8 | 12 | 4411.2291
2029 | 2008 | 8 | 8 | 13 | 4805.327
2029 | 2008 | 8 | 8 | 14 | 6268.537
2029 | 2008 | 8 | 8 | 15 | 8222.7779
2029 | 2008 | 8 | 8 | 16 | 9986.3634
2029 | 2008 | 8 | 8 | 17 | 11252.2243
2029 | 2008 | 8 | 8 | 18 | 12139.5837
2029 | 2008 | 8 | 8 | 19 | 13797.8974
2029 | 2008 | 8 | 8 | 20 | 15296.8209
2029 | 2008 | 8 | 8 | 21 | 18076.6646
2029 | 2008 | 8 | 8 | 22 | 20271.8016
2029 | 2008 | 8 | 8 | 23 | 21989.4409
2029 | 2008 | 8 | 8 | 24 | 21872.43
2029 | 2008 | 8 | 9 | 1 | 20666.2857
2029 | 2008 | 8 | 9 | 2 | 20005.0524
2029 | 2008 | 8 | 9 | 3 | 19156.8932
2029 | 2008 | 8 | 9 | 4 | 18785.8625
2029 | 2008 | 8 | 9 | 5 | 18557.4229
2029 | 2008 | 8 | 9 | 6 | 18825.314
2029 | 2008 | 8 | 9 | 7 | 18554.862
2029 | 2008 | 8 | 9 | 8 | 14770.151
2029 | 2008 | 8 | 9 | 9 | 13265.3466
2029 | 2008 | 8 | 9 | 10 | 14897.5745
2029 | 2008 | 8 | 9 | 11 | 14149.0374
2029 | 2008 | 8 | 9 | 12 | 14258.1066
2029 | 2008 | 8 | 9 | 13 | 16465.2671
2029 | 2008 | 8 | 9 | 14 | 17888.5455
2029 | 2008 | 8 | 9 | 15 | 19367.4111
2029 | 2008 | 8 | 9 | 16 | 19562.9103
2029 | 2008 | 8 | 9 | 17 | 21022.4613
2029 | 2008 | 8 | 9 | 18 | 22966.5302
2029 | 2008 | 8 | 9 | 19 | 23465.7517
2029 | 2008 | 8 | 9 | 20 | 24713.3958
2029 | 2008 | 8 | 9 | 21 | 26500.3117
2029 | 2008 | 8 | 9 | 22 | 28335.9214
2029 | 2008 | 8 | 9 | 23 | 29124.8881
2029 | 2008 | 8 | 9 | 24 | 29620.8386
2029 | 2008 | 8 | 10 | 1 | 28891.6511
2029 | 2008 | 8 | 10 | 2 | 28947.8788
2029 | 2008 | 8 | 10 | 3 | 29557.782
2029 | 2008 | 8 | 10 | 4 | 29572.7041
2029 | 2008 | 8 | 10 | 5 | 29385.8551
2029 | 2008 | 8 | 10 | 6 | 29223.5092
2029 | 2008 | 8 | 10 | 7 | 27240.6233
2029 | 2008 | 8 | 10 | 8 | 24502.6477
2029 | 2008 | 8 | 10 | 9 | 25867.7834
2029 | 2008 | 8 | 10 | 10 | 25228.2076
2029 | 2008 | 8 | 10 | 11 | 20721.5638
2029 | 2008 | 8 | 10 | 12 | 17688.8033
2029 | 2008 | 8 | 10 | 13 | 15761.349
2029 | 2008 | 8 | 10 | 14 | 14926.0587
2029 | 2008 | 8 | 10 | 15 | 13895.8159
2029 | 2008 | 8 | 10 | 16 | 13990.2578
2029 | 2008 | 8 | 10 | 17 | 15957.1377
2029 | 2008 | 8 | 10 | 18 | 19644.4929
2029 | 2008 | 8 | 10 | 19 | 21977.0954
2029 | 2008 | 8 | 10 | 20 | 21254.1206
2029 | 2008 | 8 | 10 | 21 | 21020.1521
2029 | 2008 | 8 | 10 | 22 | 20170.4333
2029 | 2008 | 8 | 10 | 23 | 20263.9167
2029 | 2008 | 8 | 10 | 24 | 18041.897
2029 | 2008 | 8 | 11 | 1 | 16483.399
2029 | 2008 | 8 | 11 | 2 | 16257.7918
2029 | 2008 | 8 | 11 | 3 | 15882.3758
2029 | 2008 | 8 | 11 | 4 | 15064.2089
2029 | 2008 | 8 | 11 | 5 | 13966.5397
2029 | 2008 | 8 | 11 | 6 | 13340.6151
2029 | 2008 | 8 | 11 | 7 | 12476.6479
2029 | 2008 | 8 | 11 | 8 | 11562.2326
2029 | 2008 | 8 | 11 | 9 | 14366.6066
2029 | 2008 | 8 | 11 | 10 | 14588.5603
2029 | 2008 | 8 | 11 | 11 | 13732.5445
2029 | 2008 | 8 | 11 | 12 | 13457.7308
2029 | 2008 | 8 | 11 | 13 | 13270.7397
2029 | 2008 | 8 | 11 | 14 | 13353.6898
2029 | 2008 | 8 | 11 | 15 | 12940.1908
2029 | 2008 | 8 | 11 | 16 | 12691.8561
2029 | 2008 | 8 | 11 | 17 | 13207.5727
2029 | 2008 | 8 | 11 | 18 | 13092.8149
2029 | 2008 | 8 | 11 | 19 | 13601.3089
2029 | 2008 | 8 | 11 | 20 | 12919.599
2029 | 2008 | 8 | 11 | 21 | 12848.6015
2029 | 2008 | 8 | 11 | 22 | 11253.7721
2029 | 2008 | 8 | 11 | 23 | 10515.0667
2029 | 2008 | 8 | 11 | 24 | 9934.2472
2029 | 2008 | 8 | 12 | 1 | 9891.111
2029 | 2008 | 8 | 12 | 2 | 10043.0903
2029 | 2008 | 8 | 12 | 3 | 9826.5142
2029 | 2008 | 8 | 12 | 4 | 9630.5543
2029 | 2008 | 8 | 12 | 5 | 8721.8338
2029 | 2008 | 8 | 12 | 6 | 8241.9611
2029 | 2008 | 8 | 12 | 7 | 7572.964
2029 | 2008 | 8 | 12 | 8 | 6200.0084
2029 | 2008 | 8 | 12 | 9 | 7370.4751
2029 | 2008 | 8 | 12 | 10 | 7658.9772
2029 | 2008 | 8 | 12 | 11 | 7194.4374
2029 | 2008 | 8 | 12 | 12 | 6614.8785
2029 | 2008 | 8 | 12 | 13 | 7683.1165
2029 | 2008 | 8 | 12 | 14 | 8755.8996
2029 | 2008 | 8 | 12 | 15 | 9528.0468
2029 | 2008 | 8 | 12 | 16 | 9991.0744
2029 | 2008 | 8 | 12 | 17 | 10353.1192
2029 | 2008 | 8 | 12 | 18 | 11066.0909
2029 | 2008 | 8 | 12 | 19 | 11625.0904
2029 | 2008 | 8 | 12 | 20 | 10864.3927
2029 | 2008 | 8 | 12 | 21 | 10776.2549
2029 | 2008 | 8 | 12 | 22 | 10622.0344
2029 | 2008 | 8 | 12 | 23 | 10074.7138
2029 | 2008 | 8 | 12 | 24 | 9147.7716
2029 | 2008 | 8 | 13 | 1 | 7886.3838
2029 | 2008 | 8 | 13 | 2 | 7261.8015
2029 | 2008 | 8 | 13 | 3 | 7035.8994
2029 | 2008 | 8 | 13 | 4 | 6800.2882
2029 | 2008 | 8 | 13 | 5 | 5849.3338
2029 | 2008 | 8 | 13 | 6 | 4801.1515
2029 | 2008 | 8 | 13 | 7 | 3648.6645
2029 | 2008 | 8 | 13 | 8 | 2314.3648
2029 | 2008 | 8 | 13 | 9 | 2668.5531
2029 | 2008 | 8 | 13 | 10 | 2785.4192
2029 | 2008 | 8 | 13 | 11 | 2361.3902
2029 | 2008 | 8 | 13 | 12 | 2402.9416
2029 | 2008 | 8 | 13 | 13 | 2408.4356
2029 | 2008 | 8 | 13 | 14 | 2890.0843
2029 | 2008 | 8 | 13 | 15 | 3910.7273
2029 | 2008 | 8 | 13 | 16 | 4692.8144
2029 | 2008 | 8 | 13 | 17 | 6086.2869
2029 | 2008 | 8 | 13 | 18 | 8136.6004
2029 | 2008 | 8 | 13 | 19 | 9277.9722
2029 | 2008 | 8 | 13 | 20 | 10201.3988
2029 | 2008 | 8 | 13 | 21 | 11830.0102
2029 | 2008 | 8 | 13 | 22 | 12204.1146
2029 | 2008 | 8 | 13 | 23 | 11399.8912
2029 | 2008 | 8 | 13 | 24 | 10285.5766
2029 | 2008 | 8 | 14 | 1 | 9501.7821
2029 | 2008 | 8 | 14 | 2 | 9213.9941
2029 | 2008 | 8 | 14 | 3 | 8909.3423
2029 | 2008 | 8 | 14 | 4 | 8774.6439
2029 | 2008 | 8 | 14 | 5 | 7923.2554
2029 | 2008 | 8 | 14 | 6 | 7278.1137
2029 | 2008 | 8 | 14 | 7 | 6311.2421
2029 | 2008 | 8 | 14 | 8 | 4294.0664
2029 | 2008 | 8 | 14 | 9 | 3876.9818
2029 | 2008 | 8 | 14 | 10 | 4065.6397
2029 | 2008 | 8 | 14 | 11 | 5092.447
2029 | 2008 | 8 | 14 | 12 | 5361.2601
2029 | 2008 | 8 | 14 | 13 | 7080.3021
2029 | 2008 | 8 | 14 | 14 | 8357.0215
2029 | 2008 | 8 | 14 | 15 | 9468.0216
2029 | 2008 | 8 | 14 | 16 | 10052.6006
2029 | 2008 | 8 | 14 | 17 | 10838.6032
2029 | 2008 | 8 | 14 | 18 | 11885.3726
2029 | 2008 | 8 | 14 | 19 | 13269.875
2029 | 2008 | 8 | 14 | 20 | 14400.7022
2029 | 2008 | 8 | 14 | 21 | 16465.5953
2029 | 2008 | 8 | 14 | 22 | 20097.5321
2029 | 2008 | 8 | 14 | 23 | 23704.5471
2029 | 2008 | 8 | 14 | 24 | 24577.1633
2029 | 2008 | 8 | 15 | 1 | 23462.6477
2029 | 2008 | 8 | 15 | 2 | 21912.2964
2029 | 2008 | 8 | 15 | 3 | 20233.5977
2029 | 2008 | 8 | 15 | 4 | 17546.3564
2029 | 2008 | 8 | 15 | 5 | 13385.478
2029 | 2008 | 8 | 15 | 6 | 10487.5418
2029 | 2008 | 8 | 15 | 7 | 8240.8292
2029 | 2008 | 8 | 15 | 8 | 5407.9523
2029 | 2008 | 8 | 15 | 9 | 4928.389
2029 | 2008 | 8 | 15 | 10 | 6019.9552
2029 | 2008 | 8 | 15 | 11 | 6767.1297
2029 | 2008 | 8 | 15 | 12 | 7251.9658
2029 | 2008 | 8 | 15 | 13 | 8381.6646
2029 | 2008 | 8 | 15 | 14 | 8900.4389
2029 | 2008 | 8 | 15 | 15 | 8795.2569
2029 | 2008 | 8 | 15 | 16 | 8735.2268
2029 | 2008 | 8 | 15 | 17 | 9390.0178
2029 | 2008 | 8 | 15 | 18 | 10960.3451
2029 | 2008 | 8 | 15 | 19 | 11860.5992
2029 | 2008 | 8 | 15 | 20 | 13895.6101
2029 | 2008 | 8 | 15 | 21 | 16667.6423
2029 | 2008 | 8 | 15 | 22 | 18801.6876
2029 | 2008 | 8 | 15 | 23 | 18918.8931
2029 | 2008 | 8 | 15 | 24 | 18666.9593
2029 | 2008 | 8 | 16 | 1 | 17753.251
2029 | 2008 | 8 | 16 | 2 | 16606.7119
2029 | 2008 | 8 | 16 | 3 | 14144.5907
2029 | 2008 | 8 | 16 | 4 | 11827.0562
2029 | 2008 | 8 | 16 | 5 | 9612.0874
2029 | 2008 | 8 | 16 | 6 | 7810.1278
2029 | 2008 | 8 | 16 | 7 | 6030.7219
2029 | 2008 | 8 | 16 | 8 | 4997.5692
2029 | 2008 | 8 | 16 | 9 | 5786.557
2029 | 2008 | 8 | 16 | 10 | 7881.3724
2029 | 2008 | 8 | 16 | 11 | 8585.1221
2029 | 2008 | 8 | 16 | 12 | 9384.918
2029 | 2008 | 8 | 16 | 13 | 11163.8451
2029 | 2008 | 8 | 16 | 14 | 13908.3411
2029 | 2008 | 8 | 16 | 15 | 14761.1828
2029 | 2008 | 8 | 16 | 16 | 15701.752
2029 | 2008 | 8 | 16 | 17 | 17124.0495
2029 | 2008 | 8 | 16 | 18 | 17725.5019
2029 | 2008 | 8 | 16 | 19 | 17495.6419
2029 | 2008 | 8 | 16 | 20 | 15905.177
2029 | 2008 | 8 | 16 | 21 | 14846.6815
2029 | 2008 | 8 | 16 | 22 | 12691.8128
2029 | 2008 | 8 | 16 | 23 | 10438.929
2029 | 2008 | 8 | 16 | 24 | 8158.4526
2029 | 2008 | 8 | 17 | 1 | 6147.5693
2029 | 2008 | 8 | 17 | 2 | 4955.7394
2029 | 2008 | 8 | 17 | 3 | 4513.4601
2029 | 2008 | 8 | 17 | 4 | 4475.2908
2029 | 2008 | 8 | 17 | 5 | 4591.1501
2029 | 2008 | 8 | 17 | 6 | 5243.5151
2029 | 2008 | 8 | 17 | 7 | 5223.3057
2029 | 2008 | 8 | 17 | 8 | 5566.014
2029 | 2008 | 8 | 17 | 9 | 7117.0612
2029 | 2008 | 8 | 17 | 10 | 8990.4288
2029 | 2008 | 8 | 17 | 11 | 9226.5375
2029 | 2008 | 8 | 17 | 12 | 9548.1685
2029 | 2008 | 8 | 17 | 13 | 9102.5641
2029 | 2008 | 8 | 17 | 14 | 8749.6146
2029 | 2008 | 8 | 17 | 15 | 7640.5099
2029 | 2008 | 8 | 17 | 16 | 7611.7835
2029 | 2008 | 8 | 17 | 17 | 9047.7787
2029 | 2008 | 8 | 17 | 18 | 10647.5876
2029 | 2008 | 8 | 17 | 19 | 11888.7131
2029 | 2008 | 8 | 17 | 20 | 11427.5987
2029 | 2008 | 8 | 17 | 21 | 12139.3241
2029 | 2008 | 8 | 17 | 22 | 12479.7372
2029 | 2008 | 8 | 17 | 23 | 12567.3606
2029 | 2008 | 8 | 17 | 24 | 12485.5363
2029 | 2008 | 8 | 18 | 1 | 11688.5522
2029 | 2008 | 8 | 18 | 2 | 11154.2058
2029 | 2008 | 8 | 18 | 3 | 10599.4392
2029 | 2008 | 8 | 18 | 4 | 10818.9767
2029 | 2008 | 8 | 18 | 5 | 10681.0168
2029 | 2008 | 8 | 18 | 6 | 10855.721
2029 | 2008 | 8 | 18 | 7 | 10099.0627
2029 | 2008 | 8 | 18 | 8 | 9324.6156
2029 | 2008 | 8 | 18 | 9 | 11144.7247
2029 | 2008 | 8 | 18 | 10 | 12136.5629
2029 | 2008 | 8 | 18 | 11 | 11777.4155
2029 | 2008 | 8 | 18 | 12 | 11640.7103
2029 | 2008 | 8 | 18 | 13 | 12124.0914
2029 | 2008 | 8 | 18 | 14 | 12669.0478
2029 | 2008 | 8 | 18 | 15 | 13414.8827
2029 | 2008 | 8 | 18 | 16 | 13515.4236
2029 | 2008 | 8 | 18 | 17 | 15061.1701
2029 | 2008 | 8 | 18 | 18 | 15497.4562
2029 | 2008 | 8 | 18 | 19 | 15396.7128
2029 | 2008 | 8 | 18 | 20 | 14483.4361
2029 | 2008 | 8 | 18 | 21 | 14458.9057
2029 | 2008 | 8 | 18 | 22 | 14181.3848
2029 | 2008 | 8 | 18 | 23 | 13115.7577
2029 | 2008 | 8 | 18 | 24 | 12022.3009
2029 | 2008 | 8 | 19 | 1 | 11341.5912
2029 | 2008 | 8 | 19 | 2 | 11040.7591
2029 | 2008 | 8 | 19 | 3 | 11830.854
2029 | 2008 | 8 | 19 | 4 | 13141.6804
2029 | 2008 | 8 | 19 | 5 | 13828.1592
2029 | 2008 | 8 | 19 | 6 | 14478.5744
2029 | 2008 | 8 | 19 | 7 | 14682.2313
2029 | 2008 | 8 | 19 | 8 | 13396.0397
2029 | 2008 | 8 | 19 | 9 | 15670.1488
2029 | 2008 | 8 | 19 | 10 | 14761.6477
2029 | 2008 | 8 | 19 | 11 | 11815.1435
2029 | 2008 | 8 | 19 | 12 | 11386.4355
2029 | 2008 | 8 | 19 | 13 | 12069.4269
2029 | 2008 | 8 | 19 | 14 | 12969.2013
2029 | 2008 | 8 | 19 | 15 | 14563.4832
2029 | 2008 | 8 | 19 | 16 | 15551.6385
2029 | 2008 | 8 | 19 | 17 | 17094.1289
2029 | 2008 | 8 | 19 | 18 | 17079.2959
2029 | 2008 | 8 | 19 | 19 | 17021.5952
2029 | 2008 | 8 | 19 | 20 | 15736.3503
2029 | 2008 | 8 | 19 | 21 | 14980.6587
2029 | 2008 | 8 | 19 | 22 | 13330.1685
2029 | 2008 | 8 | 19 | 23 | 10721.9899
2029 | 2008 | 8 | 19 | 24 | 8794.9274
2029 | 2008 | 8 | 20 | 1 | 7009.9237
2029 | 2008 | 8 | 20 | 2 | 6007.5706
2029 | 2008 | 8 | 20 | 3 | 5974.8107
2029 | 2008 | 8 | 20 | 4 | 5848.7962
2029 | 2008 | 8 | 20 | 5 | 5590.5983
2029 | 2008 | 8 | 20 | 6 | 5405.8263
2029 | 2008 | 8 | 20 | 7 | 5419.4519
2029 | 2008 | 8 | 20 | 8 | 4714.2609
2029 | 2008 | 8 | 20 | 9 | 5642.9186
2029 | 2008 | 8 | 20 | 10 | 5702.2472
2029 | 2008 | 8 | 20 | 11 | 5119.5593
2029 | 2008 | 8 | 20 | 12 | 5072.6529
2029 | 2008 | 8 | 20 | 13 | 5658.1756
2029 | 2008 | 8 | 20 | 14 | 6465.439
2029 | 2008 | 8 | 20 | 15 | 6997.5467
2029 | 2008 | 8 | 20 | 16 | 7168.0141
2029 | 2008 | 8 | 20 | 17 | 6690.5688
2029 | 2008 | 8 | 20 | 18 | 5934.5425
2029 | 2008 | 8 | 20 | 19 | 5138.6168
2029 | 2008 | 8 | 20 | 20 | 5054.67
2029 | 2008 | 8 | 20 | 21 | 5966.8249
2029 | 2008 | 8 | 20 | 22 | 7279.8179
2029 | 2008 | 8 | 20 | 23 | 8103.94
2029 | 2008 | 8 | 20 | 24 | 8418.603
2029 | 2008 | 8 | 21 | 1 | 8905.4733
2029 | 2008 | 8 | 21 | 2 | 8929.0516
2029 | 2008 | 8 | 21 | 3 | 8262.4865
2029 | 2008 | 8 | 21 | 4 | 7861.0787
2029 | 2008 | 8 | 21 | 5 | 7260.0672
2029 | 2008 | 8 | 21 | 6 | 6941.6464
2029 | 2008 | 8 | 21 | 7 | 6408.047
2029 | 2008 | 8 | 21 | 8 | 4730.476
2029 | 2008 | 8 | 21 | 9 | 4822.9254
2029 | 2008 | 8 | 21 | 10 | 5898.759
2029 | 2008 | 8 | 21 | 11 | 6937.995
2029 | 2008 | 8 | 21 | 12 | 7816.4429
2029 | 2008 | 8 | 21 | 13 | 8811.7711
2029 | 2008 | 8 | 21 | 14 | 10029.1719
2029 | 2008 | 8 | 21 | 15 | 10522.1492
2029 | 2008 | 8 | 21 | 16 | 10086.7013
2029 | 2008 | 8 | 21 | 17 | 10797.9069
2029 | 2008 | 8 | 21 | 18 | 12094.751
2029 | 2008 | 8 | 21 | 19 | 13709.1684
2029 | 2008 | 8 | 21 | 20 | 15944.0701
2029 | 2008 | 8 | 21 | 21 | 20025.5124
2029 | 2008 | 8 | 21 | 22 | 22808.0162
2029 | 2008 | 8 | 21 | 23 | 23923.0156
2029 | 2008 | 8 | 21 | 24 | 24144.7725
2029 | 2008 | 8 | 22 | 1 | 23380.1385
2029 | 2008 | 8 | 22 | 2 | 22799.7879
2029 | 2008 | 8 | 22 | 3 | 22860.7976
2029 | 2008 | 8 | 22 | 4 | 23073.7
2029 | 2008 | 8 | 22 | 5 | 23048.298
2029 | 2008 | 8 | 22 | 6 | 23710.0594
2029 | 2008 | 8 | 22 | 7 | 23997.846
2029 | 2008 | 8 | 22 | 8 | 21624.0668
2029 | 2008 | 8 | 22 | 9 | 22705.3572
2029 | 2008 | 8 | 22 | 10 | 23849.1294
2029 | 2008 | 8 | 22 | 11 | 21745.7246
2029 | 2008 | 8 | 22 | 12 | 20749.9502
2029 | 2008 | 8 | 22 | 13 | 22057.7959
2029 | 2008 | 8 | 22 | 14 | 22382.2785
2029 | 2008 | 8 | 22 | 15 | 21670.2038
2029 | 2008 | 8 | 22 | 16 | 19863.587
2029 | 2008 | 8 | 22 | 17 | 18795.667
2029 | 2008 | 8 | 22 | 18 | 19045.6784
2029 | 2008 | 8 | 22 | 19 | 18865.039
2029 | 2008 | 8 | 22 | 20 | 20374.6193
2029 | 2008 | 8 | 22 | 21 | 21882.002
2029 | 2008 | 8 | 22 | 22 | 23021.0768
2029 | 2008 | 8 | 22 | 23 | 22492.3452
2029 | 2008 | 8 | 22 | 24 | 20978.6646
2029 | 2008 | 8 | 23 | 1 | 17845.4606
2029 | 2008 | 8 | 23 | 2 | 15542.7666
2029 | 2008 | 8 | 23 | 3 | 13115.2883
2029 | 2008 | 8 | 23 | 4 | 10893.5452
2029 | 2008 | 8 | 23 | 5 | 8837.0859
2029 | 2008 | 8 | 23 | 6 | 6712.8748
2029 | 2008 | 8 | 23 | 7 | 5206.634
2029 | 2008 | 8 | 23 | 8 | 3698.7739
2029 | 2008 | 8 | 23 | 9 | 4457.8076
2029 | 2008 | 8 | 23 | 10 | 5010.5544
2029 | 2008 | 8 | 23 | 11 | 4636.8199
2029 | 2008 | 8 | 23 | 12 | 4387.1996
2029 | 2008 | 8 | 23 | 13 | 5285.2604
2029 | 2008 | 8 | 23 | 14 | 6280.6376
2029 | 2008 | 8 | 23 | 15 | 7167.7875
2029 | 2008 | 8 | 23 | 16 | 7643.8332
2029 | 2008 | 8 | 23 | 17 | 8291.1334
2029 | 2008 | 8 | 23 | 18 | 8438.5906
2029 | 2008 | 8 | 23 | 19 | 7732.2839
2029 | 2008 | 8 | 23 | 20 | 6514.3841
2029 | 2008 | 8 | 23 | 21 | 6044.7968
2029 | 2008 | 8 | 23 | 22 | 5025.602
2029 | 2008 | 8 | 23 | 23 | 3625.6458
2029 | 2008 | 8 | 23 | 24 | 2868.0901
2029 | 2008 | 8 | 24 | 1 | 2264.7679
2029 | 2008 | 8 | 24 | 2 | 1514.4573
2029 | 2008 | 8 | 24 | 3 | 1126.6933
2029 | 2008 | 8 | 24 | 4 | 864.3561
2029 | 2008 | 8 | 24 | 5 | 810.7621
2029 | 2008 | 8 | 24 | 6 | 768.6248
2029 | 2008 | 8 | 24 | 7 | 874.3706
2029 | 2008 | 8 | 24 | 8 | 590.5288
2029 | 2008 | 8 | 24 | 9 | 906.8839
2029 | 2008 | 8 | 24 | 10 | 1054.3108
2029 | 2008 | 8 | 24 | 11 | 1577.7493
2029 | 2008 | 8 | 24 | 12 | 2218.767
2029 | 2008 | 8 | 24 | 13 | 3200.8714
2029 | 2008 | 8 | 24 | 14 | 3321.1256
2029 | 2008 | 8 | 24 | 15 | 4137.9828
2029 | 2008 | 8 | 24 | 16 | 4497.518
2029 | 2008 | 8 | 24 | 17 | 4921.7547
2029 | 2008 | 8 | 24 | 18 | 5354.4504
2029 | 2008 | 8 | 24 | 19 | 5257.8269
2029 | 2008 | 8 | 24 | 20 | 4506.6665
2029 | 2008 | 8 | 24 | 21 | 4372.8768
2029 | 2008 | 8 | 24 | 22 | 4270.8209
2029 | 2008 | 8 | 24 | 23 | 3848.4425
2029 | 2008 | 8 | 24 | 24 | 3517.0326
2029 | 2008 | 8 | 25 | 1 | 3370.5043
2029 | 2008 | 8 | 25 | 2 | 3346.8259
2029 | 2008 | 8 | 25 | 3 | 3452.7518
2029 | 2008 | 8 | 25 | 4 | 3519.5599
2029 | 2008 | 8 | 25 | 5 | 3667.2501
2029 | 2008 | 8 | 25 | 6 | 3558.5899
2029 | 2008 | 8 | 25 | 7 | 3252.8197
2029 | 2008 | 8 | 25 | 8 | 2387.7161
2029 | 2008 | 8 | 25 | 9 | 2209.2703
2029 | 2008 | 8 | 25 | 10 | 1928.0274
2029 | 2008 | 8 | 25 | 11 | 1369.5184
2029 | 2008 | 8 | 25 | 12 | 1220.3985
2029 | 2008 | 8 | 25 | 13 | 1659.7827
2029 | 2008 | 8 | 25 | 14 | 2288.1808
2029 | 2008 | 8 | 25 | 15 | 2834.9708
2029 | 2008 | 8 | 25 | 16 | 3015.0414
2029 | 2008 | 8 | 25 | 17 | 3376.1983
2029 | 2008 | 8 | 25 | 18 | 3774.4771
2029 | 2008 | 8 | 25 | 19 | 4232.7927
2029 | 2008 | 8 | 25 | 20 | 4120.0063
2029 | 2008 | 8 | 25 | 21 | 4934.0695
2029 | 2008 | 8 | 25 | 22 | 5456.8336
2029 | 2008 | 8 | 25 | 23 | 5662.3132
2029 | 2008 | 8 | 25 | 24 | 5468.1893
2029 | 2008 | 8 | 26 | 1 | 5109.7205
2029 | 2008 | 8 | 26 | 2 | 5088.2164
2029 | 2008 | 8 | 26 | 3 | 5029.2189
2029 | 2008 | 8 | 26 | 4 | 4868.1473
2029 | 2008 | 8 | 26 | 5 | 4853.2034
2029 | 2008 | 8 | 26 | 6 | 4649.9917
2029 | 2008 | 8 | 26 | 7 | 3840.3562
2029 | 2008 | 8 | 26 | 8 | 2431.7077
2029 | 2008 | 8 | 26 | 9 | 1974.5839
2029 | 2008 | 8 | 26 | 10 | 2633.5597
2029 | 2008 | 8 | 26 | 11 | 3049.219
2029 | 2008 | 8 | 26 | 12 | 3356.6361
2029 | 2008 | 8 | 26 | 13 | 3726.5428
2029 | 2008 | 8 | 26 | 14 | 4004.074
2029 | 2008 | 8 | 26 | 15 | 4829.5723
2029 | 2008 | 8 | 26 | 16 | 5334.3592
2029 | 2008 | 8 | 26 | 17 | 6909.9643
2029 | 2008 | 8 | 26 | 18 | 8773.4647
2029 | 2008 | 8 | 26 | 19 | 10123.3448
2029 | 2008 | 8 | 26 | 20 | 11896.2504
2029 | 2008 | 8 | 26 | 21 | 14505.8856
2029 | 2008 | 8 | 26 | 22 | 16343.9094
2029 | 2008 | 8 | 26 | 23 | 16865.9557
2029 | 2008 | 8 | 26 | 24 | 16554.6687
2029 | 2008 | 8 | 27 | 1 | 15456.6927
2029 | 2008 | 8 | 27 | 2 | 14564.8495
2029 | 2008 | 8 | 27 | 3 | 13538.8998
2029 | 2008 | 8 | 27 | 4 | 12404.3787
2029 | 2008 | 8 | 27 | 5 | 11693.5136
2029 | 2008 | 8 | 27 | 6 | 11519.3137
2029 | 2008 | 8 | 27 | 7 | 11387.9423
2029 | 2008 | 8 | 27 | 8 | 8543.4074
2029 | 2008 | 8 | 27 | 9 | 7974.3519
2029 | 2008 | 8 | 27 | 10 | 7591.0263
2029 | 2008 | 8 | 27 | 11 | 9120.152
2029 | 2008 | 8 | 27 | 12 | 10704.2218
2029 | 2008 | 8 | 27 | 13 | 11870.0019
2029 | 2008 | 8 | 27 | 14 | 12780.5008
2029 | 2008 | 8 | 27 | 15 | 12905.2538
2029 | 2008 | 8 | 27 | 16 | 12189.8338
2029 | 2008 | 8 | 27 | 17 | 12907.7737
2029 | 2008 | 8 | 27 | 18 | 13855.4256
2029 | 2008 | 8 | 27 | 19 | 14182.8999
2029 | 2008 | 8 | 27 | 20 | 15016.4383
2029 | 2008 | 8 | 27 | 21 | 16722.3202
2029 | 2008 | 8 | 27 | 22 | 17895.3863
2029 | 2008 | 8 | 27 | 23 | 17773.7528
2029 | 2008 | 8 | 27 | 24 | 17407.4719
2029 | 2008 | 8 | 28 | 1 | 16571.2919
2029 | 2008 | 8 | 28 | 2 | 15743.5692
2029 | 2008 | 8 | 28 | 3 | 15344.8967
2029 | 2008 | 8 | 28 | 4 | 15247.5362
2029 | 2008 | 8 | 28 | 5 | 14812.731
2029 | 2008 | 8 | 28 | 6 | 14295.2569
2029 | 2008 | 8 | 28 | 7 | 13517.8111
2029 | 2008 | 8 | 28 | 8 | 10706.8901
2029 | 2008 | 8 | 28 | 9 | 10400.4426
2029 | 2008 | 8 | 28 | 10 | 8921.1891
2029 | 2008 | 8 | 28 | 11 | 8279.4842
2029 | 2008 | 8 | 28 | 12 | 8871.6988
2029 | 2008 | 8 | 28 | 13 | 9990.2507
2029 | 2008 | 8 | 28 | 14 | 11533.1041
2029 | 2008 | 8 | 28 | 15 | 12528.9775
2029 | 2008 | 8 | 28 | 16 | 12816.8522
2029 | 2008 | 8 | 28 | 17 | 13759.8679
2029 | 2008 | 8 | 28 | 18 | 15010.4306
2029 | 2008 | 8 | 28 | 19 | 14782.7508
2029 | 2008 | 8 | 28 | 20 | 14172.9621
2029 | 2008 | 8 | 28 | 21 | 14109.3173
2029 | 2008 | 8 | 28 | 22 | 14120.3756
2029 | 2008 | 8 | 28 | 23 | 13467.666
2029 | 2008 | 8 | 28 | 24 | 11857.0433
2029 | 2008 | 8 | 29 | 1 | 10448.7517
2029 | 2008 | 8 | 29 | 2 | 9055.2921
2029 | 2008 | 8 | 29 | 3 | 7560.8181
2029 | 2008 | 8 | 29 | 4 | 5659.0208
2029 | 2008 | 8 | 29 | 5 | 3876.8952
2029 | 2008 | 8 | 29 | 6 | 3142.5529
2029 | 2008 | 8 | 29 | 7 | 2878.4401
2029 | 2008 | 8 | 29 | 8 | 2901.1602
2029 | 2008 | 8 | 29 | 9 | 4414.4722
2029 | 2008 | 8 | 29 | 10 | 5123.873
2029 | 2008 | 8 | 29 | 11 | 5166.54
2029 | 2008 | 8 | 29 | 12 | 5772.6173
2029 | 2008 | 8 | 29 | 13 | 8303.8376
2029 | 2008 | 8 | 29 | 14 | 10276.852
2029 | 2008 | 8 | 29 | 15 | 12473.9049
2029 | 2008 | 8 | 29 | 16 | 12795.4191
2029 | 2008 | 8 | 29 | 17 | 12630.5531
2029 | 2008 | 8 | 29 | 18 | 12331.4686
2029 | 2008 | 8 | 29 | 19 | 11711.963
2029 | 2008 | 8 | 29 | 20 | 10663.5284
2029 | 2008 | 8 | 29 | 21 | 10331.0636
2029 | 2008 | 8 | 29 | 22 | 9642.4042
2029 | 2008 | 8 | 29 | 23 | 8475.2084
2029 | 2008 | 8 | 29 | 24 | 6752.8096
2029 | 2008 | 8 | 30 | 1 | 4999.9772
2029 | 2008 | 8 | 30 | 2 | 3479.3004
2029 | 2008 | 8 | 30 | 3 | 2844.1008
2029 | 2008 | 8 | 30 | 4 | 2417.0932
2029 | 2008 | 8 | 30 | 5 | 2174.9037
2029 | 2008 | 8 | 30 | 6 | 1902.0325
2029 | 2008 | 8 | 30 | 7 | 2311.7313
2029 | 2008 | 8 | 30 | 8 | 2354.9331
2029 | 2008 | 8 | 30 | 9 | 3452.4149
2029 | 2008 | 8 | 30 | 10 | 4662.9459
2029 | 2008 | 8 | 30 | 11 | 7359.8489
2029 | 2008 | 8 | 30 | 12 | 10451.4332
2029 | 2008 | 8 | 30 | 13 | 14165.0704
2029 | 2008 | 8 | 30 | 14 | 17124.6334
2029 | 2008 | 8 | 30 | 15 | 18786.4966
2029 | 2008 | 8 | 30 | 16 | 18815.7553
2029 | 2008 | 8 | 30 | 17 | 19057.0319
2029 | 2008 | 8 | 30 | 18 | 18958.5118
2029 | 2008 | 8 | 30 | 19 | 16998.2838
2029 | 2008 | 8 | 30 | 20 | 14551.6028
2029 | 2008 | 8 | 30 | 21 | 12925.6786
2029 | 2008 | 8 | 30 | 22 | 11194.353
2029 | 2008 | 8 | 30 | 23 | 10306.1449
2029 | 2008 | 8 | 30 | 24 | 10102.9553
2029 | 2008 | 8 | 31 | 1 | 9854.9215
2029 | 2008 | 8 | 31 | 2 | 9316.3494
2029 | 2008 | 8 | 31 | 3 | 9233.7884
2029 | 2008 | 8 | 31 | 4 | 8560.6776
2029 | 2008 | 8 | 31 | 5 | 8040.5764
2029 | 2008 | 8 | 31 | 6 | 8069.2586
2029 | 2008 | 8 | 31 | 7 | 8085.4519
2029 | 2008 | 8 | 31 | 8 | 6566.7229
2029 | 2008 | 8 | 31 | 9 | 6368.7502
2029 | 2008 | 8 | 31 | 10 | 8494.7444
2029 | 2008 | 8 | 31 | 11 | 10444.1016
2029 | 2008 | 8 | 31 | 12 | 10777.1879
2029 | 2008 | 8 | 31 | 13 | 11593.7903
2029 | 2008 | 8 | 31 | 14 | 12349.8171
2029 | 2008 | 8 | 31 | 15 | 12325.5233
2029 | 2008 | 8 | 31 | 16 | 12841.7804
2029 | 2008 | 8 | 31 | 17 | 14033.9976
2029 | 2008 | 8 | 31 | 18 | 15760.4218
2029 | 2008 | 8 | 31 | 19 | 13700.3825
2029 | 2008 | 8 | 31 | 20 | 14070.3741
2029 | 2008 | 8 | 31 | 21 | 15207.8369
2029 | 2008 | 8 | 31 | 22 | 15893.9066
2029 | 2008 | 8 | 31 | 23 | 16227.2537
2029 | 2008 | 8 | 31 | 24 | 16795.0575
2030 | 2008 | 8 | 1 | 1 | 13245.2873
2030 | 2008 | 8 | 1 | 2 | 12269.9683
2030 | 2008 | 8 | 1 | 3 | 11108.413
2030 | 2008 | 8 | 1 | 4 | 10200.383
2030 | 2008 | 8 | 1 | 5 | 9823.1042
2030 | 2008 | 8 | 1 | 6 | 9156.5714
2030 | 2008 | 8 | 1 | 7 | 8436.465
2030 | 2008 | 8 | 1 | 8 | 6644.8091
2030 | 2008 | 8 | 1 | 9 | 6781.3632
2030 | 2008 | 8 | 1 | 10 | 6065.2681
2030 | 2008 | 8 | 1 | 11 | 4077.5093
2030 | 2008 | 8 | 1 | 12 | 4442.3165
2030 | 2008 | 8 | 1 | 13 | 5129.6779
2030 | 2008 | 8 | 1 | 14 | 6531.7815
2030 | 2008 | 8 | 1 | 15 | 8268.8489
2030 | 2008 | 8 | 1 | 16 | 10044.1409
2030 | 2008 | 8 | 1 | 17 | 10882.1117
2030 | 2008 | 8 | 1 | 18 | 12495.7116
2030 | 2008 | 8 | 1 | 19 | 12390.1082
2030 | 2008 | 8 | 1 | 20 | 12447.6483
2030 | 2008 | 8 | 1 | 21 | 13558.5595
2030 | 2008 | 8 | 1 | 22 | 13907.5372
2030 | 2008 | 8 | 1 | 23 | 14700.4284
2030 | 2008 | 8 | 1 | 24 | 14790.1276
2030 | 2008 | 8 | 2 | 1 | 14273.2273
2030 | 2008 | 8 | 2 | 2 | 13549.9667
2030 | 2008 | 8 | 2 | 3 | 13382.1539
2030 | 2008 | 8 | 2 | 4 | 12432.7118
2030 | 2008 | 8 | 2 | 5 | 11258.6825
2030 | 2008 | 8 | 2 | 6 | 11002.6092
2030 | 2008 | 8 | 2 | 7 | 10764.4251
2030 | 2008 | 8 | 2 | 8 | 8086.2954
2030 | 2008 | 8 | 2 | 9 | 7742.1121
2030 | 2008 | 8 | 2 | 10 | 9760.1325
2030 | 2008 | 8 | 2 | 11 | 7818.3673
2030 | 2008 | 8 | 2 | 12 | 6737.6261
2030 | 2008 | 8 | 2 | 13 | 7414.2273
2030 | 2008 | 8 | 2 | 14 | 8799.7205
2030 | 2008 | 8 | 2 | 15 | 10478.477
2030 | 2008 | 8 | 2 | 16 | 11893.1919
2030 | 2008 | 8 | 2 | 17 | 13924.3331
2030 | 2008 | 8 | 2 | 18 | 16550.4149
2030 | 2008 | 8 | 2 | 19 | 17751.9109
2030 | 2008 | 8 | 2 | 20 | 19191.3117
2030 | 2008 | 8 | 2 | 21 | 21548.8192
2030 | 2008 | 8 | 2 | 22 | 23370.2518
2030 | 2008 | 8 | 2 | 23 | 23837.6552
2030 | 2008 | 8 | 2 | 24 | 23124.815
2030 | 2008 | 8 | 3 | 1 | 21866.2245
2030 | 2008 | 8 | 3 | 2 | 21490.8059
2030 | 2008 | 8 | 3 | 3 | 21664.5976
2030 | 2008 | 8 | 3 | 4 | 21410.5348
2030 | 2008 | 8 | 3 | 5 | 20738.8983
2030 | 2008 | 8 | 3 | 6 | 19220.0932
2030 | 2008 | 8 | 3 | 7 | 18122.6412
2030 | 2008 | 8 | 3 | 8 | 13333.8116
2030 | 2008 | 8 | 3 | 9 | 11371.0336
2030 | 2008 | 8 | 3 | 10 | 13247.3994
2030 | 2008 | 8 | 3 | 11 | 11801.5553
2030 | 2008 | 8 | 3 | 12 | 11456.636
2030 | 2008 | 8 | 3 | 13 | 12817.048
2030 | 2008 | 8 | 3 | 14 | 13345.8497
2030 | 2008 | 8 | 3 | 15 | 13488.6958
2030 | 2008 | 8 | 3 | 16 | 13207.7831
2030 | 2008 | 8 | 3 | 17 | 13780.1038
2030 | 2008 | 8 | 3 | 18 | 14985.1405
2030 | 2008 | 8 | 3 | 19 | 16215.0643
2030 | 2008 | 8 | 3 | 20 | 18744.4324
2030 | 2008 | 8 | 3 | 21 | 21822.3532
2030 | 2008 | 8 | 3 | 22 | 23937.8055
2030 | 2008 | 8 | 3 | 23 | 24554.224
2030 | 2008 | 8 | 3 | 24 | 24305.3665
2030 | 2008 | 8 | 4 | 1 | 22918.5394
2030 | 2008 | 8 | 4 | 2 | 21766.7739
2030 | 2008 | 8 | 4 | 3 | 21088.3728
2030 | 2008 | 8 | 4 | 4 | 19329.642
2030 | 2008 | 8 | 4 | 5 | 17254.3711
2030 | 2008 | 8 | 4 | 6 | 14245.6996
2030 | 2008 | 8 | 4 | 7 | 11119.1449
2030 | 2008 | 8 | 4 | 8 | 6979.3084
2030 | 2008 | 8 | 4 | 9 | 4423.6583
2030 | 2008 | 8 | 4 | 10 | 5293.8563
2030 | 2008 | 8 | 4 | 11 | 4524.7369
2030 | 2008 | 8 | 4 | 12 | 3595.0066
2030 | 2008 | 8 | 4 | 13 | 4004.304
2030 | 2008 | 8 | 4 | 14 | 5272.6379
2030 | 2008 | 8 | 4 | 15 | 5951.2626
2030 | 2008 | 8 | 4 | 16 | 6015.4396
2030 | 2008 | 8 | 4 | 17 | 7095.4784
2030 | 2008 | 8 | 4 | 18 | 8136.1262
2030 | 2008 | 8 | 4 | 19 | 9337.3359
2030 | 2008 | 8 | 4 | 20 | 11525.0642
2030 | 2008 | 8 | 4 | 21 | 14987.8047
2030 | 2008 | 8 | 4 | 22 | 17870.4671
2030 | 2008 | 8 | 4 | 23 | 17998.1292
2030 | 2008 | 8 | 4 | 24 | 16147.4949
2030 | 2008 | 8 | 5 | 1 | 14354.6054
2030 | 2008 | 8 | 5 | 2 | 12945.1011
2030 | 2008 | 8 | 5 | 3 | 11679.0102
2030 | 2008 | 8 | 5 | 4 | 9745.3863
2030 | 2008 | 8 | 5 | 5 | 8191.0339
2030 | 2008 | 8 | 5 | 6 | 6952.2099
2030 | 2008 | 8 | 5 | 7 | 5842.7884
2030 | 2008 | 8 | 5 | 8 | 3197.948
2030 | 2008 | 8 | 5 | 9 | 2205.6368
2030 | 2008 | 8 | 5 | 10 | 1808.7148
2030 | 2008 | 8 | 5 | 11 | 1880.9622
2030 | 2008 | 8 | 5 | 12 | 1695.101
2030 | 2008 | 8 | 5 | 13 | 2573.4914
2030 | 2008 | 8 | 5 | 14 | 3726.8465
2030 | 2008 | 8 | 5 | 15 | 6165.1015
2030 | 2008 | 8 | 5 | 16 | 7879.8679
2030 | 2008 | 8 | 5 | 17 | 10517.1725
2030 | 2008 | 8 | 5 | 18 | 13388.1785
2030 | 2008 | 8 | 5 | 19 | 15775.2951
2030 | 2008 | 8 | 5 | 20 | 18295.0202
2030 | 2008 | 8 | 5 | 21 | 21441.4784
2030 | 2008 | 8 | 5 | 22 | 21993.7957
2030 | 2008 | 8 | 5 | 23 | 20587.4773
2030 | 2008 | 8 | 5 | 24 | 19045.9941
2030 | 2008 | 8 | 6 | 1 | 17078.5641
2030 | 2008 | 8 | 6 | 2 | 14279.451
2030 | 2008 | 8 | 6 | 3 | 11294.6877
2030 | 2008 | 8 | 6 | 4 | 9312.5035
2030 | 2008 | 8 | 6 | 5 | 7862.5506
2030 | 2008 | 8 | 6 | 6 | 6738.1769
2030 | 2008 | 8 | 6 | 7 | 5743.8457
2030 | 2008 | 8 | 6 | 8 | 5194.8046
2030 | 2008 | 8 | 6 | 9 | 6570.5837
2030 | 2008 | 8 | 6 | 10 | 8526.039
2030 | 2008 | 8 | 6 | 11 | 9474.414
2030 | 2008 | 8 | 6 | 12 | 10500.1518
2030 | 2008 | 8 | 6 | 13 | 12271.5864
2030 | 2008 | 8 | 6 | 14 | 12830.0447
2030 | 2008 | 8 | 6 | 15 | 13834.0306
2030 | 2008 | 8 | 6 | 16 | 13454.8797
2030 | 2008 | 8 | 6 | 17 | 14439.5679
2030 | 2008 | 8 | 6 | 18 | 14941.6708
2030 | 2008 | 8 | 6 | 19 | 15302.2028
2030 | 2008 | 8 | 6 | 20 | 15217.5527
2030 | 2008 | 8 | 6 | 21 | 16135.0085
2030 | 2008 | 8 | 6 | 22 | 16283.7616
2030 | 2008 | 8 | 6 | 23 | 15464.1272
2030 | 2008 | 8 | 6 | 24 | 14611.6856
2030 | 2008 | 8 | 7 | 1 | 13341.3702
2030 | 2008 | 8 | 7 | 2 | 11932.7156
2030 | 2008 | 8 | 7 | 3 | 11409.468
2030 | 2008 | 8 | 7 | 4 | 10668.3534
2030 | 2008 | 8 | 7 | 5 | 9534.1937
2030 | 2008 | 8 | 7 | 6 | 8477.8846
2030 | 2008 | 8 | 7 | 7 | 7925.95
2030 | 2008 | 8 | 7 | 8 | 6700.3332
2030 | 2008 | 8 | 7 | 9 | 7378.3653
2030 | 2008 | 8 | 7 | 10 | 7384.087
2030 | 2008 | 8 | 7 | 11 | 7137.1827
2030 | 2008 | 8 | 7 | 12 | 7070.0939
2030 | 2008 | 8 | 7 | 13 | 7456.8912
2030 | 2008 | 8 | 7 | 14 | 8163.1847
2030 | 2008 | 8 | 7 | 15 | 9113.7163
2030 | 2008 | 8 | 7 | 16 | 9164.5088
2030 | 2008 | 8 | 7 | 17 | 10045.4853
2030 | 2008 | 8 | 7 | 18 | 10946.7451
2030 | 2008 | 8 | 7 | 19 | 11613.8187
2030 | 2008 | 8 | 7 | 20 | 11566.0471
2030 | 2008 | 8 | 7 | 21 | 12168.7744
2030 | 2008 | 8 | 7 | 22 | 13195.3011
2030 | 2008 | 8 | 7 | 23 | 13437.819
2030 | 2008 | 8 | 7 | 24 | 14267.0334
2030 | 2008 | 8 | 8 | 1 | 14486.5834
2030 | 2008 | 8 | 8 | 2 | 14404.2054
2030 | 2008 | 8 | 8 | 3 | 13940.5245
2030 | 2008 | 8 | 8 | 4 | 12579.1836
2030 | 2008 | 8 | 8 | 5 | 11428.9016
2030 | 2008 | 8 | 8 | 6 | 10811.2804
2030 | 2008 | 8 | 8 | 7 | 10013.125
2030 | 2008 | 8 | 8 | 8 | 6651.6008
2030 | 2008 | 8 | 8 | 9 | 5469.096
2030 | 2008 | 8 | 8 | 10 | 6249.1754
2030 | 2008 | 8 | 8 | 11 | 5327.2741
2030 | 2008 | 8 | 8 | 12 | 4411.2291
2030 | 2008 | 8 | 8 | 13 | 4805.327
2030 | 2008 | 8 | 8 | 14 | 6268.537
2030 | 2008 | 8 | 8 | 15 | 8222.7779
2030 | 2008 | 8 | 8 | 16 | 9986.3634
2030 | 2008 | 8 | 8 | 17 | 11252.2243
2030 | 2008 | 8 | 8 | 18 | 12139.5837
2030 | 2008 | 8 | 8 | 19 | 13797.8974
2030 | 2008 | 8 | 8 | 20 | 15296.8209
2030 | 2008 | 8 | 8 | 21 | 18076.6646
2030 | 2008 | 8 | 8 | 22 | 20271.8016
2030 | 2008 | 8 | 8 | 23 | 21989.4409
2030 | 2008 | 8 | 8 | 24 | 21872.43
2030 | 2008 | 8 | 9 | 1 | 20666.2857
2030 | 2008 | 8 | 9 | 2 | 20005.0524
2030 | 2008 | 8 | 9 | 3 | 19156.8932
2030 | 2008 | 8 | 9 | 4 | 18785.8625
2030 | 2008 | 8 | 9 | 5 | 18557.4229
2030 | 2008 | 8 | 9 | 6 | 18825.314
2030 | 2008 | 8 | 9 | 7 | 18554.862
2030 | 2008 | 8 | 9 | 8 | 14770.151
2030 | 2008 | 8 | 9 | 9 | 13265.3466
2030 | 2008 | 8 | 9 | 10 | 14897.5745
2030 | 2008 | 8 | 9 | 11 | 14149.0374
2030 | 2008 | 8 | 9 | 12 | 14258.1066
2030 | 2008 | 8 | 9 | 13 | 16465.2671
2030 | 2008 | 8 | 9 | 14 | 17888.5455
2030 | 2008 | 8 | 9 | 15 | 19367.4111
2030 | 2008 | 8 | 9 | 16 | 19562.9103
2030 | 2008 | 8 | 9 | 17 | 21022.4613
2030 | 2008 | 8 | 9 | 18 | 22966.5302
2030 | 2008 | 8 | 9 | 19 | 23465.7517
2030 | 2008 | 8 | 9 | 20 | 24713.3958
2030 | 2008 | 8 | 9 | 21 | 26500.3117
2030 | 2008 | 8 | 9 | 22 | 28335.9214
2030 | 2008 | 8 | 9 | 23 | 29124.8881
2030 | 2008 | 8 | 9 | 24 | 29620.8386
2030 | 2008 | 8 | 10 | 1 | 28891.6511
2030 | 2008 | 8 | 10 | 2 | 28947.8788
2030 | 2008 | 8 | 10 | 3 | 29557.782
2030 | 2008 | 8 | 10 | 4 | 29572.7041
2030 | 2008 | 8 | 10 | 5 | 29385.8551
2030 | 2008 | 8 | 10 | 6 | 29223.5092
2030 | 2008 | 8 | 10 | 7 | 27240.6233
2030 | 2008 | 8 | 10 | 8 | 24502.6477
2030 | 2008 | 8 | 10 | 9 | 25867.7834
2030 | 2008 | 8 | 10 | 10 | 25228.2076
2030 | 2008 | 8 | 10 | 11 | 20721.5638
2030 | 2008 | 8 | 10 | 12 | 17688.8033
2030 | 2008 | 8 | 10 | 13 | 15761.349
2030 | 2008 | 8 | 10 | 14 | 14926.0587
2030 | 2008 | 8 | 10 | 15 | 13895.8159
2030 | 2008 | 8 | 10 | 16 | 13990.2578
2030 | 2008 | 8 | 10 | 17 | 15957.1377
2030 | 2008 | 8 | 10 | 18 | 19644.4929
2030 | 2008 | 8 | 10 | 19 | 21977.0954
2030 | 2008 | 8 | 10 | 20 | 21254.1206
2030 | 2008 | 8 | 10 | 21 | 21020.1521
2030 | 2008 | 8 | 10 | 22 | 20170.4333
2030 | 2008 | 8 | 10 | 23 | 20263.9167
2030 | 2008 | 8 | 10 | 24 | 18041.897
2030 | 2008 | 8 | 11 | 1 | 16483.399
2030 | 2008 | 8 | 11 | 2 | 16257.7918
2030 | 2008 | 8 | 11 | 3 | 15882.3758
2030 | 2008 | 8 | 11 | 4 | 15064.2089
2030 | 2008 | 8 | 11 | 5 | 13966.5397
2030 | 2008 | 8 | 11 | 6 | 13340.6151
2030 | 2008 | 8 | 11 | 7 | 12476.6479
2030 | 2008 | 8 | 11 | 8 | 11562.2326
2030 | 2008 | 8 | 11 | 9 | 14366.6066
2030 | 2008 | 8 | 11 | 10 | 14588.5603
2030 | 2008 | 8 | 11 | 11 | 13732.5445
2030 | 2008 | 8 | 11 | 12 | 13457.7308
2030 | 2008 | 8 | 11 | 13 | 13270.7397
2030 | 2008 | 8 | 11 | 14 | 13353.6898
2030 | 2008 | 8 | 11 | 15 | 12940.1908
2030 | 2008 | 8 | 11 | 16 | 12691.8561
2030 | 2008 | 8 | 11 | 17 | 13207.5727
2030 | 2008 | 8 | 11 | 18 | 13092.8149
2030 | 2008 | 8 | 11 | 19 | 13601.3089
2030 | 2008 | 8 | 11 | 20 | 12919.599
2030 | 2008 | 8 | 11 | 21 | 12848.6015
2030 | 2008 | 8 | 11 | 22 | 11253.7721
2030 | 2008 | 8 | 11 | 23 | 10515.0667
2030 | 2008 | 8 | 11 | 24 | 9934.2472
2030 | 2008 | 8 | 12 | 1 | 9891.111
2030 | 2008 | 8 | 12 | 2 | 10043.0903
2030 | 2008 | 8 | 12 | 3 | 9826.5142
2030 | 2008 | 8 | 12 | 4 | 9630.5543
2030 | 2008 | 8 | 12 | 5 | 8721.8338
2030 | 2008 | 8 | 12 | 6 | 8241.9611
2030 | 2008 | 8 | 12 | 7 | 7572.964
2030 | 2008 | 8 | 12 | 8 | 6200.0084
2030 | 2008 | 8 | 12 | 9 | 7370.4751
2030 | 2008 | 8 | 12 | 10 | 7658.9772
2030 | 2008 | 8 | 12 | 11 | 7194.4374
2030 | 2008 | 8 | 12 | 12 | 6614.8785
2030 | 2008 | 8 | 12 | 13 | 7683.1165
2030 | 2008 | 8 | 12 | 14 | 8755.8996
2030 | 2008 | 8 | 12 | 15 | 9528.0468
2030 | 2008 | 8 | 12 | 16 | 9991.0744
2030 | 2008 | 8 | 12 | 17 | 10353.1192
2030 | 2008 | 8 | 12 | 18 | 11066.0909
2030 | 2008 | 8 | 12 | 19 | 11625.0904
2030 | 2008 | 8 | 12 | 20 | 10864.3927
2030 | 2008 | 8 | 12 | 21 | 10776.2549
2030 | 2008 | 8 | 12 | 22 | 10622.0344
2030 | 2008 | 8 | 12 | 23 | 10074.7138
2030 | 2008 | 8 | 12 | 24 | 9147.7716
2030 | 2008 | 8 | 13 | 1 | 7886.3838
2030 | 2008 | 8 | 13 | 2 | 7261.8015
2030 | 2008 | 8 | 13 | 3 | 7035.8994
2030 | 2008 | 8 | 13 | 4 | 6800.2882
2030 | 2008 | 8 | 13 | 5 | 5849.3338
2030 | 2008 | 8 | 13 | 6 | 4801.1515
2030 | 2008 | 8 | 13 | 7 | 3648.6645
2030 | 2008 | 8 | 13 | 8 | 2314.3648
2030 | 2008 | 8 | 13 | 9 | 2668.5531
2030 | 2008 | 8 | 13 | 10 | 2785.4192
2030 | 2008 | 8 | 13 | 11 | 2361.3902
2030 | 2008 | 8 | 13 | 12 | 2402.9416
2030 | 2008 | 8 | 13 | 13 | 2408.4356
2030 | 2008 | 8 | 13 | 14 | 2890.0843
2030 | 2008 | 8 | 13 | 15 | 3910.7273
2030 | 2008 | 8 | 13 | 16 | 4692.8144
2030 | 2008 | 8 | 13 | 17 | 6086.2869
2030 | 2008 | 8 | 13 | 18 | 8136.6004
2030 | 2008 | 8 | 13 | 19 | 9277.9722
2030 | 2008 | 8 | 13 | 20 | 10201.3988
2030 | 2008 | 8 | 13 | 21 | 11830.0102
2030 | 2008 | 8 | 13 | 22 | 12204.1146
2030 | 2008 | 8 | 13 | 23 | 11399.8912
2030 | 2008 | 8 | 13 | 24 | 10285.5766
2030 | 2008 | 8 | 14 | 1 | 9501.7821
2030 | 2008 | 8 | 14 | 2 | 9213.9941
2030 | 2008 | 8 | 14 | 3 | 8909.3423
2030 | 2008 | 8 | 14 | 4 | 8774.6439
2030 | 2008 | 8 | 14 | 5 | 7923.2554
2030 | 2008 | 8 | 14 | 6 | 7278.1137
2030 | 2008 | 8 | 14 | 7 | 6311.2421
2030 | 2008 | 8 | 14 | 8 | 4294.0664
2030 | 2008 | 8 | 14 | 9 | 3876.9818
2030 | 2008 | 8 | 14 | 10 | 4065.6397
2030 | 2008 | 8 | 14 | 11 | 5092.447
2030 | 2008 | 8 | 14 | 12 | 5361.2601
2030 | 2008 | 8 | 14 | 13 | 7080.3021
2030 | 2008 | 8 | 14 | 14 | 8357.0215
2030 | 2008 | 8 | 14 | 15 | 9468.0216
2030 | 2008 | 8 | 14 | 16 | 10052.6006
2030 | 2008 | 8 | 14 | 17 | 10838.6032
2030 | 2008 | 8 | 14 | 18 | 11885.3726
2030 | 2008 | 8 | 14 | 19 | 13269.875
2030 | 2008 | 8 | 14 | 20 | 14400.7022
2030 | 2008 | 8 | 14 | 21 | 16465.5953
2030 | 2008 | 8 | 14 | 22 | 20097.5321
2030 | 2008 | 8 | 14 | 23 | 23704.5471
2030 | 2008 | 8 | 14 | 24 | 24577.1633
2030 | 2008 | 8 | 15 | 1 | 23462.6477
2030 | 2008 | 8 | 15 | 2 | 21912.2964
2030 | 2008 | 8 | 15 | 3 | 20233.5977
2030 | 2008 | 8 | 15 | 4 | 17546.3564
2030 | 2008 | 8 | 15 | 5 | 13385.478
2030 | 2008 | 8 | 15 | 6 | 10487.5418
2030 | 2008 | 8 | 15 | 7 | 8240.8292
2030 | 2008 | 8 | 15 | 8 | 5407.9523
2030 | 2008 | 8 | 15 | 9 | 4928.389
2030 | 2008 | 8 | 15 | 10 | 6019.9552
2030 | 2008 | 8 | 15 | 11 | 6767.1297
2030 | 2008 | 8 | 15 | 12 | 7251.9658
2030 | 2008 | 8 | 15 | 13 | 8381.6646
2030 | 2008 | 8 | 15 | 14 | 8900.4389
2030 | 2008 | 8 | 15 | 15 | 8795.2569
2030 | 2008 | 8 | 15 | 16 | 8735.2268
2030 | 2008 | 8 | 15 | 17 | 9390.0178
2030 | 2008 | 8 | 15 | 18 | 10960.3451
2030 | 2008 | 8 | 15 | 19 | 11860.5992
2030 | 2008 | 8 | 15 | 20 | 13895.6101
2030 | 2008 | 8 | 15 | 21 | 16667.6423
2030 | 2008 | 8 | 15 | 22 | 18801.6876
2030 | 2008 | 8 | 15 | 23 | 18918.8931
2030 | 2008 | 8 | 15 | 24 | 18666.9593
2030 | 2008 | 8 | 16 | 1 | 17753.251
2030 | 2008 | 8 | 16 | 2 | 16606.7119
2030 | 2008 | 8 | 16 | 3 | 14144.5907
2030 | 2008 | 8 | 16 | 4 | 11827.0562
2030 | 2008 | 8 | 16 | 5 | 9612.0874
2030 | 2008 | 8 | 16 | 6 | 7810.1278
2030 | 2008 | 8 | 16 | 7 | 6030.7219
2030 | 2008 | 8 | 16 | 8 | 4997.5692
2030 | 2008 | 8 | 16 | 9 | 5786.557
2030 | 2008 | 8 | 16 | 10 | 7881.3724
2030 | 2008 | 8 | 16 | 11 | 8585.1221
2030 | 2008 | 8 | 16 | 12 | 9384.918
2030 | 2008 | 8 | 16 | 13 | 11163.8451
2030 | 2008 | 8 | 16 | 14 | 13908.3411
2030 | 2008 | 8 | 16 | 15 | 14761.1828
2030 | 2008 | 8 | 16 | 16 | 15701.752
2030 | 2008 | 8 | 16 | 17 | 17124.0495
2030 | 2008 | 8 | 16 | 18 | 17725.5019
2030 | 2008 | 8 | 16 | 19 | 17495.6419
2030 | 2008 | 8 | 16 | 20 | 15905.177
2030 | 2008 | 8 | 16 | 21 | 14846.6815
2030 | 2008 | 8 | 16 | 22 | 12691.8128
2030 | 2008 | 8 | 16 | 23 | 10438.929
2030 | 2008 | 8 | 16 | 24 | 8158.4526
2030 | 2008 | 8 | 17 | 1 | 6147.5693
2030 | 2008 | 8 | 17 | 2 | 4955.7394
2030 | 2008 | 8 | 17 | 3 | 4513.4601
2030 | 2008 | 8 | 17 | 4 | 4475.2908
2030 | 2008 | 8 | 17 | 5 | 4591.1501
2030 | 2008 | 8 | 17 | 6 | 5243.5151
2030 | 2008 | 8 | 17 | 7 | 5223.3057
2030 | 2008 | 8 | 17 | 8 | 5566.014
2030 | 2008 | 8 | 17 | 9 | 7117.0612
2030 | 2008 | 8 | 17 | 10 | 8990.4288
2030 | 2008 | 8 | 17 | 11 | 9226.5375
2030 | 2008 | 8 | 17 | 12 | 9548.1685
2030 | 2008 | 8 | 17 | 13 | 9102.5641
2030 | 2008 | 8 | 17 | 14 | 8749.6146
2030 | 2008 | 8 | 17 | 15 | 7640.5099
2030 | 2008 | 8 | 17 | 16 | 7611.7835
2030 | 2008 | 8 | 17 | 17 | 9047.7787
2030 | 2008 | 8 | 17 | 18 | 10647.5876
2030 | 2008 | 8 | 17 | 19 | 11888.7131
2030 | 2008 | 8 | 17 | 20 | 11427.5987
2030 | 2008 | 8 | 17 | 21 | 12139.3241
2030 | 2008 | 8 | 17 | 22 | 12479.7372
2030 | 2008 | 8 | 17 | 23 | 12567.3606
2030 | 2008 | 8 | 17 | 24 | 12485.5363
2030 | 2008 | 8 | 18 | 1 | 11688.5522
2030 | 2008 | 8 | 18 | 2 | 11154.2058
2030 | 2008 | 8 | 18 | 3 | 10599.4392
2030 | 2008 | 8 | 18 | 4 | 10818.9767
2030 | 2008 | 8 | 18 | 5 | 10681.0168
2030 | 2008 | 8 | 18 | 6 | 10855.721
2030 | 2008 | 8 | 18 | 7 | 10099.0627
2030 | 2008 | 8 | 18 | 8 | 9324.6156
2030 | 2008 | 8 | 18 | 9 | 11144.7247
2030 | 2008 | 8 | 18 | 10 | 12136.5629
2030 | 2008 | 8 | 18 | 11 | 11777.4155
2030 | 2008 | 8 | 18 | 12 | 11640.7103
2030 | 2008 | 8 | 18 | 13 | 12124.0914
2030 | 2008 | 8 | 18 | 14 | 12669.0478
2030 | 2008 | 8 | 18 | 15 | 13414.8827
2030 | 2008 | 8 | 18 | 16 | 13515.4236
2030 | 2008 | 8 | 18 | 17 | 15061.1701
2030 | 2008 | 8 | 18 | 18 | 15497.4562
2030 | 2008 | 8 | 18 | 19 | 15396.7128
2030 | 2008 | 8 | 18 | 20 | 14483.4361
2030 | 2008 | 8 | 18 | 21 | 14458.9057
2030 | 2008 | 8 | 18 | 22 | 14181.3848
2030 | 2008 | 8 | 18 | 23 | 13115.7577
2030 | 2008 | 8 | 18 | 24 | 12022.3009
2030 | 2008 | 8 | 19 | 1 | 11341.5912
2030 | 2008 | 8 | 19 | 2 | 11040.7591
2030 | 2008 | 8 | 19 | 3 | 11830.854
2030 | 2008 | 8 | 19 | 4 | 13141.6804
2030 | 2008 | 8 | 19 | 5 | 13828.1592
2030 | 2008 | 8 | 19 | 6 | 14478.5744
2030 | 2008 | 8 | 19 | 7 | 14682.2313
2030 | 2008 | 8 | 19 | 8 | 13396.0397
2030 | 2008 | 8 | 19 | 9 | 15670.1488
2030 | 2008 | 8 | 19 | 10 | 14761.6477
2030 | 2008 | 8 | 19 | 11 | 11815.1435
2030 | 2008 | 8 | 19 | 12 | 11386.4355
2030 | 2008 | 8 | 19 | 13 | 12069.4269
2030 | 2008 | 8 | 19 | 14 | 12969.2013
2030 | 2008 | 8 | 19 | 15 | 14563.4832
2030 | 2008 | 8 | 19 | 16 | 15551.6385
2030 | 2008 | 8 | 19 | 17 | 17094.1289
2030 | 2008 | 8 | 19 | 18 | 17079.2959
2030 | 2008 | 8 | 19 | 19 | 17021.5952
2030 | 2008 | 8 | 19 | 20 | 15736.3503
2030 | 2008 | 8 | 19 | 21 | 14980.6587
2030 | 2008 | 8 | 19 | 22 | 13330.1685
2030 | 2008 | 8 | 19 | 23 | 10721.9899
2030 | 2008 | 8 | 19 | 24 | 8794.9274
2030 | 2008 | 8 | 20 | 1 | 7009.9237
2030 | 2008 | 8 | 20 | 2 | 6007.5706
2030 | 2008 | 8 | 20 | 3 | 5974.8107
2030 | 2008 | 8 | 20 | 4 | 5848.7962
2030 | 2008 | 8 | 20 | 5 | 5590.5983
2030 | 2008 | 8 | 20 | 6 | 5405.8263
2030 | 2008 | 8 | 20 | 7 | 5419.4519
2030 | 2008 | 8 | 20 | 8 | 4714.2609
2030 | 2008 | 8 | 20 | 9 | 5642.9186
2030 | 2008 | 8 | 20 | 10 | 5702.2472
2030 | 2008 | 8 | 20 | 11 | 5119.5593
2030 | 2008 | 8 | 20 | 12 | 5072.6529
2030 | 2008 | 8 | 20 | 13 | 5658.1756
2030 | 2008 | 8 | 20 | 14 | 6465.439
2030 | 2008 | 8 | 20 | 15 | 6997.5467
2030 | 2008 | 8 | 20 | 16 | 7168.0141
2030 | 2008 | 8 | 20 | 17 | 6690.5688
2030 | 2008 | 8 | 20 | 18 | 5934.5425
2030 | 2008 | 8 | 20 | 19 | 5138.6168
2030 | 2008 | 8 | 20 | 20 | 5054.67
2030 | 2008 | 8 | 20 | 21 | 5966.8249
2030 | 2008 | 8 | 20 | 22 | 7279.8179
2030 | 2008 | 8 | 20 | 23 | 8103.94
2030 | 2008 | 8 | 20 | 24 | 8418.603
2030 | 2008 | 8 | 21 | 1 | 8905.4733
2030 | 2008 | 8 | 21 | 2 | 8929.0516
2030 | 2008 | 8 | 21 | 3 | 8262.4865
2030 | 2008 | 8 | 21 | 4 | 7861.0787
2030 | 2008 | 8 | 21 | 5 | 7260.0672
2030 | 2008 | 8 | 21 | 6 | 6941.6464
2030 | 2008 | 8 | 21 | 7 | 6408.047
2030 | 2008 | 8 | 21 | 8 | 4730.476
2030 | 2008 | 8 | 21 | 9 | 4822.9254
2030 | 2008 | 8 | 21 | 10 | 5898.759
2030 | 2008 | 8 | 21 | 11 | 6937.995
2030 | 2008 | 8 | 21 | 12 | 7816.4429
2030 | 2008 | 8 | 21 | 13 | 8811.7711
2030 | 2008 | 8 | 21 | 14 | 10029.1719
2030 | 2008 | 8 | 21 | 15 | 10522.1492
2030 | 2008 | 8 | 21 | 16 | 10086.7013
2030 | 2008 | 8 | 21 | 17 | 10797.9069
2030 | 2008 | 8 | 21 | 18 | 12094.751
2030 | 2008 | 8 | 21 | 19 | 13709.1684
2030 | 2008 | 8 | 21 | 20 | 15944.0701
2030 | 2008 | 8 | 21 | 21 | 20025.5124
2030 | 2008 | 8 | 21 | 22 | 22808.0162
2030 | 2008 | 8 | 21 | 23 | 23923.0156
2030 | 2008 | 8 | 21 | 24 | 24144.7725
2030 | 2008 | 8 | 22 | 1 | 23380.1385
2030 | 2008 | 8 | 22 | 2 | 22799.7879
2030 | 2008 | 8 | 22 | 3 | 22860.7976
2030 | 2008 | 8 | 22 | 4 | 23073.7
2030 | 2008 | 8 | 22 | 5 | 23048.298
2030 | 2008 | 8 | 22 | 6 | 23710.0594
2030 | 2008 | 8 | 22 | 7 | 23997.846
2030 | 2008 | 8 | 22 | 8 | 21624.0668
2030 | 2008 | 8 | 22 | 9 | 22705.3572
2030 | 2008 | 8 | 22 | 10 | 23849.1294
2030 | 2008 | 8 | 22 | 11 | 21745.7246
2030 | 2008 | 8 | 22 | 12 | 20749.9502
2030 | 2008 | 8 | 22 | 13 | 22057.7959
2030 | 2008 | 8 | 22 | 14 | 22382.2785
2030 | 2008 | 8 | 22 | 15 | 21670.2038
2030 | 2008 | 8 | 22 | 16 | 19863.587
2030 | 2008 | 8 | 22 | 17 | 18795.667
2030 | 2008 | 8 | 22 | 18 | 19045.6784
2030 | 2008 | 8 | 22 | 19 | 18865.039
2030 | 2008 | 8 | 22 | 20 | 20374.6193
2030 | 2008 | 8 | 22 | 21 | 21882.002
2030 | 2008 | 8 | 22 | 22 | 23021.0768
2030 | 2008 | 8 | 22 | 23 | 22492.3452
2030 | 2008 | 8 | 22 | 24 | 20978.6646
2030 | 2008 | 8 | 23 | 1 | 17845.4606
2030 | 2008 | 8 | 23 | 2 | 15542.7666
2030 | 2008 | 8 | 23 | 3 | 13115.2883
2030 | 2008 | 8 | 23 | 4 | 10893.5452
2030 | 2008 | 8 | 23 | 5 | 8837.0859
2030 | 2008 | 8 | 23 | 6 | 6712.8748
2030 | 2008 | 8 | 23 | 7 | 5206.634
2030 | 2008 | 8 | 23 | 8 | 3698.7739
2030 | 2008 | 8 | 23 | 9 | 4457.8076
2030 | 2008 | 8 | 23 | 10 | 5010.5544
2030 | 2008 | 8 | 23 | 11 | 4636.8199
2030 | 2008 | 8 | 23 | 12 | 4387.1996
2030 | 2008 | 8 | 23 | 13 | 5285.2604
2030 | 2008 | 8 | 23 | 14 | 6280.6376
2030 | 2008 | 8 | 23 | 15 | 7167.7875
2030 | 2008 | 8 | 23 | 16 | 7643.8332
2030 | 2008 | 8 | 23 | 17 | 8291.1334
2030 | 2008 | 8 | 23 | 18 | 8438.5906
2030 | 2008 | 8 | 23 | 19 | 7732.2839
2030 | 2008 | 8 | 23 | 20 | 6514.3841
2030 | 2008 | 8 | 23 | 21 | 6044.7968
2030 | 2008 | 8 | 23 | 22 | 5025.602
2030 | 2008 | 8 | 23 | 23 | 3625.6458
2030 | 2008 | 8 | 23 | 24 | 2868.0901
2030 | 2008 | 8 | 24 | 1 | 2264.7679
2030 | 2008 | 8 | 24 | 2 | 1514.4573
2030 | 2008 | 8 | 24 | 3 | 1126.6933
2030 | 2008 | 8 | 24 | 4 | 864.3561
2030 | 2008 | 8 | 24 | 5 | 810.7621
2030 | 2008 | 8 | 24 | 6 | 768.6248
2030 | 2008 | 8 | 24 | 7 | 874.3706
2030 | 2008 | 8 | 24 | 8 | 590.5288
2030 | 2008 | 8 | 24 | 9 | 906.8839
2030 | 2008 | 8 | 24 | 10 | 1054.3108
2030 | 2008 | 8 | 24 | 11 | 1577.7493
2030 | 2008 | 8 | 24 | 12 | 2218.767
2030 | 2008 | 8 | 24 | 13 | 3200.8714
2030 | 2008 | 8 | 24 | 14 | 3321.1256
2030 | 2008 | 8 | 24 | 15 | 4137.9828
2030 | 2008 | 8 | 24 | 16 | 4497.518
2030 | 2008 | 8 | 24 | 17 | 4921.7547
2030 | 2008 | 8 | 24 | 18 | 5354.4504
2030 | 2008 | 8 | 24 | 19 | 5257.8269
2030 | 2008 | 8 | 24 | 20 | 4506.6665
2030 | 2008 | 8 | 24 | 21 | 4372.8768
2030 | 2008 | 8 | 24 | 22 | 4270.8209
2030 | 2008 | 8 | 24 | 23 | 3848.4425
2030 | 2008 | 8 | 24 | 24 | 3517.0326
2030 | 2008 | 8 | 25 | 1 | 3370.5043
2030 | 2008 | 8 | 25 | 2 | 3346.8259
2030 | 2008 | 8 | 25 | 3 | 3452.7518
2030 | 2008 | 8 | 25 | 4 | 3519.5599
2030 | 2008 | 8 | 25 | 5 | 3667.2501
2030 | 2008 | 8 | 25 | 6 | 3558.5899
2030 | 2008 | 8 | 25 | 7 | 3252.8197
2030 | 2008 | 8 | 25 | 8 | 2387.7161
2030 | 2008 | 8 | 25 | 9 | 2209.2703
2030 | 2008 | 8 | 25 | 10 | 1928.0274
2030 | 2008 | 8 | 25 | 11 | 1369.5184
2030 | 2008 | 8 | 25 | 12 | 1220.3985
2030 | 2008 | 8 | 25 | 13 | 1659.7827
2030 | 2008 | 8 | 25 | 14 | 2288.1808
2030 | 2008 | 8 | 25 | 15 | 2834.9708
2030 | 2008 | 8 | 25 | 16 | 3015.0414
2030 | 2008 | 8 | 25 | 17 | 3376.1983
2030 | 2008 | 8 | 25 | 18 | 3774.4771
2030 | 2008 | 8 | 25 | 19 | 4232.7927
2030 | 2008 | 8 | 25 | 20 | 4120.0063
2030 | 2008 | 8 | 25 | 21 | 4934.0695
2030 | 2008 | 8 | 25 | 22 | 5456.8336
2030 | 2008 | 8 | 25 | 23 | 5662.3132
2030 | 2008 | 8 | 25 | 24 | 5468.1893
2030 | 2008 | 8 | 26 | 1 | 5109.7205
2030 | 2008 | 8 | 26 | 2 | 5088.2164
2030 | 2008 | 8 | 26 | 3 | 5029.2189
2030 | 2008 | 8 | 26 | 4 | 4868.1473
2030 | 2008 | 8 | 26 | 5 | 4853.2034
2030 | 2008 | 8 | 26 | 6 | 4649.9917
2030 | 2008 | 8 | 26 | 7 | 3840.3562
2030 | 2008 | 8 | 26 | 8 | 2431.7077
2030 | 2008 | 8 | 26 | 9 | 1974.5839
2030 | 2008 | 8 | 26 | 10 | 2633.5597
2030 | 2008 | 8 | 26 | 11 | 3049.219
2030 | 2008 | 8 | 26 | 12 | 3356.6361
2030 | 2008 | 8 | 26 | 13 | 3726.5428
2030 | 2008 | 8 | 26 | 14 | 4004.074
2030 | 2008 | 8 | 26 | 15 | 4829.5723
2030 | 2008 | 8 | 26 | 16 | 5334.3592
2030 | 2008 | 8 | 26 | 17 | 6909.9643
2030 | 2008 | 8 | 26 | 18 | 8773.4647
2030 | 2008 | 8 | 26 | 19 | 10123.3448
2030 | 2008 | 8 | 26 | 20 | 11896.2504
2030 | 2008 | 8 | 26 | 21 | 14505.8856
2030 | 2008 | 8 | 26 | 22 | 16343.9094
2030 | 2008 | 8 | 26 | 23 | 16865.9557
2030 | 2008 | 8 | 26 | 24 | 16554.6687
2030 | 2008 | 8 | 27 | 1 | 15456.6927
2030 | 2008 | 8 | 27 | 2 | 14564.8495
2030 | 2008 | 8 | 27 | 3 | 13538.8998
2030 | 2008 | 8 | 27 | 4 | 12404.3787
2030 | 2008 | 8 | 27 | 5 | 11693.5136
2030 | 2008 | 8 | 27 | 6 | 11519.3137
2030 | 2008 | 8 | 27 | 7 | 11387.9423
2030 | 2008 | 8 | 27 | 8 | 8543.4074
2030 | 2008 | 8 | 27 | 9 | 7974.3519
2030 | 2008 | 8 | 27 | 10 | 7591.0263
2030 | 2008 | 8 | 27 | 11 | 9120.152
2030 | 2008 | 8 | 27 | 12 | 10704.2218
2030 | 2008 | 8 | 27 | 13 | 11870.0019
2030 | 2008 | 8 | 27 | 14 | 12780.5008
2030 | 2008 | 8 | 27 | 15 | 12905.2538
2030 | 2008 | 8 | 27 | 16 | 12189.8338
2030 | 2008 | 8 | 27 | 17 | 12907.7737
2030 | 2008 | 8 | 27 | 18 | 13855.4256
2030 | 2008 | 8 | 27 | 19 | 14182.8999
2030 | 2008 | 8 | 27 | 20 | 15016.4383
2030 | 2008 | 8 | 27 | 21 | 16722.3202
2030 | 2008 | 8 | 27 | 22 | 17895.3863
2030 | 2008 | 8 | 27 | 23 | 17773.7528
2030 | 2008 | 8 | 27 | 24 | 17407.4719
2030 | 2008 | 8 | 28 | 1 | 16571.2919
2030 | 2008 | 8 | 28 | 2 | 15743.5692
2030 | 2008 | 8 | 28 | 3 | 15344.8967
2030 | 2008 | 8 | 28 | 4 | 15247.5362
2030 | 2008 | 8 | 28 | 5 | 14812.731
2030 | 2008 | 8 | 28 | 6 | 14295.2569
2030 | 2008 | 8 | 28 | 7 | 13517.8111
2030 | 2008 | 8 | 28 | 8 | 10706.8901
2030 | 2008 | 8 | 28 | 9 | 10400.4426
2030 | 2008 | 8 | 28 | 10 | 8921.1891
2030 | 2008 | 8 | 28 | 11 | 8279.4842
2030 | 2008 | 8 | 28 | 12 | 8871.6988
2030 | 2008 | 8 | 28 | 13 | 9990.2507
2030 | 2008 | 8 | 28 | 14 | 11533.1041
2030 | 2008 | 8 | 28 | 15 | 12528.9775
2030 | 2008 | 8 | 28 | 16 | 12816.8522
2030 | 2008 | 8 | 28 | 17 | 13759.8679
2030 | 2008 | 8 | 28 | 18 | 15010.4306
2030 | 2008 | 8 | 28 | 19 | 14782.7508
2030 | 2008 | 8 | 28 | 20 | 14172.9621
2030 | 2008 | 8 | 28 | 21 | 14109.3173
2030 | 2008 | 8 | 28 | 22 | 14120.3756
2030 | 2008 | 8 | 28 | 23 | 13467.666
2030 | 2008 | 8 | 28 | 24 | 11857.0433
2030 | 2008 | 8 | 29 | 1 | 10448.7517
2030 | 2008 | 8 | 29 | 2 | 9055.2921
2030 | 2008 | 8 | 29 | 3 | 7560.8181
2030 | 2008 | 8 | 29 | 4 | 5659.0208
2030 | 2008 | 8 | 29 | 5 | 3876.8952
2030 | 2008 | 8 | 29 | 6 | 3142.5529
2030 | 2008 | 8 | 29 | 7 | 2878.4401
2030 | 2008 | 8 | 29 | 8 | 2901.1602
2030 | 2008 | 8 | 29 | 9 | 4414.4722
2030 | 2008 | 8 | 29 | 10 | 5123.873
2030 | 2008 | 8 | 29 | 11 | 5166.54
2030 | 2008 | 8 | 29 | 12 | 5772.6173
2030 | 2008 | 8 | 29 | 13 | 8303.8376
2030 | 2008 | 8 | 29 | 14 | 10276.852
2030 | 2008 | 8 | 29 | 15 | 12473.9049
2030 | 2008 | 8 | 29 | 16 | 12795.4191
2030 | 2008 | 8 | 29 | 17 | 12630.5531
2030 | 2008 | 8 | 29 | 18 | 12331.4686
2030 | 2008 | 8 | 29 | 19 | 11711.963
2030 | 2008 | 8 | 29 | 20 | 10663.5284
2030 | 2008 | 8 | 29 | 21 | 10331.0636
2030 | 2008 | 8 | 29 | 22 | 9642.4042
2030 | 2008 | 8 | 29 | 23 | 8475.2084
2030 | 2008 | 8 | 29 | 24 | 6752.8096
2030 | 2008 | 8 | 30 | 1 | 4999.9772
2030 | 2008 | 8 | 30 | 2 | 3479.3004
2030 | 2008 | 8 | 30 | 3 | 2844.1008
2030 | 2008 | 8 | 30 | 4 | 2417.0932
2030 | 2008 | 8 | 30 | 5 | 2174.9037
2030 | 2008 | 8 | 30 | 6 | 1902.0325
2030 | 2008 | 8 | 30 | 7 | 2311.7313
2030 | 2008 | 8 | 30 | 8 | 2354.9331
2030 | 2008 | 8 | 30 | 9 | 3452.4149
2030 | 2008 | 8 | 30 | 10 | 4662.9459
2030 | 2008 | 8 | 30 | 11 | 7359.8489
2030 | 2008 | 8 | 30 | 12 | 10451.4332
2030 | 2008 | 8 | 30 | 13 | 14165.0704
2030 | 2008 | 8 | 30 | 14 | 17124.6334
2030 | 2008 | 8 | 30 | 15 | 18786.4966
2030 | 2008 | 8 | 30 | 16 | 18815.7553
2030 | 2008 | 8 | 30 | 17 | 19057.0319
2030 | 2008 | 8 | 30 | 18 | 18958.5118
2030 | 2008 | 8 | 30 | 19 | 16998.2838
2030 | 2008 | 8 | 30 | 20 | 14551.6028
2030 | 2008 | 8 | 30 | 21 | 12925.6786
2030 | 2008 | 8 | 30 | 22 | 11194.353
2030 | 2008 | 8 | 30 | 23 | 10306.1449
2030 | 2008 | 8 | 30 | 24 | 10102.9553
2030 | 2008 | 8 | 31 | 1 | 9854.9215
2030 | 2008 | 8 | 31 | 2 | 9316.3494
2030 | 2008 | 8 | 31 | 3 | 9233.7884
2030 | 2008 | 8 | 31 | 4 | 8560.6776
2030 | 2008 | 8 | 31 | 5 | 8040.5764
2030 | 2008 | 8 | 31 | 6 | 8069.2586
2030 | 2008 | 8 | 31 | 7 | 8085.4519
2030 | 2008 | 8 | 31 | 8 | 6566.7229
2030 | 2008 | 8 | 31 | 9 | 6368.7502
2030 | 2008 | 8 | 31 | 10 | 8494.7444
2030 | 2008 | 8 | 31 | 11 | 10444.1016
2030 | 2008 | 8 | 31 | 12 | 10777.1879
2030 | 2008 | 8 | 31 | 13 | 11593.7903
2030 | 2008 | 8 | 31 | 14 | 12349.8171
2030 | 2008 | 8 | 31 | 15 | 12325.5233
2030 | 2008 | 8 | 31 | 16 | 12841.7804
2030 | 2008 | 8 | 31 | 17 | 14033.9976
2030 | 2008 | 8 | 31 | 18 | 15760.4218
2030 | 2008 | 8 | 31 | 19 | 13700.3825
2030 | 2008 | 8 | 31 | 20 | 14070.3741
2030 | 2008 | 8 | 31 | 21 | 15207.8369
2030 | 2008 | 8 | 31 | 22 | 15893.9066
2030 | 2008 | 8 | 31 | 23 | 16227.2537
2030 | 2008 | 8 | 31 | 24 | 16795.0575
2026/2027 | 2008 | 1 | 1 | 1 | 23163.5738
2026/2027 | 2008 | 1 | 1 | 2 | 22786.5439
2026/2027 | 2008 | 1 | 1 | 3 | 21834.2824
2026/2027 | 2008 | 1 | 1 | 4 | 20681.6131
2026/2027 | 2008 | 1 | 1 | 5 | 19501.9175
2026/2027 | 2008 | 1 | 1 | 6 | 18852.9488
2026/2027 | 2008 | 1 | 1 | 7 | 17911.307
2026/2027 | 2008 | 1 | 1 | 8 | 16115.491
2026/2027 | 2008 | 1 | 1 | 9 | 14396.3597
2026/2027 | 2008 | 1 | 1 | 10 | 12320.9955
2026/2027 | 2008 | 1 | 1 | 11 | 14234.5317
2026/2027 | 2008 | 1 | 1 | 12 | 15664.4139
2026/2027 | 2008 | 1 | 1 | 13 | 15537.2119
2026/2027 | 2008 | 1 | 1 | 14 | 14754.5487
2026/2027 | 2008 | 1 | 1 | 15 | 14563.209
2026/2027 | 2008 | 1 | 1 | 16 | 13558.6639
2026/2027 | 2008 | 1 | 1 | 17 | 10616.6286
2026/2027 | 2008 | 1 | 1 | 18 | 10744.7284
2026/2027 | 2008 | 1 | 1 | 19 | 10530.1813
2026/2027 | 2008 | 1 | 1 | 20 | 11473.987
2026/2027 | 2008 | 1 | 1 | 21 | 11324.5395
2026/2027 | 2008 | 1 | 1 | 22 | 10074.2759
2026/2027 | 2008 | 1 | 1 | 23 | 9321.0517
2026/2027 | 2008 | 1 | 1 | 24 | 9341.5552
2026/2027 | 2008 | 1 | 2 | 1 | 9617.3429
2026/2027 | 2008 | 1 | 2 | 2 | 10209.1473
2026/2027 | 2008 | 1 | 2 | 3 | 9593.2103
2026/2027 | 2008 | 1 | 2 | 4 | 10583.8287
2026/2027 | 2008 | 1 | 2 | 5 | 10844.7647
2026/2027 | 2008 | 1 | 2 | 6 | 11130.1456
2026/2027 | 2008 | 1 | 2 | 7 | 11298.1106
2026/2027 | 2008 | 1 | 2 | 8 | 10750.2997
2026/2027 | 2008 | 1 | 2 | 9 | 8700.3668
2026/2027 | 2008 | 1 | 2 | 10 | 8421.6098
2026/2027 | 2008 | 1 | 2 | 11 | 9960.5053
2026/2027 | 2008 | 1 | 2 | 12 | 11042.2421
2026/2027 | 2008 | 1 | 2 | 13 | 11140.8049
2026/2027 | 2008 | 1 | 2 | 14 | 10954.8944
2026/2027 | 2008 | 1 | 2 | 15 | 11049.1679
2026/2027 | 2008 | 1 | 2 | 16 | 10633.9475
2026/2027 | 2008 | 1 | 2 | 17 | 9755.0667
2026/2027 | 2008 | 1 | 2 | 18 | 10370.3715
2026/2027 | 2008 | 1 | 2 | 19 | 12832.8602
2026/2027 | 2008 | 1 | 2 | 20 | 15465.4514
2026/2027 | 2008 | 1 | 2 | 21 | 17850.869
2026/2027 | 2008 | 1 | 2 | 22 | 19951.351
2026/2027 | 2008 | 1 | 2 | 23 | 20823.9767
2026/2027 | 2008 | 1 | 2 | 24 | 21345.065
2026/2027 | 2008 | 1 | 3 | 1 | 22663.5352
2026/2027 | 2008 | 1 | 3 | 2 | 23411.9652
2026/2027 | 2008 | 1 | 3 | 3 | 23890.6215
2026/2027 | 2008 | 1 | 3 | 4 | 24603.2909
2026/2027 | 2008 | 1 | 3 | 5 | 25743.5732
2026/2027 | 2008 | 1 | 3 | 6 | 27549.9445
2026/2027 | 2008 | 1 | 3 | 7 | 27878.0124
2026/2027 | 2008 | 1 | 3 | 8 | 26586.8832
2026/2027 | 2008 | 1 | 3 | 9 | 24622.5489
2026/2027 | 2008 | 1 | 3 | 10 | 25622.5275
2026/2027 | 2008 | 1 | 3 | 11 | 26078.6514
2026/2027 | 2008 | 1 | 3 | 12 | 26616.2033
2026/2027 | 2008 | 1 | 3 | 13 | 27205.4833
2026/2027 | 2008 | 1 | 3 | 14 | 27878.8801
2026/2027 | 2008 | 1 | 3 | 15 | 28944.4281
2026/2027 | 2008 | 1 | 3 | 16 | 29966.5471
2026/2027 | 2008 | 1 | 3 | 17 | 29634.68
2026/2027 | 2008 | 1 | 3 | 18 | 28799.9447
2026/2027 | 2008 | 1 | 3 | 19 | 29553.4536
2026/2027 | 2008 | 1 | 3 | 20 | 29623.0862
2026/2027 | 2008 | 1 | 3 | 21 | 30648.7591
2026/2027 | 2008 | 1 | 3 | 22 | 31132.5795
2026/2027 | 2008 | 1 | 3 | 23 | 31382.9237
2026/2027 | 2008 | 1 | 3 | 24 | 31399.9471
2026/2027 | 2008 | 1 | 4 | 1 | 30957.1562
2026/2027 | 2008 | 1 | 4 | 2 | 30501.0304
2026/2027 | 2008 | 1 | 4 | 3 | 31768.0656
2026/2027 | 2008 | 1 | 4 | 4 | 31357.7702
2026/2027 | 2008 | 1 | 4 | 5 | 31009.0711
2026/2027 | 2008 | 1 | 4 | 6 | 30489.7364
2026/2027 | 2008 | 1 | 4 | 7 | 29964.2568
2026/2027 | 2008 | 1 | 4 | 8 | 28205.0448
2026/2027 | 2008 | 1 | 4 | 9 | 27578.1868
2026/2027 | 2008 | 1 | 4 | 10 | 27658.1685
2026/2027 | 2008 | 1 | 4 | 11 | 28615.0684
2026/2027 | 2008 | 1 | 4 | 12 | 29270.288
2026/2027 | 2008 | 1 | 4 | 13 | 30849.8519
2026/2027 | 2008 | 1 | 4 | 14 | 31839.8526
2026/2027 | 2008 | 1 | 4 | 15 | 31807.5986
2026/2027 | 2008 | 1 | 4 | 16 | 32657.5987
2026/2027 | 2008 | 1 | 4 | 17 | 32263.7378
2026/2027 | 2008 | 1 | 4 | 18 | 32124.7396
2026/2027 | 2008 | 1 | 4 | 19 | 33301.9027
2026/2027 | 2008 | 1 | 4 | 20 | 33631.0146
2026/2027 | 2008 | 1 | 4 | 21 | 33843.8788
2026/2027 | 2008 | 1 | 4 | 22 | 34138.7734
2026/2027 | 2008 | 1 | 4 | 23 | 34217.8277
2026/2027 | 2008 | 1 | 4 | 24 | 34710.2857
2026/2027 | 2008 | 1 | 5 | 1 | 34761.7793
2026/2027 | 2008 | 1 | 5 | 2 | 34466.998
2026/2027 | 2008 | 1 | 5 | 3 | 33125.0941
2026/2027 | 2008 | 1 | 5 | 4 | 32185.8519
2026/2027 | 2008 | 1 | 5 | 5 | 31783.7188
2026/2027 | 2008 | 1 | 5 | 6 | 31461.0984
2026/2027 | 2008 | 1 | 5 | 7 | 31372.0958
2026/2027 | 2008 | 1 | 5 | 8 | 30588.5651
2026/2027 | 2008 | 1 | 5 | 9 | 28765.0733
2026/2027 | 2008 | 1 | 5 | 10 | 28018.4329
2026/2027 | 2008 | 1 | 5 | 11 | 28606.6862
2026/2027 | 2008 | 1 | 5 | 12 | 30961.2209
2026/2027 | 2008 | 1 | 5 | 13 | 32629.0243
2026/2027 | 2008 | 1 | 5 | 14 | 33279.2532
2026/2027 | 2008 | 1 | 5 | 15 | 33508.5125
2026/2027 | 2008 | 1 | 5 | 16 | 33147.0326
2026/2027 | 2008 | 1 | 5 | 17 | 30353.8737
2026/2027 | 2008 | 1 | 5 | 18 | 30477.5927
2026/2027 | 2008 | 1 | 5 | 19 | 32276.4021
2026/2027 | 2008 | 1 | 5 | 20 | 32794.6956
2026/2027 | 2008 | 1 | 5 | 21 | 32920.702
2026/2027 | 2008 | 1 | 5 | 22 | 32883.1616
2026/2027 | 2008 | 1 | 5 | 23 | 32897.0704
2026/2027 | 2008 | 1 | 5 | 24 | 32965.0251
2026/2027 | 2008 | 1 | 6 | 1 | 33003.4854
2026/2027 | 2008 | 1 | 6 | 2 | 32765.2332
2026/2027 | 2008 | 1 | 6 | 3 | 32597.0068
2026/2027 | 2008 | 1 | 6 | 4 | 32378.5943
2026/2027 | 2008 | 1 | 6 | 5 | 31803.6485
2026/2027 | 2008 | 1 | 6 | 6 | 31731.2439
2026/2027 | 2008 | 1 | 6 | 7 | 31363.3964
2026/2027 | 2008 | 1 | 6 | 8 | 29328.6338
2026/2027 | 2008 | 1 | 6 | 9 | 27525.5302
2026/2027 | 2008 | 1 | 6 | 10 | 28830.6966
2026/2027 | 2008 | 1 | 6 | 11 | 29049.5834
2026/2027 | 2008 | 1 | 6 | 12 | 30025.2332
2026/2027 | 2008 | 1 | 6 | 13 | 30381.1784
2026/2027 | 2008 | 1 | 6 | 14 | 29894.0142
2026/2027 | 2008 | 1 | 6 | 15 | 29417.6591
2026/2027 | 2008 | 1 | 6 | 16 | 28167.7477
2026/2027 | 2008 | 1 | 6 | 17 | 26131.3276
2026/2027 | 2008 | 1 | 6 | 18 | 27387.1788
2026/2027 | 2008 | 1 | 6 | 19 | 29702.0017
2026/2027 | 2008 | 1 | 6 | 20 | 30399.159
2026/2027 | 2008 | 1 | 6 | 21 | 30291.9788
2026/2027 | 2008 | 1 | 6 | 22 | 31059.3165
2026/2027 | 2008 | 1 | 6 | 23 | 30866.9858
2026/2027 | 2008 | 1 | 6 | 24 | 31997.2754
2026/2027 | 2008 | 1 | 7 | 1 | 31507.8753
2026/2027 | 2008 | 1 | 7 | 2 | 30704.3299
2026/2027 | 2008 | 1 | 7 | 3 | 30134.8124
2026/2027 | 2008 | 1 | 7 | 4 | 29143.2856
2026/2027 | 2008 | 1 | 7 | 5 | 28978.1664
2026/2027 | 2008 | 1 | 7 | 6 | 28569.6387
2026/2027 | 2008 | 1 | 7 | 7 | 28075.4609
2026/2027 | 2008 | 1 | 7 | 8 | 26032.8989
2026/2027 | 2008 | 1 | 7 | 9 | 23458.5279
2026/2027 | 2008 | 1 | 7 | 10 | 23254.3802
2026/2027 | 2008 | 1 | 7 | 11 | 23035.3954
2026/2027 | 2008 | 1 | 7 | 12 | 23042.6445
2026/2027 | 2008 | 1 | 7 | 13 | 23215.1324
2026/2027 | 2008 | 1 | 7 | 14 | 22944.7383
2026/2027 | 2008 | 1 | 7 | 15 | 22990.8556
2026/2027 | 2008 | 1 | 7 | 16 | 22366.1392
2026/2027 | 2008 | 1 | 7 | 17 | 21143.7647
2026/2027 | 2008 | 1 | 7 | 18 | 23315.3782
2026/2027 | 2008 | 1 | 7 | 19 | 25329.5049
2026/2027 | 2008 | 1 | 7 | 20 | 26278.1121
2026/2027 | 2008 | 1 | 7 | 21 | 26571.8889
2026/2027 | 2008 | 1 | 7 | 22 | 27288.1407
2026/2027 | 2008 | 1 | 7 | 23 | 27915.6287
2026/2027 | 2008 | 1 | 7 | 24 | 28137.3128
2026/2027 | 2008 | 1 | 8 | 1 | 29776.6012
2026/2027 | 2008 | 1 | 8 | 2 | 32121.8698
2026/2027 | 2008 | 1 | 8 | 3 | 32778.9822
2026/2027 | 2008 | 1 | 8 | 4 | 32281.4453
2026/2027 | 2008 | 1 | 8 | 5 | 31214.8936
2026/2027 | 2008 | 1 | 8 | 6 | 27210.9913
2026/2027 | 2008 | 1 | 8 | 7 | 29060.3734
2026/2027 | 2008 | 1 | 8 | 8 | 27616.0811
2026/2027 | 2008 | 1 | 8 | 9 | 25582.1112
2026/2027 | 2008 | 1 | 8 | 10 | 26823.7422
2026/2027 | 2008 | 1 | 8 | 11 | 28245.946
2026/2027 | 2008 | 1 | 8 | 12 | 27983.3294
2026/2027 | 2008 | 1 | 8 | 13 | 25855.7927
2026/2027 | 2008 | 1 | 8 | 14 | 22717.8915
2026/2027 | 2008 | 1 | 8 | 15 | 19703.3869
2026/2027 | 2008 | 1 | 8 | 16 | 16752.6236
2026/2027 | 2008 | 1 | 8 | 17 | 11446.9116
2026/2027 | 2008 | 1 | 8 | 18 | 9536.8787
2026/2027 | 2008 | 1 | 8 | 19 | 9041.9994
2026/2027 | 2008 | 1 | 8 | 20 | 8727.8489
2026/2027 | 2008 | 1 | 8 | 21 | 8760.6499
2026/2027 | 2008 | 1 | 8 | 22 | 9208.1181
2026/2027 | 2008 | 1 | 8 | 23 | 10145.2797
2026/2027 | 2008 | 1 | 8 | 24 | 11413.3075
2026/2027 | 2008 | 1 | 9 | 1 | 14248.9062
2026/2027 | 2008 | 1 | 9 | 2 | 17036.1005
2026/2027 | 2008 | 1 | 9 | 3 | 20376.6395
2026/2027 | 2008 | 1 | 9 | 4 | 21851.0217
2026/2027 | 2008 | 1 | 9 | 5 | 22558.6059
2026/2027 | 2008 | 1 | 9 | 6 | 23215.6112
2026/2027 | 2008 | 1 | 9 | 7 | 23515.0655
2026/2027 | 2008 | 1 | 9 | 8 | 22885.2475
2026/2027 | 2008 | 1 | 9 | 9 | 21028.7555
2026/2027 | 2008 | 1 | 9 | 10 | 16786.1621
2026/2027 | 2008 | 1 | 9 | 11 | 20290.5933
2026/2027 | 2008 | 1 | 9 | 12 | 22123.7887
2026/2027 | 2008 | 1 | 9 | 13 | 20985.6337
2026/2027 | 2008 | 1 | 9 | 14 | 21952.9152
2026/2027 | 2008 | 1 | 9 | 15 | 22369.0781
2026/2027 | 2008 | 1 | 9 | 16 | 22155.4372
2026/2027 | 2008 | 1 | 9 | 17 | 20876.9739
2026/2027 | 2008 | 1 | 9 | 18 | 22893.8547
2026/2027 | 2008 | 1 | 9 | 19 | 25361.5316
2026/2027 | 2008 | 1 | 9 | 20 | 26269.4791
2026/2027 | 2008 | 1 | 9 | 21 | 26590.6592
2026/2027 | 2008 | 1 | 9 | 22 | 28594.5137
2026/2027 | 2008 | 1 | 9 | 23 | 28357.31
2026/2027 | 2008 | 1 | 9 | 24 | 27443.6513
2026/2027 | 2008 | 1 | 10 | 1 | 25916.6318
2026/2027 | 2008 | 1 | 10 | 2 | 25275.2184
2026/2027 | 2008 | 1 | 10 | 3 | 26208.5181
2026/2027 | 2008 | 1 | 10 | 4 | 26873.9035
2026/2027 | 2008 | 1 | 10 | 5 | 26286.1632
2026/2027 | 2008 | 1 | 10 | 6 | 26188.9934
2026/2027 | 2008 | 1 | 10 | 7 | 25892.9417
2026/2027 | 2008 | 1 | 10 | 8 | 24744.1233
2026/2027 | 2008 | 1 | 10 | 9 | 21504.6697
2026/2027 | 2008 | 1 | 10 | 10 | 19362.7679
2026/2027 | 2008 | 1 | 10 | 11 | 21236.3081
2026/2027 | 2008 | 1 | 10 | 12 | 21963.4098
2026/2027 | 2008 | 1 | 10 | 13 | 20548.7204
2026/2027 | 2008 | 1 | 10 | 14 | 18672.245
2026/2027 | 2008 | 1 | 10 | 15 | 16504.4809
2026/2027 | 2008 | 1 | 10 | 16 | 13561.3356
2026/2027 | 2008 | 1 | 10 | 17 | 9324.2983
2026/2027 | 2008 | 1 | 10 | 18 | 7101.5113
2026/2027 | 2008 | 1 | 10 | 19 | 6631.4338
2026/2027 | 2008 | 1 | 10 | 20 | 6346.8124
2026/2027 | 2008 | 1 | 10 | 21 | 6992.5052
2026/2027 | 2008 | 1 | 10 | 22 | 7768.6693
2026/2027 | 2008 | 1 | 10 | 23 | 9325.0625
2026/2027 | 2008 | 1 | 10 | 24 | 11370.0724
2026/2027 | 2008 | 1 | 11 | 1 | 13713.9286
2026/2027 | 2008 | 1 | 11 | 2 | 15095.5577
2026/2027 | 2008 | 1 | 11 | 3 | 17294.5999
2026/2027 | 2008 | 1 | 11 | 4 | 18985.0068
2026/2027 | 2008 | 1 | 11 | 5 | 20426.1823
2026/2027 | 2008 | 1 | 11 | 6 | 21045.6617
2026/2027 | 2008 | 1 | 11 | 7 | 21015.6579
2026/2027 | 2008 | 1 | 11 | 8 | 19998.514
2026/2027 | 2008 | 1 | 11 | 9 | 16321.9338
2026/2027 | 2008 | 1 | 11 | 10 | 10443.6254
2026/2027 | 2008 | 1 | 11 | 11 | 9498.3364
2026/2027 | 2008 | 1 | 11 | 12 | 10243.5041
2026/2027 | 2008 | 1 | 11 | 13 | 9900.2734
2026/2027 | 2008 | 1 | 11 | 14 | 9716.9009
2026/2027 | 2008 | 1 | 11 | 15 | 9338.8351
2026/2027 | 2008 | 1 | 11 | 16 | 8334.5992
2026/2027 | 2008 | 1 | 11 | 17 | 6804.336
2026/2027 | 2008 | 1 | 11 | 18 | 6927.7667
2026/2027 | 2008 | 1 | 11 | 19 | 9162.6318
2026/2027 | 2008 | 1 | 11 | 20 | 11033.4073
2026/2027 | 2008 | 1 | 11 | 21 | 13337.8607
2026/2027 | 2008 | 1 | 11 | 22 | 15066.083
2026/2027 | 2008 | 1 | 11 | 23 | 15930.8298
2026/2027 | 2008 | 1 | 11 | 24 | 17886.1673
2026/2027 | 2008 | 1 | 12 | 1 | 20046.9344
2026/2027 | 2008 | 1 | 12 | 2 | 20447.1947
2026/2027 | 2008 | 1 | 12 | 3 | 20734.4187
2026/2027 | 2008 | 1 | 12 | 4 | 21863.1592
2026/2027 | 2008 | 1 | 12 | 5 | 22432.779
2026/2027 | 2008 | 1 | 12 | 6 | 22911.63
2026/2027 | 2008 | 1 | 12 | 7 | 24191.7672
2026/2027 | 2008 | 1 | 12 | 8 | 23804.9771
2026/2027 | 2008 | 1 | 12 | 9 | 20028.5792
2026/2027 | 2008 | 1 | 12 | 10 | 16398.8767
2026/2027 | 2008 | 1 | 12 | 11 | 17156.0147
2026/2027 | 2008 | 1 | 12 | 12 | 16422.7777
2026/2027 | 2008 | 1 | 12 | 13 | 17041.0216
2026/2027 | 2008 | 1 | 12 | 14 | 17741.8015
2026/2027 | 2008 | 1 | 12 | 15 | 17657.5941
2026/2027 | 2008 | 1 | 12 | 16 | 16792.8087
2026/2027 | 2008 | 1 | 12 | 17 | 12993.1166
2026/2027 | 2008 | 1 | 12 | 18 | 10995.6555
2026/2027 | 2008 | 1 | 12 | 19 | 11268.4742
2026/2027 | 2008 | 1 | 12 | 20 | 10927.0405
2026/2027 | 2008 | 1 | 12 | 21 | 11322.1667
2026/2027 | 2008 | 1 | 12 | 22 | 11218.7347
2026/2027 | 2008 | 1 | 12 | 23 | 10680.151
2026/2027 | 2008 | 1 | 12 | 24 | 10736.3784
2026/2027 | 2008 | 1 | 13 | 1 | 11237.7229
2026/2027 | 2008 | 1 | 13 | 2 | 11402.8265
2026/2027 | 2008 | 1 | 13 | 3 | 11408.5378
2026/2027 | 2008 | 1 | 13 | 4 | 11093.6728
2026/2027 | 2008 | 1 | 13 | 5 | 10940.3373
2026/2027 | 2008 | 1 | 13 | 6 | 10858.0375
2026/2027 | 2008 | 1 | 13 | 7 | 10543.679
2026/2027 | 2008 | 1 | 13 | 8 | 9821.1787
2026/2027 | 2008 | 1 | 13 | 9 | 6716.4098
2026/2027 | 2008 | 1 | 13 | 10 | 4367.2659
2026/2027 | 2008 | 1 | 13 | 11 | 3959.7882
2026/2027 | 2008 | 1 | 13 | 12 | 3824.7124
2026/2027 | 2008 | 1 | 13 | 13 | 3893.1743
2026/2027 | 2008 | 1 | 13 | 14 | 4540.9233
2026/2027 | 2008 | 1 | 13 | 15 | 5262.6532
2026/2027 | 2008 | 1 | 13 | 16 | 5807.8218
2026/2027 | 2008 | 1 | 13 | 17 | 5918.6801
2026/2027 | 2008 | 1 | 13 | 18 | 6863.1492
2026/2027 | 2008 | 1 | 13 | 19 | 9059.6903
2026/2027 | 2008 | 1 | 13 | 20 | 11701.689
2026/2027 | 2008 | 1 | 13 | 21 | 13369.0687
2026/2027 | 2008 | 1 | 13 | 22 | 14807.7056
2026/2027 | 2008 | 1 | 13 | 23 | 16180.5657
2026/2027 | 2008 | 1 | 13 | 24 | 17685.8447
2026/2027 | 2008 | 1 | 14 | 1 | 17210.1903
2026/2027 | 2008 | 1 | 14 | 2 | 15810.5621
2026/2027 | 2008 | 1 | 14 | 3 | 14790.3166
2026/2027 | 2008 | 1 | 14 | 4 | 13096.0873
2026/2027 | 2008 | 1 | 14 | 5 | 11722.4432
2026/2027 | 2008 | 1 | 14 | 6 | 11069.3665
2026/2027 | 2008 | 1 | 14 | 7 | 10088.1462
2026/2027 | 2008 | 1 | 14 | 8 | 9156.2718
2026/2027 | 2008 | 1 | 14 | 9 | 7810.0691
2026/2027 | 2008 | 1 | 14 | 10 | 7127.1844
2026/2027 | 2008 | 1 | 14 | 11 | 7583.3018
2026/2027 | 2008 | 1 | 14 | 12 | 8301.3266
2026/2027 | 2008 | 1 | 14 | 13 | 8463.848
2026/2027 | 2008 | 1 | 14 | 14 | 8702.0513
2026/2027 | 2008 | 1 | 14 | 15 | 8760.6348
2026/2027 | 2008 | 1 | 14 | 16 | 8489.237
2026/2027 | 2008 | 1 | 14 | 17 | 7865.7559
2026/2027 | 2008 | 1 | 14 | 18 | 7621.5657
2026/2027 | 2008 | 1 | 14 | 19 | 7775.626
2026/2027 | 2008 | 1 | 14 | 20 | 7916.5655
2026/2027 | 2008 | 1 | 14 | 21 | 7904.2824
2026/2027 | 2008 | 1 | 14 | 22 | 8088.0651
2026/2027 | 2008 | 1 | 14 | 23 | 8678.3013
2026/2027 | 2008 | 1 | 14 | 24 | 9460.1643
2026/2027 | 2008 | 1 | 15 | 1 | 10405.2103
2026/2027 | 2008 | 1 | 15 | 2 | 11422.1082
2026/2027 | 2008 | 1 | 15 | 3 | 13150.9374
2026/2027 | 2008 | 1 | 15 | 4 | 14671.8964
2026/2027 | 2008 | 1 | 15 | 5 | 16840.3996
2026/2027 | 2008 | 1 | 15 | 6 | 18231.6624
2026/2027 | 2008 | 1 | 15 | 7 | 19998.3038
2026/2027 | 2008 | 1 | 15 | 8 | 20948.1734
2026/2027 | 2008 | 1 | 15 | 9 | 20437.305
2026/2027 | 2008 | 1 | 15 | 10 | 19793.6087
2026/2027 | 2008 | 1 | 15 | 11 | 22654.0558
2026/2027 | 2008 | 1 | 15 | 12 | 26804.5487
2026/2027 | 2008 | 1 | 15 | 13 | 28925.0599
2026/2027 | 2008 | 1 | 15 | 14 | 29594.2311
2026/2027 | 2008 | 1 | 15 | 15 | 29832.0736
2026/2027 | 2008 | 1 | 15 | 16 | 30417.7226
2026/2027 | 2008 | 1 | 15 | 17 | 30219.3882
2026/2027 | 2008 | 1 | 15 | 18 | 30328.2063
2026/2027 | 2008 | 1 | 15 | 19 | 31721.013
2026/2027 | 2008 | 1 | 15 | 20 | 31680.3447
2026/2027 | 2008 | 1 | 15 | 21 | 32237.1835
2026/2027 | 2008 | 1 | 15 | 22 | 32667.9613
2026/2027 | 2008 | 1 | 15 | 23 | 31644.3728
2026/2027 | 2008 | 1 | 15 | 24 | 31480.9458
2026/2027 | 2008 | 1 | 16 | 1 | 31490.7764
2026/2027 | 2008 | 1 | 16 | 2 | 30979.9651
2026/2027 | 2008 | 1 | 16 | 3 | 30851.9319
2026/2027 | 2008 | 1 | 16 | 4 | 30460.5529
2026/2027 | 2008 | 1 | 16 | 5 | 28332.3331
2026/2027 | 2008 | 1 | 16 | 6 | 26182.4196
2026/2027 | 2008 | 1 | 16 | 7 | 24752.8469
2026/2027 | 2008 | 1 | 16 | 8 | 22235.5574
2026/2027 | 2008 | 1 | 16 | 9 | 18170.9458
2026/2027 | 2008 | 1 | 16 | 10 | 17220.9358
2026/2027 | 2008 | 1 | 16 | 11 | 16232.849
2026/2027 | 2008 | 1 | 16 | 12 | 17314.8293
2026/2027 | 2008 | 1 | 16 | 13 | 16395.5784
2026/2027 | 2008 | 1 | 16 | 14 | 15611.703
2026/2027 | 2008 | 1 | 16 | 15 | 16048.5357
2026/2027 | 2008 | 1 | 16 | 16 | 15979.4196
2026/2027 | 2008 | 1 | 16 | 17 | 16001.3878
2026/2027 | 2008 | 1 | 16 | 18 | 17215.6493
2026/2027 | 2008 | 1 | 16 | 19 | 19892.2116
2026/2027 | 2008 | 1 | 16 | 20 | 21888.4621
2026/2027 | 2008 | 1 | 16 | 21 | 22330.6529
2026/2027 | 2008 | 1 | 16 | 22 | 22118.7135
2026/2027 | 2008 | 1 | 16 | 23 | 22986.9474
2026/2027 | 2008 | 1 | 16 | 24 | 22598.6733
2026/2027 | 2008 | 1 | 17 | 1 | 22023.6661
2026/2027 | 2008 | 1 | 17 | 2 | 21307.7918
2026/2027 | 2008 | 1 | 17 | 3 | 21434.5183
2026/2027 | 2008 | 1 | 17 | 4 | 20202.9358
2026/2027 | 2008 | 1 | 17 | 5 | 19177.2505
2026/2027 | 2008 | 1 | 17 | 6 | 18190.5089
2026/2027 | 2008 | 1 | 17 | 7 | 16502.4453
2026/2027 | 2008 | 1 | 17 | 8 | 14691.9745
2026/2027 | 2008 | 1 | 17 | 9 | 12071.4557
2026/2027 | 2008 | 1 | 17 | 10 | 13064.9159
2026/2027 | 2008 | 1 | 17 | 11 | 12296.8134
2026/2027 | 2008 | 1 | 17 | 12 | 10588.808
2026/2027 | 2008 | 1 | 17 | 13 | 10233.0104
2026/2027 | 2008 | 1 | 17 | 14 | 9679.0992
2026/2027 | 2008 | 1 | 17 | 15 | 9090.9488
2026/2027 | 2008 | 1 | 17 | 16 | 8456.7926
2026/2027 | 2008 | 1 | 17 | 17 | 6998.6133
2026/2027 | 2008 | 1 | 17 | 18 | 5479.1161
2026/2027 | 2008 | 1 | 17 | 19 | 5717.1499
2026/2027 | 2008 | 1 | 17 | 20 | 6582.6717
2026/2027 | 2008 | 1 | 17 | 21 | 7827.35
2026/2027 | 2008 | 1 | 17 | 22 | 8786.3288
2026/2027 | 2008 | 1 | 17 | 23 | 9301.6877
2026/2027 | 2008 | 1 | 17 | 24 | 9558.4938
2026/2027 | 2008 | 1 | 18 | 1 | 10583.2589
2026/2027 | 2008 | 1 | 18 | 2 | 11085.2935
2026/2027 | 2008 | 1 | 18 | 3 | 11480.5879
2026/2027 | 2008 | 1 | 18 | 4 | 11426.8274
2026/2027 | 2008 | 1 | 18 | 5 | 10804.9235
2026/2027 | 2008 | 1 | 18 | 6 | 10556.6164
2026/2027 | 2008 | 1 | 18 | 7 | 9741.1613
2026/2027 | 2008 | 1 | 18 | 8 | 8620.0828
2026/2027 | 2008 | 1 | 18 | 9 | 8737.4718
2026/2027 | 2008 | 1 | 18 | 10 | 8857.0274
2026/2027 | 2008 | 1 | 18 | 11 | 9531.9622
2026/2027 | 2008 | 1 | 18 | 12 | 10021.0442
2026/2027 | 2008 | 1 | 18 | 13 | 10824.7662
2026/2027 | 2008 | 1 | 18 | 14 | 10958.5268
2026/2027 | 2008 | 1 | 18 | 15 | 10996.2641
2026/2027 | 2008 | 1 | 18 | 16 | 10913.3411
2026/2027 | 2008 | 1 | 18 | 17 | 10674.3511
2026/2027 | 2008 | 1 | 18 | 18 | 11486.4677
2026/2027 | 2008 | 1 | 18 | 19 | 12695.92
2026/2027 | 2008 | 1 | 18 | 20 | 13749.7503
2026/2027 | 2008 | 1 | 18 | 21 | 15327.8157
2026/2027 | 2008 | 1 | 18 | 22 | 16540.6335
2026/2027 | 2008 | 1 | 18 | 23 | 17237.9714
2026/2027 | 2008 | 1 | 18 | 24 | 18764.9181
2026/2027 | 2008 | 1 | 19 | 1 | 20273.5728
2026/2027 | 2008 | 1 | 19 | 2 | 20900.6865
2026/2027 | 2008 | 1 | 19 | 3 | 20774.7474
2026/2027 | 2008 | 1 | 19 | 4 | 19629.4927
2026/2027 | 2008 | 1 | 19 | 5 | 19297.4173
2026/2027 | 2008 | 1 | 19 | 6 | 18967.8931
2026/2027 | 2008 | 1 | 19 | 7 | 18345.0784
2026/2027 | 2008 | 1 | 19 | 8 | 17167.6537
2026/2027 | 2008 | 1 | 19 | 9 | 13333.7228
2026/2027 | 2008 | 1 | 19 | 10 | 13634.159
2026/2027 | 2008 | 1 | 19 | 11 | 13658.9303
2026/2027 | 2008 | 1 | 19 | 12 | 12917.6964
2026/2027 | 2008 | 1 | 19 | 13 | 12093.0719
2026/2027 | 2008 | 1 | 19 | 14 | 11788.1307
2026/2027 | 2008 | 1 | 19 | 15 | 11096.9011
2026/2027 | 2008 | 1 | 19 | 16 | 10129.7082
2026/2027 | 2008 | 1 | 19 | 17 | 8129.9059
2026/2027 | 2008 | 1 | 19 | 18 | 7413.4174
2026/2027 | 2008 | 1 | 19 | 19 | 9216.1726
2026/2027 | 2008 | 1 | 19 | 20 | 11026.1756
2026/2027 | 2008 | 1 | 19 | 21 | 11724.585
2026/2027 | 2008 | 1 | 19 | 22 | 14088.0989
2026/2027 | 2008 | 1 | 19 | 23 | 17114.3932
2026/2027 | 2008 | 1 | 19 | 24 | 20505.9418
2026/2027 | 2008 | 1 | 20 | 1 | 23294.1993
2026/2027 | 2008 | 1 | 20 | 2 | 25434.4443
2026/2027 | 2008 | 1 | 20 | 3 | 26363.217
2026/2027 | 2008 | 1 | 20 | 4 | 26886.4877
2026/2027 | 2008 | 1 | 20 | 5 | 27116.2375
2026/2027 | 2008 | 1 | 20 | 6 | 27109.3815
2026/2027 | 2008 | 1 | 20 | 7 | 27675.3032
2026/2027 | 2008 | 1 | 20 | 8 | 26413.9844
2026/2027 | 2008 | 1 | 20 | 9 | 23517.1381
2026/2027 | 2008 | 1 | 20 | 10 | 22287.2994
2026/2027 | 2008 | 1 | 20 | 11 | 24629.8454
2026/2027 | 2008 | 1 | 20 | 12 | 25883.8751
2026/2027 | 2008 | 1 | 20 | 13 | 28795.3622
2026/2027 | 2008 | 1 | 20 | 14 | 29966.1339
2026/2027 | 2008 | 1 | 20 | 15 | 29095.4571
2026/2027 | 2008 | 1 | 20 | 16 | 29806.4679
2026/2027 | 2008 | 1 | 20 | 17 | 29533.5417
2026/2027 | 2008 | 1 | 20 | 18 | 29601.6024
2026/2027 | 2008 | 1 | 20 | 19 | 29720.4805
2026/2027 | 2008 | 1 | 20 | 20 | 30348.3019
2026/2027 | 2008 | 1 | 20 | 21 | 31802.0817
2026/2027 | 2008 | 1 | 20 | 22 | 32593.4153
2026/2027 | 2008 | 1 | 20 | 23 | 32182.5219
2026/2027 | 2008 | 1 | 20 | 24 | 31988.0602
2026/2027 | 2008 | 1 | 21 | 1 | 31322.3767
2026/2027 | 2008 | 1 | 21 | 2 | 29102.0573
2026/2027 | 2008 | 1 | 21 | 3 | 27202.1446
2026/2027 | 2008 | 1 | 21 | 4 | 28372.7843
2026/2027 | 2008 | 1 | 21 | 5 | 27757.5293
2026/2027 | 2008 | 1 | 21 | 6 | 28207.8687
2026/2027 | 2008 | 1 | 21 | 7 | 28359.2526
2026/2027 | 2008 | 1 | 21 | 8 | 27236.322
2026/2027 | 2008 | 1 | 21 | 9 | 25012.6852
2026/2027 | 2008 | 1 | 21 | 10 | 26526.8216
2026/2027 | 2008 | 1 | 21 | 11 | 26379.0044
2026/2027 | 2008 | 1 | 21 | 12 | 25183.9791
2026/2027 | 2008 | 1 | 21 | 13 | 24193.167
2026/2027 | 2008 | 1 | 21 | 14 | 23910.2293
2026/2027 | 2008 | 1 | 21 | 15 | 22851.4577
2026/2027 | 2008 | 1 | 21 | 16 | 21710.8778
2026/2027 | 2008 | 1 | 21 | 17 | 19484.3291
2026/2027 | 2008 | 1 | 21 | 18 | 19774.5128
2026/2027 | 2008 | 1 | 21 | 19 | 20633.2488
2026/2027 | 2008 | 1 | 21 | 20 | 21330.3367
2026/2027 | 2008 | 1 | 21 | 21 | 21507.2213
2026/2027 | 2008 | 1 | 21 | 22 | 20187.2435
2026/2027 | 2008 | 1 | 21 | 23 | 19572.6596
2026/2027 | 2008 | 1 | 21 | 24 | 18910.1673
2026/2027 | 2008 | 1 | 22 | 1 | 18450.3336
2026/2027 | 2008 | 1 | 22 | 2 | 17112.8062
2026/2027 | 2008 | 1 | 22 | 3 | 14923.2396
2026/2027 | 2008 | 1 | 22 | 4 | 12901.2921
2026/2027 | 2008 | 1 | 22 | 5 | 12348.4344
2026/2027 | 2008 | 1 | 22 | 6 | 12953.2127
2026/2027 | 2008 | 1 | 22 | 7 | 14072.9958
2026/2027 | 2008 | 1 | 22 | 8 | 15034.072
2026/2027 | 2008 | 1 | 22 | 9 | 12672.4401
2026/2027 | 2008 | 1 | 22 | 10 | 13066.3455
2026/2027 | 2008 | 1 | 22 | 11 | 12727.843
2026/2027 | 2008 | 1 | 22 | 12 | 11255.8982
2026/2027 | 2008 | 1 | 22 | 13 | 9649.4388
2026/2027 | 2008 | 1 | 22 | 14 | 8014.2955
2026/2027 | 2008 | 1 | 22 | 15 | 6685.7305
2026/2027 | 2008 | 1 | 22 | 16 | 6503.5667
2026/2027 | 2008 | 1 | 22 | 17 | 6168.2936
2026/2027 | 2008 | 1 | 22 | 18 | 6298.4368
2026/2027 | 2008 | 1 | 22 | 19 | 6244.3904
2026/2027 | 2008 | 1 | 22 | 20 | 6401.2218
2026/2027 | 2008 | 1 | 22 | 21 | 6264.5629
2026/2027 | 2008 | 1 | 22 | 22 | 6093.8173
2026/2027 | 2008 | 1 | 22 | 23 | 6518.4756
2026/2027 | 2008 | 1 | 22 | 24 | 6662.5475
2026/2027 | 2008 | 1 | 23 | 1 | 7809.8504
2026/2027 | 2008 | 1 | 23 | 2 | 8687.9551
2026/2027 | 2008 | 1 | 23 | 3 | 9105.711
2026/2027 | 2008 | 1 | 23 | 4 | 8966.2318
2026/2027 | 2008 | 1 | 23 | 5 | 8769.7637
2026/2027 | 2008 | 1 | 23 | 6 | 8449.396
2026/2027 | 2008 | 1 | 23 | 7 | 7884.2346
2026/2027 | 2008 | 1 | 23 | 8 | 7410.4798
2026/2027 | 2008 | 1 | 23 | 9 | 6837.7082
2026/2027 | 2008 | 1 | 23 | 10 | 6195.4205
2026/2027 | 2008 | 1 | 23 | 11 | 6211.5153
2026/2027 | 2008 | 1 | 23 | 12 | 6168.588
2026/2027 | 2008 | 1 | 23 | 13 | 6411.3169
2026/2027 | 2008 | 1 | 23 | 14 | 6614.0854
2026/2027 | 2008 | 1 | 23 | 15 | 6852.8855
2026/2027 | 2008 | 1 | 23 | 16 | 7476.0085
2026/2027 | 2008 | 1 | 23 | 17 | 7278.1654
2026/2027 | 2008 | 1 | 23 | 18 | 8085.6172
2026/2027 | 2008 | 1 | 23 | 19 | 9879.0217
2026/2027 | 2008 | 1 | 23 | 20 | 12760.9967
2026/2027 | 2008 | 1 | 23 | 21 | 14117.5791
2026/2027 | 2008 | 1 | 23 | 22 | 15488.3311
2026/2027 | 2008 | 1 | 23 | 23 | 17494.472
2026/2027 | 2008 | 1 | 23 | 24 | 19290.3851
2026/2027 | 2008 | 1 | 24 | 1 | 21503.0615
2026/2027 | 2008 | 1 | 24 | 2 | 22324.9004
2026/2027 | 2008 | 1 | 24 | 3 | 22675.2503
2026/2027 | 2008 | 1 | 24 | 4 | 21503.5716
2026/2027 | 2008 | 1 | 24 | 5 | 20999.7544
2026/2027 | 2008 | 1 | 24 | 6 | 20604.4211
2026/2027 | 2008 | 1 | 24 | 7 | 18520.6913
2026/2027 | 2008 | 1 | 24 | 8 | 16850.3055
2026/2027 | 2008 | 1 | 24 | 9 | 14489.5192
2026/2027 | 2008 | 1 | 24 | 10 | 15927.9764
2026/2027 | 2008 | 1 | 24 | 11 | 16403.5023
2026/2027 | 2008 | 1 | 24 | 12 | 15558.7137
2026/2027 | 2008 | 1 | 24 | 13 | 15347.1748
2026/2027 | 2008 | 1 | 24 | 14 | 15339.1133
2026/2027 | 2008 | 1 | 24 | 15 | 15301.768
2026/2027 | 2008 | 1 | 24 | 16 | 14712.1749
2026/2027 | 2008 | 1 | 24 | 17 | 13172.6668
2026/2027 | 2008 | 1 | 24 | 18 | 12505.9394
2026/2027 | 2008 | 1 | 24 | 19 | 12930.8068
2026/2027 | 2008 | 1 | 24 | 20 | 12371.0361
2026/2027 | 2008 | 1 | 24 | 21 | 12330.079
2026/2027 | 2008 | 1 | 24 | 22 | 11949.0915
2026/2027 | 2008 | 1 | 24 | 23 | 11295.358
2026/2027 | 2008 | 1 | 24 | 24 | 10979.5568
2026/2027 | 2008 | 1 | 25 | 1 | 11380.5992
2026/2027 | 2008 | 1 | 25 | 2 | 11527.588
2026/2027 | 2008 | 1 | 25 | 3 | 10949.4223
2026/2027 | 2008 | 1 | 25 | 4 | 11147.8064
2026/2027 | 2008 | 1 | 25 | 5 | 11666.4475
2026/2027 | 2008 | 1 | 25 | 6 | 12484.1647
2026/2027 | 2008 | 1 | 25 | 7 | 11849.0236
2026/2027 | 2008 | 1 | 25 | 8 | 10813.4247
2026/2027 | 2008 | 1 | 25 | 9 | 10125.2012
2026/2027 | 2008 | 1 | 25 | 10 | 11167.9177
2026/2027 | 2008 | 1 | 25 | 11 | 11713.2673
2026/2027 | 2008 | 1 | 25 | 12 | 11147.1875
2026/2027 | 2008 | 1 | 25 | 13 | 11660.0324
2026/2027 | 2008 | 1 | 25 | 14 | 12157.4253
2026/2027 | 2008 | 1 | 25 | 15 | 12067.6598
2026/2027 | 2008 | 1 | 25 | 16 | 12127.9867
2026/2027 | 2008 | 1 | 25 | 17 | 10480.8279
2026/2027 | 2008 | 1 | 25 | 18 | 11079.3632
2026/2027 | 2008 | 1 | 25 | 19 | 13229.196
2026/2027 | 2008 | 1 | 25 | 20 | 15415.7687
2026/2027 | 2008 | 1 | 25 | 21 | 17315.8328
2026/2027 | 2008 | 1 | 25 | 22 | 18484.2781
2026/2027 | 2008 | 1 | 25 | 23 | 18112.2557
2026/2027 | 2008 | 1 | 25 | 24 | 18288.9171
2026/2027 | 2008 | 1 | 26 | 1 | 18572.7229
2026/2027 | 2008 | 1 | 26 | 2 | 18137.4846
2026/2027 | 2008 | 1 | 26 | 3 | 18130.0349
2026/2027 | 2008 | 1 | 26 | 4 | 17758.5849
2026/2027 | 2008 | 1 | 26 | 5 | 17806.3816
2026/2027 | 2008 | 1 | 26 | 6 | 18656.9758
2026/2027 | 2008 | 1 | 26 | 7 | 19281.2515
2026/2027 | 2008 | 1 | 26 | 8 | 19045.5804
2026/2027 | 2008 | 1 | 26 | 9 | 17138.8722
2026/2027 | 2008 | 1 | 26 | 10 | 12825.1321
2026/2027 | 2008 | 1 | 26 | 11 | 9360.1153
2026/2027 | 2008 | 1 | 26 | 12 | 7422.8272
2026/2027 | 2008 | 1 | 26 | 13 | 6218.4149
2026/2027 | 2008 | 1 | 26 | 14 | 4361.2179
2026/2027 | 2008 | 1 | 26 | 15 | 2801.3327
2026/2027 | 2008 | 1 | 26 | 16 | 1577.4209
2026/2027 | 2008 | 1 | 26 | 17 | 1030.6588
2026/2027 | 2008 | 1 | 26 | 18 | 1183.4919
2026/2027 | 2008 | 1 | 26 | 19 | 1532.1046
2026/2027 | 2008 | 1 | 26 | 20 | 2042.8737
2026/2027 | 2008 | 1 | 26 | 21 | 3230.1681
2026/2027 | 2008 | 1 | 26 | 22 | 4348.5577
2026/2027 | 2008 | 1 | 26 | 23 | 5346.1108
2026/2027 | 2008 | 1 | 26 | 24 | 6831.7071
2026/2027 | 2008 | 1 | 27 | 1 | 8453.644
2026/2027 | 2008 | 1 | 27 | 2 | 9369.8392
2026/2027 | 2008 | 1 | 27 | 3 | 10023.8749
2026/2027 | 2008 | 1 | 27 | 4 | 10287.527
2026/2027 | 2008 | 1 | 27 | 5 | 10954.245
2026/2027 | 2008 | 1 | 27 | 6 | 11377.878
2026/2027 | 2008 | 1 | 27 | 7 | 12911.5977
2026/2027 | 2008 | 1 | 27 | 8 | 13952.5986
2026/2027 | 2008 | 1 | 27 | 9 | 14899.3811
2026/2027 | 2008 | 1 | 27 | 10 | 14098.4048
2026/2027 | 2008 | 1 | 27 | 11 | 12025.0603
2026/2027 | 2008 | 1 | 27 | 12 | 14738.7566
2026/2027 | 2008 | 1 | 27 | 13 | 18336.9448
2026/2027 | 2008 | 1 | 27 | 14 | 21019.4953
2026/2027 | 2008 | 1 | 27 | 15 | 22935.1199
2026/2027 | 2008 | 1 | 27 | 16 | 24266.6404
2026/2027 | 2008 | 1 | 27 | 17 | 24753.0722
2026/2027 | 2008 | 1 | 27 | 18 | 27177.9358
2026/2027 | 2008 | 1 | 27 | 19 | 29201.4104
2026/2027 | 2008 | 1 | 27 | 20 | 30301.6846
2026/2027 | 2008 | 1 | 27 | 21 | 30345.4831
2026/2027 | 2008 | 1 | 27 | 22 | 30795.5303
2026/2027 | 2008 | 1 | 27 | 23 | 30721.0443
2026/2027 | 2008 | 1 | 27 | 24 | 30715.0578
2026/2027 | 2008 | 1 | 28 | 1 | 28766.6531
2026/2027 | 2008 | 1 | 28 | 2 | 27805.1402
2026/2027 | 2008 | 1 | 28 | 3 | 27865.1599
2026/2027 | 2008 | 1 | 28 | 4 | 28149.2276
2026/2027 | 2008 | 1 | 28 | 5 | 28960.7071
2026/2027 | 2008 | 1 | 28 | 6 | 29401.9986
2026/2027 | 2008 | 1 | 28 | 7 | 29539.9385
2026/2027 | 2008 | 1 | 28 | 8 | 31362.9796
2026/2027 | 2008 | 1 | 28 | 9 | 31787.9699
2026/2027 | 2008 | 1 | 28 | 10 | 33114.5546
2026/2027 | 2008 | 1 | 28 | 11 | 33116.511
2026/2027 | 2008 | 1 | 28 | 12 | 32880.9538
2026/2027 | 2008 | 1 | 28 | 13 | 33235.1033
2026/2027 | 2008 | 1 | 28 | 14 | 32673.996
2026/2027 | 2008 | 1 | 28 | 15 | 32507.0361
2026/2027 | 2008 | 1 | 28 | 16 | 32062.445
2026/2027 | 2008 | 1 | 28 | 17 | 30895.6356
2026/2027 | 2008 | 1 | 28 | 18 | 29636.0038
2026/2027 | 2008 | 1 | 28 | 19 | 31288.1521
2026/2027 | 2008 | 1 | 28 | 20 | 31785.9998
2026/2027 | 2008 | 1 | 28 | 21 | 32902.0067
2026/2027 | 2008 | 1 | 28 | 22 | 33259.4488
2026/2027 | 2008 | 1 | 28 | 23 | 33105.3775
2026/2027 | 2008 | 1 | 28 | 24 | 33072.9086
2026/2027 | 2008 | 1 | 29 | 1 | 33811.5258
2026/2027 | 2008 | 1 | 29 | 2 | 33795.4701
2026/2027 | 2008 | 1 | 29 | 3 | 33372.3513
2026/2027 | 2008 | 1 | 29 | 4 | 32907.4
2026/2027 | 2008 | 1 | 29 | 5 | 31749.9867
2026/2027 | 2008 | 1 | 29 | 6 | 31544.1942
2026/2027 | 2008 | 1 | 29 | 7 | 28647.4722
2026/2027 | 2008 | 1 | 29 | 8 | 27626.0567
2026/2027 | 2008 | 1 | 29 | 9 | 26987.1544
2026/2027 | 2008 | 1 | 29 | 10 | 25816.7554
2026/2027 | 2008 | 1 | 29 | 11 | 24476.5781
2026/2027 | 2008 | 1 | 29 | 12 | 25764.1545
2026/2027 | 2008 | 1 | 29 | 13 | 27652.1093
2026/2027 | 2008 | 1 | 29 | 14 | 27689.4149
2026/2027 | 2008 | 1 | 29 | 15 | 25945.9273
2026/2027 | 2008 | 1 | 29 | 16 | 21696.2834
2026/2027 | 2008 | 1 | 29 | 17 | 15558.199
2026/2027 | 2008 | 1 | 29 | 18 | 12163.1168
2026/2027 | 2008 | 1 | 29 | 19 | 12279.9695
2026/2027 | 2008 | 1 | 29 | 20 | 13479.7575
2026/2027 | 2008 | 1 | 29 | 21 | 16845.8019
2026/2027 | 2008 | 1 | 29 | 22 | 21415.6149
2026/2027 | 2008 | 1 | 29 | 23 | 25965.5964
2026/2027 | 2008 | 1 | 29 | 24 | 29058.9071
2026/2027 | 2008 | 1 | 30 | 1 | 31118.7443
2026/2027 | 2008 | 1 | 30 | 2 | 31137.2992
2026/2027 | 2008 | 1 | 30 | 3 | 31630.2559
2026/2027 | 2008 | 1 | 30 | 4 | 30399.7649
2026/2027 | 2008 | 1 | 30 | 5 | 30192.4429
2026/2027 | 2008 | 1 | 30 | 6 | 29731.0301
2026/2027 | 2008 | 1 | 30 | 7 | 29068.2951
2026/2027 | 2008 | 1 | 30 | 8 | 28170.3785
2026/2027 | 2008 | 1 | 30 | 9 | 26447.7857
2026/2027 | 2008 | 1 | 30 | 10 | 26629.9162
2026/2027 | 2008 | 1 | 30 | 11 | 27493.5549
2026/2027 | 2008 | 1 | 30 | 12 | 28503.0677
2026/2027 | 2008 | 1 | 30 | 13 | 28929.2903
2026/2027 | 2008 | 1 | 30 | 14 | 28517.7327
2026/2027 | 2008 | 1 | 30 | 15 | 27471.2904
2026/2027 | 2008 | 1 | 30 | 16 | 27395.6829
2026/2027 | 2008 | 1 | 30 | 17 | 26909.8509
2026/2027 | 2008 | 1 | 30 | 18 | 25662.1833
2026/2027 | 2008 | 1 | 30 | 19 | 26999.8931
2026/2027 | 2008 | 1 | 30 | 20 | 27835.2579
2026/2027 | 2008 | 1 | 30 | 21 | 27732.0885
2026/2027 | 2008 | 1 | 30 | 22 | 27494.7534
2026/2027 | 2008 | 1 | 30 | 23 | 26097.3437
2026/2027 | 2008 | 1 | 30 | 24 | 25764.6706
2026/2027 | 2008 | 1 | 31 | 1 | 27509.6001
2026/2027 | 2008 | 1 | 31 | 2 | 26362.9444
2026/2027 | 2008 | 1 | 31 | 3 | 25317.8841
2026/2027 | 2008 | 1 | 31 | 4 | 25152.8308
2026/2027 | 2008 | 1 | 31 | 5 | 25822.9698
2026/2027 | 2008 | 1 | 31 | 6 | 27029.0121
2026/2027 | 2008 | 1 | 31 | 7 | 29122.7253
2026/2027 | 2008 | 1 | 31 | 8 | 31005.3874
2026/2027 | 2008 | 1 | 31 | 9 | 30529.3893
2026/2027 | 2008 | 1 | 31 | 10 | 29931.3923
2026/2027 | 2008 | 1 | 31 | 11 | 30462.9509
2026/2027 | 2008 | 1 | 31 | 12 | 31051.5402
2026/2027 | 2008 | 1 | 31 | 13 | 32900.9684
2026/2027 | 2008 | 1 | 31 | 14 | 33013.6253
2026/2027 | 2008 | 1 | 31 | 15 | 32303.8307
2026/2027 | 2008 | 1 | 31 | 16 | 32829.2409
2026/2027 | 2008 | 1 | 31 | 17 | 27388.7562
2026/2027 | 2008 | 1 | 31 | 18 | 27978.3664
2026/2027 | 2008 | 1 | 31 | 19 | 24044.5605
2026/2027 | 2008 | 1 | 31 | 20 | 20286.1526
2026/2027 | 2008 | 1 | 31 | 21 | 14902.2101
2026/2027 | 2008 | 1 | 31 | 22 | 11952.6214
2026/2027 | 2008 | 1 | 31 | 23 | 11501.649
2026/2027 | 2008 | 1 | 31 | 24 | 12199.5436
2027/2028 | 2008 | 1 | 1 | 1 | 25048.0743
2027/2028 | 2008 | 1 | 1 | 2 | 24714.5684
2027/2028 | 2008 | 1 | 1 | 3 | 23638.7247
2027/2028 | 2008 | 1 | 1 | 4 | 22263.2976
2027/2028 | 2008 | 1 | 1 | 5 | 21130.386
2027/2028 | 2008 | 1 | 1 | 6 | 20311.4881
2027/2028 | 2008 | 1 | 1 | 7 | 19285.2965
2027/2028 | 2008 | 1 | 1 | 8 | 17502.1642
2027/2028 | 2008 | 1 | 1 | 9 | 15600.944
2027/2028 | 2008 | 1 | 1 | 10 | 13046.3115
2027/2028 | 2008 | 1 | 1 | 11 | 15315.7947
2027/2028 | 2008 | 1 | 1 | 12 | 17098.1837
2027/2028 | 2008 | 1 | 1 | 13 | 16914.5002
2027/2028 | 2008 | 1 | 1 | 14 | 15261.9762
2027/2028 | 2008 | 1 | 1 | 15 | 15140.5684
2027/2028 | 2008 | 1 | 1 | 16 | 14586.2369
2027/2028 | 2008 | 1 | 1 | 17 | 11578.2751
2027/2028 | 2008 | 1 | 1 | 18 | 11577.8617
2027/2028 | 2008 | 1 | 1 | 19 | 11450.3319
2027/2028 | 2008 | 1 | 1 | 20 | 12339.1697
2027/2028 | 2008 | 1 | 1 | 21 | 12095.2956
2027/2028 | 2008 | 1 | 1 | 22 | 10729.7844
2027/2028 | 2008 | 1 | 1 | 23 | 10064.9977
2027/2028 | 2008 | 1 | 1 | 24 | 10265.0151
2027/2028 | 2008 | 1 | 2 | 1 | 10541.5188
2027/2028 | 2008 | 1 | 2 | 2 | 11163.3064
2027/2028 | 2008 | 1 | 2 | 3 | 10439.6674
2027/2028 | 2008 | 1 | 2 | 4 | 11352.36
2027/2028 | 2008 | 1 | 2 | 5 | 11657.8109
2027/2028 | 2008 | 1 | 2 | 6 | 11937.0603
2027/2028 | 2008 | 1 | 2 | 7 | 12121.1708
2027/2028 | 2008 | 1 | 2 | 8 | 11610.49
2027/2028 | 2008 | 1 | 2 | 9 | 9475.8545
2027/2028 | 2008 | 1 | 2 | 10 | 9244.5836
2027/2028 | 2008 | 1 | 2 | 11 | 10755.1191
2027/2028 | 2008 | 1 | 2 | 12 | 11796.467
2027/2028 | 2008 | 1 | 2 | 13 | 12017.6307
2027/2028 | 2008 | 1 | 2 | 14 | 11803.3796
2027/2028 | 2008 | 1 | 2 | 15 | 11910.5239
2027/2028 | 2008 | 1 | 2 | 16 | 11107.009
2027/2028 | 2008 | 1 | 2 | 17 | 10125.8874
2027/2028 | 2008 | 1 | 2 | 18 | 10888.4153
2027/2028 | 2008 | 1 | 2 | 19 | 13570.6866
2027/2028 | 2008 | 1 | 2 | 20 | 16411.8335
2027/2028 | 2008 | 1 | 2 | 21 | 19007.3356
2027/2028 | 2008 | 1 | 2 | 22 | 21255.6047
2027/2028 | 2008 | 1 | 2 | 23 | 22278.4554
2027/2028 | 2008 | 1 | 2 | 24 | 22813.1015
2027/2028 | 2008 | 1 | 3 | 1 | 24195.9206
2027/2028 | 2008 | 1 | 3 | 2 | 25073.6771
2027/2028 | 2008 | 1 | 3 | 3 | 25581.4786
2027/2028 | 2008 | 1 | 3 | 4 | 26535.7344
2027/2028 | 2008 | 1 | 3 | 5 | 27852.1169
2027/2028 | 2008 | 1 | 3 | 6 | 29697.0547
2027/2028 | 2008 | 1 | 3 | 7 | 30002.5075
2027/2028 | 2008 | 1 | 3 | 8 | 28641.3542
2027/2028 | 2008 | 1 | 3 | 9 | 26532.1942
2027/2028 | 2008 | 1 | 3 | 10 | 27571.8437
2027/2028 | 2008 | 1 | 3 | 11 | 28047.0801
2027/2028 | 2008 | 1 | 3 | 12 | 28628.3591
2027/2028 | 2008 | 1 | 3 | 13 | 29190.9565
2027/2028 | 2008 | 1 | 3 | 14 | 29838.888
2027/2028 | 2008 | 1 | 3 | 15 | 30978.7349
2027/2028 | 2008 | 1 | 3 | 16 | 32008.8314
2027/2028 | 2008 | 1 | 3 | 17 | 31683.5926
2027/2028 | 2008 | 1 | 3 | 18 | 30847.1101
2027/2028 | 2008 | 1 | 3 | 19 | 31626.6687
2027/2028 | 2008 | 1 | 3 | 20 | 31717.7465
2027/2028 | 2008 | 1 | 3 | 21 | 32741.6175
2027/2028 | 2008 | 1 | 3 | 22 | 33224.1541
2027/2028 | 2008 | 1 | 3 | 23 | 33509.613
2027/2028 | 2008 | 1 | 3 | 24 | 33495.1698
2027/2028 | 2008 | 1 | 4 | 1 | 33018.9359
2027/2028 | 2008 | 1 | 4 | 2 | 32645.855
2027/2028 | 2008 | 1 | 4 | 3 | 34017.422
2027/2028 | 2008 | 1 | 4 | 4 | 33584.988
2027/2028 | 2008 | 1 | 4 | 5 | 33208.2599
2027/2028 | 2008 | 1 | 4 | 6 | 32790.5234
2027/2028 | 2008 | 1 | 4 | 7 | 32303.1901
2027/2028 | 2008 | 1 | 4 | 8 | 30512.625
2027/2028 | 2008 | 1 | 4 | 9 | 29878.1025
2027/2028 | 2008 | 1 | 4 | 10 | 29738.9695
2027/2028 | 2008 | 1 | 4 | 11 | 30777.4599
2027/2028 | 2008 | 1 | 4 | 12 | 31448.0634
2027/2028 | 2008 | 1 | 4 | 13 | 32940.8087
2027/2028 | 2008 | 1 | 4 | 14 | 33883.0696
2027/2028 | 2008 | 1 | 4 | 15 | 33930.3425
2027/2028 | 2008 | 1 | 4 | 16 | 34947.2884
2027/2028 | 2008 | 1 | 4 | 17 | 34411.4051
2027/2028 | 2008 | 1 | 4 | 18 | 34137.0211
2027/2028 | 2008 | 1 | 4 | 19 | 35431.9845
2027/2028 | 2008 | 1 | 4 | 20 | 35844.0416
2027/2028 | 2008 | 1 | 4 | 21 | 36211.7599
2027/2028 | 2008 | 1 | 4 | 22 | 36509.0364
2027/2028 | 2008 | 1 | 4 | 23 | 36476.1339
2027/2028 | 2008 | 1 | 4 | 24 | 36986.4371
2027/2028 | 2008 | 1 | 5 | 1 | 36984.6631
2027/2028 | 2008 | 1 | 5 | 2 | 36742.1033
2027/2028 | 2008 | 1 | 5 | 3 | 35403.8708
2027/2028 | 2008 | 1 | 5 | 4 | 34485.8706
2027/2028 | 2008 | 1 | 5 | 5 | 34096.3913
2027/2028 | 2008 | 1 | 5 | 6 | 33799.4152
2027/2028 | 2008 | 1 | 5 | 7 | 33732.956
2027/2028 | 2008 | 1 | 5 | 8 | 32952.5537
2027/2028 | 2008 | 1 | 5 | 9 | 31062.075
2027/2028 | 2008 | 1 | 5 | 10 | 30319.3913
2027/2028 | 2008 | 1 | 5 | 11 | 30956.8192
2027/2028 | 2008 | 1 | 5 | 12 | 33138.4407
2027/2028 | 2008 | 1 | 5 | 13 | 34795.4033
2027/2028 | 2008 | 1 | 5 | 14 | 35413.6444
2027/2028 | 2008 | 1 | 5 | 15 | 35779.2766
2027/2028 | 2008 | 1 | 5 | 16 | 35282.9705
2027/2028 | 2008 | 1 | 5 | 17 | 32408.5003
2027/2028 | 2008 | 1 | 5 | 18 | 32674.684
2027/2028 | 2008 | 1 | 5 | 19 | 34513.393
2027/2028 | 2008 | 1 | 5 | 20 | 34967.3659
2027/2028 | 2008 | 1 | 5 | 21 | 34855.0866
2027/2028 | 2008 | 1 | 5 | 22 | 35065.6498
2027/2028 | 2008 | 1 | 5 | 23 | 35174.6635
2027/2028 | 2008 | 1 | 5 | 24 | 35251.8526
2027/2028 | 2008 | 1 | 6 | 1 | 35281.8887
2027/2028 | 2008 | 1 | 6 | 2 | 35046.7511
2027/2028 | 2008 | 1 | 6 | 3 | 34860.7641
2027/2028 | 2008 | 1 | 6 | 4 | 34627.5284
2027/2028 | 2008 | 1 | 6 | 5 | 33996.1432
2027/2028 | 2008 | 1 | 6 | 6 | 33781.2286
2027/2028 | 2008 | 1 | 6 | 7 | 33327.9916
2027/2028 | 2008 | 1 | 6 | 8 | 31189.1922
2027/2028 | 2008 | 1 | 6 | 9 | 29332.8352
2027/2028 | 2008 | 1 | 6 | 10 | 30536.3198
2027/2028 | 2008 | 1 | 6 | 11 | 30941.493
2027/2028 | 2008 | 1 | 6 | 12 | 31821.5262
2027/2028 | 2008 | 1 | 6 | 13 | 32215.4785
2027/2028 | 2008 | 1 | 6 | 14 | 31664.7107
2027/2028 | 2008 | 1 | 6 | 15 | 31232.5715
2027/2028 | 2008 | 1 | 6 | 16 | 29946.0259
2027/2028 | 2008 | 1 | 6 | 17 | 27875.0588
2027/2028 | 2008 | 1 | 6 | 18 | 29143.8982
2027/2028 | 2008 | 1 | 6 | 19 | 31488.6126
2027/2028 | 2008 | 1 | 6 | 20 | 32228.6903
2027/2028 | 2008 | 1 | 6 | 21 | 32169.8444
2027/2028 | 2008 | 1 | 6 | 22 | 32997.4628
2027/2028 | 2008 | 1 | 6 | 23 | 32891.187
2027/2028 | 2008 | 1 | 6 | 24 | 34085.5334
2027/2028 | 2008 | 1 | 7 | 1 | 33600.8179
2027/2028 | 2008 | 1 | 7 | 2 | 32730.7685
2027/2028 | 2008 | 1 | 7 | 3 | 32106.3181
2027/2028 | 2008 | 1 | 7 | 4 | 31059.5472
2027/2028 | 2008 | 1 | 7 | 5 | 30822.074
2027/2028 | 2008 | 1 | 7 | 6 | 30385.2795
2027/2028 | 2008 | 1 | 7 | 7 | 29837.1852
2027/2028 | 2008 | 1 | 7 | 8 | 27645.7522
2027/2028 | 2008 | 1 | 7 | 9 | 24834.4795
2027/2028 | 2008 | 1 | 7 | 10 | 24730.807
2027/2028 | 2008 | 1 | 7 | 11 | 24706.866
2027/2028 | 2008 | 1 | 7 | 12 | 24596.8352
2027/2028 | 2008 | 1 | 7 | 13 | 24649.6831
2027/2028 | 2008 | 1 | 7 | 14 | 24351.1397
2027/2028 | 2008 | 1 | 7 | 15 | 24382.3971
2027/2028 | 2008 | 1 | 7 | 16 | 23708.1979
2027/2028 | 2008 | 1 | 7 | 17 | 22325.0624
2027/2028 | 2008 | 1 | 7 | 18 | 24824.6281
2027/2028 | 2008 | 1 | 7 | 19 | 27116.1437
2027/2028 | 2008 | 1 | 7 | 20 | 28185.2406
2027/2028 | 2008 | 1 | 7 | 21 | 28372.0548
2027/2028 | 2008 | 1 | 7 | 22 | 29138.0206
2027/2028 | 2008 | 1 | 7 | 23 | 29795.2834
2027/2028 | 2008 | 1 | 7 | 24 | 30014.1871
2027/2028 | 2008 | 1 | 8 | 1 | 32024.1778
2027/2028 | 2008 | 1 | 8 | 2 | 34419.1495
2027/2028 | 2008 | 1 | 8 | 3 | 35076.5114
2027/2028 | 2008 | 1 | 8 | 4 | 34569.1177
2027/2028 | 2008 | 1 | 8 | 5 | 33467.1313
2027/2028 | 2008 | 1 | 8 | 6 | 29023.7599
2027/2028 | 2008 | 1 | 8 | 7 | 31221.9022
2027/2028 | 2008 | 1 | 8 | 8 | 29882.9746
2027/2028 | 2008 | 1 | 8 | 9 | 27723.0005
2027/2028 | 2008 | 1 | 8 | 10 | 29001.2678
2027/2028 | 2008 | 1 | 8 | 11 | 30518.4712
2027/2028 | 2008 | 1 | 8 | 12 | 30204.6701
2027/2028 | 2008 | 1 | 8 | 13 | 27953.1592
2027/2028 | 2008 | 1 | 8 | 14 | 24532.4098
2027/2028 | 2008 | 1 | 8 | 15 | 21414.4367
2027/2028 | 2008 | 1 | 8 | 16 | 18145.7785
2027/2028 | 2008 | 1 | 8 | 17 | 12346.2456
2027/2028 | 2008 | 1 | 8 | 18 | 10145.4199
2027/2028 | 2008 | 1 | 8 | 19 | 9587.2136
2027/2028 | 2008 | 1 | 8 | 20 | 9108.8841
2027/2028 | 2008 | 1 | 8 | 21 | 9215.0571
2027/2028 | 2008 | 1 | 8 | 22 | 9606.0758
2027/2028 | 2008 | 1 | 8 | 23 | 10569.033
2027/2028 | 2008 | 1 | 8 | 24 | 11861.8402
2027/2028 | 2008 | 1 | 9 | 1 | 14967.0286
2027/2028 | 2008 | 1 | 9 | 2 | 18148.3263
2027/2028 | 2008 | 1 | 9 | 3 | 21880.6533
2027/2028 | 2008 | 1 | 9 | 4 | 23554.9559
2027/2028 | 2008 | 1 | 9 | 5 | 24256.8571
2027/2028 | 2008 | 1 | 9 | 6 | 24994.8424
2027/2028 | 2008 | 1 | 9 | 7 | 25202.2108
2027/2028 | 2008 | 1 | 9 | 8 | 24590.8015
2027/2028 | 2008 | 1 | 9 | 9 | 22808.2479
2027/2028 | 2008 | 1 | 9 | 10 | 18277.0366
2027/2028 | 2008 | 1 | 9 | 11 | 21977.867
2027/2028 | 2008 | 1 | 9 | 12 | 23896.9155
2027/2028 | 2008 | 1 | 9 | 13 | 22355.2014
2027/2028 | 2008 | 1 | 9 | 14 | 23333.4578
2027/2028 | 2008 | 1 | 9 | 15 | 23765.0728
2027/2028 | 2008 | 1 | 9 | 16 | 23549.5528
2027/2028 | 2008 | 1 | 9 | 17 | 22276.0946
2027/2028 | 2008 | 1 | 9 | 18 | 24400.078
2027/2028 | 2008 | 1 | 9 | 19 | 27007.5313
2027/2028 | 2008 | 1 | 9 | 20 | 27940.28
2027/2028 | 2008 | 1 | 9 | 21 | 28301.4391
2027/2028 | 2008 | 1 | 9 | 22 | 30720.0243
2027/2028 | 2008 | 1 | 9 | 23 | 30526.5886
2027/2028 | 2008 | 1 | 9 | 24 | 29688.1461
2027/2028 | 2008 | 1 | 10 | 1 | 28262.7624
2027/2028 | 2008 | 1 | 10 | 2 | 27573.7536
2027/2028 | 2008 | 1 | 10 | 3 | 28475.5601
2027/2028 | 2008 | 1 | 10 | 4 | 29213.0655
2027/2028 | 2008 | 1 | 10 | 5 | 28650.2077
2027/2028 | 2008 | 1 | 10 | 6 | 28548.3028
2027/2028 | 2008 | 1 | 10 | 7 | 28219.3862
2027/2028 | 2008 | 1 | 10 | 8 | 27099.3012
2027/2028 | 2008 | 1 | 10 | 9 | 23738.4225
2027/2028 | 2008 | 1 | 10 | 10 | 21517.484
2027/2028 | 2008 | 1 | 10 | 11 | 23313.5512
2027/2028 | 2008 | 1 | 10 | 12 | 23875.2796
2027/2028 | 2008 | 1 | 10 | 13 | 22279.4451
2027/2028 | 2008 | 1 | 10 | 14 | 20239.3991
2027/2028 | 2008 | 1 | 10 | 15 | 18001.3309
2027/2028 | 2008 | 1 | 10 | 16 | 14990.8648
2027/2028 | 2008 | 1 | 10 | 17 | 10337.0755
2027/2028 | 2008 | 1 | 10 | 18 | 7810.5199
2027/2028 | 2008 | 1 | 10 | 19 | 7191.1392
2027/2028 | 2008 | 1 | 10 | 20 | 6780.0045
2027/2028 | 2008 | 1 | 10 | 21 | 7386.3645
2027/2028 | 2008 | 1 | 10 | 22 | 8098.9613
2027/2028 | 2008 | 1 | 10 | 23 | 9659.4629
2027/2028 | 2008 | 1 | 10 | 24 | 11767.2484
2027/2028 | 2008 | 1 | 11 | 1 | 14367.4005
2027/2028 | 2008 | 1 | 11 | 2 | 16075.2964
2027/2028 | 2008 | 1 | 11 | 3 | 18597.461
2027/2028 | 2008 | 1 | 11 | 4 | 20425.7828
2027/2028 | 2008 | 1 | 11 | 5 | 21974.8109
2027/2028 | 2008 | 1 | 11 | 6 | 22576.0556
2027/2028 | 2008 | 1 | 11 | 7 | 22539.8408
2027/2028 | 2008 | 1 | 11 | 8 | 21496.4963
2027/2028 | 2008 | 1 | 11 | 9 | 17703.6764
2027/2028 | 2008 | 1 | 11 | 10 | 11427.2079
2027/2028 | 2008 | 1 | 11 | 11 | 10132.1429
2027/2028 | 2008 | 1 | 11 | 12 | 11143.454
2027/2028 | 2008 | 1 | 11 | 13 | 10961.3063
2027/2028 | 2008 | 1 | 11 | 14 | 10847.8773
2027/2028 | 2008 | 1 | 11 | 15 | 10540.7079
2027/2028 | 2008 | 1 | 11 | 16 | 9309.0363
2027/2028 | 2008 | 1 | 11 | 17 | 7369.1349
2027/2028 | 2008 | 1 | 11 | 18 | 7374.0478
2027/2028 | 2008 | 1 | 11 | 19 | 9679.0655
2027/2028 | 2008 | 1 | 11 | 20 | 11550.8668
2027/2028 | 2008 | 1 | 11 | 21 | 13891.3214
2027/2028 | 2008 | 1 | 11 | 22 | 15689.0674
2027/2028 | 2008 | 1 | 11 | 23 | 16715.4572
2027/2028 | 2008 | 1 | 11 | 24 | 18689.2869
2027/2028 | 2008 | 1 | 12 | 1 | 20820.8619
2027/2028 | 2008 | 1 | 12 | 2 | 21448.2172
2027/2028 | 2008 | 1 | 12 | 3 | 22103.068
2027/2028 | 2008 | 1 | 12 | 4 | 23840.7547
2027/2028 | 2008 | 1 | 12 | 5 | 24537.2862
2027/2028 | 2008 | 1 | 12 | 6 | 25025.7381
2027/2028 | 2008 | 1 | 12 | 7 | 26322.683
2027/2028 | 2008 | 1 | 12 | 8 | 25946.4819
2027/2028 | 2008 | 1 | 12 | 9 | 22085.66
2027/2028 | 2008 | 1 | 12 | 10 | 18128.4872
2027/2028 | 2008 | 1 | 12 | 11 | 18955.7458
2027/2028 | 2008 | 1 | 12 | 12 | 18060.1266
2027/2028 | 2008 | 1 | 12 | 13 | 18464.3302
2027/2028 | 2008 | 1 | 12 | 14 | 19266.5328
2027/2028 | 2008 | 1 | 12 | 15 | 19246.2953
2027/2028 | 2008 | 1 | 12 | 16 | 18272.6071
2027/2028 | 2008 | 1 | 12 | 17 | 14117.2314
2027/2028 | 2008 | 1 | 12 | 18 | 11772.3232
2027/2028 | 2008 | 1 | 12 | 19 | 11966.0885
2027/2028 | 2008 | 1 | 12 | 20 | 11488.7845
2027/2028 | 2008 | 1 | 12 | 21 | 11815.631
2027/2028 | 2008 | 1 | 12 | 22 | 11702.6347
2027/2028 | 2008 | 1 | 12 | 23 | 11223.6474
2027/2028 | 2008 | 1 | 12 | 24 | 11259.0319
2027/2028 | 2008 | 1 | 13 | 1 | 11968.7257
2027/2028 | 2008 | 1 | 13 | 2 | 12153.2298
2027/2028 | 2008 | 1 | 13 | 3 | 12089.1302
2027/2028 | 2008 | 1 | 13 | 4 | 11767.7931
2027/2028 | 2008 | 1 | 13 | 5 | 11617.5909
2027/2028 | 2008 | 1 | 13 | 6 | 11590.108
2027/2028 | 2008 | 1 | 13 | 7 | 11269.6111
2027/2028 | 2008 | 1 | 13 | 8 | 10530.2314
2027/2028 | 2008 | 1 | 13 | 9 | 7288.9654
2027/2028 | 2008 | 1 | 13 | 10 | 4901.5052
2027/2028 | 2008 | 1 | 13 | 11 | 4660.1087
2027/2028 | 2008 | 1 | 13 | 12 | 4333.6824
2027/2028 | 2008 | 1 | 13 | 13 | 4315.9372
2027/2028 | 2008 | 1 | 13 | 14 | 4953.7048
2027/2028 | 2008 | 1 | 13 | 15 | 5690.5968
2027/2028 | 2008 | 1 | 13 | 16 | 6287.1679
2027/2028 | 2008 | 1 | 13 | 17 | 6350.1808
2027/2028 | 2008 | 1 | 13 | 18 | 7422.8352
2027/2028 | 2008 | 1 | 13 | 19 | 9774.1469
2027/2028 | 2008 | 1 | 13 | 20 | 12567.6735
2027/2028 | 2008 | 1 | 13 | 21 | 14458.3737
2027/2028 | 2008 | 1 | 13 | 22 | 15982.6955
2027/2028 | 2008 | 1 | 13 | 23 | 17302.9824
2027/2028 | 2008 | 1 | 13 | 24 | 18951.2772
2027/2028 | 2008 | 1 | 14 | 1 | 18475.0758
2027/2028 | 2008 | 1 | 14 | 2 | 16965.2509
2027/2028 | 2008 | 1 | 14 | 3 | 15596.9501
2027/2028 | 2008 | 1 | 14 | 4 | 13805.9592
2027/2028 | 2008 | 1 | 14 | 5 | 12214.0985
2027/2028 | 2008 | 1 | 14 | 6 | 11475.2401
2027/2028 | 2008 | 1 | 14 | 7 | 10445.5847
2027/2028 | 2008 | 1 | 14 | 8 | 9447.3483
2027/2028 | 2008 | 1 | 14 | 9 | 8054.0751
2027/2028 | 2008 | 1 | 14 | 10 | 7257.6993
2027/2028 | 2008 | 1 | 14 | 11 | 7729.4329
2027/2028 | 2008 | 1 | 14 | 12 | 8483.0883
2027/2028 | 2008 | 1 | 14 | 13 | 8674.4884
2027/2028 | 2008 | 1 | 14 | 14 | 8933.733
2027/2028 | 2008 | 1 | 14 | 15 | 9010.4163
2027/2028 | 2008 | 1 | 14 | 16 | 8683.6084
2027/2028 | 2008 | 1 | 14 | 17 | 7978.3544
2027/2028 | 2008 | 1 | 14 | 18 | 7752.3638
2027/2028 | 2008 | 1 | 14 | 19 | 7895.6411
2027/2028 | 2008 | 1 | 14 | 20 | 8050.8275
2027/2028 | 2008 | 1 | 14 | 21 | 8095.3235
2027/2028 | 2008 | 1 | 14 | 22 | 8287.3221
2027/2028 | 2008 | 1 | 14 | 23 | 8994.0622
2027/2028 | 2008 | 1 | 14 | 24 | 9826.378
2027/2028 | 2008 | 1 | 15 | 1 | 10835.9684
2027/2028 | 2008 | 1 | 15 | 2 | 11803.7863
2027/2028 | 2008 | 1 | 15 | 3 | 13732.2215
2027/2028 | 2008 | 1 | 15 | 4 | 15370.3507
2027/2028 | 2008 | 1 | 15 | 5 | 17691.9164
2027/2028 | 2008 | 1 | 15 | 6 | 19294.6906
2027/2028 | 2008 | 1 | 15 | 7 | 21154.0397
2027/2028 | 2008 | 1 | 15 | 8 | 22248.4291
2027/2028 | 2008 | 1 | 15 | 9 | 21786.835
2027/2028 | 2008 | 1 | 15 | 10 | 21037.2779
2027/2028 | 2008 | 1 | 15 | 11 | 23458.3072
2027/2028 | 2008 | 1 | 15 | 12 | 27538.3147
2027/2028 | 2008 | 1 | 15 | 13 | 29874.7824
2027/2028 | 2008 | 1 | 15 | 14 | 30594.8627
2027/2028 | 2008 | 1 | 15 | 15 | 30860.1326
2027/2028 | 2008 | 1 | 15 | 16 | 31415.9464
2027/2028 | 2008 | 1 | 15 | 17 | 31202.2983
2027/2028 | 2008 | 1 | 15 | 18 | 31286.2752
2027/2028 | 2008 | 1 | 15 | 19 | 32855.0421
2027/2028 | 2008 | 1 | 15 | 20 | 32879.0144
2027/2028 | 2008 | 1 | 15 | 21 | 33428.4344
2027/2028 | 2008 | 1 | 15 | 22 | 33912.4253
2027/2028 | 2008 | 1 | 15 | 23 | 33546.5433
2027/2028 | 2008 | 1 | 15 | 24 | 33305.1128
2027/2028 | 2008 | 1 | 16 | 1 | 33328.753
2027/2028 | 2008 | 1 | 16 | 2 | 32786.0753
2027/2028 | 2008 | 1 | 16 | 3 | 32853.4146
2027/2028 | 2008 | 1 | 16 | 4 | 32592.7261
2027/2028 | 2008 | 1 | 16 | 5 | 30482.1935
2027/2028 | 2008 | 1 | 16 | 6 | 28250.9426
2027/2028 | 2008 | 1 | 16 | 7 | 26766.0406
2027/2028 | 2008 | 1 | 16 | 8 | 24233.2835
2027/2028 | 2008 | 1 | 16 | 9 | 19963.8079
2027/2028 | 2008 | 1 | 16 | 10 | 18965.4223
2027/2028 | 2008 | 1 | 16 | 11 | 18035.8308
2027/2028 | 2008 | 1 | 16 | 12 | 19017.668
2027/2028 | 2008 | 1 | 16 | 13 | 17968.5054
2027/2028 | 2008 | 1 | 16 | 14 | 16874.749
2027/2028 | 2008 | 1 | 16 | 15 | 17439.9548
2027/2028 | 2008 | 1 | 16 | 16 | 17349.093
2027/2028 | 2008 | 1 | 16 | 17 | 17326.1888
2027/2028 | 2008 | 1 | 16 | 18 | 18749.1114
2027/2028 | 2008 | 1 | 16 | 19 | 21562.9657
2027/2028 | 2008 | 1 | 16 | 20 | 23592.2319
2027/2028 | 2008 | 1 | 16 | 21 | 24032.2225
2027/2028 | 2008 | 1 | 16 | 22 | 23877.6757
2027/2028 | 2008 | 1 | 16 | 23 | 24967.4594
2027/2028 | 2008 | 1 | 16 | 24 | 24559.2784
2027/2028 | 2008 | 1 | 17 | 1 | 23982.5015
2027/2028 | 2008 | 1 | 17 | 2 | 23242.3391
2027/2028 | 2008 | 1 | 17 | 3 | 23392.1846
2027/2028 | 2008 | 1 | 17 | 4 | 22152.7879
2027/2028 | 2008 | 1 | 17 | 5 | 21112.6049
2027/2028 | 2008 | 1 | 17 | 6 | 19996.6322
2027/2028 | 2008 | 1 | 17 | 7 | 18010.9696
2027/2028 | 2008 | 1 | 17 | 8 | 15833.3534
2027/2028 | 2008 | 1 | 17 | 9 | 12841.5547
2027/2028 | 2008 | 1 | 17 | 10 | 13969.9241
2027/2028 | 2008 | 1 | 17 | 11 | 13249.1683
2027/2028 | 2008 | 1 | 17 | 12 | 11375.1889
2027/2028 | 2008 | 1 | 17 | 13 | 10880.4823
2027/2028 | 2008 | 1 | 17 | 14 | 10206.9907
2027/2028 | 2008 | 1 | 17 | 15 | 9411.3126
2027/2028 | 2008 | 1 | 17 | 16 | 8598.1558
2027/2028 | 2008 | 1 | 17 | 17 | 7106.996
2027/2028 | 2008 | 1 | 17 | 18 | 5519.2711
2027/2028 | 2008 | 1 | 17 | 19 | 5765.3535
2027/2028 | 2008 | 1 | 17 | 20 | 6700.953
2027/2028 | 2008 | 1 | 17 | 21 | 8046.6511
2027/2028 | 2008 | 1 | 17 | 22 | 9118.7803
2027/2028 | 2008 | 1 | 17 | 23 | 9846.872
2027/2028 | 2008 | 1 | 17 | 24 | 10259.7241
2027/2028 | 2008 | 1 | 18 | 1 | 11332.8427
2027/2028 | 2008 | 1 | 18 | 2 | 11933.5937
2027/2028 | 2008 | 1 | 18 | 3 | 12367.2755
2027/2028 | 2008 | 1 | 18 | 4 | 12279.6773
2027/2028 | 2008 | 1 | 18 | 5 | 11579.935
2027/2028 | 2008 | 1 | 18 | 6 | 11209.1808
2027/2028 | 2008 | 1 | 18 | 7 | 10261.7409
2027/2028 | 2008 | 1 | 18 | 8 | 9051.522
2027/2028 | 2008 | 1 | 18 | 9 | 9095.3381
2027/2028 | 2008 | 1 | 18 | 10 | 9158.4864
2027/2028 | 2008 | 1 | 18 | 11 | 9866.2759
2027/2028 | 2008 | 1 | 18 | 12 | 10291.3194
2027/2028 | 2008 | 1 | 18 | 13 | 11126.1599
2027/2028 | 2008 | 1 | 18 | 14 | 11259.8175
2027/2028 | 2008 | 1 | 18 | 15 | 11299.0278
2027/2028 | 2008 | 1 | 18 | 16 | 11237.4092
2027/2028 | 2008 | 1 | 18 | 17 | 11032.0229
2027/2028 | 2008 | 1 | 18 | 18 | 11915.0564
2027/2028 | 2008 | 1 | 18 | 19 | 13084.377
2027/2028 | 2008 | 1 | 18 | 20 | 14218.4046
2027/2028 | 2008 | 1 | 18 | 21 | 16023.5007
2027/2028 | 2008 | 1 | 18 | 22 | 17296.0931
2027/2028 | 2008 | 1 | 18 | 23 | 18214.0491
2027/2028 | 2008 | 1 | 18 | 24 | 20554.9983
2027/2028 | 2008 | 1 | 19 | 1 | 22072.092
2027/2028 | 2008 | 1 | 19 | 2 | 22603.5548
2027/2028 | 2008 | 1 | 19 | 3 | 22365.9423
2027/2028 | 2008 | 1 | 19 | 4 | 21247.7242
2027/2028 | 2008 | 1 | 19 | 5 | 20758.0502
2027/2028 | 2008 | 1 | 19 | 6 | 20636.1727
2027/2028 | 2008 | 1 | 19 | 7 | 19717.9113
2027/2028 | 2008 | 1 | 19 | 8 | 18276.9694
2027/2028 | 2008 | 1 | 19 | 9 | 14088.6158
2027/2028 | 2008 | 1 | 19 | 10 | 14328.0267
2027/2028 | 2008 | 1 | 19 | 11 | 14326.9811
2027/2028 | 2008 | 1 | 19 | 12 | 13478.9764
2027/2028 | 2008 | 1 | 19 | 13 | 12588.2722
2027/2028 | 2008 | 1 | 19 | 14 | 12227.9625
2027/2028 | 2008 | 1 | 19 | 15 | 11552.508
2027/2028 | 2008 | 1 | 19 | 16 | 10577.6783
2027/2028 | 2008 | 1 | 19 | 17 | 8520.1099
2027/2028 | 2008 | 1 | 19 | 18 | 7802.8132
2027/2028 | 2008 | 1 | 19 | 19 | 9705.4214
2027/2028 | 2008 | 1 | 19 | 20 | 11631.5298
2027/2028 | 2008 | 1 | 19 | 21 | 12464.2875
2027/2028 | 2008 | 1 | 19 | 22 | 15177.4931
2027/2028 | 2008 | 1 | 19 | 23 | 18506.72
2027/2028 | 2008 | 1 | 19 | 24 | 22187.9758
2027/2028 | 2008 | 1 | 20 | 1 | 25233.8684
2027/2028 | 2008 | 1 | 20 | 2 | 27401.1086
2027/2028 | 2008 | 1 | 20 | 3 | 28364.9054
2027/2028 | 2008 | 1 | 20 | 4 | 28902.1521
2027/2028 | 2008 | 1 | 20 | 5 | 29223.6185
2027/2028 | 2008 | 1 | 20 | 6 | 29282.2309
2027/2028 | 2008 | 1 | 20 | 7 | 29866.057
2027/2028 | 2008 | 1 | 20 | 8 | 28557.793
2027/2028 | 2008 | 1 | 20 | 9 | 25504.2913
2027/2028 | 2008 | 1 | 20 | 10 | 24197.3481
2027/2028 | 2008 | 1 | 20 | 11 | 26722.5507
2027/2028 | 2008 | 1 | 20 | 12 | 27965.7764
2027/2028 | 2008 | 1 | 20 | 13 | 30979.6594
2027/2028 | 2008 | 1 | 20 | 14 | 32228.4083
2027/2028 | 2008 | 1 | 20 | 15 | 31383.7988
2027/2028 | 2008 | 1 | 20 | 16 | 32083.4872
2027/2028 | 2008 | 1 | 20 | 17 | 31748.049
2027/2028 | 2008 | 1 | 20 | 18 | 31896.3636
2027/2028 | 2008 | 1 | 20 | 19 | 32044.4835
2027/2028 | 2008 | 1 | 20 | 20 | 32682.0845
2027/2028 | 2008 | 1 | 20 | 21 | 34139.8212
2027/2028 | 2008 | 1 | 20 | 22 | 34931.6445
2027/2028 | 2008 | 1 | 20 | 23 | 34521.0822
2027/2028 | 2008 | 1 | 20 | 24 | 34334.7575
2027/2028 | 2008 | 1 | 21 | 1 | 33667.5753
2027/2028 | 2008 | 1 | 21 | 2 | 31326.0385
2027/2028 | 2008 | 1 | 21 | 3 | 29470.1116
2027/2028 | 2008 | 1 | 21 | 4 | 30684.5874
2027/2028 | 2008 | 1 | 21 | 5 | 29836.5499
2027/2028 | 2008 | 1 | 21 | 6 | 30245.2243
2027/2028 | 2008 | 1 | 21 | 7 | 30352.7321
2027/2028 | 2008 | 1 | 21 | 8 | 29145.8394
2027/2028 | 2008 | 1 | 21 | 9 | 27048.2372
2027/2028 | 2008 | 1 | 21 | 10 | 28683.0931
2027/2028 | 2008 | 1 | 21 | 11 | 28580.686
2027/2028 | 2008 | 1 | 21 | 12 | 27416.2687
2027/2028 | 2008 | 1 | 21 | 13 | 26297.1024
2027/2028 | 2008 | 1 | 21 | 14 | 25976.2498
2027/2028 | 2008 | 1 | 21 | 15 | 24701.2377
2027/2028 | 2008 | 1 | 21 | 16 | 23400.9211
2027/2028 | 2008 | 1 | 21 | 17 | 20994.5954
2027/2028 | 2008 | 1 | 21 | 18 | 21266.1149
2027/2028 | 2008 | 1 | 21 | 19 | 22214.9729
2027/2028 | 2008 | 1 | 21 | 20 | 22933.5919
2027/2028 | 2008 | 1 | 21 | 21 | 23169.9273
2027/2028 | 2008 | 1 | 21 | 22 | 21693.5356
2027/2028 | 2008 | 1 | 21 | 23 | 20833.2323
2027/2028 | 2008 | 1 | 21 | 24 | 20064.092
2027/2028 | 2008 | 1 | 22 | 1 | 19637.8724
2027/2028 | 2008 | 1 | 22 | 2 | 17911.3585
2027/2028 | 2008 | 1 | 22 | 3 | 15719.0893
2027/2028 | 2008 | 1 | 22 | 4 | 14077.5561
2027/2028 | 2008 | 1 | 22 | 5 | 13661.6622
2027/2028 | 2008 | 1 | 22 | 6 | 14498.0497
2027/2028 | 2008 | 1 | 22 | 7 | 15666.48
2027/2028 | 2008 | 1 | 22 | 8 | 16816.8893
2027/2028 | 2008 | 1 | 22 | 9 | 14321.8554
2027/2028 | 2008 | 1 | 22 | 10 | 14748.012
2027/2028 | 2008 | 1 | 22 | 11 | 14569.8792
2027/2028 | 2008 | 1 | 22 | 12 | 12956.4984
2027/2028 | 2008 | 1 | 22 | 13 | 11003.136
2027/2028 | 2008 | 1 | 22 | 14 | 9052.9971
2027/2028 | 2008 | 1 | 22 | 15 | 7512.4638
2027/2028 | 2008 | 1 | 22 | 16 | 7171.0115
2027/2028 | 2008 | 1 | 22 | 17 | 6690.5575
2027/2028 | 2008 | 1 | 22 | 18 | 6738.0419
2027/2028 | 2008 | 1 | 22 | 19 | 6753.7529
2027/2028 | 2008 | 1 | 22 | 20 | 6777.7006
2027/2028 | 2008 | 1 | 22 | 21 | 6612.9456
2027/2028 | 2008 | 1 | 22 | 22 | 6486.2299
2027/2028 | 2008 | 1 | 22 | 23 | 6877.1903
2027/2028 | 2008 | 1 | 22 | 24 | 6954.5027
2027/2028 | 2008 | 1 | 23 | 1 | 8102.1627
2027/2028 | 2008 | 1 | 23 | 2 | 8871.533
2027/2028 | 2008 | 1 | 23 | 3 | 9280.139
2027/2028 | 2008 | 1 | 23 | 4 | 9239.7915
2027/2028 | 2008 | 1 | 23 | 5 | 9030.1793
2027/2028 | 2008 | 1 | 23 | 6 | 8694.1663
2027/2028 | 2008 | 1 | 23 | 7 | 8237.2279
2027/2028 | 2008 | 1 | 23 | 8 | 7787.7468
2027/2028 | 2008 | 1 | 23 | 9 | 7266.1313
2027/2028 | 2008 | 1 | 23 | 10 | 6665.2692
2027/2028 | 2008 | 1 | 23 | 11 | 6707.3291
2027/2028 | 2008 | 1 | 23 | 12 | 6582.0275
2027/2028 | 2008 | 1 | 23 | 13 | 6870.6518
2027/2028 | 2008 | 1 | 23 | 14 | 7008.8118
2027/2028 | 2008 | 1 | 23 | 15 | 7111.755
2027/2028 | 2008 | 1 | 23 | 16 | 7546.5782
2027/2028 | 2008 | 1 | 23 | 17 | 7383.7561
2027/2028 | 2008 | 1 | 23 | 18 | 8321.5968
2027/2028 | 2008 | 1 | 23 | 19 | 10385.7102
2027/2028 | 2008 | 1 | 23 | 20 | 13642.6366
2027/2028 | 2008 | 1 | 23 | 21 | 14807.7126
2027/2028 | 2008 | 1 | 23 | 22 | 16476.6826
2027/2028 | 2008 | 1 | 23 | 23 | 19171.4093
2027/2028 | 2008 | 1 | 23 | 24 | 21288.2916
2027/2028 | 2008 | 1 | 24 | 1 | 23708.8482
2027/2028 | 2008 | 1 | 24 | 2 | 24499.4488
2027/2028 | 2008 | 1 | 24 | 3 | 24843.1781
2027/2028 | 2008 | 1 | 24 | 4 | 23599.3501
2027/2028 | 2008 | 1 | 24 | 5 | 22967.4647
2027/2028 | 2008 | 1 | 24 | 6 | 22482.7278
2027/2028 | 2008 | 1 | 24 | 7 | 20291.3978
2027/2028 | 2008 | 1 | 24 | 8 | 18598.9487
2027/2028 | 2008 | 1 | 24 | 9 | 15851.4192
2027/2028 | 2008 | 1 | 24 | 10 | 17392.7795
2027/2028 | 2008 | 1 | 24 | 11 | 17854.0373
2027/2028 | 2008 | 1 | 24 | 12 | 16904.1299
2027/2028 | 2008 | 1 | 24 | 13 | 16337.9363
2027/2028 | 2008 | 1 | 24 | 14 | 16272.301
2027/2028 | 2008 | 1 | 24 | 15 | 16198.0066
2027/2028 | 2008 | 1 | 24 | 16 | 15522.087
2027/2028 | 2008 | 1 | 24 | 17 | 13922.6081
2027/2028 | 2008 | 1 | 24 | 18 | 13262.1079
2027/2028 | 2008 | 1 | 24 | 19 | 13671.1353
2027/2028 | 2008 | 1 | 24 | 20 | 13071.6297
2027/2028 | 2008 | 1 | 24 | 21 | 12981.7228
2027/2028 | 2008 | 1 | 24 | 22 | 12579.1699
2027/2028 | 2008 | 1 | 24 | 23 | 11865.1779
2027/2028 | 2008 | 1 | 24 | 24 | 11554.1747
2027/2028 | 2008 | 1 | 25 | 1 | 12089.1506
2027/2028 | 2008 | 1 | 25 | 2 | 12150.8014
2027/2028 | 2008 | 1 | 25 | 3 | 11507.8126
2027/2028 | 2008 | 1 | 25 | 4 | 11722.3279
2027/2028 | 2008 | 1 | 25 | 5 | 12214.5041
2027/2028 | 2008 | 1 | 25 | 6 | 12985.0725
2027/2028 | 2008 | 1 | 25 | 7 | 12324.5408
2027/2028 | 2008 | 1 | 25 | 8 | 11232.8356
2027/2028 | 2008 | 1 | 25 | 9 | 10566.9839
2027/2028 | 2008 | 1 | 25 | 10 | 11668.7857
2027/2028 | 2008 | 1 | 25 | 11 | 12341.9809
2027/2028 | 2008 | 1 | 25 | 12 | 12038.2806
2027/2028 | 2008 | 1 | 25 | 13 | 12676.0905
2027/2028 | 2008 | 1 | 25 | 14 | 13181.909
2027/2028 | 2008 | 1 | 25 | 15 | 13082.2705
2027/2028 | 2008 | 1 | 25 | 16 | 13134.9521
2027/2028 | 2008 | 1 | 25 | 17 | 11433.6091
2027/2028 | 2008 | 1 | 25 | 18 | 12219.4714
2027/2028 | 2008 | 1 | 25 | 19 | 14512.5527
2027/2028 | 2008 | 1 | 25 | 20 | 16738.9506
2027/2028 | 2008 | 1 | 25 | 21 | 18640.1571
2027/2028 | 2008 | 1 | 25 | 22 | 19919.1614
2027/2028 | 2008 | 1 | 25 | 23 | 19455.4409
2027/2028 | 2008 | 1 | 25 | 24 | 19506.7974
2027/2028 | 2008 | 1 | 26 | 1 | 19851.6173
2027/2028 | 2008 | 1 | 26 | 2 | 19525.4615
2027/2028 | 2008 | 1 | 26 | 3 | 19497.3648
2027/2028 | 2008 | 1 | 26 | 4 | 18965.0279
2027/2028 | 2008 | 1 | 26 | 5 | 18952.0759
2027/2028 | 2008 | 1 | 26 | 6 | 20023.3987
2027/2028 | 2008 | 1 | 26 | 7 | 20664.819
2027/2028 | 2008 | 1 | 26 | 8 | 20428.8431
2027/2028 | 2008 | 1 | 26 | 9 | 18434.3737
2027/2028 | 2008 | 1 | 26 | 10 | 13570.4192
2027/2028 | 2008 | 1 | 26 | 11 | 9858.6316
2027/2028 | 2008 | 1 | 26 | 12 | 7913.4746
2027/2028 | 2008 | 1 | 26 | 13 | 6668.6994
2027/2028 | 2008 | 1 | 26 | 14 | 4811.304
2027/2028 | 2008 | 1 | 26 | 15 | 3175.5995
2027/2028 | 2008 | 1 | 26 | 16 | 1819.1599
2027/2028 | 2008 | 1 | 26 | 17 | 1113.1681
2027/2028 | 2008 | 1 | 26 | 18 | 1228.0723
2027/2028 | 2008 | 1 | 26 | 19 | 1573.8073
2027/2028 | 2008 | 1 | 26 | 20 | 2088.2542
2027/2028 | 2008 | 1 | 26 | 21 | 3327.4552
2027/2028 | 2008 | 1 | 26 | 22 | 4528.001
2027/2028 | 2008 | 1 | 26 | 23 | 5594.8154
2027/2028 | 2008 | 1 | 26 | 24 | 7311.1043
2027/2028 | 2008 | 1 | 27 | 1 | 9159.3827
2027/2028 | 2008 | 1 | 27 | 2 | 10100.0676
2027/2028 | 2008 | 1 | 27 | 3 | 10816.7618
2027/2028 | 2008 | 1 | 27 | 4 | 11195.459
2027/2028 | 2008 | 1 | 27 | 5 | 12037.7475
2027/2028 | 2008 | 1 | 27 | 6 | 12360.5034
2027/2028 | 2008 | 1 | 27 | 7 | 14033.2861
2027/2028 | 2008 | 1 | 27 | 8 | 15154.0241
2027/2028 | 2008 | 1 | 27 | 9 | 16115.0742
2027/2028 | 2008 | 1 | 27 | 10 | 15313.723
2027/2028 | 2008 | 1 | 27 | 11 | 12822.2647
2027/2028 | 2008 | 1 | 27 | 12 | 15723.821
2027/2028 | 2008 | 1 | 27 | 13 | 19546.8856
2027/2028 | 2008 | 1 | 27 | 14 | 22370.0893
2027/2028 | 2008 | 1 | 27 | 15 | 24344.1472
2027/2028 | 2008 | 1 | 27 | 16 | 25734.437
2027/2028 | 2008 | 1 | 27 | 17 | 26237.9515
2027/2028 | 2008 | 1 | 27 | 18 | 28845.2187
2027/2028 | 2008 | 1 | 27 | 19 | 30981.8161
2027/2028 | 2008 | 1 | 27 | 20 | 32125.9203
2027/2028 | 2008 | 1 | 27 | 21 | 32200.9091
2027/2028 | 2008 | 1 | 27 | 22 | 32717.9506
2027/2028 | 2008 | 1 | 27 | 23 | 32648.3581
2027/2028 | 2008 | 1 | 27 | 24 | 32479.2666
2027/2028 | 2008 | 1 | 28 | 1 | 30546.5633
2027/2028 | 2008 | 1 | 28 | 2 | 29595.9832
2027/2028 | 2008 | 1 | 28 | 3 | 29703.0434
2027/2028 | 2008 | 1 | 28 | 4 | 29995.4011
2027/2028 | 2008 | 1 | 28 | 5 | 30938.0569
2027/2028 | 2008 | 1 | 28 | 6 | 31406.2152
2027/2028 | 2008 | 1 | 28 | 7 | 31596.4895
2027/2028 | 2008 | 1 | 28 | 8 | 33418.0177
2027/2028 | 2008 | 1 | 28 | 9 | 33809.4811
2027/2028 | 2008 | 1 | 28 | 10 | 35144.9755
2027/2028 | 2008 | 1 | 28 | 11 | 35226.7776
2027/2028 | 2008 | 1 | 28 | 12 | 34991.7525
2027/2028 | 2008 | 1 | 28 | 13 | 35243.3121
2027/2028 | 2008 | 1 | 28 | 14 | 34657.732
2027/2028 | 2008 | 1 | 28 | 15 | 34628.2694
2027/2028 | 2008 | 1 | 28 | 16 | 34179.1116
2027/2028 | 2008 | 1 | 28 | 17 | 33073.7539
2027/2028 | 2008 | 1 | 28 | 18 | 31807.4962
2027/2028 | 2008 | 1 | 28 | 19 | 33182.3528
2027/2028 | 2008 | 1 | 28 | 20 | 33679.0025
2027/2028 | 2008 | 1 | 28 | 21 | 34947.4983
2027/2028 | 2008 | 1 | 28 | 22 | 35244.8352
2027/2028 | 2008 | 1 | 28 | 23 | 35096.6811
2027/2028 | 2008 | 1 | 28 | 24 | 35075.3137
2027/2028 | 2008 | 1 | 29 | 1 | 35846.9453
2027/2028 | 2008 | 1 | 29 | 2 | 35830.9181
2027/2028 | 2008 | 1 | 29 | 3 | 35409.0668
2027/2028 | 2008 | 1 | 29 | 4 | 35246.7969
2027/2028 | 2008 | 1 | 29 | 5 | 34089.7389
2027/2028 | 2008 | 1 | 29 | 6 | 33883.293
2027/2028 | 2008 | 1 | 29 | 7 | 30986.0152
2027/2028 | 2008 | 1 | 29 | 8 | 29963.2721
2027/2028 | 2008 | 1 | 29 | 9 | 29316.2113
2027/2028 | 2008 | 1 | 29 | 10 | 28133.2313
2027/2028 | 2008 | 1 | 29 | 11 | 26635.1537
2027/2028 | 2008 | 1 | 29 | 12 | 27780.1443
2027/2028 | 2008 | 1 | 29 | 13 | 29715.3507
2027/2028 | 2008 | 1 | 29 | 14 | 29764.5906
2027/2028 | 2008 | 1 | 29 | 15 | 28040.7217
2027/2028 | 2008 | 1 | 29 | 16 | 23693.2203
2027/2028 | 2008 | 1 | 29 | 17 | 16934.2001
2027/2028 | 2008 | 1 | 29 | 18 | 12930.6812
2027/2028 | 2008 | 1 | 29 | 19 | 12894.3516
2027/2028 | 2008 | 1 | 29 | 20 | 14039.9657
2027/2028 | 2008 | 1 | 29 | 21 | 17589.2644
2027/2028 | 2008 | 1 | 29 | 22 | 22780.9131
2027/2028 | 2008 | 1 | 29 | 23 | 27942.0902
2027/2028 | 2008 | 1 | 29 | 24 | 31162.0893
2027/2028 | 2008 | 1 | 30 | 1 | 32994.8638
2027/2028 | 2008 | 1 | 30 | 2 | 33125.9756
2027/2028 | 2008 | 1 | 30 | 3 | 33678.2369
2027/2028 | 2008 | 1 | 30 | 4 | 32519.1945
2027/2028 | 2008 | 1 | 30 | 5 | 32311.0187
2027/2028 | 2008 | 1 | 30 | 6 | 31836.5179
2027/2028 | 2008 | 1 | 30 | 7 | 31189.77
2027/2028 | 2008 | 1 | 30 | 8 | 30244.4832
2027/2028 | 2008 | 1 | 30 | 9 | 28355.8238
2027/2028 | 2008 | 1 | 30 | 10 | 28662.8168
2027/2028 | 2008 | 1 | 30 | 11 | 29669.5243
2027/2028 | 2008 | 1 | 30 | 12 | 30834.2271
2027/2028 | 2008 | 1 | 30 | 13 | 31278.7218
2027/2028 | 2008 | 1 | 30 | 14 | 30864.3392
2027/2028 | 2008 | 1 | 30 | 15 | 29783.5426
2027/2028 | 2008 | 1 | 30 | 16 | 29707.8976
2027/2028 | 2008 | 1 | 30 | 17 | 29228.0831
2027/2028 | 2008 | 1 | 30 | 18 | 27871.5761
2027/2028 | 2008 | 1 | 30 | 19 | 29007.4975
2027/2028 | 2008 | 1 | 30 | 20 | 29703.4856
2027/2028 | 2008 | 1 | 30 | 21 | 29728.9112
2027/2028 | 2008 | 1 | 30 | 22 | 29394.9993
2027/2028 | 2008 | 1 | 30 | 23 | 28081.8544
2027/2028 | 2008 | 1 | 30 | 24 | 27917.0775
2027/2028 | 2008 | 1 | 31 | 1 | 29693.046
2027/2028 | 2008 | 1 | 31 | 2 | 28481.4558
2027/2028 | 2008 | 1 | 31 | 3 | 27108.2728
2027/2028 | 2008 | 1 | 31 | 4 | 27048.1704
2027/2028 | 2008 | 1 | 31 | 5 | 27736.0043
2027/2028 | 2008 | 1 | 31 | 6 | 28801.6474
2027/2028 | 2008 | 1 | 31 | 7 | 30866.656
2027/2028 | 2008 | 1 | 31 | 8 | 32758.5482
2027/2028 | 2008 | 1 | 31 | 9 | 32446.6217
2027/2028 | 2008 | 1 | 31 | 10 | 31983.9957
2027/2028 | 2008 | 1 | 31 | 11 | 32727.2553
2027/2028 | 2008 | 1 | 31 | 12 | 33327.6287
2027/2028 | 2008 | 1 | 31 | 13 | 35153.349
2027/2028 | 2008 | 1 | 31 | 14 | 35159.3518
2027/2028 | 2008 | 1 | 31 | 15 | 34383.0469
2027/2028 | 2008 | 1 | 31 | 16 | 35030.3589
2027/2028 | 2008 | 1 | 31 | 17 | 29514.3716
2027/2028 | 2008 | 1 | 31 | 18 | 30028.6968
2027/2028 | 2008 | 1 | 31 | 19 | 25951.9426
2027/2028 | 2008 | 1 | 31 | 20 | 21951.8599
2027/2028 | 2008 | 1 | 31 | 21 | 16125.5256
2027/2028 | 2008 | 1 | 31 | 22 | 12704.5923
2027/2028 | 2008 | 1 | 31 | 23 | 12217.5494
2027/2028 | 2008 | 1 | 31 | 24 | 12989.8238
2028/2029 | 2008 | 1 | 1 | 1 | 25186.4182
2028/2029 | 2008 | 1 | 1 | 2 | 24852.8639
2028/2029 | 2008 | 1 | 1 | 3 | 23776.839
2028/2029 | 2008 | 1 | 1 | 4 | 22401.0651
2028/2029 | 2008 | 1 | 1 | 5 | 21268.7
2028/2029 | 2008 | 1 | 1 | 6 | 20449.8325
2028/2029 | 2008 | 1 | 1 | 7 | 19423.6818
2028/2029 | 2008 | 1 | 1 | 8 | 17640.6616
2028/2029 | 2008 | 1 | 1 | 9 | 15739.4869
2028/2029 | 2008 | 1 | 1 | 10 | 13184.7141
2028/2029 | 2008 | 1 | 1 | 11 | 15454.3749
2028/2029 | 2008 | 1 | 1 | 12 | 17236.783
2028/2029 | 2008 | 1 | 1 | 13 | 17053.2697
2028/2029 | 2008 | 1 | 1 | 14 | 15400.6393
2028/2029 | 2008 | 1 | 1 | 15 | 15279.373
2028/2029 | 2008 | 1 | 1 | 16 | 14725.0933
2028/2029 | 2008 | 1 | 1 | 17 | 11716.6241
2028/2029 | 2008 | 1 | 1 | 18 | 11693.7185
2028/2029 | 2008 | 1 | 1 | 19 | 11570.0593
2028/2029 | 2008 | 1 | 1 | 20 | 12467.876
2028/2029 | 2008 | 1 | 1 | 21 | 12224.0939
2028/2029 | 2008 | 1 | 1 | 22 | 10863.5686
2028/2029 | 2008 | 1 | 1 | 23 | 10192.5145
2028/2029 | 2008 | 1 | 1 | 24 | 10322.1604
2028/2029 | 2008 | 1 | 2 | 1 | 10601.7513
2028/2029 | 2008 | 1 | 2 | 2 | 11273.9444
2028/2029 | 2008 | 1 | 2 | 3 | 10578.5008
2028/2029 | 2008 | 1 | 2 | 4 | 11490.9691
2028/2029 | 2008 | 1 | 2 | 5 | 11796.7524
2028/2029 | 2008 | 1 | 2 | 6 | 12075.9362
2028/2029 | 2008 | 1 | 2 | 7 | 12260.0064
2028/2029 | 2008 | 1 | 2 | 8 | 11749.4356
2028/2029 | 2008 | 1 | 2 | 9 | 9614.0373
2028/2029 | 2008 | 1 | 2 | 10 | 9380.8958
2028/2029 | 2008 | 1 | 2 | 11 | 10893.586
2028/2029 | 2008 | 1 | 2 | 12 | 11934.9132
2028/2029 | 2008 | 1 | 2 | 13 | 12155.8055
2028/2029 | 2008 | 1 | 2 | 14 | 11938.2056
2028/2029 | 2008 | 1 | 2 | 15 | 12047.6322
2028/2029 | 2008 | 1 | 2 | 16 | 11241.446
2028/2029 | 2008 | 1 | 2 | 17 | 10242.1199
2028/2029 | 2008 | 1 | 2 | 18 | 10979.489
2028/2029 | 2008 | 1 | 2 | 19 | 13622.3208
2028/2029 | 2008 | 1 | 2 | 20 | 16441.2827
2028/2029 | 2008 | 1 | 2 | 21 | 19023.4165
2028/2029 | 2008 | 1 | 2 | 22 | 21269.9026
2028/2029 | 2008 | 1 | 2 | 23 | 22286.529
2028/2029 | 2008 | 1 | 2 | 24 | 22819.97
2028/2029 | 2008 | 1 | 3 | 1 | 24203.7422
2028/2029 | 2008 | 1 | 3 | 2 | 25092.8325
2028/2029 | 2008 | 1 | 3 | 3 | 25611.1907
2028/2029 | 2008 | 1 | 3 | 4 | 26579.3803
2028/2029 | 2008 | 1 | 3 | 5 | 27904.9419
2028/2029 | 2008 | 1 | 3 | 6 | 29753.3481
2028/2029 | 2008 | 1 | 3 | 7 | 30060.1124
2028/2029 | 2008 | 1 | 3 | 8 | 28686.7987
2028/2029 | 2008 | 1 | 3 | 9 | 26569.8752
2028/2029 | 2008 | 1 | 3 | 10 | 27580.5149
2028/2029 | 2008 | 1 | 3 | 11 | 28066.5202
2028/2029 | 2008 | 1 | 3 | 12 | 28646.5292
2028/2029 | 2008 | 1 | 3 | 13 | 29213.0167
2028/2029 | 2008 | 1 | 3 | 14 | 29873.3726
2028/2029 | 2008 | 1 | 3 | 15 | 31019.6762
2028/2029 | 2008 | 1 | 3 | 16 | 32067.941
2028/2029 | 2008 | 1 | 3 | 17 | 31720.0375
2028/2029 | 2008 | 1 | 3 | 18 | 30928.1695
2028/2029 | 2008 | 1 | 3 | 19 | 31700.1204
2028/2029 | 2008 | 1 | 3 | 20 | 31784.6524
2028/2029 | 2008 | 1 | 3 | 21 | 32804.1214
2028/2029 | 2008 | 1 | 3 | 22 | 33275.1143
2028/2029 | 2008 | 1 | 3 | 23 | 33562.9441
2028/2029 | 2008 | 1 | 3 | 24 | 33548.1484
2028/2029 | 2008 | 1 | 4 | 1 | 33091.847
2028/2029 | 2008 | 1 | 4 | 2 | 32701.0405
2028/2029 | 2008 | 1 | 4 | 3 | 34047.4574
2028/2029 | 2008 | 1 | 4 | 4 | 33630.3531
2028/2029 | 2008 | 1 | 4 | 5 | 33236.0796
2028/2029 | 2008 | 1 | 4 | 6 | 32816.2649
2028/2029 | 2008 | 1 | 4 | 7 | 32323.3015
2028/2029 | 2008 | 1 | 4 | 8 | 30526.813
2028/2029 | 2008 | 1 | 4 | 9 | 29896.1788
2028/2029 | 2008 | 1 | 4 | 10 | 29740.9453
2028/2029 | 2008 | 1 | 4 | 11 | 30777.4599
2028/2029 | 2008 | 1 | 4 | 12 | 31454.2141
2028/2029 | 2008 | 1 | 4 | 13 | 32986.5863
2028/2029 | 2008 | 1 | 4 | 14 | 34003.4729
2028/2029 | 2008 | 1 | 4 | 15 | 34068.8768
2028/2029 | 2008 | 1 | 4 | 16 | 35085.856
2028/2029 | 2008 | 1 | 4 | 17 | 34549.7581
2028/2029 | 2008 | 1 | 4 | 18 | 34241.3705
2028/2029 | 2008 | 1 | 4 | 19 | 35526.7579
2028/2029 | 2008 | 1 | 4 | 20 | 35925.8786
2028/2029 | 2008 | 1 | 4 | 21 | 36299.8476
2028/2029 | 2008 | 1 | 4 | 22 | 36606.1118
2028/2029 | 2008 | 1 | 4 | 23 | 36567.5009
2028/2029 | 2008 | 1 | 4 | 24 | 37090.8474
2028/2029 | 2008 | 1 | 5 | 1 | 37088.7335
2028/2029 | 2008 | 1 | 5 | 2 | 36846.6769
2028/2029 | 2008 | 1 | 5 | 3 | 35506.7884
2028/2029 | 2008 | 1 | 5 | 4 | 34578.9598
2028/2029 | 2008 | 1 | 5 | 5 | 34199.5351
2028/2029 | 2008 | 1 | 5 | 6 | 33901.0789
2028/2029 | 2008 | 1 | 5 | 7 | 33861.6772
2028/2029 | 2008 | 1 | 5 | 8 | 33073.8629
2028/2029 | 2008 | 1 | 5 | 9 | 31146.7731
2028/2029 | 2008 | 1 | 5 | 10 | 30353.1983
2028/2029 | 2008 | 1 | 5 | 11 | 31046.3013
2028/2029 | 2008 | 1 | 5 | 12 | 33270.2801
2028/2029 | 2008 | 1 | 5 | 13 | 34931.3837
2028/2029 | 2008 | 1 | 5 | 14 | 35548.1902
2028/2029 | 2008 | 1 | 5 | 15 | 35913.8748
2028/2029 | 2008 | 1 | 5 | 16 | 35417.6498
2028/2029 | 2008 | 1 | 5 | 17 | 32544.4513
2028/2029 | 2008 | 1 | 5 | 18 | 32812.3123
2028/2029 | 2008 | 1 | 5 | 19 | 34651.7829
2028/2029 | 2008 | 1 | 5 | 20 | 35105.7235
2028/2029 | 2008 | 1 | 5 | 21 | 34992.616
2028/2029 | 2008 | 1 | 5 | 22 | 35202.9393
2028/2029 | 2008 | 1 | 5 | 23 | 35310.8647
2028/2029 | 2008 | 1 | 5 | 24 | 35390.0228
2028/2029 | 2008 | 1 | 6 | 1 | 35420.2722
2028/2029 | 2008 | 1 | 6 | 2 | 35185.1174
2028/2029 | 2008 | 1 | 6 | 3 | 34999.1678
2028/2029 | 2008 | 1 | 6 | 4 | 34766.0419
2028/2029 | 2008 | 1 | 6 | 5 | 34134.5147
2028/2029 | 2008 | 1 | 6 | 6 | 33919.6254
2028/2029 | 2008 | 1 | 6 | 7 | 33466.4948
2028/2029 | 2008 | 1 | 6 | 8 | 31199.0989
2028/2029 | 2008 | 1 | 6 | 9 | 29342.5803
2028/2029 | 2008 | 1 | 6 | 10 | 30617.611
2028/2029 | 2008 | 1 | 6 | 11 | 31021.9087
2028/2029 | 2008 | 1 | 6 | 12 | 31957.3858
2028/2029 | 2008 | 1 | 6 | 13 | 32350.3608
2028/2029 | 2008 | 1 | 6 | 14 | 31798.9769
2028/2029 | 2008 | 1 | 6 | 15 | 31366.9045
2028/2029 | 2008 | 1 | 6 | 16 | 30080.6252
2028/2029 | 2008 | 1 | 6 | 17 | 28010.7912
2028/2029 | 2008 | 1 | 6 | 18 | 29281.0111
2028/2029 | 2008 | 1 | 6 | 19 | 31627.0456
2028/2029 | 2008 | 1 | 6 | 20 | 32367.1038
2028/2029 | 2008 | 1 | 6 | 21 | 32307.5423
2028/2029 | 2008 | 1 | 6 | 22 | 33124.5108
2028/2029 | 2008 | 1 | 6 | 23 | 33018.9897
2028/2029 | 2008 | 1 | 6 | 24 | 34223.4965
2028/2029 | 2008 | 1 | 7 | 1 | 33739.1577
2028/2029 | 2008 | 1 | 7 | 2 | 32868.9738
2028/2029 | 2008 | 1 | 7 | 3 | 32241.3281
2028/2029 | 2008 | 1 | 7 | 4 | 31185.779
2028/2029 | 2008 | 1 | 7 | 5 | 30936.8805
2028/2029 | 2008 | 1 | 7 | 6 | 30503.34
2028/2029 | 2008 | 1 | 7 | 7 | 29959.6828
2028/2029 | 2008 | 1 | 7 | 8 | 27761.5049
2028/2029 | 2008 | 1 | 7 | 9 | 24942.1195
2028/2029 | 2008 | 1 | 7 | 10 | 24859.0043
2028/2029 | 2008 | 1 | 7 | 11 | 24844.8694
2028/2029 | 2008 | 1 | 7 | 12 | 24732.6062
2028/2029 | 2008 | 1 | 7 | 13 | 24783.335
2028/2029 | 2008 | 1 | 7 | 14 | 24484.1134
2028/2029 | 2008 | 1 | 7 | 15 | 24514.1894
2028/2029 | 2008 | 1 | 7 | 16 | 23841.0549
2028/2029 | 2008 | 1 | 7 | 17 | 22459.8573
2028/2029 | 2008 | 1 | 7 | 18 | 24960.7097
2028/2029 | 2008 | 1 | 7 | 19 | 27253.5983
2028/2029 | 2008 | 1 | 7 | 20 | 28322.6198
2028/2029 | 2008 | 1 | 7 | 21 | 28508.8514
2028/2029 | 2008 | 1 | 7 | 22 | 29274.6296
2028/2029 | 2008 | 1 | 7 | 23 | 29932.5355
2028/2029 | 2008 | 1 | 7 | 24 | 30151.4887
2028/2029 | 2008 | 1 | 8 | 1 | 32161.434
2028/2029 | 2008 | 1 | 8 | 2 | 34556.676
2028/2029 | 2008 | 1 | 8 | 3 | 35214.2047
2028/2029 | 2008 | 1 | 8 | 4 | 34706.6252
2028/2029 | 2008 | 1 | 8 | 5 | 33604.7596
2028/2029 | 2008 | 1 | 8 | 6 | 29161.903
2028/2029 | 2008 | 1 | 8 | 7 | 31360.2656
2028/2029 | 2008 | 1 | 8 | 8 | 29994.7078
2028/2029 | 2008 | 1 | 8 | 9 | 27802.7593
2028/2029 | 2008 | 1 | 8 | 10 | 29078.3945
2028/2029 | 2008 | 1 | 8 | 11 | 30557.2986
2028/2029 | 2008 | 1 | 8 | 12 | 30253.9604
2028/2029 | 2008 | 1 | 8 | 13 | 28007.7972
2028/2029 | 2008 | 1 | 8 | 14 | 24620.2842
2028/2029 | 2008 | 1 | 8 | 15 | 21544.2538
2028/2029 | 2008 | 1 | 8 | 16 | 18260.1387
2028/2029 | 2008 | 1 | 8 | 17 | 12451.6798
2028/2029 | 2008 | 1 | 8 | 18 | 10222.9786
2028/2029 | 2008 | 1 | 8 | 19 | 9719.8399
2028/2029 | 2008 | 1 | 8 | 20 | 9246.3214
2028/2029 | 2008 | 1 | 8 | 21 | 9353.5804
2028/2029 | 2008 | 1 | 8 | 22 | 9744.8361
2028/2029 | 2008 | 1 | 8 | 23 | 10706.9046
2028/2029 | 2008 | 1 | 8 | 24 | 11989.2718
2028/2029 | 2008 | 1 | 9 | 1 | 15077.1484
2028/2029 | 2008 | 1 | 9 | 2 | 18279.5514
2028/2029 | 2008 | 1 | 9 | 3 | 22015.5885
2028/2029 | 2008 | 1 | 9 | 4 | 23687.8163
2028/2029 | 2008 | 1 | 9 | 5 | 24385.0107
2028/2029 | 2008 | 1 | 9 | 6 | 25116.1804
2028/2029 | 2008 | 1 | 9 | 7 | 25270.3327
2028/2029 | 2008 | 1 | 9 | 8 | 24620.838
2028/2029 | 2008 | 1 | 9 | 9 | 22815.3787
2028/2029 | 2008 | 1 | 9 | 10 | 18280.6063
2028/2029 | 2008 | 1 | 9 | 11 | 21977.9757
2028/2029 | 2008 | 1 | 9 | 12 | 23896.9155
2028/2029 | 2008 | 1 | 9 | 13 | 22355.2014
2028/2029 | 2008 | 1 | 9 | 14 | 23333.4578
2028/2029 | 2008 | 1 | 9 | 15 | 23765.0728
2028/2029 | 2008 | 1 | 9 | 16 | 23549.5528
2028/2029 | 2008 | 1 | 9 | 17 | 22276.1826
2028/2029 | 2008 | 1 | 9 | 18 | 24404.9494
2028/2029 | 2008 | 1 | 9 | 19 | 27015.977
2028/2029 | 2008 | 1 | 9 | 20 | 27953.8801
2028/2029 | 2008 | 1 | 9 | 21 | 28319.4096
2028/2029 | 2008 | 1 | 9 | 22 | 30739.0785
2028/2029 | 2008 | 1 | 9 | 23 | 30568.4329
2028/2029 | 2008 | 1 | 9 | 24 | 29725.6661
2028/2029 | 2008 | 1 | 10 | 1 | 28306.7712
2028/2029 | 2008 | 1 | 10 | 2 | 27599.2581
2028/2029 | 2008 | 1 | 10 | 3 | 28501.0801
2028/2029 | 2008 | 1 | 10 | 4 | 29230.3464
2028/2029 | 2008 | 1 | 10 | 5 | 28665.4639
2028/2029 | 2008 | 1 | 10 | 6 | 28558.5638
2028/2029 | 2008 | 1 | 10 | 7 | 28230.0407
2028/2029 | 2008 | 1 | 10 | 8 | 27106.5062
2028/2029 | 2008 | 1 | 10 | 9 | 23738.4536
2028/2029 | 2008 | 1 | 10 | 10 | 21519.7336
2028/2029 | 2008 | 1 | 10 | 11 | 23353.0958
2028/2029 | 2008 | 1 | 10 | 12 | 23937.8704
2028/2029 | 2008 | 1 | 10 | 13 | 22381.2463
2028/2029 | 2008 | 1 | 10 | 14 | 20377.2017
2028/2029 | 2008 | 1 | 10 | 15 | 18137.0519
2028/2029 | 2008 | 1 | 10 | 16 | 15121.6493
2028/2029 | 2008 | 1 | 10 | 17 | 10451.8734
2028/2029 | 2008 | 1 | 10 | 18 | 7865.2717
2028/2029 | 2008 | 1 | 10 | 19 | 7233.576
2028/2029 | 2008 | 1 | 10 | 20 | 6829.3932
2028/2029 | 2008 | 1 | 10 | 21 | 7468.3913
2028/2029 | 2008 | 1 | 10 | 22 | 8179.0405
2028/2029 | 2008 | 1 | 10 | 23 | 9745.8992
2028/2029 | 2008 | 1 | 10 | 24 | 11847.6578
2028/2029 | 2008 | 1 | 11 | 1 | 14483.6289
2028/2029 | 2008 | 1 | 11 | 2 | 16185.4427
2028/2029 | 2008 | 1 | 11 | 3 | 18694.5282
2028/2029 | 2008 | 1 | 11 | 4 | 20505.0441
2028/2029 | 2008 | 1 | 11 | 5 | 22041.2336
2028/2029 | 2008 | 1 | 11 | 6 | 22621.8539
2028/2029 | 2008 | 1 | 11 | 7 | 22563.5058
2028/2029 | 2008 | 1 | 11 | 8 | 21504.9346
2028/2029 | 2008 | 1 | 11 | 9 | 17706.821
2028/2029 | 2008 | 1 | 11 | 10 | 11427.2079
2028/2029 | 2008 | 1 | 11 | 11 | 10132.1429
2028/2029 | 2008 | 1 | 11 | 12 | 11143.454
2028/2029 | 2008 | 1 | 11 | 13 | 10961.3063
2028/2029 | 2008 | 1 | 11 | 14 | 10847.9532
2028/2029 | 2008 | 1 | 11 | 15 | 10540.8701
2028/2029 | 2008 | 1 | 11 | 16 | 9315.4228
2028/2029 | 2008 | 1 | 11 | 17 | 7381.6255
2028/2029 | 2008 | 1 | 11 | 18 | 7457.2602
2028/2029 | 2008 | 1 | 11 | 19 | 9752.8664
2028/2029 | 2008 | 1 | 11 | 20 | 11625.6702
2028/2029 | 2008 | 1 | 11 | 21 | 13942.1136
2028/2029 | 2008 | 1 | 11 | 22 | 15735.4328
2028/2029 | 2008 | 1 | 11 | 23 | 16773.4981
2028/2029 | 2008 | 1 | 11 | 24 | 18726.7919
2028/2029 | 2008 | 1 | 12 | 1 | 20858.4118
2028/2029 | 2008 | 1 | 12 | 2 | 21473.3559
2028/2029 | 2008 | 1 | 12 | 3 | 22153.5426
2028/2029 | 2008 | 1 | 12 | 4 | 23906.203
2028/2029 | 2008 | 1 | 12 | 5 | 24578.0917
2028/2029 | 2008 | 1 | 12 | 6 | 25046.4914
2028/2029 | 2008 | 1 | 12 | 7 | 26328.1693
2028/2029 | 2008 | 1 | 12 | 8 | 25946.4819
2028/2029 | 2008 | 1 | 12 | 9 | 22085.66
2028/2029 | 2008 | 1 | 12 | 10 | 18128.4872
2028/2029 | 2008 | 1 | 12 | 11 | 18955.7958
2028/2029 | 2008 | 1 | 12 | 12 | 18060.1726
2028/2029 | 2008 | 1 | 12 | 13 | 18468.929
2028/2029 | 2008 | 1 | 12 | 14 | 19286.8467
2028/2029 | 2008 | 1 | 12 | 15 | 19248.2585
2028/2029 | 2008 | 1 | 12 | 16 | 18275.3864
2028/2029 | 2008 | 1 | 12 | 17 | 14119.1261
2028/2029 | 2008 | 1 | 12 | 18 | 11774.3002
2028/2029 | 2008 | 1 | 12 | 19 | 11998.3999
2028/2029 | 2008 | 1 | 12 | 20 | 11550.5976
2028/2029 | 2008 | 1 | 12 | 21 | 11854.6021
2028/2029 | 2008 | 1 | 12 | 22 | 11773.7712
2028/2029 | 2008 | 1 | 12 | 23 | 11293.5403
2028/2029 | 2008 | 1 | 12 | 24 | 11327.6807
2028/2029 | 2008 | 1 | 13 | 1 | 12042.1774
2028/2029 | 2008 | 1 | 13 | 2 | 12226.9444
2028/2029 | 2008 | 1 | 13 | 3 | 12161.309
2028/2029 | 2008 | 1 | 13 | 4 | 11829.8
2028/2029 | 2008 | 1 | 13 | 5 | 11682.7148
2028/2029 | 2008 | 1 | 13 | 6 | 11661.5425
2028/2029 | 2008 | 1 | 13 | 7 | 11343.221
2028/2029 | 2008 | 1 | 13 | 8 | 10603.9081
2028/2029 | 2008 | 1 | 13 | 9 | 7346.0141
2028/2029 | 2008 | 1 | 13 | 10 | 4921.627
2028/2029 | 2008 | 1 | 13 | 11 | 4686.0526
2028/2029 | 2008 | 1 | 13 | 12 | 4355.6914
2028/2029 | 2008 | 1 | 13 | 13 | 4333.5442
2028/2029 | 2008 | 1 | 13 | 14 | 4985.2288
2028/2029 | 2008 | 1 | 13 | 15 | 5737.6306
2028/2029 | 2008 | 1 | 13 | 16 | 6338.5974
2028/2029 | 2008 | 1 | 13 | 17 | 6411.1
2028/2029 | 2008 | 1 | 13 | 18 | 7489.7319
2028/2029 | 2008 | 1 | 13 | 19 | 9834.0997
2028/2029 | 2008 | 1 | 13 | 20 | 12617.9417
2028/2029 | 2008 | 1 | 13 | 21 | 14492.4528
2028/2029 | 2008 | 1 | 13 | 22 | 16012.548
2028/2029 | 2008 | 1 | 13 | 23 | 17333.0805
2028/2029 | 2008 | 1 | 13 | 24 | 18992.5043
2028/2029 | 2008 | 1 | 14 | 1 | 18513.3084
2028/2029 | 2008 | 1 | 14 | 2 | 17002.1778
2028/2029 | 2008 | 1 | 14 | 3 | 15632.1042
2028/2029 | 2008 | 1 | 14 | 4 | 13845.972
2028/2029 | 2008 | 1 | 14 | 5 | 12271.6442
2028/2029 | 2008 | 1 | 14 | 6 | 11536.918
2028/2029 | 2008 | 1 | 14 | 7 | 10525.183
2028/2029 | 2008 | 1 | 14 | 8 | 9537.2203
2028/2029 | 2008 | 1 | 14 | 9 | 8141.4991
2028/2029 | 2008 | 1 | 14 | 10 | 7350.7373
2028/2029 | 2008 | 1 | 14 | 11 | 7829.5902
2028/2029 | 2008 | 1 | 14 | 12 | 8583.7017
2028/2029 | 2008 | 1 | 14 | 13 | 8775.3744
2028/2029 | 2008 | 1 | 14 | 14 | 9035.3829
2028/2029 | 2008 | 1 | 14 | 15 | 9112.0691
2028/2029 | 2008 | 1 | 14 | 16 | 8785.0622
2028/2029 | 2008 | 1 | 14 | 17 | 8078.8614
2028/2029 | 2008 | 1 | 14 | 18 | 7847.7848
2028/2029 | 2008 | 1 | 14 | 19 | 7991.8904
2028/2029 | 2008 | 1 | 14 | 20 | 8146.8428
2028/2029 | 2008 | 1 | 14 | 21 | 8192.6117
2028/2029 | 2008 | 1 | 14 | 22 | 8378.4217
2028/2029 | 2008 | 1 | 14 | 23 | 9078.7948
2028/2029 | 2008 | 1 | 14 | 24 | 9918.4899
2028/2029 | 2008 | 1 | 15 | 1 | 10928.1148
2028/2029 | 2008 | 1 | 15 | 2 | 11897.4524
2028/2029 | 2008 | 1 | 15 | 3 | 13819.6029
2028/2029 | 2008 | 1 | 15 | 4 | 15458.8543
2028/2029 | 2008 | 1 | 15 | 5 | 17821.6172
2028/2029 | 2008 | 1 | 15 | 6 | 19431.7121
2028/2029 | 2008 | 1 | 15 | 7 | 21287.1221
2028/2029 | 2008 | 1 | 15 | 8 | 22376.0109
2028/2029 | 2008 | 1 | 15 | 9 | 21915.8825
2028/2029 | 2008 | 1 | 15 | 10 | 21175.9962
2028/2029 | 2008 | 1 | 15 | 11 | 23597.1141
2028/2029 | 2008 | 1 | 15 | 12 | 27677.266
2028/2029 | 2008 | 1 | 15 | 13 | 30013.7285
2028/2029 | 2008 | 1 | 15 | 14 | 30733.7864
2028/2029 | 2008 | 1 | 15 | 15 | 30999.0137
2028/2029 | 2008 | 1 | 15 | 16 | 31554.8131
2028/2029 | 2008 | 1 | 15 | 17 | 31341.1794
2028/2029 | 2008 | 1 | 15 | 18 | 31415.528
2028/2029 | 2008 | 1 | 15 | 19 | 32952.5224
2028/2029 | 2008 | 1 | 15 | 20 | 32927.3297
2028/2029 | 2008 | 1 | 15 | 21 | 33488.6415
2028/2029 | 2008 | 1 | 15 | 22 | 33959.2043
2028/2029 | 2008 | 1 | 15 | 23 | 33685.4911
2028/2029 | 2008 | 1 | 15 | 24 | 33444.0221
2028/2029 | 2008 | 1 | 16 | 1 | 33467.817
2028/2029 | 2008 | 1 | 16 | 2 | 32925.1186
2028/2029 | 2008 | 1 | 16 | 3 | 32992.4453
2028/2029 | 2008 | 1 | 16 | 4 | 32731.3329
2028/2029 | 2008 | 1 | 16 | 5 | 30591.3694
2028/2029 | 2008 | 1 | 16 | 6 | 28305.519
2028/2029 | 2008 | 1 | 16 | 7 | 26815.2808
2028/2029 | 2008 | 1 | 16 | 8 | 24262.9697
2028/2029 | 2008 | 1 | 16 | 9 | 19978.5941
2028/2029 | 2008 | 1 | 16 | 10 | 18982.251
2028/2029 | 2008 | 1 | 16 | 11 | 18035.8308
2028/2029 | 2008 | 1 | 16 | 12 | 19017.668
2028/2029 | 2008 | 1 | 16 | 13 | 17968.5054
2028/2029 | 2008 | 1 | 16 | 14 | 16874.749
2028/2029 | 2008 | 1 | 16 | 15 | 17439.9548
2028/2029 | 2008 | 1 | 16 | 16 | 17349.093
2028/2029 | 2008 | 1 | 16 | 17 | 17326.1888
2028/2029 | 2008 | 1 | 16 | 18 | 18750.7444
2028/2029 | 2008 | 1 | 16 | 19 | 21570.0608
2028/2029 | 2008 | 1 | 16 | 20 | 23605.8555
2028/2029 | 2008 | 1 | 16 | 21 | 24087.0204
2028/2029 | 2008 | 1 | 16 | 22 | 23927.4998
2028/2029 | 2008 | 1 | 16 | 23 | 25006.8361
2028/2029 | 2008 | 1 | 16 | 24 | 24591.4231
2028/2029 | 2008 | 1 | 17 | 1 | 24008.1487
2028/2029 | 2008 | 1 | 17 | 2 | 23258.2003
2028/2029 | 2008 | 1 | 17 | 3 | 23398.2748
2028/2029 | 2008 | 1 | 17 | 4 | 22152.8868
2028/2029 | 2008 | 1 | 17 | 5 | 21112.6049
2028/2029 | 2008 | 1 | 17 | 6 | 20004.4487
2028/2029 | 2008 | 1 | 17 | 7 | 18062.5487
2028/2029 | 2008 | 1 | 17 | 8 | 15957.0348
2028/2029 | 2008 | 1 | 17 | 9 | 12966.555
2028/2029 | 2008 | 1 | 17 | 10 | 14108.1765
2028/2029 | 2008 | 1 | 17 | 11 | 13387.576
2028/2029 | 2008 | 1 | 17 | 12 | 11513.7042
2028/2029 | 2008 | 1 | 17 | 13 | 11018.8014
2028/2029 | 2008 | 1 | 17 | 14 | 10345.101
2028/2029 | 2008 | 1 | 17 | 15 | 9541.0831
2028/2029 | 2008 | 1 | 17 | 16 | 8705.3127
2028/2029 | 2008 | 1 | 17 | 17 | 7192.458
2028/2029 | 2008 | 1 | 17 | 18 | 5618.9308
2028/2029 | 2008 | 1 | 17 | 19 | 5882.2509
2028/2029 | 2008 | 1 | 17 | 20 | 6813.1314
2028/2029 | 2008 | 1 | 17 | 21 | 8138.4518
2028/2029 | 2008 | 1 | 17 | 22 | 9187.6459
2028/2029 | 2008 | 1 | 17 | 23 | 9914.0465
2028/2029 | 2008 | 1 | 17 | 24 | 10318.7888
2028/2029 | 2008 | 1 | 18 | 1 | 11391.9736
2028/2029 | 2008 | 1 | 18 | 2 | 12020.0772
2028/2029 | 2008 | 1 | 18 | 3 | 12461.706
2028/2029 | 2008 | 1 | 18 | 4 | 12366.1154
2028/2029 | 2008 | 1 | 18 | 5 | 11714.9847
2028/2029 | 2008 | 1 | 18 | 6 | 11343.4195
2028/2029 | 2008 | 1 | 18 | 7 | 10390.541
2028/2029 | 2008 | 1 | 18 | 8 | 9173.1258
2028/2029 | 2008 | 1 | 18 | 9 | 9204.1884
2028/2029 | 2008 | 1 | 18 | 10 | 9296.1791
2028/2029 | 2008 | 1 | 18 | 11 | 10005.0431
2028/2029 | 2008 | 1 | 18 | 12 | 10430.078
2028/2029 | 2008 | 1 | 18 | 13 | 11264.8494
2028/2029 | 2008 | 1 | 18 | 14 | 11398.4162
2028/2029 | 2008 | 1 | 18 | 15 | 11437.6046
2028/2029 | 2008 | 1 | 18 | 16 | 11375.9872
2028/2029 | 2008 | 1 | 18 | 17 | 11170.6055
2028/2029 | 2008 | 1 | 18 | 18 | 12053.4026
2028/2029 | 2008 | 1 | 18 | 19 | 13222.8118
2028/2029 | 2008 | 1 | 18 | 20 | 14356.7548
2028/2029 | 2008 | 1 | 18 | 21 | 16130.3781
2028/2029 | 2008 | 1 | 18 | 22 | 17405.8212
2028/2029 | 2008 | 1 | 18 | 23 | 18350.2814
2028/2029 | 2008 | 1 | 18 | 24 | 20667.3873
2028/2029 | 2008 | 1 | 19 | 1 | 22182.6046
2028/2029 | 2008 | 1 | 19 | 2 | 22741.2631
2028/2029 | 2008 | 1 | 19 | 3 | 22477.4684
2028/2029 | 2008 | 1 | 19 | 4 | 21349.071
2028/2029 | 2008 | 1 | 19 | 5 | 20885.9955
2028/2029 | 2008 | 1 | 19 | 6 | 20774.3451
2028/2029 | 2008 | 1 | 19 | 7 | 19856.3109
2028/2029 | 2008 | 1 | 19 | 8 | 18415.4444
2028/2029 | 2008 | 1 | 19 | 9 | 14226.7394
2028/2029 | 2008 | 1 | 19 | 10 | 14466.6294
2028/2029 | 2008 | 1 | 19 | 11 | 14465.5488
2028/2029 | 2008 | 1 | 19 | 12 | 13617.0033
2028/2029 | 2008 | 1 | 19 | 13 | 12725.8735
2028/2029 | 2008 | 1 | 19 | 14 | 12366.64
2028/2029 | 2008 | 1 | 19 | 15 | 11691.4248
2028/2029 | 2008 | 1 | 19 | 16 | 10715.4188
2028/2029 | 2008 | 1 | 19 | 17 | 8633.3231
2028/2029 | 2008 | 1 | 19 | 18 | 7890.6203
2028/2029 | 2008 | 1 | 19 | 19 | 9768.2387
2028/2029 | 2008 | 1 | 19 | 20 | 11673.5817
2028/2029 | 2008 | 1 | 19 | 21 | 12486.4507
2028/2029 | 2008 | 1 | 19 | 22 | 15196.9931
2028/2029 | 2008 | 1 | 19 | 23 | 18531.4152
2028/2029 | 2008 | 1 | 19 | 24 | 22223.7902
2028/2029 | 2008 | 1 | 20 | 1 | 25275.7881
2028/2029 | 2008 | 1 | 20 | 2 | 27447.1093
2028/2029 | 2008 | 1 | 20 | 3 | 28414.1382
2028/2029 | 2008 | 1 | 20 | 4 | 28946.9403
2028/2029 | 2008 | 1 | 20 | 5 | 29271.8315
2028/2029 | 2008 | 1 | 20 | 6 | 29330.0389
2028/2029 | 2008 | 1 | 20 | 7 | 29908.5047
2028/2029 | 2008 | 1 | 20 | 8 | 28590.7044
2028/2029 | 2008 | 1 | 20 | 9 | 25533.2563
2028/2029 | 2008 | 1 | 20 | 10 | 24205.5338
2028/2029 | 2008 | 1 | 20 | 11 | 26735.0337
2028/2029 | 2008 | 1 | 20 | 12 | 27979.2569
2028/2029 | 2008 | 1 | 20 | 13 | 30993.0087
2028/2029 | 2008 | 1 | 20 | 14 | 32267.4134
2028/2029 | 2008 | 1 | 20 | 15 | 31413.1129
2028/2029 | 2008 | 1 | 20 | 16 | 32165.5647
2028/2029 | 2008 | 1 | 20 | 17 | 31786.9161
2028/2029 | 2008 | 1 | 20 | 18 | 31973.7497
2028/2029 | 2008 | 1 | 20 | 19 | 32147.4621
2028/2029 | 2008 | 1 | 20 | 20 | 32801.6365
2028/2029 | 2008 | 1 | 20 | 21 | 34251.6338
2028/2029 | 2008 | 1 | 20 | 22 | 35047.6429
2028/2029 | 2008 | 1 | 20 | 23 | 34632.2178
2028/2029 | 2008 | 1 | 20 | 24 | 34445.1936
2028/2029 | 2008 | 1 | 21 | 1 | 33781.3862
2028/2029 | 2008 | 1 | 21 | 2 | 31438.5092
2028/2029 | 2008 | 1 | 21 | 3 | 29594.5994
2028/2029 | 2008 | 1 | 21 | 4 | 30821.2885
2028/2029 | 2008 | 1 | 21 | 5 | 29974.7598
2028/2029 | 2008 | 1 | 21 | 6 | 30373.6609
2028/2029 | 2008 | 1 | 21 | 7 | 30435.9013
2028/2029 | 2008 | 1 | 21 | 8 | 29181.2155
2028/2029 | 2008 | 1 | 21 | 9 | 27062.8726
2028/2029 | 2008 | 1 | 21 | 10 | 28703.9563
2028/2029 | 2008 | 1 | 21 | 11 | 28589.207
2028/2029 | 2008 | 1 | 21 | 12 | 27426.9756
2028/2029 | 2008 | 1 | 21 | 13 | 26335.6612
2028/2029 | 2008 | 1 | 21 | 14 | 26095.9392
2028/2029 | 2008 | 1 | 21 | 15 | 24836.6491
2028/2029 | 2008 | 1 | 21 | 16 | 23538.1606
2028/2029 | 2008 | 1 | 21 | 17 | 21132.0431
2028/2029 | 2008 | 1 | 21 | 18 | 21404.9574
2028/2029 | 2008 | 1 | 21 | 19 | 22352.0864
2028/2029 | 2008 | 1 | 21 | 20 | 23033.3736
2028/2029 | 2008 | 1 | 21 | 21 | 23243.2497
2028/2029 | 2008 | 1 | 21 | 22 | 21693.5356
2028/2029 | 2008 | 1 | 21 | 23 | 20833.2323
2028/2029 | 2008 | 1 | 21 | 24 | 20064.092
2028/2029 | 2008 | 1 | 22 | 1 | 19643.3253
2028/2029 | 2008 | 1 | 22 | 2 | 17916.8465
2028/2029 | 2008 | 1 | 22 | 3 | 15725.1169
2028/2029 | 2008 | 1 | 22 | 4 | 14083.4733
2028/2029 | 2008 | 1 | 22 | 5 | 13669.4171
2028/2029 | 2008 | 1 | 22 | 6 | 14504.5415
2028/2029 | 2008 | 1 | 22 | 7 | 15700.788
2028/2029 | 2008 | 1 | 22 | 8 | 16842.8471
2028/2029 | 2008 | 1 | 22 | 9 | 14328.0043
2028/2029 | 2008 | 1 | 22 | 10 | 14748.012
2028/2029 | 2008 | 1 | 22 | 11 | 14569.8792
2028/2029 | 2008 | 1 | 22 | 12 | 12956.4984
2028/2029 | 2008 | 1 | 22 | 13 | 11003.136
2028/2029 | 2008 | 1 | 22 | 14 | 9063.6413
2028/2029 | 2008 | 1 | 22 | 15 | 7512.4638
2028/2029 | 2008 | 1 | 22 | 16 | 7175.387
2028/2029 | 2008 | 1 | 22 | 17 | 6692.1416
2028/2029 | 2008 | 1 | 22 | 18 | 6749.4108
2028/2029 | 2008 | 1 | 22 | 19 | 6772.3504
2028/2029 | 2008 | 1 | 22 | 20 | 6816.9841
2028/2029 | 2008 | 1 | 22 | 21 | 6668.8927
2028/2029 | 2008 | 1 | 22 | 22 | 6503.3151
2028/2029 | 2008 | 1 | 22 | 23 | 6887.4145
2028/2029 | 2008 | 1 | 22 | 24 | 6966.7523
2028/2029 | 2008 | 1 | 23 | 1 | 8154.7173
2028/2029 | 2008 | 1 | 23 | 2 | 8913.2899
2028/2029 | 2008 | 1 | 23 | 3 | 9353.8633
2028/2029 | 2008 | 1 | 23 | 4 | 9321.728
2028/2029 | 2008 | 1 | 23 | 5 | 9085.6818
2028/2029 | 2008 | 1 | 23 | 6 | 8763.7607
2028/2029 | 2008 | 1 | 23 | 7 | 8283.4029
2028/2029 | 2008 | 1 | 23 | 8 | 7818.9499
2028/2029 | 2008 | 1 | 23 | 9 | 7295.5748
2028/2029 | 2008 | 1 | 23 | 10 | 6708.727
2028/2029 | 2008 | 1 | 23 | 11 | 6747.9672
2028/2029 | 2008 | 1 | 23 | 12 | 6615.1465
2028/2029 | 2008 | 1 | 23 | 13 | 6899.6978
2028/2029 | 2008 | 1 | 23 | 14 | 7033.3011
2028/2029 | 2008 | 1 | 23 | 15 | 7136.3996
2028/2029 | 2008 | 1 | 23 | 16 | 7578.1333
2028/2029 | 2008 | 1 | 23 | 17 | 7422.2821
2028/2029 | 2008 | 1 | 23 | 18 | 8353.0213
2028/2029 | 2008 | 1 | 23 | 19 | 10413.152
2028/2029 | 2008 | 1 | 23 | 20 | 13678.9014
2028/2029 | 2008 | 1 | 23 | 21 | 14851.1289
2028/2029 | 2008 | 1 | 23 | 22 | 16507.3588
2028/2029 | 2008 | 1 | 23 | 23 | 19207.1231
2028/2029 | 2008 | 1 | 23 | 24 | 21319.1593
2028/2029 | 2008 | 1 | 24 | 1 | 23762.3082
2028/2029 | 2008 | 1 | 24 | 2 | 24558.9571
2028/2029 | 2008 | 1 | 24 | 3 | 24907.7803
2028/2029 | 2008 | 1 | 24 | 4 | 23668.0581
2028/2029 | 2008 | 1 | 24 | 5 | 23027.1179
2028/2029 | 2008 | 1 | 24 | 6 | 22558.0293
2028/2029 | 2008 | 1 | 24 | 7 | 20372.3352
2028/2029 | 2008 | 1 | 24 | 8 | 18664.8572
2028/2029 | 2008 | 1 | 24 | 9 | 15903.9323
2028/2029 | 2008 | 1 | 24 | 10 | 17474.3209
2028/2029 | 2008 | 1 | 24 | 11 | 17951.5894
2028/2029 | 2008 | 1 | 24 | 12 | 17011.0625
2028/2029 | 2008 | 1 | 24 | 13 | 16463.2213
2028/2029 | 2008 | 1 | 24 | 14 | 16410.4533
2028/2029 | 2008 | 1 | 24 | 15 | 16336.5898
2028/2029 | 2008 | 1 | 24 | 16 | 15655.6998
2028/2029 | 2008 | 1 | 24 | 17 | 14043.632
2028/2029 | 2008 | 1 | 24 | 18 | 13396.5058
2028/2029 | 2008 | 1 | 24 | 19 | 13801.6702
2028/2029 | 2008 | 1 | 24 | 20 | 13201.9805
2028/2029 | 2008 | 1 | 24 | 21 | 13108.7512
2028/2029 | 2008 | 1 | 24 | 22 | 12704.8519
2028/2029 | 2008 | 1 | 24 | 23 | 11986.9398
2028/2029 | 2008 | 1 | 24 | 24 | 11685.1813
2028/2029 | 2008 | 1 | 25 | 1 | 12225.9662
2028/2029 | 2008 | 1 | 25 | 2 | 12284.8871
2028/2029 | 2008 | 1 | 25 | 3 | 11643.5836
2028/2029 | 2008 | 1 | 25 | 4 | 11860.9979
2028/2029 | 2008 | 1 | 25 | 5 | 12353.2143
2028/2029 | 2008 | 1 | 25 | 6 | 13120.6106
2028/2029 | 2008 | 1 | 25 | 7 | 12459.2051
2028/2029 | 2008 | 1 | 25 | 8 | 11356.4939
2028/2029 | 2008 | 1 | 25 | 9 | 10684.6946
2028/2029 | 2008 | 1 | 25 | 10 | 11799.331
2028/2029 | 2008 | 1 | 25 | 11 | 12425.0293
2028/2029 | 2008 | 1 | 25 | 12 | 12096.3313
2028/2029 | 2008 | 1 | 25 | 13 | 12757.1539
2028/2029 | 2008 | 1 | 25 | 14 | 13278.3062
2028/2029 | 2008 | 1 | 25 | 15 | 13192.0515
2028/2029 | 2008 | 1 | 25 | 16 | 13218.7598
2028/2029 | 2008 | 1 | 25 | 17 | 11479.1174
2028/2029 | 2008 | 1 | 25 | 18 | 12260.7279
2028/2029 | 2008 | 1 | 25 | 19 | 14565.8487
2028/2029 | 2008 | 1 | 25 | 20 | 16799.5661
2028/2029 | 2008 | 1 | 25 | 21 | 18679.3514
2028/2029 | 2008 | 1 | 25 | 22 | 19952.9517
2028/2029 | 2008 | 1 | 25 | 23 | 19481.3141
2028/2029 | 2008 | 1 | 25 | 24 | 19527.239
2028/2029 | 2008 | 1 | 26 | 1 | 19871.3485
2028/2029 | 2008 | 1 | 26 | 2 | 19542.1913
2028/2029 | 2008 | 1 | 26 | 3 | 19514.4938
2028/2029 | 2008 | 1 | 26 | 4 | 18974.6045
2028/2029 | 2008 | 1 | 26 | 5 | 18959.079
2028/2029 | 2008 | 1 | 26 | 6 | 20032.8999
2028/2029 | 2008 | 1 | 26 | 7 | 20673.5045
2028/2029 | 2008 | 1 | 26 | 8 | 20434.4048
2028/2029 | 2008 | 1 | 26 | 9 | 18441.0167
2028/2029 | 2008 | 1 | 26 | 10 | 13582.5497
2028/2029 | 2008 | 1 | 26 | 11 | 9870.0511
2028/2029 | 2008 | 1 | 26 | 12 | 7922.7779
2028/2029 | 2008 | 1 | 26 | 13 | 6675.4621
2028/2029 | 2008 | 1 | 26 | 14 | 4812.6931
2028/2029 | 2008 | 1 | 26 | 15 | 3175.5995
2028/2029 | 2008 | 1 | 26 | 16 | 1819.1599
2028/2029 | 2008 | 1 | 26 | 17 | 1113.1681
2028/2029 | 2008 | 1 | 26 | 18 | 1228.0723
2028/2029 | 2008 | 1 | 26 | 19 | 1573.8073
2028/2029 | 2008 | 1 | 26 | 20 | 2088.2542
2028/2029 | 2008 | 1 | 26 | 21 | 3327.4552
2028/2029 | 2008 | 1 | 26 | 22 | 4528.001
2028/2029 | 2008 | 1 | 26 | 23 | 5594.8154
2028/2029 | 2008 | 1 | 26 | 24 | 7311.1043
2028/2029 | 2008 | 1 | 27 | 1 | 9159.3827
2028/2029 | 2008 | 1 | 27 | 2 | 10100.0676
2028/2029 | 2008 | 1 | 27 | 3 | 10816.7618
2028/2029 | 2008 | 1 | 27 | 4 | 11195.459
2028/2029 | 2008 | 1 | 27 | 5 | 12037.7475
2028/2029 | 2008 | 1 | 27 | 6 | 12360.5034
2028/2029 | 2008 | 1 | 27 | 7 | 14033.2861
2028/2029 | 2008 | 1 | 27 | 8 | 15154.0241
2028/2029 | 2008 | 1 | 27 | 9 | 16115.0742
2028/2029 | 2008 | 1 | 27 | 10 | 15313.723
2028/2029 | 2008 | 1 | 27 | 11 | 12827.7654
2028/2029 | 2008 | 1 | 27 | 12 | 15732.7166
2028/2029 | 2008 | 1 | 27 | 13 | 19551.7242
2028/2029 | 2008 | 1 | 27 | 14 | 22370.5374
2028/2029 | 2008 | 1 | 27 | 15 | 24345.8832
2028/2029 | 2008 | 1 | 27 | 16 | 25738.8407
2028/2029 | 2008 | 1 | 27 | 17 | 26259.7437
2028/2029 | 2008 | 1 | 27 | 18 | 28873.0896
2028/2029 | 2008 | 1 | 27 | 19 | 31023.1185
2028/2029 | 2008 | 1 | 27 | 20 | 32185.8864
2028/2029 | 2008 | 1 | 27 | 21 | 32263.3371
2028/2029 | 2008 | 1 | 27 | 22 | 32772.4885
2028/2029 | 2008 | 1 | 27 | 23 | 32713.6413
2028/2029 | 2008 | 1 | 27 | 24 | 32551.7761
2028/2029 | 2008 | 1 | 28 | 1 | 30621.0073
2028/2029 | 2008 | 1 | 28 | 2 | 29665.6075
2028/2029 | 2008 | 1 | 28 | 3 | 29759.5191
2028/2029 | 2008 | 1 | 28 | 4 | 30056.6022
2028/2029 | 2008 | 1 | 28 | 5 | 31029.4182
2028/2029 | 2008 | 1 | 28 | 6 | 31535.7832
2028/2029 | 2008 | 1 | 28 | 7 | 31727.0463
2028/2029 | 2008 | 1 | 28 | 8 | 33541.8705
2028/2029 | 2008 | 1 | 28 | 9 | 33936.6787
2028/2029 | 2008 | 1 | 28 | 10 | 35272.6234
2028/2029 | 2008 | 1 | 28 | 11 | 35356.9064
2028/2029 | 2008 | 1 | 28 | 12 | 35123.5568
2028/2029 | 2008 | 1 | 28 | 13 | 35373.618
2028/2029 | 2008 | 1 | 28 | 14 | 34787.2201
2028/2029 | 2008 | 1 | 28 | 15 | 34756.9119
2028/2029 | 2008 | 1 | 28 | 16 | 34307.807
2028/2029 | 2008 | 1 | 28 | 17 | 33203.0124
2028/2029 | 2008 | 1 | 28 | 18 | 31938.0874
2028/2029 | 2008 | 1 | 28 | 19 | 33314.1342
2028/2029 | 2008 | 1 | 28 | 20 | 33810.8206
2028/2029 | 2008 | 1 | 28 | 21 | 35078.846
2028/2029 | 2008 | 1 | 28 | 22 | 35375.9735
2028/2029 | 2008 | 1 | 28 | 23 | 35224.4056
2028/2029 | 2008 | 1 | 28 | 24 | 35205.1934
2028/2029 | 2008 | 1 | 29 | 1 | 35976.4673
2028/2029 | 2008 | 1 | 29 | 2 | 35952.4747
2028/2029 | 2008 | 1 | 29 | 3 | 35512.5654
2028/2029 | 2008 | 1 | 29 | 4 | 35350.1229
2028/2029 | 2008 | 1 | 29 | 5 | 34171.0364
2028/2029 | 2008 | 1 | 29 | 6 | 33948.9127
2028/2029 | 2008 | 1 | 29 | 7 | 31041.1381
2028/2029 | 2008 | 1 | 29 | 8 | 29997.6532
2028/2029 | 2008 | 1 | 29 | 9 | 29355.152
2028/2029 | 2008 | 1 | 29 | 10 | 28184.4877
2028/2029 | 2008 | 1 | 29 | 11 | 26686.7799
2028/2029 | 2008 | 1 | 29 | 12 | 27799.2606
2028/2029 | 2008 | 1 | 29 | 13 | 29716.3194
2028/2029 | 2008 | 1 | 29 | 14 | 29773.9728
2028/2029 | 2008 | 1 | 29 | 15 | 28159.0335
2028/2029 | 2008 | 1 | 29 | 16 | 23813.4499
2028/2029 | 2008 | 1 | 29 | 17 | 17056.5735
2028/2029 | 2008 | 1 | 29 | 18 | 13055.5129
2028/2029 | 2008 | 1 | 29 | 19 | 13019.6285
2028/2029 | 2008 | 1 | 29 | 20 | 14165.1097
2028/2029 | 2008 | 1 | 29 | 21 | 17713.066
2028/2029 | 2008 | 1 | 29 | 22 | 22906.224
2028/2029 | 2008 | 1 | 29 | 23 | 28080.5975
2028/2029 | 2008 | 1 | 29 | 24 | 31296.3446
2028/2029 | 2008 | 1 | 30 | 1 | 33133.3089
2028/2029 | 2008 | 1 | 30 | 2 | 33264.6479
2028/2029 | 2008 | 1 | 30 | 3 | 33816.9218
2028/2029 | 2008 | 1 | 30 | 4 | 32655.2249
2028/2029 | 2008 | 1 | 30 | 5 | 32442.9933
2028/2029 | 2008 | 1 | 30 | 6 | 31965.4876
2028/2029 | 2008 | 1 | 30 | 7 | 31284.2184
2028/2029 | 2008 | 1 | 30 | 8 | 30291.2449
2028/2029 | 2008 | 1 | 30 | 9 | 28367.3106
2028/2029 | 2008 | 1 | 30 | 10 | 28669.113
2028/2029 | 2008 | 1 | 30 | 11 | 29669.9223
2028/2029 | 2008 | 1 | 30 | 12 | 30834.2518
2028/2029 | 2008 | 1 | 30 | 13 | 31278.9053
2028/2029 | 2008 | 1 | 30 | 14 | 30864.3392
2028/2029 | 2008 | 1 | 30 | 15 | 29783.5426
2028/2029 | 2008 | 1 | 30 | 16 | 29707.8976
2028/2029 | 2008 | 1 | 30 | 17 | 29228.8791
2028/2029 | 2008 | 1 | 30 | 18 | 27889.179
2028/2029 | 2008 | 1 | 30 | 19 | 29028.8128
2028/2029 | 2008 | 1 | 30 | 20 | 29732.0894
2028/2029 | 2008 | 1 | 30 | 21 | 29746.5078
2028/2029 | 2008 | 1 | 30 | 22 | 29405.2908
2028/2029 | 2008 | 1 | 30 | 23 | 28095.4332
2028/2029 | 2008 | 1 | 30 | 24 | 27941.7462
2028/2029 | 2008 | 1 | 31 | 1 | 29721.3949
2028/2029 | 2008 | 1 | 31 | 2 | 28507.7662
2028/2029 | 2008 | 1 | 31 | 3 | 27141.8998
2028/2029 | 2008 | 1 | 31 | 4 | 27100.9925
2028/2029 | 2008 | 1 | 31 | 5 | 27761.835
2028/2029 | 2008 | 1 | 31 | 6 | 28832.3529
2028/2029 | 2008 | 1 | 31 | 7 | 30912.4491
2028/2029 | 2008 | 1 | 31 | 8 | 32860.6002
2028/2029 | 2008 | 1 | 31 | 9 | 32509.7129
2028/2029 | 2008 | 1 | 31 | 10 | 31983.9957
2028/2029 | 2008 | 1 | 31 | 11 | 32727.2553
2028/2029 | 2008 | 1 | 31 | 12 | 33327.6287
2028/2029 | 2008 | 1 | 31 | 13 | 35153.349
2028/2029 | 2008 | 1 | 31 | 14 | 35159.3518
2028/2029 | 2008 | 1 | 31 | 15 | 34383.0469
2028/2029 | 2008 | 1 | 31 | 16 | 35163.6634
2028/2029 | 2008 | 1 | 31 | 17 | 29652.6643
2028/2029 | 2008 | 1 | 31 | 18 | 30167.032
2028/2029 | 2008 | 1 | 31 | 19 | 26090.233
2028/2029 | 2008 | 1 | 31 | 20 | 22090.1554
2028/2029 | 2008 | 1 | 31 | 21 | 16261.9995
2028/2029 | 2008 | 1 | 31 | 22 | 12839.3055
2028/2029 | 2008 | 1 | 31 | 23 | 12330.2714
2028/2029 | 2008 | 1 | 31 | 24 | 13089.2374
2029/2030 | 2008 | 1 | 1 | 1 | 25186.4182
2029/2030 | 2008 | 1 | 1 | 2 | 24852.8639
2029/2030 | 2008 | 1 | 1 | 3 | 23776.839
2029/2030 | 2008 | 1 | 1 | 4 | 22401.0651
2029/2030 | 2008 | 1 | 1 | 5 | 21268.7
2029/2030 | 2008 | 1 | 1 | 6 | 20449.8325
2029/2030 | 2008 | 1 | 1 | 7 | 19423.6818
2029/2030 | 2008 | 1 | 1 | 8 | 17640.6616
2029/2030 | 2008 | 1 | 1 | 9 | 15739.4869
2029/2030 | 2008 | 1 | 1 | 10 | 13184.7141
2029/2030 | 2008 | 1 | 1 | 11 | 15454.3749
2029/2030 | 2008 | 1 | 1 | 12 | 17236.783
2029/2030 | 2008 | 1 | 1 | 13 | 17053.2697
2029/2030 | 2008 | 1 | 1 | 14 | 15400.6393
2029/2030 | 2008 | 1 | 1 | 15 | 15279.373
2029/2030 | 2008 | 1 | 1 | 16 | 14725.0933
2029/2030 | 2008 | 1 | 1 | 17 | 11716.6241
2029/2030 | 2008 | 1 | 1 | 18 | 11693.7185
2029/2030 | 2008 | 1 | 1 | 19 | 11570.0593
2029/2030 | 2008 | 1 | 1 | 20 | 12467.876
2029/2030 | 2008 | 1 | 1 | 21 | 12224.0939
2029/2030 | 2008 | 1 | 1 | 22 | 10863.5686
2029/2030 | 2008 | 1 | 1 | 23 | 10192.5145
2029/2030 | 2008 | 1 | 1 | 24 | 10322.1604
2029/2030 | 2008 | 1 | 2 | 1 | 10601.7513
2029/2030 | 2008 | 1 | 2 | 2 | 11273.9444
2029/2030 | 2008 | 1 | 2 | 3 | 10578.5008
2029/2030 | 2008 | 1 | 2 | 4 | 11490.9691
2029/2030 | 2008 | 1 | 2 | 5 | 11796.7524
2029/2030 | 2008 | 1 | 2 | 6 | 12075.9362
2029/2030 | 2008 | 1 | 2 | 7 | 12260.0064
2029/2030 | 2008 | 1 | 2 | 8 | 11749.4356
2029/2030 | 2008 | 1 | 2 | 9 | 9614.0373
2029/2030 | 2008 | 1 | 2 | 10 | 9380.8958
2029/2030 | 2008 | 1 | 2 | 11 | 10893.586
2029/2030 | 2008 | 1 | 2 | 12 | 11934.9132
2029/2030 | 2008 | 1 | 2 | 13 | 12155.8055
2029/2030 | 2008 | 1 | 2 | 14 | 11938.2056
2029/2030 | 2008 | 1 | 2 | 15 | 12047.6322
2029/2030 | 2008 | 1 | 2 | 16 | 11241.446
2029/2030 | 2008 | 1 | 2 | 17 | 10242.1199
2029/2030 | 2008 | 1 | 2 | 18 | 10979.489
2029/2030 | 2008 | 1 | 2 | 19 | 13622.3208
2029/2030 | 2008 | 1 | 2 | 20 | 16441.2827
2029/2030 | 2008 | 1 | 2 | 21 | 19023.4165
2029/2030 | 2008 | 1 | 2 | 22 | 21269.9026
2029/2030 | 2008 | 1 | 2 | 23 | 22286.529
2029/2030 | 2008 | 1 | 2 | 24 | 22819.97
2029/2030 | 2008 | 1 | 3 | 1 | 24203.7422
2029/2030 | 2008 | 1 | 3 | 2 | 25092.8325
2029/2030 | 2008 | 1 | 3 | 3 | 25611.1907
2029/2030 | 2008 | 1 | 3 | 4 | 26579.3803
2029/2030 | 2008 | 1 | 3 | 5 | 27904.9419
2029/2030 | 2008 | 1 | 3 | 6 | 29753.3481
2029/2030 | 2008 | 1 | 3 | 7 | 30060.1124
2029/2030 | 2008 | 1 | 3 | 8 | 28686.7987
2029/2030 | 2008 | 1 | 3 | 9 | 26569.8752
2029/2030 | 2008 | 1 | 3 | 10 | 27580.5149
2029/2030 | 2008 | 1 | 3 | 11 | 28066.5202
2029/2030 | 2008 | 1 | 3 | 12 | 28646.5292
2029/2030 | 2008 | 1 | 3 | 13 | 29213.0167
2029/2030 | 2008 | 1 | 3 | 14 | 29873.3726
2029/2030 | 2008 | 1 | 3 | 15 | 31019.6762
2029/2030 | 2008 | 1 | 3 | 16 | 32067.941
2029/2030 | 2008 | 1 | 3 | 17 | 31720.0375
2029/2030 | 2008 | 1 | 3 | 18 | 30928.1695
2029/2030 | 2008 | 1 | 3 | 19 | 31700.1204
2029/2030 | 2008 | 1 | 3 | 20 | 31784.6524
2029/2030 | 2008 | 1 | 3 | 21 | 32804.1214
2029/2030 | 2008 | 1 | 3 | 22 | 33275.1143
2029/2030 | 2008 | 1 | 3 | 23 | 33562.9441
2029/2030 | 2008 | 1 | 3 | 24 | 33548.1484
2029/2030 | 2008 | 1 | 4 | 1 | 33091.847
2029/2030 | 2008 | 1 | 4 | 2 | 32701.0405
2029/2030 | 2008 | 1 | 4 | 3 | 34047.4574
2029/2030 | 2008 | 1 | 4 | 4 | 33630.3531
2029/2030 | 2008 | 1 | 4 | 5 | 33236.0796
2029/2030 | 2008 | 1 | 4 | 6 | 32816.2649
2029/2030 | 2008 | 1 | 4 | 7 | 32323.3015
2029/2030 | 2008 | 1 | 4 | 8 | 30526.813
2029/2030 | 2008 | 1 | 4 | 9 | 29896.1788
2029/2030 | 2008 | 1 | 4 | 10 | 29740.9453
2029/2030 | 2008 | 1 | 4 | 11 | 30777.4599
2029/2030 | 2008 | 1 | 4 | 12 | 31454.2141
2029/2030 | 2008 | 1 | 4 | 13 | 32986.5863
2029/2030 | 2008 | 1 | 4 | 14 | 34003.4729
2029/2030 | 2008 | 1 | 4 | 15 | 34068.8768
2029/2030 | 2008 | 1 | 4 | 16 | 35085.856
2029/2030 | 2008 | 1 | 4 | 17 | 34549.7581
2029/2030 | 2008 | 1 | 4 | 18 | 34241.3705
2029/2030 | 2008 | 1 | 4 | 19 | 35526.7579
2029/2030 | 2008 | 1 | 4 | 20 | 35925.8786
2029/2030 | 2008 | 1 | 4 | 21 | 36299.8476
2029/2030 | 2008 | 1 | 4 | 22 | 36606.1118
2029/2030 | 2008 | 1 | 4 | 23 | 36567.5009
2029/2030 | 2008 | 1 | 4 | 24 | 37090.8474
2029/2030 | 2008 | 1 | 5 | 1 | 37088.7335
2029/2030 | 2008 | 1 | 5 | 2 | 36846.6769
2029/2030 | 2008 | 1 | 5 | 3 | 35506.7884
2029/2030 | 2008 | 1 | 5 | 4 | 34578.9598
2029/2030 | 2008 | 1 | 5 | 5 | 34199.5351
2029/2030 | 2008 | 1 | 5 | 6 | 33901.0789
2029/2030 | 2008 | 1 | 5 | 7 | 33861.6772
2029/2030 | 2008 | 1 | 5 | 8 | 33073.8629
2029/2030 | 2008 | 1 | 5 | 9 | 31146.7731
2029/2030 | 2008 | 1 | 5 | 10 | 30353.1983
2029/2030 | 2008 | 1 | 5 | 11 | 31046.3013
2029/2030 | 2008 | 1 | 5 | 12 | 33270.2801
2029/2030 | 2008 | 1 | 5 | 13 | 34931.3837
2029/2030 | 2008 | 1 | 5 | 14 | 35548.1902
2029/2030 | 2008 | 1 | 5 | 15 | 35913.8748
2029/2030 | 2008 | 1 | 5 | 16 | 35417.6498
2029/2030 | 2008 | 1 | 5 | 17 | 32544.4513
2029/2030 | 2008 | 1 | 5 | 18 | 32812.3123
2029/2030 | 2008 | 1 | 5 | 19 | 34651.7829
2029/2030 | 2008 | 1 | 5 | 20 | 35105.7235
2029/2030 | 2008 | 1 | 5 | 21 | 34992.616
2029/2030 | 2008 | 1 | 5 | 22 | 35202.9393
2029/2030 | 2008 | 1 | 5 | 23 | 35310.8647
2029/2030 | 2008 | 1 | 5 | 24 | 35390.0228
2029/2030 | 2008 | 1 | 6 | 1 | 35420.2722
2029/2030 | 2008 | 1 | 6 | 2 | 35185.1174
2029/2030 | 2008 | 1 | 6 | 3 | 34999.1678
2029/2030 | 2008 | 1 | 6 | 4 | 34766.0419
2029/2030 | 2008 | 1 | 6 | 5 | 34134.5147
2029/2030 | 2008 | 1 | 6 | 6 | 33919.6254
2029/2030 | 2008 | 1 | 6 | 7 | 33466.4948
2029/2030 | 2008 | 1 | 6 | 8 | 31199.0989
2029/2030 | 2008 | 1 | 6 | 9 | 29342.5803
2029/2030 | 2008 | 1 | 6 | 10 | 30617.611
2029/2030 | 2008 | 1 | 6 | 11 | 31021.9087
2029/2030 | 2008 | 1 | 6 | 12 | 31957.3858
2029/2030 | 2008 | 1 | 6 | 13 | 32350.3608
2029/2030 | 2008 | 1 | 6 | 14 | 31798.9769
2029/2030 | 2008 | 1 | 6 | 15 | 31366.9045
2029/2030 | 2008 | 1 | 6 | 16 | 30080.6252
2029/2030 | 2008 | 1 | 6 | 17 | 28010.7912
2029/2030 | 2008 | 1 | 6 | 18 | 29281.0111
2029/2030 | 2008 | 1 | 6 | 19 | 31627.0456
2029/2030 | 2008 | 1 | 6 | 20 | 32367.1038
2029/2030 | 2008 | 1 | 6 | 21 | 32307.5423
2029/2030 | 2008 | 1 | 6 | 22 | 33124.5108
2029/2030 | 2008 | 1 | 6 | 23 | 33018.9897
2029/2030 | 2008 | 1 | 6 | 24 | 34223.4965
2029/2030 | 2008 | 1 | 7 | 1 | 33739.1577
2029/2030 | 2008 | 1 | 7 | 2 | 32868.9738
2029/2030 | 2008 | 1 | 7 | 3 | 32241.3281
2029/2030 | 2008 | 1 | 7 | 4 | 31185.779
2029/2030 | 2008 | 1 | 7 | 5 | 30936.8805
2029/2030 | 2008 | 1 | 7 | 6 | 30503.34
2029/2030 | 2008 | 1 | 7 | 7 | 29959.6828
2029/2030 | 2008 | 1 | 7 | 8 | 27761.5049
2029/2030 | 2008 | 1 | 7 | 9 | 24942.1195
2029/2030 | 2008 | 1 | 7 | 10 | 24859.0043
2029/2030 | 2008 | 1 | 7 | 11 | 24844.8694
2029/2030 | 2008 | 1 | 7 | 12 | 24732.6062
2029/2030 | 2008 | 1 | 7 | 13 | 24783.335
2029/2030 | 2008 | 1 | 7 | 14 | 24484.1134
2029/2030 | 2008 | 1 | 7 | 15 | 24514.1894
2029/2030 | 2008 | 1 | 7 | 16 | 23841.0549
2029/2030 | 2008 | 1 | 7 | 17 | 22459.8573
2029/2030 | 2008 | 1 | 7 | 18 | 24960.7097
2029/2030 | 2008 | 1 | 7 | 19 | 27253.5983
2029/2030 | 2008 | 1 | 7 | 20 | 28322.6198
2029/2030 | 2008 | 1 | 7 | 21 | 28508.8514
2029/2030 | 2008 | 1 | 7 | 22 | 29274.6296
2029/2030 | 2008 | 1 | 7 | 23 | 29932.5355
2029/2030 | 2008 | 1 | 7 | 24 | 30151.4887
2029/2030 | 2008 | 1 | 8 | 1 | 32161.434
2029/2030 | 2008 | 1 | 8 | 2 | 34556.676
2029/2030 | 2008 | 1 | 8 | 3 | 35214.2047
2029/2030 | 2008 | 1 | 8 | 4 | 34706.6252
2029/2030 | 2008 | 1 | 8 | 5 | 33604.7596
2029/2030 | 2008 | 1 | 8 | 6 | 29161.903
2029/2030 | 2008 | 1 | 8 | 7 | 31360.2656
2029/2030 | 2008 | 1 | 8 | 8 | 29994.7078
2029/2030 | 2008 | 1 | 8 | 9 | 27802.7593
2029/2030 | 2008 | 1 | 8 | 10 | 29078.3945
2029/2030 | 2008 | 1 | 8 | 11 | 30557.2986
2029/2030 | 2008 | 1 | 8 | 12 | 30253.9604
2029/2030 | 2008 | 1 | 8 | 13 | 28007.7972
2029/2030 | 2008 | 1 | 8 | 14 | 24620.2842
2029/2030 | 2008 | 1 | 8 | 15 | 21544.2538
2029/2030 | 2008 | 1 | 8 | 16 | 18260.1387
2029/2030 | 2008 | 1 | 8 | 17 | 12451.6798
2029/2030 | 2008 | 1 | 8 | 18 | 10222.9786
2029/2030 | 2008 | 1 | 8 | 19 | 9719.8399
2029/2030 | 2008 | 1 | 8 | 20 | 9246.3214
2029/2030 | 2008 | 1 | 8 | 21 | 9353.5804
2029/2030 | 2008 | 1 | 8 | 22 | 9744.8361
2029/2030 | 2008 | 1 | 8 | 23 | 10706.9046
2029/2030 | 2008 | 1 | 8 | 24 | 11989.2718
2029/2030 | 2008 | 1 | 9 | 1 | 15077.1484
2029/2030 | 2008 | 1 | 9 | 2 | 18279.5514
2029/2030 | 2008 | 1 | 9 | 3 | 22015.5885
2029/2030 | 2008 | 1 | 9 | 4 | 23687.8163
2029/2030 | 2008 | 1 | 9 | 5 | 24385.0107
2029/2030 | 2008 | 1 | 9 | 6 | 25116.1804
2029/2030 | 2008 | 1 | 9 | 7 | 25270.3327
2029/2030 | 2008 | 1 | 9 | 8 | 24620.838
2029/2030 | 2008 | 1 | 9 | 9 | 22815.3787
2029/2030 | 2008 | 1 | 9 | 10 | 18280.6063
2029/2030 | 2008 | 1 | 9 | 11 | 21977.9757
2029/2030 | 2008 | 1 | 9 | 12 | 23896.9155
2029/2030 | 2008 | 1 | 9 | 13 | 22355.2014
2029/2030 | 2008 | 1 | 9 | 14 | 23333.4578
2029/2030 | 2008 | 1 | 9 | 15 | 23765.0728
2029/2030 | 2008 | 1 | 9 | 16 | 23549.5528
2029/2030 | 2008 | 1 | 9 | 17 | 22276.1826
2029/2030 | 2008 | 1 | 9 | 18 | 24404.9494
2029/2030 | 2008 | 1 | 9 | 19 | 27015.977
2029/2030 | 2008 | 1 | 9 | 20 | 27953.8801
2029/2030 | 2008 | 1 | 9 | 21 | 28319.4096
2029/2030 | 2008 | 1 | 9 | 22 | 30739.0785
2029/2030 | 2008 | 1 | 9 | 23 | 30568.4329
2029/2030 | 2008 | 1 | 9 | 24 | 29725.6661
2029/2030 | 2008 | 1 | 10 | 1 | 28306.7712
2029/2030 | 2008 | 1 | 10 | 2 | 27599.2581
2029/2030 | 2008 | 1 | 10 | 3 | 28501.0801
2029/2030 | 2008 | 1 | 10 | 4 | 29230.3464
2029/2030 | 2008 | 1 | 10 | 5 | 28665.4639
2029/2030 | 2008 | 1 | 10 | 6 | 28558.5638
2029/2030 | 2008 | 1 | 10 | 7 | 28230.0407
2029/2030 | 2008 | 1 | 10 | 8 | 27106.5062
2029/2030 | 2008 | 1 | 10 | 9 | 23738.4536
2029/2030 | 2008 | 1 | 10 | 10 | 21519.7336
2029/2030 | 2008 | 1 | 10 | 11 | 23353.0958
2029/2030 | 2008 | 1 | 10 | 12 | 23937.8704
2029/2030 | 2008 | 1 | 10 | 13 | 22381.2463
2029/2030 | 2008 | 1 | 10 | 14 | 20377.2017
2029/2030 | 2008 | 1 | 10 | 15 | 18137.0519
2029/2030 | 2008 | 1 | 10 | 16 | 15121.6493
2029/2030 | 2008 | 1 | 10 | 17 | 10451.8734
2029/2030 | 2008 | 1 | 10 | 18 | 7865.2717
2029/2030 | 2008 | 1 | 10 | 19 | 7233.576
2029/2030 | 2008 | 1 | 10 | 20 | 6829.3932
2029/2030 | 2008 | 1 | 10 | 21 | 7468.3913
2029/2030 | 2008 | 1 | 10 | 22 | 8179.0405
2029/2030 | 2008 | 1 | 10 | 23 | 9745.8992
2029/2030 | 2008 | 1 | 10 | 24 | 11847.6578
2029/2030 | 2008 | 1 | 11 | 1 | 14483.6289
2029/2030 | 2008 | 1 | 11 | 2 | 16185.4427
2029/2030 | 2008 | 1 | 11 | 3 | 18694.5282
2029/2030 | 2008 | 1 | 11 | 4 | 20505.0441
2029/2030 | 2008 | 1 | 11 | 5 | 22041.2336
2029/2030 | 2008 | 1 | 11 | 6 | 22621.8539
2029/2030 | 2008 | 1 | 11 | 7 | 22563.5058
2029/2030 | 2008 | 1 | 11 | 8 | 21504.9346
2029/2030 | 2008 | 1 | 11 | 9 | 17706.821
2029/2030 | 2008 | 1 | 11 | 10 | 11427.2079
2029/2030 | 2008 | 1 | 11 | 11 | 10132.1429
2029/2030 | 2008 | 1 | 11 | 12 | 11143.454
2029/2030 | 2008 | 1 | 11 | 13 | 10961.3063
2029/2030 | 2008 | 1 | 11 | 14 | 10847.9532
2029/2030 | 2008 | 1 | 11 | 15 | 10540.8701
2029/2030 | 2008 | 1 | 11 | 16 | 9315.4228
2029/2030 | 2008 | 1 | 11 | 17 | 7381.6255
2029/2030 | 2008 | 1 | 11 | 18 | 7457.2602
2029/2030 | 2008 | 1 | 11 | 19 | 9752.8664
2029/2030 | 2008 | 1 | 11 | 20 | 11625.6702
2029/2030 | 2008 | 1 | 11 | 21 | 13942.1136
2029/2030 | 2008 | 1 | 11 | 22 | 15735.4328
2029/2030 | 2008 | 1 | 11 | 23 | 16773.4981
2029/2030 | 2008 | 1 | 11 | 24 | 18726.7919
2029/2030 | 2008 | 1 | 12 | 1 | 20858.4118
2029/2030 | 2008 | 1 | 12 | 2 | 21473.3559
2029/2030 | 2008 | 1 | 12 | 3 | 22153.5426
2029/2030 | 2008 | 1 | 12 | 4 | 23906.203
2029/2030 | 2008 | 1 | 12 | 5 | 24578.0917
2029/2030 | 2008 | 1 | 12 | 6 | 25046.4914
2029/2030 | 2008 | 1 | 12 | 7 | 26328.1693
2029/2030 | 2008 | 1 | 12 | 8 | 25946.4819
2029/2030 | 2008 | 1 | 12 | 9 | 22085.66
2029/2030 | 2008 | 1 | 12 | 10 | 18128.4872
2029/2030 | 2008 | 1 | 12 | 11 | 18955.7958
2029/2030 | 2008 | 1 | 12 | 12 | 18060.1726
2029/2030 | 2008 | 1 | 12 | 13 | 18468.929
2029/2030 | 2008 | 1 | 12 | 14 | 19286.8467
2029/2030 | 2008 | 1 | 12 | 15 | 19248.2585
2029/2030 | 2008 | 1 | 12 | 16 | 18275.3864
2029/2030 | 2008 | 1 | 12 | 17 | 14119.1261
2029/2030 | 2008 | 1 | 12 | 18 | 11774.3002
2029/2030 | 2008 | 1 | 12 | 19 | 11998.3999
2029/2030 | 2008 | 1 | 12 | 20 | 11550.5976
2029/2030 | 2008 | 1 | 12 | 21 | 11854.6021
2029/2030 | 2008 | 1 | 12 | 22 | 11773.7712
2029/2030 | 2008 | 1 | 12 | 23 | 11293.5403
2029/2030 | 2008 | 1 | 12 | 24 | 11327.6807
2029/2030 | 2008 | 1 | 13 | 1 | 12042.1774
2029/2030 | 2008 | 1 | 13 | 2 | 12226.9444
2029/2030 | 2008 | 1 | 13 | 3 | 12161.309
2029/2030 | 2008 | 1 | 13 | 4 | 11829.8
2029/2030 | 2008 | 1 | 13 | 5 | 11682.7148
2029/2030 | 2008 | 1 | 13 | 6 | 11661.5425
2029/2030 | 2008 | 1 | 13 | 7 | 11343.221
2029/2030 | 2008 | 1 | 13 | 8 | 10603.9081
2029/2030 | 2008 | 1 | 13 | 9 | 7346.0141
2029/2030 | 2008 | 1 | 13 | 10 | 4921.627
2029/2030 | 2008 | 1 | 13 | 11 | 4686.0526
2029/2030 | 2008 | 1 | 13 | 12 | 4355.6914
2029/2030 | 2008 | 1 | 13 | 13 | 4333.5442
2029/2030 | 2008 | 1 | 13 | 14 | 4985.2288
2029/2030 | 2008 | 1 | 13 | 15 | 5737.6306
2029/2030 | 2008 | 1 | 13 | 16 | 6338.5974
2029/2030 | 2008 | 1 | 13 | 17 | 6411.1
2029/2030 | 2008 | 1 | 13 | 18 | 7489.7319
2029/2030 | 2008 | 1 | 13 | 19 | 9834.0997
2029/2030 | 2008 | 1 | 13 | 20 | 12617.9417
2029/2030 | 2008 | 1 | 13 | 21 | 14492.4528
2029/2030 | 2008 | 1 | 13 | 22 | 16012.548
2029/2030 | 2008 | 1 | 13 | 23 | 17333.0805
2029/2030 | 2008 | 1 | 13 | 24 | 18992.5043
2029/2030 | 2008 | 1 | 14 | 1 | 18513.3084
2029/2030 | 2008 | 1 | 14 | 2 | 17002.1778
2029/2030 | 2008 | 1 | 14 | 3 | 15632.1042
2029/2030 | 2008 | 1 | 14 | 4 | 13845.972
2029/2030 | 2008 | 1 | 14 | 5 | 12271.6442
2029/2030 | 2008 | 1 | 14 | 6 | 11536.918
2029/2030 | 2008 | 1 | 14 | 7 | 10525.183
2029/2030 | 2008 | 1 | 14 | 8 | 9537.2203
2029/2030 | 2008 | 1 | 14 | 9 | 8141.4991
2029/2030 | 2008 | 1 | 14 | 10 | 7350.7373
2029/2030 | 2008 | 1 | 14 | 11 | 7829.5902
2029/2030 | 2008 | 1 | 14 | 12 | 8583.7017
2029/2030 | 2008 | 1 | 14 | 13 | 8775.3744
2029/2030 | 2008 | 1 | 14 | 14 | 9035.3829
2029/2030 | 2008 | 1 | 14 | 15 | 9112.0691
2029/2030 | 2008 | 1 | 14 | 16 | 8785.0622
2029/2030 | 2008 | 1 | 14 | 17 | 8078.8614
2029/2030 | 2008 | 1 | 14 | 18 | 7847.7848
2029/2030 | 2008 | 1 | 14 | 19 | 7991.8904
2029/2030 | 2008 | 1 | 14 | 20 | 8146.8428
2029/2030 | 2008 | 1 | 14 | 21 | 8192.6117
2029/2030 | 2008 | 1 | 14 | 22 | 8378.4217
2029/2030 | 2008 | 1 | 14 | 23 | 9078.7948
2029/2030 | 2008 | 1 | 14 | 24 | 9918.4899
2029/2030 | 2008 | 1 | 15 | 1 | 10928.1148
2029/2030 | 2008 | 1 | 15 | 2 | 11897.4524
2029/2030 | 2008 | 1 | 15 | 3 | 13819.6029
2029/2030 | 2008 | 1 | 15 | 4 | 15458.8543
2029/2030 | 2008 | 1 | 15 | 5 | 17821.6172
2029/2030 | 2008 | 1 | 15 | 6 | 19431.7121
2029/2030 | 2008 | 1 | 15 | 7 | 21287.1221
2029/2030 | 2008 | 1 | 15 | 8 | 22376.0109
2029/2030 | 2008 | 1 | 15 | 9 | 21915.8825
2029/2030 | 2008 | 1 | 15 | 10 | 21175.9962
2029/2030 | 2008 | 1 | 15 | 11 | 23597.1141
2029/2030 | 2008 | 1 | 15 | 12 | 27677.266
2029/2030 | 2008 | 1 | 15 | 13 | 30013.7285
2029/2030 | 2008 | 1 | 15 | 14 | 30733.7864
2029/2030 | 2008 | 1 | 15 | 15 | 30999.0137
2029/2030 | 2008 | 1 | 15 | 16 | 31554.8131
2029/2030 | 2008 | 1 | 15 | 17 | 31341.1794
2029/2030 | 2008 | 1 | 15 | 18 | 31415.528
2029/2030 | 2008 | 1 | 15 | 19 | 32952.5224
2029/2030 | 2008 | 1 | 15 | 20 | 32927.3297
2029/2030 | 2008 | 1 | 15 | 21 | 33488.6415
2029/2030 | 2008 | 1 | 15 | 22 | 33959.2043
2029/2030 | 2008 | 1 | 15 | 23 | 33685.4911
2029/2030 | 2008 | 1 | 15 | 24 | 33444.0221
2029/2030 | 2008 | 1 | 16 | 1 | 33467.817
2029/2030 | 2008 | 1 | 16 | 2 | 32925.1186
2029/2030 | 2008 | 1 | 16 | 3 | 32992.4453
2029/2030 | 2008 | 1 | 16 | 4 | 32731.3329
2029/2030 | 2008 | 1 | 16 | 5 | 30591.3694
2029/2030 | 2008 | 1 | 16 | 6 | 28305.519
2029/2030 | 2008 | 1 | 16 | 7 | 26815.2808
2029/2030 | 2008 | 1 | 16 | 8 | 24262.9697
2029/2030 | 2008 | 1 | 16 | 9 | 19978.5941
2029/2030 | 2008 | 1 | 16 | 10 | 18982.251
2029/2030 | 2008 | 1 | 16 | 11 | 18035.8308
2029/2030 | 2008 | 1 | 16 | 12 | 19017.668
2029/2030 | 2008 | 1 | 16 | 13 | 17968.5054
2029/2030 | 2008 | 1 | 16 | 14 | 16874.749
2029/2030 | 2008 | 1 | 16 | 15 | 17439.9548
2029/2030 | 2008 | 1 | 16 | 16 | 17349.093
2029/2030 | 2008 | 1 | 16 | 17 | 17326.1888
2029/2030 | 2008 | 1 | 16 | 18 | 18750.7444
2029/2030 | 2008 | 1 | 16 | 19 | 21570.0608
2029/2030 | 2008 | 1 | 16 | 20 | 23605.8555
2029/2030 | 2008 | 1 | 16 | 21 | 24087.0204
2029/2030 | 2008 | 1 | 16 | 22 | 23927.4998
2029/2030 | 2008 | 1 | 16 | 23 | 25006.8361
2029/2030 | 2008 | 1 | 16 | 24 | 24591.4231
2029/2030 | 2008 | 1 | 17 | 1 | 24008.1487
2029/2030 | 2008 | 1 | 17 | 2 | 23258.2003
2029/2030 | 2008 | 1 | 17 | 3 | 23398.2748
2029/2030 | 2008 | 1 | 17 | 4 | 22152.8868
2029/2030 | 2008 | 1 | 17 | 5 | 21112.6049
2029/2030 | 2008 | 1 | 17 | 6 | 20004.4487
2029/2030 | 2008 | 1 | 17 | 7 | 18062.5487
2029/2030 | 2008 | 1 | 17 | 8 | 15957.0348
2029/2030 | 2008 | 1 | 17 | 9 | 12966.555
2029/2030 | 2008 | 1 | 17 | 10 | 14108.1765
2029/2030 | 2008 | 1 | 17 | 11 | 13387.576
2029/2030 | 2008 | 1 | 17 | 12 | 11513.7042
2029/2030 | 2008 | 1 | 17 | 13 | 11018.8014
2029/2030 | 2008 | 1 | 17 | 14 | 10345.101
2029/2030 | 2008 | 1 | 17 | 15 | 9541.0831
2029/2030 | 2008 | 1 | 17 | 16 | 8705.3127
2029/2030 | 2008 | 1 | 17 | 17 | 7192.458
2029/2030 | 2008 | 1 | 17 | 18 | 5618.9308
2029/2030 | 2008 | 1 | 17 | 19 | 5882.2509
2029/2030 | 2008 | 1 | 17 | 20 | 6813.1314
2029/2030 | 2008 | 1 | 17 | 21 | 8138.4518
2029/2030 | 2008 | 1 | 17 | 22 | 9187.6459
2029/2030 | 2008 | 1 | 17 | 23 | 9914.0465
2029/2030 | 2008 | 1 | 17 | 24 | 10318.7888
2029/2030 | 2008 | 1 | 18 | 1 | 11391.9736
2029/2030 | 2008 | 1 | 18 | 2 | 12020.0772
2029/2030 | 2008 | 1 | 18 | 3 | 12461.706
2029/2030 | 2008 | 1 | 18 | 4 | 12366.1154
2029/2030 | 2008 | 1 | 18 | 5 | 11714.9847
2029/2030 | 2008 | 1 | 18 | 6 | 11343.4195
2029/2030 | 2008 | 1 | 18 | 7 | 10390.541
2029/2030 | 2008 | 1 | 18 | 8 | 9173.1258
2029/2030 | 2008 | 1 | 18 | 9 | 9204.1884
2029/2030 | 2008 | 1 | 18 | 10 | 9296.1791
2029/2030 | 2008 | 1 | 18 | 11 | 10005.0431
2029/2030 | 2008 | 1 | 18 | 12 | 10430.078
2029/2030 | 2008 | 1 | 18 | 13 | 11264.8494
2029/2030 | 2008 | 1 | 18 | 14 | 11398.4162
2029/2030 | 2008 | 1 | 18 | 15 | 11437.6046
2029/2030 | 2008 | 1 | 18 | 16 | 11375.9872
2029/2030 | 2008 | 1 | 18 | 17 | 11170.6055
2029/2030 | 2008 | 1 | 18 | 18 | 12053.4026
2029/2030 | 2008 | 1 | 18 | 19 | 13222.8118
2029/2030 | 2008 | 1 | 18 | 20 | 14356.7548
2029/2030 | 2008 | 1 | 18 | 21 | 16130.3781
2029/2030 | 2008 | 1 | 18 | 22 | 17405.8212
2029/2030 | 2008 | 1 | 18 | 23 | 18350.2814
2029/2030 | 2008 | 1 | 18 | 24 | 20667.3873
2029/2030 | 2008 | 1 | 19 | 1 | 22182.6046
2029/2030 | 2008 | 1 | 19 | 2 | 22741.2631
2029/2030 | 2008 | 1 | 19 | 3 | 22477.4684
2029/2030 | 2008 | 1 | 19 | 4 | 21349.071
2029/2030 | 2008 | 1 | 19 | 5 | 20885.9955
2029/2030 | 2008 | 1 | 19 | 6 | 20774.3451
2029/2030 | 2008 | 1 | 19 | 7 | 19856.3109
2029/2030 | 2008 | 1 | 19 | 8 | 18415.4444
2029/2030 | 2008 | 1 | 19 | 9 | 14226.7394
2029/2030 | 2008 | 1 | 19 | 10 | 14466.6294
2029/2030 | 2008 | 1 | 19 | 11 | 14465.5488
2029/2030 | 2008 | 1 | 19 | 12 | 13617.0033
2029/2030 | 2008 | 1 | 19 | 13 | 12725.8735
2029/2030 | 2008 | 1 | 19 | 14 | 12366.64
2029/2030 | 2008 | 1 | 19 | 15 | 11691.4248
2029/2030 | 2008 | 1 | 19 | 16 | 10715.4188
2029/2030 | 2008 | 1 | 19 | 17 | 8633.3231
2029/2030 | 2008 | 1 | 19 | 18 | 7890.6203
2029/2030 | 2008 | 1 | 19 | 19 | 9768.2387
2029/2030 | 2008 | 1 | 19 | 20 | 11673.5817
2029/2030 | 2008 | 1 | 19 | 21 | 12486.4507
2029/2030 | 2008 | 1 | 19 | 22 | 15196.9931
2029/2030 | 2008 | 1 | 19 | 23 | 18531.4152
2029/2030 | 2008 | 1 | 19 | 24 | 22223.7902
2029/2030 | 2008 | 1 | 20 | 1 | 25275.7881
2029/2030 | 2008 | 1 | 20 | 2 | 27447.1093
2029/2030 | 2008 | 1 | 20 | 3 | 28414.1382
2029/2030 | 2008 | 1 | 20 | 4 | 28946.9403
2029/2030 | 2008 | 1 | 20 | 5 | 29271.8315
2029/2030 | 2008 | 1 | 20 | 6 | 29330.0389
2029/2030 | 2008 | 1 | 20 | 7 | 29908.5047
2029/2030 | 2008 | 1 | 20 | 8 | 28590.7044
2029/2030 | 2008 | 1 | 20 | 9 | 25533.2563
2029/2030 | 2008 | 1 | 20 | 10 | 24205.5338
2029/2030 | 2008 | 1 | 20 | 11 | 26735.0337
2029/2030 | 2008 | 1 | 20 | 12 | 27979.2569
2029/2030 | 2008 | 1 | 20 | 13 | 30993.0087
2029/2030 | 2008 | 1 | 20 | 14 | 32267.4134
2029/2030 | 2008 | 1 | 20 | 15 | 31413.1129
2029/2030 | 2008 | 1 | 20 | 16 | 32165.5647
2029/2030 | 2008 | 1 | 20 | 17 | 31786.9161
2029/2030 | 2008 | 1 | 20 | 18 | 31973.7497
2029/2030 | 2008 | 1 | 20 | 19 | 32147.4621
2029/2030 | 2008 | 1 | 20 | 20 | 32801.6365
2029/2030 | 2008 | 1 | 20 | 21 | 34251.6338
2029/2030 | 2008 | 1 | 20 | 22 | 35047.6429
2029/2030 | 2008 | 1 | 20 | 23 | 34632.2178
2029/2030 | 2008 | 1 | 20 | 24 | 34445.1936
2029/2030 | 2008 | 1 | 21 | 1 | 33781.3862
2029/2030 | 2008 | 1 | 21 | 2 | 31438.5092
2029/2030 | 2008 | 1 | 21 | 3 | 29594.5994
2029/2030 | 2008 | 1 | 21 | 4 | 30821.2885
2029/2030 | 2008 | 1 | 21 | 5 | 29974.7598
2029/2030 | 2008 | 1 | 21 | 6 | 30373.6609
2029/2030 | 2008 | 1 | 21 | 7 | 30435.9013
2029/2030 | 2008 | 1 | 21 | 8 | 29181.2155
2029/2030 | 2008 | 1 | 21 | 9 | 27062.8726
2029/2030 | 2008 | 1 | 21 | 10 | 28703.9563
2029/2030 | 2008 | 1 | 21 | 11 | 28589.207
2029/2030 | 2008 | 1 | 21 | 12 | 27426.9756
2029/2030 | 2008 | 1 | 21 | 13 | 26335.6612
2029/2030 | 2008 | 1 | 21 | 14 | 26095.9392
2029/2030 | 2008 | 1 | 21 | 15 | 24836.6491
2029/2030 | 2008 | 1 | 21 | 16 | 23538.1606
2029/2030 | 2008 | 1 | 21 | 17 | 21132.0431
2029/2030 | 2008 | 1 | 21 | 18 | 21404.9574
2029/2030 | 2008 | 1 | 21 | 19 | 22352.0864
2029/2030 | 2008 | 1 | 21 | 20 | 23033.3736
2029/2030 | 2008 | 1 | 21 | 21 | 23243.2497
2029/2030 | 2008 | 1 | 21 | 22 | 21693.5356
2029/2030 | 2008 | 1 | 21 | 23 | 20833.2323
2029/2030 | 2008 | 1 | 21 | 24 | 20064.092
2029/2030 | 2008 | 1 | 22 | 1 | 19643.3253
2029/2030 | 2008 | 1 | 22 | 2 | 17916.8465
2029/2030 | 2008 | 1 | 22 | 3 | 15725.1169
2029/2030 | 2008 | 1 | 22 | 4 | 14083.4733
2029/2030 | 2008 | 1 | 22 | 5 | 13669.4171
2029/2030 | 2008 | 1 | 22 | 6 | 14504.5415
2029/2030 | 2008 | 1 | 22 | 7 | 15700.788
2029/2030 | 2008 | 1 | 22 | 8 | 16842.8471
2029/2030 | 2008 | 1 | 22 | 9 | 14328.0043
2029/2030 | 2008 | 1 | 22 | 10 | 14748.012
2029/2030 | 2008 | 1 | 22 | 11 | 14569.8792
2029/2030 | 2008 | 1 | 22 | 12 | 12956.4984
2029/2030 | 2008 | 1 | 22 | 13 | 11003.136
2029/2030 | 2008 | 1 | 22 | 14 | 9063.6413
2029/2030 | 2008 | 1 | 22 | 15 | 7512.4638
2029/2030 | 2008 | 1 | 22 | 16 | 7175.387
2029/2030 | 2008 | 1 | 22 | 17 | 6692.1416
2029/2030 | 2008 | 1 | 22 | 18 | 6749.4108
2029/2030 | 2008 | 1 | 22 | 19 | 6772.3504
2029/2030 | 2008 | 1 | 22 | 20 | 6816.9841
2029/2030 | 2008 | 1 | 22 | 21 | 6668.8927
2029/2030 | 2008 | 1 | 22 | 22 | 6503.3151
2029/2030 | 2008 | 1 | 22 | 23 | 6887.4145
2029/2030 | 2008 | 1 | 22 | 24 | 6966.7523
2029/2030 | 2008 | 1 | 23 | 1 | 8154.7173
2029/2030 | 2008 | 1 | 23 | 2 | 8913.2899
2029/2030 | 2008 | 1 | 23 | 3 | 9353.8633
2029/2030 | 2008 | 1 | 23 | 4 | 9321.728
2029/2030 | 2008 | 1 | 23 | 5 | 9085.6818
2029/2030 | 2008 | 1 | 23 | 6 | 8763.7607
2029/2030 | 2008 | 1 | 23 | 7 | 8283.4029
2029/2030 | 2008 | 1 | 23 | 8 | 7818.9499
2029/2030 | 2008 | 1 | 23 | 9 | 7295.5748
2029/2030 | 2008 | 1 | 23 | 10 | 6708.727
2029/2030 | 2008 | 1 | 23 | 11 | 6747.9672
2029/2030 | 2008 | 1 | 23 | 12 | 6615.1465
2029/2030 | 2008 | 1 | 23 | 13 | 6899.6978
2029/2030 | 2008 | 1 | 23 | 14 | 7033.3011
2029/2030 | 2008 | 1 | 23 | 15 | 7136.3996
2029/2030 | 2008 | 1 | 23 | 16 | 7578.1333
2029/2030 | 2008 | 1 | 23 | 17 | 7422.2821
2029/2030 | 2008 | 1 | 23 | 18 | 8353.0213
2029/2030 | 2008 | 1 | 23 | 19 | 10413.152
2029/2030 | 2008 | 1 | 23 | 20 | 13678.9014
2029/2030 | 2008 | 1 | 23 | 21 | 14851.1289
2029/2030 | 2008 | 1 | 23 | 22 | 16507.3588
2029/2030 | 2008 | 1 | 23 | 23 | 19207.1231
2029/2030 | 2008 | 1 | 23 | 24 | 21319.1593
2029/2030 | 2008 | 1 | 24 | 1 | 23762.3082
2029/2030 | 2008 | 1 | 24 | 2 | 24558.9571
2029/2030 | 2008 | 1 | 24 | 3 | 24907.7803
2029/2030 | 2008 | 1 | 24 | 4 | 23668.0581
2029/2030 | 2008 | 1 | 24 | 5 | 23027.1179
2029/2030 | 2008 | 1 | 24 | 6 | 22558.0293
2029/2030 | 2008 | 1 | 24 | 7 | 20372.3352
2029/2030 | 2008 | 1 | 24 | 8 | 18664.8572
2029/2030 | 2008 | 1 | 24 | 9 | 15903.9323
2029/2030 | 2008 | 1 | 24 | 10 | 17474.3209
2029/2030 | 2008 | 1 | 24 | 11 | 17951.5894
2029/2030 | 2008 | 1 | 24 | 12 | 17011.0625
2029/2030 | 2008 | 1 | 24 | 13 | 16463.2213
2029/2030 | 2008 | 1 | 24 | 14 | 16410.4533
2029/2030 | 2008 | 1 | 24 | 15 | 16336.5898
2029/2030 | 2008 | 1 | 24 | 16 | 15655.6998
2029/2030 | 2008 | 1 | 24 | 17 | 14043.632
2029/2030 | 2008 | 1 | 24 | 18 | 13396.5058
2029/2030 | 2008 | 1 | 24 | 19 | 13801.6702
2029/2030 | 2008 | 1 | 24 | 20 | 13201.9805
2029/2030 | 2008 | 1 | 24 | 21 | 13108.7512
2029/2030 | 2008 | 1 | 24 | 22 | 12704.8519
2029/2030 | 2008 | 1 | 24 | 23 | 11986.9398
2029/2030 | 2008 | 1 | 24 | 24 | 11685.1813
2029/2030 | 2008 | 1 | 25 | 1 | 12225.9662
2029/2030 | 2008 | 1 | 25 | 2 | 12284.8871
2029/2030 | 2008 | 1 | 25 | 3 | 11643.5836
2029/2030 | 2008 | 1 | 25 | 4 | 11860.9979
2029/2030 | 2008 | 1 | 25 | 5 | 12353.2143
2029/2030 | 2008 | 1 | 25 | 6 | 13120.6106
2029/2030 | 2008 | 1 | 25 | 7 | 12459.2051
2029/2030 | 2008 | 1 | 25 | 8 | 11356.4939
2029/2030 | 2008 | 1 | 25 | 9 | 10684.6946
2029/2030 | 2008 | 1 | 25 | 10 | 11799.331
2029/2030 | 2008 | 1 | 25 | 11 | 12425.0293
2029/2030 | 2008 | 1 | 25 | 12 | 12096.3313
2029/2030 | 2008 | 1 | 25 | 13 | 12757.1539
2029/2030 | 2008 | 1 | 25 | 14 | 13278.3062
2029/2030 | 2008 | 1 | 25 | 15 | 13192.0515
2029/2030 | 2008 | 1 | 25 | 16 | 13218.7598
2029/2030 | 2008 | 1 | 25 | 17 | 11479.1174
2029/2030 | 2008 | 1 | 25 | 18 | 12260.7279
2029/2030 | 2008 | 1 | 25 | 19 | 14565.8487
2029/2030 | 2008 | 1 | 25 | 20 | 16799.5661
2029/2030 | 2008 | 1 | 25 | 21 | 18679.3514
2029/2030 | 2008 | 1 | 25 | 22 | 19952.9517
2029/2030 | 2008 | 1 | 25 | 23 | 19481.3141
2029/2030 | 2008 | 1 | 25 | 24 | 19527.239
2029/2030 | 2008 | 1 | 26 | 1 | 19871.3485
2029/2030 | 2008 | 1 | 26 | 2 | 19542.1913
2029/2030 | 2008 | 1 | 26 | 3 | 19514.4938
2029/2030 | 2008 | 1 | 26 | 4 | 18974.6045
2029/2030 | 2008 | 1 | 26 | 5 | 18959.079
2029/2030 | 2008 | 1 | 26 | 6 | 20032.8999
2029/2030 | 2008 | 1 | 26 | 7 | 20673.5045
2029/2030 | 2008 | 1 | 26 | 8 | 20434.4048
2029/2030 | 2008 | 1 | 26 | 9 | 18441.0167
2029/2030 | 2008 | 1 | 26 | 10 | 13582.5497
2029/2030 | 2008 | 1 | 26 | 11 | 9870.0511
2029/2030 | 2008 | 1 | 26 | 12 | 7922.7779
2029/2030 | 2008 | 1 | 26 | 13 | 6675.4621
2029/2030 | 2008 | 1 | 26 | 14 | 4812.6931
2029/2030 | 2008 | 1 | 26 | 15 | 3175.5995
2029/2030 | 2008 | 1 | 26 | 16 | 1819.1599
2029/2030 | 2008 | 1 | 26 | 17 | 1113.1681
2029/2030 | 2008 | 1 | 26 | 18 | 1228.0723
2029/2030 | 2008 | 1 | 26 | 19 | 1573.8073
2029/2030 | 2008 | 1 | 26 | 20 | 2088.2542
2029/2030 | 2008 | 1 | 26 | 21 | 3327.4552
2029/2030 | 2008 | 1 | 26 | 22 | 4528.001
2029/2030 | 2008 | 1 | 26 | 23 | 5594.8154
2029/2030 | 2008 | 1 | 26 | 24 | 7311.1043
2029/2030 | 2008 | 1 | 27 | 1 | 9159.3827
2029/2030 | 2008 | 1 | 27 | 2 | 10100.0676
2029/2030 | 2008 | 1 | 27 | 3 | 10816.7618
2029/2030 | 2008 | 1 | 27 | 4 | 11195.459
2029/2030 | 2008 | 1 | 27 | 5 | 12037.7475
2029/2030 | 2008 | 1 | 27 | 6 | 12360.5034
2029/2030 | 2008 | 1 | 27 | 7 | 14033.2861
2029/2030 | 2008 | 1 | 27 | 8 | 15154.0241
2029/2030 | 2008 | 1 | 27 | 9 | 16115.0742
2029/2030 | 2008 | 1 | 27 | 10 | 15313.723
2029/2030 | 2008 | 1 | 27 | 11 | 12827.7654
2029/2030 | 2008 | 1 | 27 | 12 | 15732.7166
2029/2030 | 2008 | 1 | 27 | 13 | 19551.7242
2029/2030 | 2008 | 1 | 27 | 14 | 22370.5374
2029/2030 | 2008 | 1 | 27 | 15 | 24345.8832
2029/2030 | 2008 | 1 | 27 | 16 | 25738.8407
2029/2030 | 2008 | 1 | 27 | 17 | 26259.7437
2029/2030 | 2008 | 1 | 27 | 18 | 28873.0896
2029/2030 | 2008 | 1 | 27 | 19 | 31023.1185
2029/2030 | 2008 | 1 | 27 | 20 | 32185.8864
2029/2030 | 2008 | 1 | 27 | 21 | 32263.3371
2029/2030 | 2008 | 1 | 27 | 22 | 32772.4885
2029/2030 | 2008 | 1 | 27 | 23 | 32713.6413
2029/2030 | 2008 | 1 | 27 | 24 | 32551.7761
2029/2030 | 2008 | 1 | 28 | 1 | 30621.0073
2029/2030 | 2008 | 1 | 28 | 2 | 29665.6075
2029/2030 | 2008 | 1 | 28 | 3 | 29759.5191
2029/2030 | 2008 | 1 | 28 | 4 | 30056.6022
2029/2030 | 2008 | 1 | 28 | 5 | 31029.4182
2029/2030 | 2008 | 1 | 28 | 6 | 31535.7832
2029/2030 | 2008 | 1 | 28 | 7 | 31727.0463
2029/2030 | 2008 | 1 | 28 | 8 | 33541.8705
2029/2030 | 2008 | 1 | 28 | 9 | 33936.6787
2029/2030 | 2008 | 1 | 28 | 10 | 35272.6234
2029/2030 | 2008 | 1 | 28 | 11 | 35356.9064
2029/2030 | 2008 | 1 | 28 | 12 | 35123.5568
2029/2030 | 2008 | 1 | 28 | 13 | 35373.618
2029/2030 | 2008 | 1 | 28 | 14 | 34787.2201
2029/2030 | 2008 | 1 | 28 | 15 | 34756.9119
2029/2030 | 2008 | 1 | 28 | 16 | 34307.807
2029/2030 | 2008 | 1 | 28 | 17 | 33203.0124
2029/2030 | 2008 | 1 | 28 | 18 | 31938.0874
2029/2030 | 2008 | 1 | 28 | 19 | 33314.1342
2029/2030 | 2008 | 1 | 28 | 20 | 33810.8206
2029/2030 | 2008 | 1 | 28 | 21 | 35078.846
2029/2030 | 2008 | 1 | 28 | 22 | 35375.9735
2029/2030 | 2008 | 1 | 28 | 23 | 35224.4056
2029/2030 | 2008 | 1 | 28 | 24 | 35205.1934
2029/2030 | 2008 | 1 | 29 | 1 | 35976.4673
2029/2030 | 2008 | 1 | 29 | 2 | 35952.4747
2029/2030 | 2008 | 1 | 29 | 3 | 35512.5654
2029/2030 | 2008 | 1 | 29 | 4 | 35350.1229
2029/2030 | 2008 | 1 | 29 | 5 | 34171.0364
2029/2030 | 2008 | 1 | 29 | 6 | 33948.9127
2029/2030 | 2008 | 1 | 29 | 7 | 31041.1381
2029/2030 | 2008 | 1 | 29 | 8 | 29997.6532
2029/2030 | 2008 | 1 | 29 | 9 | 29355.152
2029/2030 | 2008 | 1 | 29 | 10 | 28184.4877
2029/2030 | 2008 | 1 | 29 | 11 | 26686.7799
2029/2030 | 2008 | 1 | 29 | 12 | 27799.2606
2029/2030 | 2008 | 1 | 29 | 13 | 29716.3194
2029/2030 | 2008 | 1 | 29 | 14 | 29773.9728
2029/2030 | 2008 | 1 | 29 | 15 | 28159.0335
2029/2030 | 2008 | 1 | 29 | 16 | 23813.4499
2029/2030 | 2008 | 1 | 29 | 17 | 17056.5735
2029/2030 | 2008 | 1 | 29 | 18 | 13055.5129
2029/2030 | 2008 | 1 | 29 | 19 | 13019.6285
2029/2030 | 2008 | 1 | 29 | 20 | 14165.1097
2029/2030 | 2008 | 1 | 29 | 21 | 17713.066
2029/2030 | 2008 | 1 | 29 | 22 | 22906.224
2029/2030 | 2008 | 1 | 29 | 23 | 28080.5975
2029/2030 | 2008 | 1 | 29 | 24 | 31296.3446
2029/2030 | 2008 | 1 | 30 | 1 | 33133.3089
2029/2030 | 2008 | 1 | 30 | 2 | 33264.6479
2029/2030 | 2008 | 1 | 30 | 3 | 33816.9218
2029/2030 | 2008 | 1 | 30 | 4 | 32655.2249
2029/2030 | 2008 | 1 | 30 | 5 | 32442.9933
2029/2030 | 2008 | 1 | 30 | 6 | 31965.4876
2029/2030 | 2008 | 1 | 30 | 7 | 31284.2184
2029/2030 | 2008 | 1 | 30 | 8 | 30291.2449
2029/2030 | 2008 | 1 | 30 | 9 | 28367.3106
2029/2030 | 2008 | 1 | 30 | 10 | 28669.113
2029/2030 | 2008 | 1 | 30 | 11 | 29669.9223
2029/2030 | 2008 | 1 | 30 | 12 | 30834.2518
2029/2030 | 2008 | 1 | 30 | 13 | 31278.9053
2029/2030 | 2008 | 1 | 30 | 14 | 30864.3392
2029/2030 | 2008 | 1 | 30 | 15 | 29783.5426
2029/2030 | 2008 | 1 | 30 | 16 | 29707.8976
2029/2030 | 2008 | 1 | 30 | 17 | 29228.8791
2029/2030 | 2008 | 1 | 30 | 18 | 27889.179
2029/2030 | 2008 | 1 | 30 | 19 | 29028.8128
2029/2030 | 2008 | 1 | 30 | 20 | 29732.0894
2029/2030 | 2008 | 1 | 30 | 21 | 29746.5078
2029/2030 | 2008 | 1 | 30 | 22 | 29405.2908
2029/2030 | 2008 | 1 | 30 | 23 | 28095.4332
2029/2030 | 2008 | 1 | 30 | 24 | 27941.7462
2029/2030 | 2008 | 1 | 31 | 1 | 29721.3949
2029/2030 | 2008 | 1 | 31 | 2 | 28507.7662
2029/2030 | 2008 | 1 | 31 | 3 | 27141.8998
2029/2030 | 2008 | 1 | 31 | 4 | 27100.9925
2029/2030 | 2008 | 1 | 31 | 5 | 27761.835
2029/2030 | 2008 | 1 | 31 | 6 | 28832.3529
2029/2030 | 2008 | 1 | 31 | 7 | 30912.4491
2029/2030 | 2008 | 1 | 31 | 8 | 32860.6002
2029/2030 | 2008 | 1 | 31 | 9 | 32509.7129
2029/2030 | 2008 | 1 | 31 | 10 | 31983.9957
2029/2030 | 2008 | 1 | 31 | 11 | 32727.2553
2029/2030 | 2008 | 1 | 31 | 12 | 33327.6287
2029/2030 | 2008 | 1 | 31 | 13 | 35153.349
2029/2030 | 2008 | 1 | 31 | 14 | 35159.3518
2029/2030 | 2008 | 1 | 31 | 15 | 34383.0469
2029/2030 | 2008 | 1 | 31 | 16 | 35163.6634
2029/2030 | 2008 | 1 | 31 | 17 | 29652.6643
2029/2030 | 2008 | 1 | 31 | 18 | 30167.032
2029/2030 | 2008 | 1 | 31 | 19 | 26090.233
2029/2030 | 2008 | 1 | 31 | 20 | 22090.1554
2029/2030 | 2008 | 1 | 31 | 21 | 16261.9995
2029/2030 | 2008 | 1 | 31 | 22 | 12839.3055
2029/2030 | 2008 | 1 | 31 | 23 | 12330.2714
2029/2030 | 2008 | 1 | 31 | 24 | 13089.2374
2030/2031 | 2008 | 1 | 1 | 1 | 25186.4182
2030/2031 | 2008 | 1 | 1 | 2 | 24852.8639
2030/2031 | 2008 | 1 | 1 | 3 | 23776.839
2030/2031 | 2008 | 1 | 1 | 4 | 22401.0651
2030/2031 | 2008 | 1 | 1 | 5 | 21268.7
2030/2031 | 2008 | 1 | 1 | 6 | 20449.8325
2030/2031 | 2008 | 1 | 1 | 7 | 19423.6818
2030/2031 | 2008 | 1 | 1 | 8 | 17640.6616
2030/2031 | 2008 | 1 | 1 | 9 | 15739.4869
2030/2031 | 2008 | 1 | 1 | 10 | 13184.7141
2030/2031 | 2008 | 1 | 1 | 11 | 15454.3749
2030/2031 | 2008 | 1 | 1 | 12 | 17236.783
2030/2031 | 2008 | 1 | 1 | 13 | 17053.2697
2030/2031 | 2008 | 1 | 1 | 14 | 15400.6393
2030/2031 | 2008 | 1 | 1 | 15 | 15279.373
2030/2031 | 2008 | 1 | 1 | 16 | 14725.0933
2030/2031 | 2008 | 1 | 1 | 17 | 11716.6241
2030/2031 | 2008 | 1 | 1 | 18 | 11693.7185
2030/2031 | 2008 | 1 | 1 | 19 | 11570.0593
2030/2031 | 2008 | 1 | 1 | 20 | 12467.876
2030/2031 | 2008 | 1 | 1 | 21 | 12224.0939
2030/2031 | 2008 | 1 | 1 | 22 | 10863.5686
2030/2031 | 2008 | 1 | 1 | 23 | 10192.5145
2030/2031 | 2008 | 1 | 1 | 24 | 10322.1604
2030/2031 | 2008 | 1 | 2 | 1 | 10601.7513
2030/2031 | 2008 | 1 | 2 | 2 | 11273.9444
2030/2031 | 2008 | 1 | 2 | 3 | 10578.5008
2030/2031 | 2008 | 1 | 2 | 4 | 11490.9691
2030/2031 | 2008 | 1 | 2 | 5 | 11796.7524
2030/2031 | 2008 | 1 | 2 | 6 | 12075.9362
2030/2031 | 2008 | 1 | 2 | 7 | 12260.0064
2030/2031 | 2008 | 1 | 2 | 8 | 11749.4356
2030/2031 | 2008 | 1 | 2 | 9 | 9614.0373
2030/2031 | 2008 | 1 | 2 | 10 | 9380.8958
2030/2031 | 2008 | 1 | 2 | 11 | 10893.586
2030/2031 | 2008 | 1 | 2 | 12 | 11934.9132
2030/2031 | 2008 | 1 | 2 | 13 | 12155.8055
2030/2031 | 2008 | 1 | 2 | 14 | 11938.2056
2030/2031 | 2008 | 1 | 2 | 15 | 12047.6322
2030/2031 | 2008 | 1 | 2 | 16 | 11241.446
2030/2031 | 2008 | 1 | 2 | 17 | 10242.1199
2030/2031 | 2008 | 1 | 2 | 18 | 10979.489
2030/2031 | 2008 | 1 | 2 | 19 | 13622.3208
2030/2031 | 2008 | 1 | 2 | 20 | 16441.2827
2030/2031 | 2008 | 1 | 2 | 21 | 19023.4165
2030/2031 | 2008 | 1 | 2 | 22 | 21269.9026
2030/2031 | 2008 | 1 | 2 | 23 | 22286.529
2030/2031 | 2008 | 1 | 2 | 24 | 22819.97
2030/2031 | 2008 | 1 | 3 | 1 | 24203.7422
2030/2031 | 2008 | 1 | 3 | 2 | 25092.8325
2030/2031 | 2008 | 1 | 3 | 3 | 25611.1907
2030/2031 | 2008 | 1 | 3 | 4 | 26579.3803
2030/2031 | 2008 | 1 | 3 | 5 | 27904.9419
2030/2031 | 2008 | 1 | 3 | 6 | 29753.3481
2030/2031 | 2008 | 1 | 3 | 7 | 30060.1124
2030/2031 | 2008 | 1 | 3 | 8 | 28686.7987
2030/2031 | 2008 | 1 | 3 | 9 | 26569.8752
2030/2031 | 2008 | 1 | 3 | 10 | 27580.5149
2030/2031 | 2008 | 1 | 3 | 11 | 28066.5202
2030/2031 | 2008 | 1 | 3 | 12 | 28646.5292
2030/2031 | 2008 | 1 | 3 | 13 | 29213.0167
2030/2031 | 2008 | 1 | 3 | 14 | 29873.3726
2030/2031 | 2008 | 1 | 3 | 15 | 31019.6762
2030/2031 | 2008 | 1 | 3 | 16 | 32067.941
2030/2031 | 2008 | 1 | 3 | 17 | 31720.0375
2030/2031 | 2008 | 1 | 3 | 18 | 30928.1695
2030/2031 | 2008 | 1 | 3 | 19 | 31700.1204
2030/2031 | 2008 | 1 | 3 | 20 | 31784.6524
2030/2031 | 2008 | 1 | 3 | 21 | 32804.1214
2030/2031 | 2008 | 1 | 3 | 22 | 33275.1143
2030/2031 | 2008 | 1 | 3 | 23 | 33562.9441
2030/2031 | 2008 | 1 | 3 | 24 | 33548.1484
2030/2031 | 2008 | 1 | 4 | 1 | 33091.847
2030/2031 | 2008 | 1 | 4 | 2 | 32701.0405
2030/2031 | 2008 | 1 | 4 | 3 | 34047.4574
2030/2031 | 2008 | 1 | 4 | 4 | 33630.3531
2030/2031 | 2008 | 1 | 4 | 5 | 33236.0796
2030/2031 | 2008 | 1 | 4 | 6 | 32816.2649
2030/2031 | 2008 | 1 | 4 | 7 | 32323.3015
2030/2031 | 2008 | 1 | 4 | 8 | 30526.813
2030/2031 | 2008 | 1 | 4 | 9 | 29896.1788
2030/2031 | 2008 | 1 | 4 | 10 | 29740.9453
2030/2031 | 2008 | 1 | 4 | 11 | 30777.4599
2030/2031 | 2008 | 1 | 4 | 12 | 31454.2141
2030/2031 | 2008 | 1 | 4 | 13 | 32986.5863
2030/2031 | 2008 | 1 | 4 | 14 | 34003.4729
2030/2031 | 2008 | 1 | 4 | 15 | 34068.8768
2030/2031 | 2008 | 1 | 4 | 16 | 35085.856
2030/2031 | 2008 | 1 | 4 | 17 | 34549.7581
2030/2031 | 2008 | 1 | 4 | 18 | 34241.3705
2030/2031 | 2008 | 1 | 4 | 19 | 35526.7579
2030/2031 | 2008 | 1 | 4 | 20 | 35925.8786
2030/2031 | 2008 | 1 | 4 | 21 | 36299.8476
2030/2031 | 2008 | 1 | 4 | 22 | 36606.1118
2030/2031 | 2008 | 1 | 4 | 23 | 36567.5009
2030/2031 | 2008 | 1 | 4 | 24 | 37090.8474
2030/2031 | 2008 | 1 | 5 | 1 | 37088.7335
2030/2031 | 2008 | 1 | 5 | 2 | 36846.6769
2030/2031 | 2008 | 1 | 5 | 3 | 35506.7884
2030/2031 | 2008 | 1 | 5 | 4 | 34578.9598
2030/2031 | 2008 | 1 | 5 | 5 | 34199.5351
2030/2031 | 2008 | 1 | 5 | 6 | 33901.0789
2030/2031 | 2008 | 1 | 5 | 7 | 33861.6772
2030/2031 | 2008 | 1 | 5 | 8 | 33073.8629
2030/2031 | 2008 | 1 | 5 | 9 | 31146.7731
2030/2031 | 2008 | 1 | 5 | 10 | 30353.1983
2030/2031 | 2008 | 1 | 5 | 11 | 31046.3013
2030/2031 | 2008 | 1 | 5 | 12 | 33270.2801
2030/2031 | 2008 | 1 | 5 | 13 | 34931.3837
2030/2031 | 2008 | 1 | 5 | 14 | 35548.1902
2030/2031 | 2008 | 1 | 5 | 15 | 35913.8748
2030/2031 | 2008 | 1 | 5 | 16 | 35417.6498
2030/2031 | 2008 | 1 | 5 | 17 | 32544.4513
2030/2031 | 2008 | 1 | 5 | 18 | 32812.3123
2030/2031 | 2008 | 1 | 5 | 19 | 34651.7829
2030/2031 | 2008 | 1 | 5 | 20 | 35105.7235
2030/2031 | 2008 | 1 | 5 | 21 | 34992.616
2030/2031 | 2008 | 1 | 5 | 22 | 35202.9393
2030/2031 | 2008 | 1 | 5 | 23 | 35310.8647
2030/2031 | 2008 | 1 | 5 | 24 | 35390.0228
2030/2031 | 2008 | 1 | 6 | 1 | 35420.2722
2030/2031 | 2008 | 1 | 6 | 2 | 35185.1174
2030/2031 | 2008 | 1 | 6 | 3 | 34999.1678
2030/2031 | 2008 | 1 | 6 | 4 | 34766.0419
2030/2031 | 2008 | 1 | 6 | 5 | 34134.5147
2030/2031 | 2008 | 1 | 6 | 6 | 33919.6254
2030/2031 | 2008 | 1 | 6 | 7 | 33466.4948
2030/2031 | 2008 | 1 | 6 | 8 | 31199.0989
2030/2031 | 2008 | 1 | 6 | 9 | 29342.5803
2030/2031 | 2008 | 1 | 6 | 10 | 30617.611
2030/2031 | 2008 | 1 | 6 | 11 | 31021.9087
2030/2031 | 2008 | 1 | 6 | 12 | 31957.3858
2030/2031 | 2008 | 1 | 6 | 13 | 32350.3608
2030/2031 | 2008 | 1 | 6 | 14 | 31798.9769
2030/2031 | 2008 | 1 | 6 | 15 | 31366.9045
2030/2031 | 2008 | 1 | 6 | 16 | 30080.6252
2030/2031 | 2008 | 1 | 6 | 17 | 28010.7912
2030/2031 | 2008 | 1 | 6 | 18 | 29281.0111
2030/2031 | 2008 | 1 | 6 | 19 | 31627.0456
2030/2031 | 2008 | 1 | 6 | 20 | 32367.1038
2030/2031 | 2008 | 1 | 6 | 21 | 32307.5423
2030/2031 | 2008 | 1 | 6 | 22 | 33124.5108
2030/2031 | 2008 | 1 | 6 | 23 | 33018.9897
2030/2031 | 2008 | 1 | 6 | 24 | 34223.4965
2030/2031 | 2008 | 1 | 7 | 1 | 33739.1577
2030/2031 | 2008 | 1 | 7 | 2 | 32868.9738
2030/2031 | 2008 | 1 | 7 | 3 | 32241.3281
2030/2031 | 2008 | 1 | 7 | 4 | 31185.779
2030/2031 | 2008 | 1 | 7 | 5 | 30936.8805
2030/2031 | 2008 | 1 | 7 | 6 | 30503.34
2030/2031 | 2008 | 1 | 7 | 7 | 29959.6828
2030/2031 | 2008 | 1 | 7 | 8 | 27761.5049
2030/2031 | 2008 | 1 | 7 | 9 | 24942.1195
2030/2031 | 2008 | 1 | 7 | 10 | 24859.0043
2030/2031 | 2008 | 1 | 7 | 11 | 24844.8694
2030/2031 | 2008 | 1 | 7 | 12 | 24732.6062
2030/2031 | 2008 | 1 | 7 | 13 | 24783.335
2030/2031 | 2008 | 1 | 7 | 14 | 24484.1134
2030/2031 | 2008 | 1 | 7 | 15 | 24514.1894
2030/2031 | 2008 | 1 | 7 | 16 | 23841.0549
2030/2031 | 2008 | 1 | 7 | 17 | 22459.8573
2030/2031 | 2008 | 1 | 7 | 18 | 24960.7097
2030/2031 | 2008 | 1 | 7 | 19 | 27253.5983
2030/2031 | 2008 | 1 | 7 | 20 | 28322.6198
2030/2031 | 2008 | 1 | 7 | 21 | 28508.8514
2030/2031 | 2008 | 1 | 7 | 22 | 29274.6296
2030/2031 | 2008 | 1 | 7 | 23 | 29932.5355
2030/2031 | 2008 | 1 | 7 | 24 | 30151.4887
2030/2031 | 2008 | 1 | 8 | 1 | 32161.434
2030/2031 | 2008 | 1 | 8 | 2 | 34556.676
2030/2031 | 2008 | 1 | 8 | 3 | 35214.2047
2030/2031 | 2008 | 1 | 8 | 4 | 34706.6252
2030/2031 | 2008 | 1 | 8 | 5 | 33604.7596
2030/2031 | 2008 | 1 | 8 | 6 | 29161.903
2030/2031 | 2008 | 1 | 8 | 7 | 31360.2656
2030/2031 | 2008 | 1 | 8 | 8 | 29994.7078
2030/2031 | 2008 | 1 | 8 | 9 | 27802.7593
2030/2031 | 2008 | 1 | 8 | 10 | 29078.3945
2030/2031 | 2008 | 1 | 8 | 11 | 30557.2986
2030/2031 | 2008 | 1 | 8 | 12 | 30253.9604
2030/2031 | 2008 | 1 | 8 | 13 | 28007.7972
2030/2031 | 2008 | 1 | 8 | 14 | 24620.2842
2030/2031 | 2008 | 1 | 8 | 15 | 21544.2538
2030/2031 | 2008 | 1 | 8 | 16 | 18260.1387
2030/2031 | 2008 | 1 | 8 | 17 | 12451.6798
2030/2031 | 2008 | 1 | 8 | 18 | 10222.9786
2030/2031 | 2008 | 1 | 8 | 19 | 9719.8399
2030/2031 | 2008 | 1 | 8 | 20 | 9246.3214
2030/2031 | 2008 | 1 | 8 | 21 | 9353.5804
2030/2031 | 2008 | 1 | 8 | 22 | 9744.8361
2030/2031 | 2008 | 1 | 8 | 23 | 10706.9046
2030/2031 | 2008 | 1 | 8 | 24 | 11989.2718
2030/2031 | 2008 | 1 | 9 | 1 | 15077.1484
2030/2031 | 2008 | 1 | 9 | 2 | 18279.5514
2030/2031 | 2008 | 1 | 9 | 3 | 22015.5885
2030/2031 | 2008 | 1 | 9 | 4 | 23687.8163
2030/2031 | 2008 | 1 | 9 | 5 | 24385.0107
2030/2031 | 2008 | 1 | 9 | 6 | 25116.1804
2030/2031 | 2008 | 1 | 9 | 7 | 25270.3327
2030/2031 | 2008 | 1 | 9 | 8 | 24620.838
2030/2031 | 2008 | 1 | 9 | 9 | 22815.3787
2030/2031 | 2008 | 1 | 9 | 10 | 18280.6063
2030/2031 | 2008 | 1 | 9 | 11 | 21977.9757
2030/2031 | 2008 | 1 | 9 | 12 | 23896.9155
2030/2031 | 2008 | 1 | 9 | 13 | 22355.2014
2030/2031 | 2008 | 1 | 9 | 14 | 23333.4578
2030/2031 | 2008 | 1 | 9 | 15 | 23765.0728
2030/2031 | 2008 | 1 | 9 | 16 | 23549.5528
2030/2031 | 2008 | 1 | 9 | 17 | 22276.1826
2030/2031 | 2008 | 1 | 9 | 18 | 24404.9494
2030/2031 | 2008 | 1 | 9 | 19 | 27015.977
2030/2031 | 2008 | 1 | 9 | 20 | 27953.8801
2030/2031 | 2008 | 1 | 9 | 21 | 28319.4096
2030/2031 | 2008 | 1 | 9 | 22 | 30739.0785
2030/2031 | 2008 | 1 | 9 | 23 | 30568.4329
2030/2031 | 2008 | 1 | 9 | 24 | 29725.6661
2030/2031 | 2008 | 1 | 10 | 1 | 28306.7712
2030/2031 | 2008 | 1 | 10 | 2 | 27599.2581
2030/2031 | 2008 | 1 | 10 | 3 | 28501.0801
2030/2031 | 2008 | 1 | 10 | 4 | 29230.3464
2030/2031 | 2008 | 1 | 10 | 5 | 28665.4639
2030/2031 | 2008 | 1 | 10 | 6 | 28558.5638
2030/2031 | 2008 | 1 | 10 | 7 | 28230.0407
2030/2031 | 2008 | 1 | 10 | 8 | 27106.5062
2030/2031 | 2008 | 1 | 10 | 9 | 23738.4536
2030/2031 | 2008 | 1 | 10 | 10 | 21519.7336
2030/2031 | 2008 | 1 | 10 | 11 | 23353.0958
2030/2031 | 2008 | 1 | 10 | 12 | 23937.8704
2030/2031 | 2008 | 1 | 10 | 13 | 22381.2463
2030/2031 | 2008 | 1 | 10 | 14 | 20377.2017
2030/2031 | 2008 | 1 | 10 | 15 | 18137.0519
2030/2031 | 2008 | 1 | 10 | 16 | 15121.6493
2030/2031 | 2008 | 1 | 10 | 17 | 10451.8734
2030/2031 | 2008 | 1 | 10 | 18 | 7865.2717
2030/2031 | 2008 | 1 | 10 | 19 | 7233.576
2030/2031 | 2008 | 1 | 10 | 20 | 6829.3932
2030/2031 | 2008 | 1 | 10 | 21 | 7468.3913
2030/2031 | 2008 | 1 | 10 | 22 | 8179.0405
2030/2031 | 2008 | 1 | 10 | 23 | 9745.8992
2030/2031 | 2008 | 1 | 10 | 24 | 11847.6578
2030/2031 | 2008 | 1 | 11 | 1 | 14483.6289
2030/2031 | 2008 | 1 | 11 | 2 | 16185.4427
2030/2031 | 2008 | 1 | 11 | 3 | 18694.5282
2030/2031 | 2008 | 1 | 11 | 4 | 20505.0441
2030/2031 | 2008 | 1 | 11 | 5 | 22041.2336
2030/2031 | 2008 | 1 | 11 | 6 | 22621.8539
2030/2031 | 2008 | 1 | 11 | 7 | 22563.5058
2030/2031 | 2008 | 1 | 11 | 8 | 21504.9346
2030/2031 | 2008 | 1 | 11 | 9 | 17706.821
2030/2031 | 2008 | 1 | 11 | 10 | 11427.2079
2030/2031 | 2008 | 1 | 11 | 11 | 10132.1429
2030/2031 | 2008 | 1 | 11 | 12 | 11143.454
2030/2031 | 2008 | 1 | 11 | 13 | 10961.3063
2030/2031 | 2008 | 1 | 11 | 14 | 10847.9532
2030/2031 | 2008 | 1 | 11 | 15 | 10540.8701
2030/2031 | 2008 | 1 | 11 | 16 | 9315.4228
2030/2031 | 2008 | 1 | 11 | 17 | 7381.6255
2030/2031 | 2008 | 1 | 11 | 18 | 7457.2602
2030/2031 | 2008 | 1 | 11 | 19 | 9752.8664
2030/2031 | 2008 | 1 | 11 | 20 | 11625.6702
2030/2031 | 2008 | 1 | 11 | 21 | 13942.1136
2030/2031 | 2008 | 1 | 11 | 22 | 15735.4328
2030/2031 | 2008 | 1 | 11 | 23 | 16773.4981
2030/2031 | 2008 | 1 | 11 | 24 | 18726.7919
2030/2031 | 2008 | 1 | 12 | 1 | 20858.4118
2030/2031 | 2008 | 1 | 12 | 2 | 21473.3559
2030/2031 | 2008 | 1 | 12 | 3 | 22153.5426
2030/2031 | 2008 | 1 | 12 | 4 | 23906.203
2030/2031 | 2008 | 1 | 12 | 5 | 24578.0917
2030/2031 | 2008 | 1 | 12 | 6 | 25046.4914
2030/2031 | 2008 | 1 | 12 | 7 | 26328.1693
2030/2031 | 2008 | 1 | 12 | 8 | 25946.4819
2030/2031 | 2008 | 1 | 12 | 9 | 22085.66
2030/2031 | 2008 | 1 | 12 | 10 | 18128.4872
2030/2031 | 2008 | 1 | 12 | 11 | 18955.7958
2030/2031 | 2008 | 1 | 12 | 12 | 18060.1726
2030/2031 | 2008 | 1 | 12 | 13 | 18468.929
2030/2031 | 2008 | 1 | 12 | 14 | 19286.8467
2030/2031 | 2008 | 1 | 12 | 15 | 19248.2585
2030/2031 | 2008 | 1 | 12 | 16 | 18275.3864
2030/2031 | 2008 | 1 | 12 | 17 | 14119.1261
2030/2031 | 2008 | 1 | 12 | 18 | 11774.3002
2030/2031 | 2008 | 1 | 12 | 19 | 11998.3999
2030/2031 | 2008 | 1 | 12 | 20 | 11550.5976
2030/2031 | 2008 | 1 | 12 | 21 | 11854.6021
2030/2031 | 2008 | 1 | 12 | 22 | 11773.7712
2030/2031 | 2008 | 1 | 12 | 23 | 11293.5403
2030/2031 | 2008 | 1 | 12 | 24 | 11327.6807
2030/2031 | 2008 | 1 | 13 | 1 | 12042.1774
2030/2031 | 2008 | 1 | 13 | 2 | 12226.9444
2030/2031 | 2008 | 1 | 13 | 3 | 12161.309
2030/2031 | 2008 | 1 | 13 | 4 | 11829.8
2030/2031 | 2008 | 1 | 13 | 5 | 11682.7148
2030/2031 | 2008 | 1 | 13 | 6 | 11661.5425
2030/2031 | 2008 | 1 | 13 | 7 | 11343.221
2030/2031 | 2008 | 1 | 13 | 8 | 10603.9081
2030/2031 | 2008 | 1 | 13 | 9 | 7346.0141
2030/2031 | 2008 | 1 | 13 | 10 | 4921.627
2030/2031 | 2008 | 1 | 13 | 11 | 4686.0526
2030/2031 | 2008 | 1 | 13 | 12 | 4355.6914
2030/2031 | 2008 | 1 | 13 | 13 | 4333.5442
2030/2031 | 2008 | 1 | 13 | 14 | 4985.2288
2030/2031 | 2008 | 1 | 13 | 15 | 5737.6306
2030/2031 | 2008 | 1 | 13 | 16 | 6338.5974
2030/2031 | 2008 | 1 | 13 | 17 | 6411.1
2030/2031 | 2008 | 1 | 13 | 18 | 7489.7319
2030/2031 | 2008 | 1 | 13 | 19 | 9834.0997
2030/2031 | 2008 | 1 | 13 | 20 | 12617.9417
2030/2031 | 2008 | 1 | 13 | 21 | 14492.4528
2030/2031 | 2008 | 1 | 13 | 22 | 16012.548
2030/2031 | 2008 | 1 | 13 | 23 | 17333.0805
2030/2031 | 2008 | 1 | 13 | 24 | 18992.5043
2030/2031 | 2008 | 1 | 14 | 1 | 18513.3084
2030/2031 | 2008 | 1 | 14 | 2 | 17002.1778
2030/2031 | 2008 | 1 | 14 | 3 | 15632.1042
2030/2031 | 2008 | 1 | 14 | 4 | 13845.972
2030/2031 | 2008 | 1 | 14 | 5 | 12271.6442
2030/2031 | 2008 | 1 | 14 | 6 | 11536.918
2030/2031 | 2008 | 1 | 14 | 7 | 10525.183
2030/2031 | 2008 | 1 | 14 | 8 | 9537.2203
2030/2031 | 2008 | 1 | 14 | 9 | 8141.4991
2030/2031 | 2008 | 1 | 14 | 10 | 7350.7373
2030/2031 | 2008 | 1 | 14 | 11 | 7829.5902
2030/2031 | 2008 | 1 | 14 | 12 | 8583.7017
2030/2031 | 2008 | 1 | 14 | 13 | 8775.3744
2030/2031 | 2008 | 1 | 14 | 14 | 9035.3829
2030/2031 | 2008 | 1 | 14 | 15 | 9112.0691
2030/2031 | 2008 | 1 | 14 | 16 | 8785.0622
2030/2031 | 2008 | 1 | 14 | 17 | 8078.8614
2030/2031 | 2008 | 1 | 14 | 18 | 7847.7848
2030/2031 | 2008 | 1 | 14 | 19 | 7991.8904
2030/2031 | 2008 | 1 | 14 | 20 | 8146.8428
2030/2031 | 2008 | 1 | 14 | 21 | 8192.6117
2030/2031 | 2008 | 1 | 14 | 22 | 8378.4217
2030/2031 | 2008 | 1 | 14 | 23 | 9078.7948
2030/2031 | 2008 | 1 | 14 | 24 | 9918.4899
2030/2031 | 2008 | 1 | 15 | 1 | 10928.1148
2030/2031 | 2008 | 1 | 15 | 2 | 11897.4524
2030/2031 | 2008 | 1 | 15 | 3 | 13819.6029
2030/2031 | 2008 | 1 | 15 | 4 | 15458.8543
2030/2031 | 2008 | 1 | 15 | 5 | 17821.6172
2030/2031 | 2008 | 1 | 15 | 6 | 19431.7121
2030/2031 | 2008 | 1 | 15 | 7 | 21287.1221
2030/2031 | 2008 | 1 | 15 | 8 | 22376.0109
2030/2031 | 2008 | 1 | 15 | 9 | 21915.8825
2030/2031 | 2008 | 1 | 15 | 10 | 21175.9962
2030/2031 | 2008 | 1 | 15 | 11 | 23597.1141
2030/2031 | 2008 | 1 | 15 | 12 | 27677.266
2030/2031 | 2008 | 1 | 15 | 13 | 30013.7285
2030/2031 | 2008 | 1 | 15 | 14 | 30733.7864
2030/2031 | 2008 | 1 | 15 | 15 | 30999.0137
2030/2031 | 2008 | 1 | 15 | 16 | 31554.8131
2030/2031 | 2008 | 1 | 15 | 17 | 31341.1794
2030/2031 | 2008 | 1 | 15 | 18 | 31415.528
2030/2031 | 2008 | 1 | 15 | 19 | 32952.5224
2030/2031 | 2008 | 1 | 15 | 20 | 32927.3297
2030/2031 | 2008 | 1 | 15 | 21 | 33488.6415
2030/2031 | 2008 | 1 | 15 | 22 | 33959.2043
2030/2031 | 2008 | 1 | 15 | 23 | 33685.4911
2030/2031 | 2008 | 1 | 15 | 24 | 33444.0221
2030/2031 | 2008 | 1 | 16 | 1 | 33467.817
2030/2031 | 2008 | 1 | 16 | 2 | 32925.1186
2030/2031 | 2008 | 1 | 16 | 3 | 32992.4453
2030/2031 | 2008 | 1 | 16 | 4 | 32731.3329
2030/2031 | 2008 | 1 | 16 | 5 | 30591.3694
2030/2031 | 2008 | 1 | 16 | 6 | 28305.519
2030/2031 | 2008 | 1 | 16 | 7 | 26815.2808
2030/2031 | 2008 | 1 | 16 | 8 | 24262.9697
2030/2031 | 2008 | 1 | 16 | 9 | 19978.5941
2030/2031 | 2008 | 1 | 16 | 10 | 18982.251
2030/2031 | 2008 | 1 | 16 | 11 | 18035.8308
2030/2031 | 2008 | 1 | 16 | 12 | 19017.668
2030/2031 | 2008 | 1 | 16 | 13 | 17968.5054
2030/2031 | 2008 | 1 | 16 | 14 | 16874.749
2030/2031 | 2008 | 1 | 16 | 15 | 17439.9548
2030/2031 | 2008 | 1 | 16 | 16 | 17349.093
2030/2031 | 2008 | 1 | 16 | 17 | 17326.1888
2030/2031 | 2008 | 1 | 16 | 18 | 18750.7444
2030/2031 | 2008 | 1 | 16 | 19 | 21570.0608
2030/2031 | 2008 | 1 | 16 | 20 | 23605.8555
2030/2031 | 2008 | 1 | 16 | 21 | 24087.0204
2030/2031 | 2008 | 1 | 16 | 22 | 23927.4998
2030/2031 | 2008 | 1 | 16 | 23 | 25006.8361
2030/2031 | 2008 | 1 | 16 | 24 | 24591.4231
2030/2031 | 2008 | 1 | 17 | 1 | 24008.1487
2030/2031 | 2008 | 1 | 17 | 2 | 23258.2003
2030/2031 | 2008 | 1 | 17 | 3 | 23398.2748
2030/2031 | 2008 | 1 | 17 | 4 | 22152.8868
2030/2031 | 2008 | 1 | 17 | 5 | 21112.6049
2030/2031 | 2008 | 1 | 17 | 6 | 20004.4487
2030/2031 | 2008 | 1 | 17 | 7 | 18062.5487
2030/2031 | 2008 | 1 | 17 | 8 | 15957.0348
2030/2031 | 2008 | 1 | 17 | 9 | 12966.555
2030/2031 | 2008 | 1 | 17 | 10 | 14108.1765
2030/2031 | 2008 | 1 | 17 | 11 | 13387.576
2030/2031 | 2008 | 1 | 17 | 12 | 11513.7042
2030/2031 | 2008 | 1 | 17 | 13 | 11018.8014
2030/2031 | 2008 | 1 | 17 | 14 | 10345.101
2030/2031 | 2008 | 1 | 17 | 15 | 9541.0831
2030/2031 | 2008 | 1 | 17 | 16 | 8705.3127
2030/2031 | 2008 | 1 | 17 | 17 | 7192.458
2030/2031 | 2008 | 1 | 17 | 18 | 5618.9308
2030/2031 | 2008 | 1 | 17 | 19 | 5882.2509
2030/2031 | 2008 | 1 | 17 | 20 | 6813.1314
2030/2031 | 2008 | 1 | 17 | 21 | 8138.4518
2030/2031 | 2008 | 1 | 17 | 22 | 9187.6459
2030/2031 | 2008 | 1 | 17 | 23 | 9914.0465
2030/2031 | 2008 | 1 | 17 | 24 | 10318.7888
2030/2031 | 2008 | 1 | 18 | 1 | 11391.9736
2030/2031 | 2008 | 1 | 18 | 2 | 12020.0772
2030/2031 | 2008 | 1 | 18 | 3 | 12461.706
2030/2031 | 2008 | 1 | 18 | 4 | 12366.1154
2030/2031 | 2008 | 1 | 18 | 5 | 11714.9847
2030/2031 | 2008 | 1 | 18 | 6 | 11343.4195
2030/2031 | 2008 | 1 | 18 | 7 | 10390.541
2030/2031 | 2008 | 1 | 18 | 8 | 9173.1258
2030/2031 | 2008 | 1 | 18 | 9 | 9204.1884
2030/2031 | 2008 | 1 | 18 | 10 | 9296.1791
2030/2031 | 2008 | 1 | 18 | 11 | 10005.0431
2030/2031 | 2008 | 1 | 18 | 12 | 10430.078
2030/2031 | 2008 | 1 | 18 | 13 | 11264.8494
2030/2031 | 2008 | 1 | 18 | 14 | 11398.4162
2030/2031 | 2008 | 1 | 18 | 15 | 11437.6046
2030/2031 | 2008 | 1 | 18 | 16 | 11375.9872
2030/2031 | 2008 | 1 | 18 | 17 | 11170.6055
2030/2031 | 2008 | 1 | 18 | 18 | 12053.4026
2030/2031 | 2008 | 1 | 18 | 19 | 13222.8118
2030/2031 | 2008 | 1 | 18 | 20 | 14356.7548
2030/2031 | 2008 | 1 | 18 | 21 | 16130.3781
2030/2031 | 2008 | 1 | 18 | 22 | 17405.8212
2030/2031 | 2008 | 1 | 18 | 23 | 18350.2814
2030/2031 | 2008 | 1 | 18 | 24 | 20667.3873
2030/2031 | 2008 | 1 | 19 | 1 | 22182.6046
2030/2031 | 2008 | 1 | 19 | 2 | 22741.2631
2030/2031 | 2008 | 1 | 19 | 3 | 22477.4684
2030/2031 | 2008 | 1 | 19 | 4 | 21349.071
2030/2031 | 2008 | 1 | 19 | 5 | 20885.9955
2030/2031 | 2008 | 1 | 19 | 6 | 20774.3451
2030/2031 | 2008 | 1 | 19 | 7 | 19856.3109
2030/2031 | 2008 | 1 | 19 | 8 | 18415.4444
2030/2031 | 2008 | 1 | 19 | 9 | 14226.7394
2030/2031 | 2008 | 1 | 19 | 10 | 14466.6294
2030/2031 | 2008 | 1 | 19 | 11 | 14465.5488
2030/2031 | 2008 | 1 | 19 | 12 | 13617.0033
2030/2031 | 2008 | 1 | 19 | 13 | 12725.8735
2030/2031 | 2008 | 1 | 19 | 14 | 12366.64
2030/2031 | 2008 | 1 | 19 | 15 | 11691.4248
2030/2031 | 2008 | 1 | 19 | 16 | 10715.4188
2030/2031 | 2008 | 1 | 19 | 17 | 8633.3231
2030/2031 | 2008 | 1 | 19 | 18 | 7890.6203
2030/2031 | 2008 | 1 | 19 | 19 | 9768.2387
2030/2031 | 2008 | 1 | 19 | 20 | 11673.5817
2030/2031 | 2008 | 1 | 19 | 21 | 12486.4507
2030/2031 | 2008 | 1 | 19 | 22 | 15196.9931
2030/2031 | 2008 | 1 | 19 | 23 | 18531.4152
2030/2031 | 2008 | 1 | 19 | 24 | 22223.7902
2030/2031 | 2008 | 1 | 20 | 1 | 25275.7881
2030/2031 | 2008 | 1 | 20 | 2 | 27447.1093
2030/2031 | 2008 | 1 | 20 | 3 | 28414.1382
2030/2031 | 2008 | 1 | 20 | 4 | 28946.9403
2030/2031 | 2008 | 1 | 20 | 5 | 29271.8315
2030/2031 | 2008 | 1 | 20 | 6 | 29330.0389
2030/2031 | 2008 | 1 | 20 | 7 | 29908.5047
2030/2031 | 2008 | 1 | 20 | 8 | 28590.7044
2030/2031 | 2008 | 1 | 20 | 9 | 25533.2563
2030/2031 | 2008 | 1 | 20 | 10 | 24205.5338
2030/2031 | 2008 | 1 | 20 | 11 | 26735.0337
2030/2031 | 2008 | 1 | 20 | 12 | 27979.2569
2030/2031 | 2008 | 1 | 20 | 13 | 30993.0087
2030/2031 | 2008 | 1 | 20 | 14 | 32267.4134
2030/2031 | 2008 | 1 | 20 | 15 | 31413.1129
2030/2031 | 2008 | 1 | 20 | 16 | 32165.5647
2030/2031 | 2008 | 1 | 20 | 17 | 31786.9161
2030/2031 | 2008 | 1 | 20 | 18 | 31973.7497
2030/2031 | 2008 | 1 | 20 | 19 | 32147.4621
2030/2031 | 2008 | 1 | 20 | 20 | 32801.6365
2030/2031 | 2008 | 1 | 20 | 21 | 34251.6338
2030/2031 | 2008 | 1 | 20 | 22 | 35047.6429
2030/2031 | 2008 | 1 | 20 | 23 | 34632.2178
2030/2031 | 2008 | 1 | 20 | 24 | 34445.1936
2030/2031 | 2008 | 1 | 21 | 1 | 33781.3862
2030/2031 | 2008 | 1 | 21 | 2 | 31438.5092
2030/2031 | 2008 | 1 | 21 | 3 | 29594.5994
2030/2031 | 2008 | 1 | 21 | 4 | 30821.2885
2030/2031 | 2008 | 1 | 21 | 5 | 29974.7598
2030/2031 | 2008 | 1 | 21 | 6 | 30373.6609
2030/2031 | 2008 | 1 | 21 | 7 | 30435.9013
2030/2031 | 2008 | 1 | 21 | 8 | 29181.2155
2030/2031 | 2008 | 1 | 21 | 9 | 27062.8726
2030/2031 | 2008 | 1 | 21 | 10 | 28703.9563
2030/2031 | 2008 | 1 | 21 | 11 | 28589.207
2030/2031 | 2008 | 1 | 21 | 12 | 27426.9756
2030/2031 | 2008 | 1 | 21 | 13 | 26335.6612
2030/2031 | 2008 | 1 | 21 | 14 | 26095.9392
2030/2031 | 2008 | 1 | 21 | 15 | 24836.6491
2030/2031 | 2008 | 1 | 21 | 16 | 23538.1606
2030/2031 | 2008 | 1 | 21 | 17 | 21132.0431
2030/2031 | 2008 | 1 | 21 | 18 | 21404.9574
2030/2031 | 2008 | 1 | 21 | 19 | 22352.0864
2030/2031 | 2008 | 1 | 21 | 20 | 23033.3736
2030/2031 | 2008 | 1 | 21 | 21 | 23243.2497
2030/2031 | 2008 | 1 | 21 | 22 | 21693.5356
2030/2031 | 2008 | 1 | 21 | 23 | 20833.2323
2030/2031 | 2008 | 1 | 21 | 24 | 20064.092
2030/2031 | 2008 | 1 | 22 | 1 | 19643.3253
2030/2031 | 2008 | 1 | 22 | 2 | 17916.8465
2030/2031 | 2008 | 1 | 22 | 3 | 15725.1169
2030/2031 | 2008 | 1 | 22 | 4 | 14083.4733
2030/2031 | 2008 | 1 | 22 | 5 | 13669.4171
2030/2031 | 2008 | 1 | 22 | 6 | 14504.5415
2030/2031 | 2008 | 1 | 22 | 7 | 15700.788
2030/2031 | 2008 | 1 | 22 | 8 | 16842.8471
2030/2031 | 2008 | 1 | 22 | 9 | 14328.0043
2030/2031 | 2008 | 1 | 22 | 10 | 14748.012
2030/2031 | 2008 | 1 | 22 | 11 | 14569.8792
2030/2031 | 2008 | 1 | 22 | 12 | 12956.4984
2030/2031 | 2008 | 1 | 22 | 13 | 11003.136
2030/2031 | 2008 | 1 | 22 | 14 | 9063.6413
2030/2031 | 2008 | 1 | 22 | 15 | 7512.4638
2030/2031 | 2008 | 1 | 22 | 16 | 7175.387
2030/2031 | 2008 | 1 | 22 | 17 | 6692.1416
2030/2031 | 2008 | 1 | 22 | 18 | 6749.4108
2030/2031 | 2008 | 1 | 22 | 19 | 6772.3504
2030/2031 | 2008 | 1 | 22 | 20 | 6816.9841
2030/2031 | 2008 | 1 | 22 | 21 | 6668.8927
2030/2031 | 2008 | 1 | 22 | 22 | 6503.3151
2030/2031 | 2008 | 1 | 22 | 23 | 6887.4145
2030/2031 | 2008 | 1 | 22 | 24 | 6966.7523
2030/2031 | 2008 | 1 | 23 | 1 | 8154.7173
2030/2031 | 2008 | 1 | 23 | 2 | 8913.2899
2030/2031 | 2008 | 1 | 23 | 3 | 9353.8633
2030/2031 | 2008 | 1 | 23 | 4 | 9321.728
2030/2031 | 2008 | 1 | 23 | 5 | 9085.6818
2030/2031 | 2008 | 1 | 23 | 6 | 8763.7607
2030/2031 | 2008 | 1 | 23 | 7 | 8283.4029
2030/2031 | 2008 | 1 | 23 | 8 | 7818.9499
2030/2031 | 2008 | 1 | 23 | 9 | 7295.5748
2030/2031 | 2008 | 1 | 23 | 10 | 6708.727
2030/2031 | 2008 | 1 | 23 | 11 | 6747.9672
2030/2031 | 2008 | 1 | 23 | 12 | 6615.1465
2030/2031 | 2008 | 1 | 23 | 13 | 6899.6978
2030/2031 | 2008 | 1 | 23 | 14 | 7033.3011
2030/2031 | 2008 | 1 | 23 | 15 | 7136.3996
2030/2031 | 2008 | 1 | 23 | 16 | 7578.1333
2030/2031 | 2008 | 1 | 23 | 17 | 7422.2821
2030/2031 | 2008 | 1 | 23 | 18 | 8353.0213
2030/2031 | 2008 | 1 | 23 | 19 | 10413.152
2030/2031 | 2008 | 1 | 23 | 20 | 13678.9014
2030/2031 | 2008 | 1 | 23 | 21 | 14851.1289
2030/2031 | 2008 | 1 | 23 | 22 | 16507.3588
2030/2031 | 2008 | 1 | 23 | 23 | 19207.1231
2030/2031 | 2008 | 1 | 23 | 24 | 21319.1593
2030/2031 | 2008 | 1 | 24 | 1 | 23762.3082
2030/2031 | 2008 | 1 | 24 | 2 | 24558.9571
2030/2031 | 2008 | 1 | 24 | 3 | 24907.7803
2030/2031 | 2008 | 1 | 24 | 4 | 23668.0581
2030/2031 | 2008 | 1 | 24 | 5 | 23027.1179
2030/2031 | 2008 | 1 | 24 | 6 | 22558.0293
2030/2031 | 2008 | 1 | 24 | 7 | 20372.3352
2030/2031 | 2008 | 1 | 24 | 8 | 18664.8572
2030/2031 | 2008 | 1 | 24 | 9 | 15903.9323
2030/2031 | 2008 | 1 | 24 | 10 | 17474.3209
2030/2031 | 2008 | 1 | 24 | 11 | 17951.5894
2030/2031 | 2008 | 1 | 24 | 12 | 17011.0625
2030/2031 | 2008 | 1 | 24 | 13 | 16463.2213
2030/2031 | 2008 | 1 | 24 | 14 | 16410.4533
2030/2031 | 2008 | 1 | 24 | 15 | 16336.5898
2030/2031 | 2008 | 1 | 24 | 16 | 15655.6998
2030/2031 | 2008 | 1 | 24 | 17 | 14043.632
2030/2031 | 2008 | 1 | 24 | 18 | 13396.5058
2030/2031 | 2008 | 1 | 24 | 19 | 13801.6702
2030/2031 | 2008 | 1 | 24 | 20 | 13201.9805
2030/2031 | 2008 | 1 | 24 | 21 | 13108.7512
2030/2031 | 2008 | 1 | 24 | 22 | 12704.8519
2030/2031 | 2008 | 1 | 24 | 23 | 11986.9398
2030/2031 | 2008 | 1 | 24 | 24 | 11685.1813
2030/2031 | 2008 | 1 | 25 | 1 | 12225.9662
2030/2031 | 2008 | 1 | 25 | 2 | 12284.8871
2030/2031 | 2008 | 1 | 25 | 3 | 11643.5836
2030/2031 | 2008 | 1 | 25 | 4 | 11860.9979
2030/2031 | 2008 | 1 | 25 | 5 | 12353.2143
2030/2031 | 2008 | 1 | 25 | 6 | 13120.6106
2030/2031 | 2008 | 1 | 25 | 7 | 12459.2051
2030/2031 | 2008 | 1 | 25 | 8 | 11356.4939
2030/2031 | 2008 | 1 | 25 | 9 | 10684.6946
2030/2031 | 2008 | 1 | 25 | 10 | 11799.331
2030/2031 | 2008 | 1 | 25 | 11 | 12425.0293
2030/2031 | 2008 | 1 | 25 | 12 | 12096.3313
2030/2031 | 2008 | 1 | 25 | 13 | 12757.1539
2030/2031 | 2008 | 1 | 25 | 14 | 13278.3062
2030/2031 | 2008 | 1 | 25 | 15 | 13192.0515
2030/2031 | 2008 | 1 | 25 | 16 | 13218.7598
2030/2031 | 2008 | 1 | 25 | 17 | 11479.1174
2030/2031 | 2008 | 1 | 25 | 18 | 12260.7279
2030/2031 | 2008 | 1 | 25 | 19 | 14565.8487
2030/2031 | 2008 | 1 | 25 | 20 | 16799.5661
2030/2031 | 2008 | 1 | 25 | 21 | 18679.3514
2030/2031 | 2008 | 1 | 25 | 22 | 19952.9517
2030/2031 | 2008 | 1 | 25 | 23 | 19481.3141
2030/2031 | 2008 | 1 | 25 | 24 | 19527.239
2030/2031 | 2008 | 1 | 26 | 1 | 19871.3485
2030/2031 | 2008 | 1 | 26 | 2 | 19542.1913
2030/2031 | 2008 | 1 | 26 | 3 | 19514.4938
2030/2031 | 2008 | 1 | 26 | 4 | 18974.6045
2030/2031 | 2008 | 1 | 26 | 5 | 18959.079
2030/2031 | 2008 | 1 | 26 | 6 | 20032.8999
2030/2031 | 2008 | 1 | 26 | 7 | 20673.5045
2030/2031 | 2008 | 1 | 26 | 8 | 20434.4048
2030/2031 | 2008 | 1 | 26 | 9 | 18441.0167
2030/2031 | 2008 | 1 | 26 | 10 | 13582.5497
2030/2031 | 2008 | 1 | 26 | 11 | 9870.0511
2030/2031 | 2008 | 1 | 26 | 12 | 7922.7779
2030/2031 | 2008 | 1 | 26 | 13 | 6675.4621
2030/2031 | 2008 | 1 | 26 | 14 | 4812.6931
2030/2031 | 2008 | 1 | 26 | 15 | 3175.5995
2030/2031 | 2008 | 1 | 26 | 16 | 1819.1599
2030/2031 | 2008 | 1 | 26 | 17 | 1113.1681
2030/2031 | 2008 | 1 | 26 | 18 | 1228.0723
2030/2031 | 2008 | 1 | 26 | 19 | 1573.8073
2030/2031 | 2008 | 1 | 26 | 20 | 2088.2542
2030/2031 | 2008 | 1 | 26 | 21 | 3327.4552
2030/2031 | 2008 | 1 | 26 | 22 | 4528.001
2030/2031 | 2008 | 1 | 26 | 23 | 5594.8154
2030/2031 | 2008 | 1 | 26 | 24 | 7311.1043
2030/2031 | 2008 | 1 | 27 | 1 | 9159.3827
2030/2031 | 2008 | 1 | 27 | 2 | 10100.0676
2030/2031 | 2008 | 1 | 27 | 3 | 10816.7618
2030/2031 | 2008 | 1 | 27 | 4 | 11195.459
2030/2031 | 2008 | 1 | 27 | 5 | 12037.7475
2030/2031 | 2008 | 1 | 27 | 6 | 12360.5034
2030/2031 | 2008 | 1 | 27 | 7 | 14033.2861
2030/2031 | 2008 | 1 | 27 | 8 | 15154.0241
2030/2031 | 2008 | 1 | 27 | 9 | 16115.0742
2030/2031 | 2008 | 1 | 27 | 10 | 15313.723
2030/2031 | 2008 | 1 | 27 | 11 | 12827.7654
2030/2031 | 2008 | 1 | 27 | 12 | 15732.7166
2030/2031 | 2008 | 1 | 27 | 13 | 19551.7242
2030/2031 | 2008 | 1 | 27 | 14 | 22370.5374
2030/2031 | 2008 | 1 | 27 | 15 | 24345.8832
2030/2031 | 2008 | 1 | 27 | 16 | 25738.8407
2030/2031 | 2008 | 1 | 27 | 17 | 26259.7437
2030/2031 | 2008 | 1 | 27 | 18 | 28873.0896
2030/2031 | 2008 | 1 | 27 | 19 | 31023.1185
2030/2031 | 2008 | 1 | 27 | 20 | 32185.8864
2030/2031 | 2008 | 1 | 27 | 21 | 32263.3371
2030/2031 | 2008 | 1 | 27 | 22 | 32772.4885
2030/2031 | 2008 | 1 | 27 | 23 | 32713.6413
2030/2031 | 2008 | 1 | 27 | 24 | 32551.7761
2030/2031 | 2008 | 1 | 28 | 1 | 30621.0073
2030/2031 | 2008 | 1 | 28 | 2 | 29665.6075
2030/2031 | 2008 | 1 | 28 | 3 | 29759.5191
2030/2031 | 2008 | 1 | 28 | 4 | 30056.6022
2030/2031 | 2008 | 1 | 28 | 5 | 31029.4182
2030/2031 | 2008 | 1 | 28 | 6 | 31535.7832
2030/2031 | 2008 | 1 | 28 | 7 | 31727.0463
2030/2031 | 2008 | 1 | 28 | 8 | 33541.8705
2030/2031 | 2008 | 1 | 28 | 9 | 33936.6787
2030/2031 | 2008 | 1 | 28 | 10 | 35272.6234
2030/2031 | 2008 | 1 | 28 | 11 | 35356.9064
2030/2031 | 2008 | 1 | 28 | 12 | 35123.5568
2030/2031 | 2008 | 1 | 28 | 13 | 35373.618
2030/2031 | 2008 | 1 | 28 | 14 | 34787.2201
2030/2031 | 2008 | 1 | 28 | 15 | 34756.9119
2030/2031 | 2008 | 1 | 28 | 16 | 34307.807
2030/2031 | 2008 | 1 | 28 | 17 | 33203.0124
2030/2031 | 2008 | 1 | 28 | 18 | 31938.0874
2030/2031 | 2008 | 1 | 28 | 19 | 33314.1342
2030/2031 | 2008 | 1 | 28 | 20 | 33810.8206
2030/2031 | 2008 | 1 | 28 | 21 | 35078.846
2030/2031 | 2008 | 1 | 28 | 22 | 35375.9735
2030/2031 | 2008 | 1 | 28 | 23 | 35224.4056
2030/2031 | 2008 | 1 | 28 | 24 | 35205.1934
2030/2031 | 2008 | 1 | 29 | 1 | 35976.4673
2030/2031 | 2008 | 1 | 29 | 2 | 35952.4747
2030/2031 | 2008 | 1 | 29 | 3 | 35512.5654
2030/2031 | 2008 | 1 | 29 | 4 | 35350.1229
2030/2031 | 2008 | 1 | 29 | 5 | 34171.0364
2030/2031 | 2008 | 1 | 29 | 6 | 33948.9127
2030/2031 | 2008 | 1 | 29 | 7 | 31041.1381
2030/2031 | 2008 | 1 | 29 | 8 | 29997.6532
2030/2031 | 2008 | 1 | 29 | 9 | 29355.152
2030/2031 | 2008 | 1 | 29 | 10 | 28184.4877
2030/2031 | 2008 | 1 | 29 | 11 | 26686.7799
2030/2031 | 2008 | 1 | 29 | 12 | 27799.2606
2030/2031 | 2008 | 1 | 29 | 13 | 29716.3194
2030/2031 | 2008 | 1 | 29 | 14 | 29773.9728
2030/2031 | 2008 | 1 | 29 | 15 | 28159.0335
2030/2031 | 2008 | 1 | 29 | 16 | 23813.4499
2030/2031 | 2008 | 1 | 29 | 17 | 17056.5735
2030/2031 | 2008 | 1 | 29 | 18 | 13055.5129
2030/2031 | 2008 | 1 | 29 | 19 | 13019.6285
2030/2031 | 2008 | 1 | 29 | 20 | 14165.1097
2030/2031 | 2008 | 1 | 29 | 21 | 17713.066
2030/2031 | 2008 | 1 | 29 | 22 | 22906.224
2030/2031 | 2008 | 1 | 29 | 23 | 28080.5975
2030/2031 | 2008 | 1 | 29 | 24 | 31296.3446
2030/2031 | 2008 | 1 | 30 | 1 | 33133.3089
2030/2031 | 2008 | 1 | 30 | 2 | 33264.6479
2030/2031 | 2008 | 1 | 30 | 3 | 33816.9218
2030/2031 | 2008 | 1 | 30 | 4 | 32655.2249
2030/2031 | 2008 | 1 | 30 | 5 | 32442.9933
2030/2031 | 2008 | 1 | 30 | 6 | 31965.4876
2030/2031 | 2008 | 1 | 30 | 7 | 31284.2184
2030/2031 | 2008 | 1 | 30 | 8 | 30291.2449
2030/2031 | 2008 | 1 | 30 | 9 | 28367.3106
2030/2031 | 2008 | 1 | 30 | 10 | 28669.113
2030/2031 | 2008 | 1 | 30 | 11 | 29669.9223
2030/2031 | 2008 | 1 | 30 | 12 | 30834.2518
2030/2031 | 2008 | 1 | 30 | 13 | 31278.9053
2030/2031 | 2008 | 1 | 30 | 14 | 30864.3392
2030/2031 | 2008 | 1 | 30 | 15 | 29783.5426
2030/2031 | 2008 | 1 | 30 | 16 | 29707.8976
2030/2031 | 2008 | 1 | 30 | 17 | 29228.8791
2030/2031 | 2008 | 1 | 30 | 18 | 27889.179
2030/2031 | 2008 | 1 | 30 | 19 | 29028.8128
2030/2031 | 2008 | 1 | 30 | 20 | 29732.0894
2030/2031 | 2008 | 1 | 30 | 21 | 29746.5078
2030/2031 | 2008 | 1 | 30 | 22 | 29405.2908
2030/2031 | 2008 | 1 | 30 | 23 | 28095.4332
2030/2031 | 2008 | 1 | 30 | 24 | 27941.7462
2030/2031 | 2008 | 1 | 31 | 1 | 29721.3949
2030/2031 | 2008 | 1 | 31 | 2 | 28507.7662
2030/2031 | 2008 | 1 | 31 | 3 | 27141.8998
2030/2031 | 2008 | 1 | 31 | 4 | 27100.9925
2030/2031 | 2008 | 1 | 31 | 5 | 27761.835
2030/2031 | 2008 | 1 | 31 | 6 | 28832.3529
2030/2031 | 2008 | 1 | 31 | 7 | 30912.4491
2030/2031 | 2008 | 1 | 31 | 8 | 32860.6002
2030/2031 | 2008 | 1 | 31 | 9 | 32509.7129
2030/2031 | 2008 | 1 | 31 | 10 | 31983.9957
2030/2031 | 2008 | 1 | 31 | 11 | 32727.2553
2030/2031 | 2008 | 1 | 31 | 12 | 33327.6287
2030/2031 | 2008 | 1 | 31 | 13 | 35153.349
2030/2031 | 2008 | 1 | 31 | 14 | 35159.3518
2030/2031 | 2008 | 1 | 31 | 15 | 34383.0469
2030/2031 | 2008 | 1 | 31 | 16 | 35163.6634
2030/2031 | 2008 | 1 | 31 | 17 | 29652.6643
2030/2031 | 2008 | 1 | 31 | 18 | 30167.032
2030/2031 | 2008 | 1 | 31 | 19 | 26090.233
2030/2031 | 2008 | 1 | 31 | 20 | 22090.1554
2030/2031 | 2008 | 1 | 31 | 21 | 16261.9995
2030/2031 | 2008 | 1 | 31 | 22 | 12839.3055
2030/2031 | 2008 | 1 | 31 | 23 | 12330.2714
2030/2031 | 2008 | 1 | 31 | 24 | 13089.2374
2026 | 2008 | 5 | 1 | 1 | 34623.3121
2026 | 2008 | 5 | 1 | 2 | 34191.4048
2026 | 2008 | 5 | 1 | 3 | 33495.7005
2026 | 2008 | 5 | 1 | 4 | 32251.2074
2026 | 2008 | 5 | 1 | 5 | 31647.837
2026 | 2008 | 5 | 1 | 6 | 31486.4557
2026 | 2008 | 5 | 1 | 7 | 30373.3743
2026 | 2008 | 5 | 1 | 8 | 28519.5804
2026 | 2008 | 5 | 1 | 9 | 28131.0567
2026 | 2008 | 5 | 1 | 10 | 28029.4099
2026 | 2008 | 5 | 1 | 11 | 27925.506
2026 | 2008 | 5 | 1 | 12 | 26942.354
2026 | 2008 | 5 | 1 | 13 | 26130.4962
2026 | 2008 | 5 | 1 | 14 | 25613.431
2026 | 2008 | 5 | 1 | 15 | 25224.9399
2026 | 2008 | 5 | 1 | 16 | 24665.561
2026 | 2008 | 5 | 1 | 17 | 26402.4985
2026 | 2008 | 5 | 1 | 18 | 26785.3367
2026 | 2008 | 5 | 1 | 19 | 28174.6928
2026 | 2008 | 5 | 1 | 20 | 28541.336
2026 | 2008 | 5 | 1 | 21 | 29459.0519
2026 | 2008 | 5 | 1 | 22 | 30733.9783
2026 | 2008 | 5 | 1 | 23 | 30604.78
2026 | 2008 | 5 | 1 | 24 | 30391.5409
2026 | 2008 | 5 | 2 | 1 | 30725.2118
2026 | 2008 | 5 | 2 | 2 | 29563.0845
2026 | 2008 | 5 | 2 | 3 | 29682.5821
2026 | 2008 | 5 | 2 | 4 | 29439.2568
2026 | 2008 | 5 | 2 | 5 | 28910.9487
2026 | 2008 | 5 | 2 | 6 | 27193.2442
2026 | 2008 | 5 | 2 | 7 | 25215.7183
2026 | 2008 | 5 | 2 | 8 | 18852.2288
2026 | 2008 | 5 | 2 | 9 | 13437.1833
2026 | 2008 | 5 | 2 | 10 | 10096.4214
2026 | 2008 | 5 | 2 | 11 | 6764.9549
2026 | 2008 | 5 | 2 | 12 | 6538.8656
2026 | 2008 | 5 | 2 | 13 | 8666.2985
2026 | 2008 | 5 | 2 | 14 | 11334.3701
2026 | 2008 | 5 | 2 | 15 | 13844.5355
2026 | 2008 | 5 | 2 | 16 | 14642.768
2026 | 2008 | 5 | 2 | 17 | 14913.6882
2026 | 2008 | 5 | 2 | 18 | 13982.0854
2026 | 2008 | 5 | 2 | 19 | 11230.2858
2026 | 2008 | 5 | 2 | 20 | 9834.6634
2026 | 2008 | 5 | 2 | 21 | 9770.7684
2026 | 2008 | 5 | 2 | 22 | 10584.5411
2026 | 2008 | 5 | 2 | 23 | 12403.5983
2026 | 2008 | 5 | 2 | 24 | 15465.1058
2026 | 2008 | 5 | 3 | 1 | 19166.7308
2026 | 2008 | 5 | 3 | 2 | 21456.6183
2026 | 2008 | 5 | 3 | 3 | 22636.7869
2026 | 2008 | 5 | 3 | 4 | 23504.6679
2026 | 2008 | 5 | 3 | 5 | 23908.7016
2026 | 2008 | 5 | 3 | 6 | 24007.1492
2026 | 2008 | 5 | 3 | 7 | 22999.0099
2026 | 2008 | 5 | 3 | 8 | 22608.078
2026 | 2008 | 5 | 3 | 9 | 23686.3637
2026 | 2008 | 5 | 3 | 10 | 22930.2881
2026 | 2008 | 5 | 3 | 11 | 18061.6273
2026 | 2008 | 5 | 3 | 12 | 14332.384
2026 | 2008 | 5 | 3 | 13 | 12392.8957
2026 | 2008 | 5 | 3 | 14 | 11114.8601
2026 | 2008 | 5 | 3 | 15 | 10202.0979
2026 | 2008 | 5 | 3 | 16 | 9377.7113
2026 | 2008 | 5 | 3 | 17 | 9173.4696
2026 | 2008 | 5 | 3 | 18 | 9290.2016
2026 | 2008 | 5 | 3 | 19 | 8847.8206
2026 | 2008 | 5 | 3 | 20 | 8438.2113
2026 | 2008 | 5 | 3 | 21 | 8787.3245
2026 | 2008 | 5 | 3 | 22 | 9781.7094
2026 | 2008 | 5 | 3 | 23 | 11579.1167
2026 | 2008 | 5 | 3 | 24 | 12129.1884
2026 | 2008 | 5 | 4 | 1 | 12306.5277
2026 | 2008 | 5 | 4 | 2 | 12330.345
2026 | 2008 | 5 | 4 | 3 | 12164.044
2026 | 2008 | 5 | 4 | 4 | 12092.3391
2026 | 2008 | 5 | 4 | 5 | 12384.696
2026 | 2008 | 5 | 4 | 6 | 12244.1768
2026 | 2008 | 5 | 4 | 7 | 12733.251
2026 | 2008 | 5 | 4 | 8 | 10171.9567
2026 | 2008 | 5 | 4 | 9 | 9728.1732
2026 | 2008 | 5 | 4 | 10 | 11649.1739
2026 | 2008 | 5 | 4 | 11 | 12986.1589
2026 | 2008 | 5 | 4 | 12 | 13688.6226
2026 | 2008 | 5 | 4 | 13 | 14647.098
2026 | 2008 | 5 | 4 | 14 | 15617.9129
2026 | 2008 | 5 | 4 | 15 | 16281.0103
2026 | 2008 | 5 | 4 | 16 | 16655.7724
2026 | 2008 | 5 | 4 | 17 | 18504.009
2026 | 2008 | 5 | 4 | 18 | 19934.4275
2026 | 2008 | 5 | 4 | 19 | 21148.5984
2026 | 2008 | 5 | 4 | 20 | 20598.5517
2026 | 2008 | 5 | 4 | 21 | 21264.5939
2026 | 2008 | 5 | 4 | 22 | 22221.5174
2026 | 2008 | 5 | 4 | 23 | 21990.2508
2026 | 2008 | 5 | 4 | 24 | 20523.7168
2026 | 2008 | 5 | 5 | 1 | 19202.9826
2026 | 2008 | 5 | 5 | 2 | 18849.6154
2026 | 2008 | 5 | 5 | 3 | 18641.7789
2026 | 2008 | 5 | 5 | 4 | 17548.8134
2026 | 2008 | 5 | 5 | 5 | 15721.8597
2026 | 2008 | 5 | 5 | 6 | 14456.9824
2026 | 2008 | 5 | 5 | 7 | 13123.3183
2026 | 2008 | 5 | 5 | 8 | 13582.3158
2026 | 2008 | 5 | 5 | 9 | 16224.5104
2026 | 2008 | 5 | 5 | 10 | 17835.2641
2026 | 2008 | 5 | 5 | 11 | 18722.9866
2026 | 2008 | 5 | 5 | 12 | 19655.2648
2026 | 2008 | 5 | 5 | 13 | 19881.4524
2026 | 2008 | 5 | 5 | 14 | 20714.8041
2026 | 2008 | 5 | 5 | 15 | 20128.5254
2026 | 2008 | 5 | 5 | 16 | 19366.982
2026 | 2008 | 5 | 5 | 17 | 21833.1976
2026 | 2008 | 5 | 5 | 18 | 23802.6391
2026 | 2008 | 5 | 5 | 19 | 25430.9325
2026 | 2008 | 5 | 5 | 20 | 27216.0674
2026 | 2008 | 5 | 5 | 21 | 28728.0336
2026 | 2008 | 5 | 5 | 22 | 29045.4665
2026 | 2008 | 5 | 5 | 23 | 28822.3322
2026 | 2008 | 5 | 5 | 24 | 27498.0194
2026 | 2008 | 5 | 6 | 1 | 25445.2932
2026 | 2008 | 5 | 6 | 2 | 22565.6892
2026 | 2008 | 5 | 6 | 3 | 19593.4714
2026 | 2008 | 5 | 6 | 4 | 17174.222
2026 | 2008 | 5 | 6 | 5 | 16952.6743
2026 | 2008 | 5 | 6 | 6 | 18263.4748
2026 | 2008 | 5 | 6 | 7 | 19260.7448
2026 | 2008 | 5 | 6 | 8 | 21492.4777
2026 | 2008 | 5 | 6 | 9 | 25413.5978
2026 | 2008 | 5 | 6 | 10 | 26881.3163
2026 | 2008 | 5 | 6 | 11 | 26694.6082
2026 | 2008 | 5 | 6 | 12 | 27054.7262
2026 | 2008 | 5 | 6 | 13 | 28583.0475
2026 | 2008 | 5 | 6 | 14 | 30567.5308
2026 | 2008 | 5 | 6 | 15 | 31534.7215
2026 | 2008 | 5 | 6 | 16 | 31794.4591
2026 | 2008 | 5 | 6 | 17 | 31157.1768
2026 | 2008 | 5 | 6 | 18 | 31473.8835
2026 | 2008 | 5 | 6 | 19 | 30492.7175
2026 | 2008 | 5 | 6 | 20 | 30824.4256
2026 | 2008 | 5 | 6 | 21 | 30052.4494
2026 | 2008 | 5 | 6 | 22 | 30700.7913
2026 | 2008 | 5 | 6 | 23 | 30894.3217
2026 | 2008 | 5 | 6 | 24 | 29578.8373
2026 | 2008 | 5 | 7 | 1 | 28769.6284
2026 | 2008 | 5 | 7 | 2 | 28570.0862
2026 | 2008 | 5 | 7 | 3 | 28560.0105
2026 | 2008 | 5 | 7 | 4 | 28473.9671
2026 | 2008 | 5 | 7 | 5 | 28669.3043
2026 | 2008 | 5 | 7 | 6 | 28613.6751
2026 | 2008 | 5 | 7 | 7 | 28716.439
2026 | 2008 | 5 | 7 | 8 | 28971.6257
2026 | 2008 | 5 | 7 | 9 | 29985.2245
2026 | 2008 | 5 | 7 | 10 | 29219.726
2026 | 2008 | 5 | 7 | 11 | 28626.6714
2026 | 2008 | 5 | 7 | 12 | 27056.7198
2026 | 2008 | 5 | 7 | 13 | 27037.0172
2026 | 2008 | 5 | 7 | 14 | 27769.4315
2026 | 2008 | 5 | 7 | 15 | 29209.4079
2026 | 2008 | 5 | 7 | 16 | 29306.4197
2026 | 2008 | 5 | 7 | 17 | 29990.0644
2026 | 2008 | 5 | 7 | 18 | 29188.8872
2026 | 2008 | 5 | 7 | 19 | 26000.8219
2026 | 2008 | 5 | 7 | 20 | 24850.7992
2026 | 2008 | 5 | 7 | 21 | 22714.7642
2026 | 2008 | 5 | 7 | 22 | 20709.2523
2026 | 2008 | 5 | 7 | 23 | 19928.6377
2026 | 2008 | 5 | 7 | 24 | 18582.7699
2026 | 2008 | 5 | 8 | 1 | 16294.0686
2026 | 2008 | 5 | 8 | 2 | 15454.5923
2026 | 2008 | 5 | 8 | 3 | 12601.2317
2026 | 2008 | 5 | 8 | 4 | 10294.9264
2026 | 2008 | 5 | 8 | 5 | 8952.1073
2026 | 2008 | 5 | 8 | 6 | 7011.3272
2026 | 2008 | 5 | 8 | 7 | 6182.9854
2026 | 2008 | 5 | 8 | 8 | 4143.3811
2026 | 2008 | 5 | 8 | 9 | 3115.1651
2026 | 2008 | 5 | 8 | 10 | 2325.458
2026 | 2008 | 5 | 8 | 11 | 2593.6778
2026 | 2008 | 5 | 8 | 12 | 3757.047
2026 | 2008 | 5 | 8 | 13 | 5258.5808
2026 | 2008 | 5 | 8 | 14 | 7230.1095
2026 | 2008 | 5 | 8 | 15 | 8900.1585
2026 | 2008 | 5 | 8 | 16 | 11554.0982
2026 | 2008 | 5 | 8 | 17 | 14760.4035
2026 | 2008 | 5 | 8 | 18 | 17994.5012
2026 | 2008 | 5 | 8 | 19 | 18372.7889
2026 | 2008 | 5 | 8 | 20 | 20687.2595
2026 | 2008 | 5 | 8 | 21 | 23343.6285
2026 | 2008 | 5 | 8 | 22 | 26986.7691
2026 | 2008 | 5 | 8 | 23 | 27475.0901
2026 | 2008 | 5 | 8 | 24 | 27012.6053
2026 | 2008 | 5 | 9 | 1 | 28046.8045
2026 | 2008 | 5 | 9 | 2 | 27060.0467
2026 | 2008 | 5 | 9 | 3 | 26553.5499
2026 | 2008 | 5 | 9 | 4 | 24699.3731
2026 | 2008 | 5 | 9 | 5 | 22959.5836
2026 | 2008 | 5 | 9 | 6 | 21048.4598
2026 | 2008 | 5 | 9 | 7 | 17157.0066
2026 | 2008 | 5 | 9 | 8 | 11811.2819
2026 | 2008 | 5 | 9 | 9 | 8047.9315
2026 | 2008 | 5 | 9 | 10 | 6541.9125
2026 | 2008 | 5 | 9 | 11 | 6070.6093
2026 | 2008 | 5 | 9 | 12 | 6159.8628
2026 | 2008 | 5 | 9 | 13 | 5916.2474
2026 | 2008 | 5 | 9 | 14 | 5662.5332
2026 | 2008 | 5 | 9 | 15 | 5404.8838
2026 | 2008 | 5 | 9 | 16 | 5992.551
2026 | 2008 | 5 | 9 | 17 | 6896.5689
2026 | 2008 | 5 | 9 | 18 | 7886.5579
2026 | 2008 | 5 | 9 | 19 | 8563.087
2026 | 2008 | 5 | 9 | 20 | 10154.8598
2026 | 2008 | 5 | 9 | 21 | 13489.8979
2026 | 2008 | 5 | 9 | 22 | 17291.4071
2026 | 2008 | 5 | 9 | 23 | 20404.5018
2026 | 2008 | 5 | 9 | 24 | 22170.6252
2026 | 2008 | 5 | 10 | 1 | 23841.9625
2026 | 2008 | 5 | 10 | 2 | 23981.2049
2026 | 2008 | 5 | 10 | 3 | 23169.7579
2026 | 2008 | 5 | 10 | 4 | 22482.1592
2026 | 2008 | 5 | 10 | 5 | 22546.648
2026 | 2008 | 5 | 10 | 6 | 23008.4346
2026 | 2008 | 5 | 10 | 7 | 22099.3801
2026 | 2008 | 5 | 10 | 8 | 20659.9118
2026 | 2008 | 5 | 10 | 9 | 20818.7559
2026 | 2008 | 5 | 10 | 10 | 21535.8762
2026 | 2008 | 5 | 10 | 11 | 21819.6675
2026 | 2008 | 5 | 10 | 12 | 23545.9625
2026 | 2008 | 5 | 10 | 13 | 24528.8669
2026 | 2008 | 5 | 10 | 14 | 23827.0215
2026 | 2008 | 5 | 10 | 15 | 23149.7717
2026 | 2008 | 5 | 10 | 16 | 22248.3504
2026 | 2008 | 5 | 10 | 17 | 21245.3631
2026 | 2008 | 5 | 10 | 18 | 19562.8953
2026 | 2008 | 5 | 10 | 19 | 17365.1634
2026 | 2008 | 5 | 10 | 20 | 16453.9458
2026 | 2008 | 5 | 10 | 21 | 16214.731
2026 | 2008 | 5 | 10 | 22 | 17152.7593
2026 | 2008 | 5 | 10 | 23 | 20764.29
2026 | 2008 | 5 | 10 | 24 | 23421.2661
2026 | 2008 | 5 | 11 | 1 | 25436.8587
2026 | 2008 | 5 | 11 | 2 | 26351.5593
2026 | 2008 | 5 | 11 | 3 | 26466.7437
2026 | 2008 | 5 | 11 | 4 | 25432.4424
2026 | 2008 | 5 | 11 | 5 | 24212.6967
2026 | 2008 | 5 | 11 | 6 | 23006.2513
2026 | 2008 | 5 | 11 | 7 | 21341.6319
2026 | 2008 | 5 | 11 | 8 | 20017.6698
2026 | 2008 | 5 | 11 | 9 | 20390.4613
2026 | 2008 | 5 | 11 | 10 | 18455.5241
2026 | 2008 | 5 | 11 | 11 | 14459.8529
2026 | 2008 | 5 | 11 | 12 | 13528.4192
2026 | 2008 | 5 | 11 | 13 | 13000.2631
2026 | 2008 | 5 | 11 | 14 | 12462.9424
2026 | 2008 | 5 | 11 | 15 | 11917.0777
2026 | 2008 | 5 | 11 | 16 | 11245.8304
2026 | 2008 | 5 | 11 | 17 | 11192.5796
2026 | 2008 | 5 | 11 | 18 | 11214.0937
2026 | 2008 | 5 | 11 | 19 | 11184.338
2026 | 2008 | 5 | 11 | 20 | 11176.9441
2026 | 2008 | 5 | 11 | 21 | 12293.7112
2026 | 2008 | 5 | 11 | 22 | 14101.6637
2026 | 2008 | 5 | 11 | 23 | 15949.5472
2026 | 2008 | 5 | 11 | 24 | 16713.1932
2026 | 2008 | 5 | 12 | 1 | 18613.9134
2026 | 2008 | 5 | 12 | 2 | 19846.3177
2026 | 2008 | 5 | 12 | 3 | 19947.286
2026 | 2008 | 5 | 12 | 4 | 20635.0156
2026 | 2008 | 5 | 12 | 5 | 21247.8452
2026 | 2008 | 5 | 12 | 6 | 22225.0714
2026 | 2008 | 5 | 12 | 7 | 22951.7607
2026 | 2008 | 5 | 12 | 8 | 21961.5377
2026 | 2008 | 5 | 12 | 9 | 21880.0826
2026 | 2008 | 5 | 12 | 10 | 25396.7922
2026 | 2008 | 5 | 12 | 11 | 26899.5896
2026 | 2008 | 5 | 12 | 12 | 27996.2325
2026 | 2008 | 5 | 12 | 13 | 28546.2124
2026 | 2008 | 5 | 12 | 14 | 29908.1199
2026 | 2008 | 5 | 12 | 15 | 30571.7185
2026 | 2008 | 5 | 12 | 16 | 31934.8107
2026 | 2008 | 5 | 12 | 17 | 32800.7242
2026 | 2008 | 5 | 12 | 18 | 33357.7
2026 | 2008 | 5 | 12 | 19 | 33053.2852
2026 | 2008 | 5 | 12 | 20 | 31353.5309
2026 | 2008 | 5 | 12 | 21 | 30164.0896
2026 | 2008 | 5 | 12 | 22 | 30772.8172
2026 | 2008 | 5 | 12 | 23 | 31254.3959
2026 | 2008 | 5 | 12 | 24 | 31665.1889
2026 | 2008 | 5 | 13 | 1 | 32060.7223
2026 | 2008 | 5 | 13 | 2 | 32358.6322
2026 | 2008 | 5 | 13 | 3 | 31678.1012
2026 | 2008 | 5 | 13 | 4 | 30042.6188
2026 | 2008 | 5 | 13 | 5 | 29372.2695
2026 | 2008 | 5 | 13 | 6 | 27522.7711
2026 | 2008 | 5 | 13 | 7 | 25931.8783
2026 | 2008 | 5 | 13 | 8 | 24212.5001
2026 | 2008 | 5 | 13 | 9 | 23704.4655
2026 | 2008 | 5 | 13 | 10 | 21750.1469
2026 | 2008 | 5 | 13 | 11 | 17799.1367
2026 | 2008 | 5 | 13 | 12 | 14473.9609
2026 | 2008 | 5 | 13 | 13 | 12614.7833
2026 | 2008 | 5 | 13 | 14 | 11291.5263
2026 | 2008 | 5 | 13 | 15 | 10946.6569
2026 | 2008 | 5 | 13 | 16 | 11331.9205
2026 | 2008 | 5 | 13 | 17 | 12862.3408
2026 | 2008 | 5 | 13 | 18 | 14830.6704
2026 | 2008 | 5 | 13 | 19 | 18012.6749
2026 | 2008 | 5 | 13 | 20 | 20087.8902
2026 | 2008 | 5 | 13 | 21 | 23606.5344
2026 | 2008 | 5 | 13 | 22 | 22508.0723
2026 | 2008 | 5 | 13 | 23 | 22587.7684
2026 | 2008 | 5 | 13 | 24 | 23225.0638
2026 | 2008 | 5 | 14 | 1 | 23292.1593
2026 | 2008 | 5 | 14 | 2 | 22235.1331
2026 | 2008 | 5 | 14 | 3 | 20048.7404
2026 | 2008 | 5 | 14 | 4 | 18370.8873
2026 | 2008 | 5 | 14 | 5 | 17561.3671
2026 | 2008 | 5 | 14 | 6 | 16870.0392
2026 | 2008 | 5 | 14 | 7 | 16782.1044
2026 | 2008 | 5 | 14 | 8 | 16657.0215
2026 | 2008 | 5 | 14 | 9 | 18122.2989
2026 | 2008 | 5 | 14 | 10 | 17875.4462
2026 | 2008 | 5 | 14 | 11 | 16318.968
2026 | 2008 | 5 | 14 | 12 | 14654.7889
2026 | 2008 | 5 | 14 | 13 | 13001.3922
2026 | 2008 | 5 | 14 | 14 | 11559.5207
2026 | 2008 | 5 | 14 | 15 | 11821.5504
2026 | 2008 | 5 | 14 | 16 | 12191.8206
2026 | 2008 | 5 | 14 | 17 | 12442.5665
2026 | 2008 | 5 | 14 | 18 | 13787.2351
2026 | 2008 | 5 | 14 | 19 | 13743.0901
2026 | 2008 | 5 | 14 | 20 | 12170.199
2026 | 2008 | 5 | 14 | 21 | 12441.2237
2026 | 2008 | 5 | 14 | 22 | 11735.4856
2026 | 2008 | 5 | 14 | 23 | 9693.3256
2026 | 2008 | 5 | 14 | 24 | 7029.857
2026 | 2008 | 5 | 15 | 1 | 5677.1733
2026 | 2008 | 5 | 15 | 2 | 4432.1424
2026 | 2008 | 5 | 15 | 3 | 4510.0957
2026 | 2008 | 5 | 15 | 4 | 5484.9181
2026 | 2008 | 5 | 15 | 5 | 6555.2893
2026 | 2008 | 5 | 15 | 6 | 6474.1823
2026 | 2008 | 5 | 15 | 7 | 9391.8541
2026 | 2008 | 5 | 15 | 8 | 9701.353
2026 | 2008 | 5 | 15 | 9 | 11810.6458
2026 | 2008 | 5 | 15 | 10 | 11068.3106
2026 | 2008 | 5 | 15 | 11 | 9252.9619
2026 | 2008 | 5 | 15 | 12 | 8406.3508
2026 | 2008 | 5 | 15 | 13 | 8613.5662
2026 | 2008 | 5 | 15 | 14 | 8255.1278
2026 | 2008 | 5 | 15 | 15 | 6889.8105
2026 | 2008 | 5 | 15 | 16 | 6773.1175
2026 | 2008 | 5 | 15 | 17 | 6683.5867
2026 | 2008 | 5 | 15 | 18 | 7094.6931
2026 | 2008 | 5 | 15 | 19 | 8379.0931
2026 | 2008 | 5 | 15 | 20 | 9438.3696
2026 | 2008 | 5 | 15 | 21 | 11982.592
2026 | 2008 | 5 | 15 | 22 | 11366.9828
2026 | 2008 | 5 | 15 | 23 | 10552.7576
2026 | 2008 | 5 | 15 | 24 | 9788.3361
2026 | 2008 | 5 | 16 | 1 | 8618.3172
2026 | 2008 | 5 | 16 | 2 | 7908.1637
2026 | 2008 | 5 | 16 | 3 | 8120.4338
2026 | 2008 | 5 | 16 | 4 | 8482.7965
2026 | 2008 | 5 | 16 | 5 | 9722.0137
2026 | 2008 | 5 | 16 | 6 | 11305.9209
2026 | 2008 | 5 | 16 | 7 | 13469.5212
2026 | 2008 | 5 | 16 | 8 | 13476.6427
2026 | 2008 | 5 | 16 | 9 | 12480.6283
2026 | 2008 | 5 | 16 | 10 | 16615.2798
2026 | 2008 | 5 | 16 | 11 | 17250.1694
2026 | 2008 | 5 | 16 | 12 | 16355.6168
2026 | 2008 | 5 | 16 | 13 | 14574.3657
2026 | 2008 | 5 | 16 | 14 | 12518.3595
2026 | 2008 | 5 | 16 | 15 | 10844.6686
2026 | 2008 | 5 | 16 | 16 | 9433.0665
2026 | 2008 | 5 | 16 | 17 | 9025.1226
2026 | 2008 | 5 | 16 | 18 | 8013.8597
2026 | 2008 | 5 | 16 | 19 | 6203.0468
2026 | 2008 | 5 | 16 | 20 | 4024.3684
2026 | 2008 | 5 | 16 | 21 | 2911.5679
2026 | 2008 | 5 | 16 | 22 | 2302.5547
2026 | 2008 | 5 | 16 | 23 | 2155.2148
2026 | 2008 | 5 | 16 | 24 | 2320.8049
2026 | 2008 | 5 | 17 | 1 | 3042.146
2026 | 2008 | 5 | 17 | 2 | 4310.1384
2026 | 2008 | 5 | 17 | 3 | 5863.6281
2026 | 2008 | 5 | 17 | 4 | 8280.864
2026 | 2008 | 5 | 17 | 5 | 9876.1948
2026 | 2008 | 5 | 17 | 6 | 10330.0786
2026 | 2008 | 5 | 17 | 7 | 10193.1838
2026 | 2008 | 5 | 17 | 8 | 7784.6135
2026 | 2008 | 5 | 17 | 9 | 7156.7267
2026 | 2008 | 5 | 17 | 10 | 4465.61
2026 | 2008 | 5 | 17 | 11 | 4887.4744
2026 | 2008 | 5 | 17 | 12 | 3804.2077
2026 | 2008 | 5 | 17 | 13 | 3412.6692
2026 | 2008 | 5 | 17 | 14 | 3907.0992
2026 | 2008 | 5 | 17 | 15 | 3909.6402
2026 | 2008 | 5 | 17 | 16 | 3953.8823
2026 | 2008 | 5 | 17 | 17 | 3720.4355
2026 | 2008 | 5 | 17 | 18 | 3950.9855
2026 | 2008 | 5 | 17 | 19 | 4028.4478
2026 | 2008 | 5 | 17 | 20 | 3709.2631
2026 | 2008 | 5 | 17 | 21 | 4662.6352
2026 | 2008 | 5 | 17 | 22 | 5897.8058
2026 | 2008 | 5 | 17 | 23 | 7422.2757
2026 | 2008 | 5 | 17 | 24 | 8198.9944
2026 | 2008 | 5 | 18 | 1 | 9667.9335
2026 | 2008 | 5 | 18 | 2 | 10666.4851
2026 | 2008 | 5 | 18 | 3 | 13085.0287
2026 | 2008 | 5 | 18 | 4 | 14674.3498
2026 | 2008 | 5 | 18 | 5 | 16283.8985
2026 | 2008 | 5 | 18 | 6 | 17365.1123
2026 | 2008 | 5 | 18 | 7 | 17991.237
2026 | 2008 | 5 | 18 | 8 | 13188.3569
2026 | 2008 | 5 | 18 | 9 | 9287.5903
2026 | 2008 | 5 | 18 | 10 | 6118.932
2026 | 2008 | 5 | 18 | 11 | 6527.2502
2026 | 2008 | 5 | 18 | 12 | 5990.5549
2026 | 2008 | 5 | 18 | 13 | 5062.2442
2026 | 2008 | 5 | 18 | 14 | 4356.3469
2026 | 2008 | 5 | 18 | 15 | 3391.8177
2026 | 2008 | 5 | 18 | 16 | 2680.5567
2026 | 2008 | 5 | 18 | 17 | 2305.0916
2026 | 2008 | 5 | 18 | 18 | 1986.0761
2026 | 2008 | 5 | 18 | 19 | 1686.8792
2026 | 2008 | 5 | 18 | 20 | 2264.7183
2026 | 2008 | 5 | 18 | 21 | 3906.8108
2026 | 2008 | 5 | 18 | 22 | 7737.8379
2026 | 2008 | 5 | 18 | 23 | 13547.9117
2026 | 2008 | 5 | 18 | 24 | 18433.9783
2026 | 2008 | 5 | 19 | 1 | 22522.9494
2026 | 2008 | 5 | 19 | 2 | 25650.4741
2026 | 2008 | 5 | 19 | 3 | 27071.642
2026 | 2008 | 5 | 19 | 4 | 27429.9757
2026 | 2008 | 5 | 19 | 5 | 27114.5303
2026 | 2008 | 5 | 19 | 6 | 26439.2254
2026 | 2008 | 5 | 19 | 7 | 25701.1584
2026 | 2008 | 5 | 19 | 8 | 22714.016
2026 | 2008 | 5 | 19 | 9 | 20437.367
2026 | 2008 | 5 | 19 | 10 | 18411.8204
2026 | 2008 | 5 | 19 | 11 | 19161.0168
2026 | 2008 | 5 | 19 | 12 | 18810.9652
2026 | 2008 | 5 | 19 | 13 | 17304.3756
2026 | 2008 | 5 | 19 | 14 | 16050.7994
2026 | 2008 | 5 | 19 | 15 | 14038.5607
2026 | 2008 | 5 | 19 | 16 | 13600.5373
2026 | 2008 | 5 | 19 | 17 | 13775.8595
2026 | 2008 | 5 | 19 | 18 | 13686.9476
2026 | 2008 | 5 | 19 | 19 | 13085.2473
2026 | 2008 | 5 | 19 | 20 | 14418.2715
2026 | 2008 | 5 | 19 | 21 | 16619.0944
2026 | 2008 | 5 | 19 | 22 | 20172.2322
2026 | 2008 | 5 | 19 | 23 | 22927.8615
2026 | 2008 | 5 | 19 | 24 | 24142.2826
2026 | 2008 | 5 | 20 | 1 | 24957.8392
2026 | 2008 | 5 | 20 | 2 | 24834.6804
2026 | 2008 | 5 | 20 | 3 | 24927.4855
2026 | 2008 | 5 | 20 | 4 | 24253.5651
2026 | 2008 | 5 | 20 | 5 | 24127.0074
2026 | 2008 | 5 | 20 | 6 | 22175.7516
2026 | 2008 | 5 | 20 | 7 | 19077.3447
2026 | 2008 | 5 | 20 | 8 | 14150.1575
2026 | 2008 | 5 | 20 | 9 | 11351.2151
2026 | 2008 | 5 | 20 | 10 | 10831.4424
2026 | 2008 | 5 | 20 | 11 | 12635.4131
2026 | 2008 | 5 | 20 | 12 | 13263.9822
2026 | 2008 | 5 | 20 | 13 | 13289.2056
2026 | 2008 | 5 | 20 | 14 | 13071.4624
2026 | 2008 | 5 | 20 | 15 | 12272.8206
2026 | 2008 | 5 | 20 | 16 | 11847.9429
2026 | 2008 | 5 | 20 | 17 | 12440.5184
2026 | 2008 | 5 | 20 | 18 | 14023.871
2026 | 2008 | 5 | 20 | 19 | 15769.0549
2026 | 2008 | 5 | 20 | 20 | 18240.7568
2026 | 2008 | 5 | 20 | 21 | 22111.589
2026 | 2008 | 5 | 20 | 22 | 22983.6541
2026 | 2008 | 5 | 20 | 23 | 22348.6913
2026 | 2008 | 5 | 20 | 24 | 20879.3351
2026 | 2008 | 5 | 21 | 1 | 18982.3436
2026 | 2008 | 5 | 21 | 2 | 17807.9044
2026 | 2008 | 5 | 21 | 3 | 17957.0916
2026 | 2008 | 5 | 21 | 4 | 17863.1811
2026 | 2008 | 5 | 21 | 5 | 17862.5521
2026 | 2008 | 5 | 21 | 6 | 18317.262
2026 | 2008 | 5 | 21 | 7 | 18678.1751
2026 | 2008 | 5 | 21 | 8 | 18109.9649
2026 | 2008 | 5 | 21 | 9 | 19189.9418
2026 | 2008 | 5 | 21 | 10 | 22548.8416
2026 | 2008 | 5 | 21 | 11 | 25032.4138
2026 | 2008 | 5 | 21 | 12 | 26527.0584
2026 | 2008 | 5 | 21 | 13 | 28349.1582
2026 | 2008 | 5 | 21 | 14 | 30078.2706
2026 | 2008 | 5 | 21 | 15 | 31057.0214
2026 | 2008 | 5 | 21 | 16 | 31120.9085
2026 | 2008 | 5 | 21 | 17 | 31428.2744
2026 | 2008 | 5 | 21 | 18 | 31528.6857
2026 | 2008 | 5 | 21 | 19 | 31446.7997
2026 | 2008 | 5 | 21 | 20 | 31809.9051
2026 | 2008 | 5 | 21 | 21 | 31883.7045
2026 | 2008 | 5 | 21 | 22 | 31628.1489
2026 | 2008 | 5 | 21 | 23 | 31931.2447
2026 | 2008 | 5 | 21 | 24 | 32375.7467
2026 | 2008 | 5 | 22 | 1 | 32554.3441
2026 | 2008 | 5 | 22 | 2 | 32955.6333
2026 | 2008 | 5 | 22 | 3 | 33469.3384
2026 | 2008 | 5 | 22 | 4 | 33516.6663
2026 | 2008 | 5 | 22 | 5 | 33202.2231
2026 | 2008 | 5 | 22 | 6 | 32575.7424
2026 | 2008 | 5 | 22 | 7 | 32599.0601
2026 | 2008 | 5 | 22 | 8 | 33624.329
2026 | 2008 | 5 | 22 | 9 | 34468.9513
2026 | 2008 | 5 | 22 | 10 | 34663.3283
2026 | 2008 | 5 | 22 | 11 | 34508.5238
2026 | 2008 | 5 | 22 | 12 | 33447.1568
2026 | 2008 | 5 | 22 | 13 | 31899.8466
2026 | 2008 | 5 | 22 | 14 | 30573.7433
2026 | 2008 | 5 | 22 | 15 | 28196.0573
2026 | 2008 | 5 | 22 | 16 | 27765.2783
2026 | 2008 | 5 | 22 | 17 | 28631.6516
2026 | 2008 | 5 | 22 | 18 | 29247.264
2026 | 2008 | 5 | 22 | 19 | 27869.5996
2026 | 2008 | 5 | 22 | 20 | 26927.4329
2026 | 2008 | 5 | 22 | 21 | 25859.2221
2026 | 2008 | 5 | 22 | 22 | 27394.7045
2026 | 2008 | 5 | 22 | 23 | 27717.8658
2026 | 2008 | 5 | 22 | 24 | 27461.0758
2026 | 2008 | 5 | 23 | 1 | 27906.7319
2026 | 2008 | 5 | 23 | 2 | 29137.0442
2026 | 2008 | 5 | 23 | 3 | 29825.074
2026 | 2008 | 5 | 23 | 4 | 28682.552
2026 | 2008 | 5 | 23 | 5 | 27769.9859
2026 | 2008 | 5 | 23 | 6 | 26117.9113
2026 | 2008 | 5 | 23 | 7 | 23974.0963
2026 | 2008 | 5 | 23 | 8 | 21574.9417
2026 | 2008 | 5 | 23 | 9 | 21516.1495
2026 | 2008 | 5 | 23 | 10 | 23508.9615
2026 | 2008 | 5 | 23 | 11 | 21909.5619
2026 | 2008 | 5 | 23 | 12 | 19739.9025
2026 | 2008 | 5 | 23 | 13 | 18695.7024
2026 | 2008 | 5 | 23 | 14 | 19241.0684
2026 | 2008 | 5 | 23 | 15 | 19893.1753
2026 | 2008 | 5 | 23 | 16 | 21890.1162
2026 | 2008 | 5 | 23 | 17 | 24933.2377
2026 | 2008 | 5 | 23 | 18 | 26007.5615
2026 | 2008 | 5 | 23 | 19 | 27254.3764
2026 | 2008 | 5 | 23 | 20 | 26566.0497
2026 | 2008 | 5 | 23 | 21 | 26211.7316
2026 | 2008 | 5 | 23 | 22 | 24176.2488
2026 | 2008 | 5 | 23 | 23 | 23261.4671
2026 | 2008 | 5 | 23 | 24 | 24324.5897
2026 | 2008 | 5 | 24 | 1 | 23938.7308
2026 | 2008 | 5 | 24 | 2 | 22994.1847
2026 | 2008 | 5 | 24 | 3 | 21477.9313
2026 | 2008 | 5 | 24 | 4 | 19120.4805
2026 | 2008 | 5 | 24 | 5 | 17125.7734
2026 | 2008 | 5 | 24 | 6 | 16131.2304
2026 | 2008 | 5 | 24 | 7 | 13721.5549
2026 | 2008 | 5 | 24 | 8 | 9881.6354
2026 | 2008 | 5 | 24 | 9 | 8500.2575
2026 | 2008 | 5 | 24 | 10 | 7981.952
2026 | 2008 | 5 | 24 | 11 | 6364.9523
2026 | 2008 | 5 | 24 | 12 | 5586.8723
2026 | 2008 | 5 | 24 | 13 | 5342.3552
2026 | 2008 | 5 | 24 | 14 | 6030.3822
2026 | 2008 | 5 | 24 | 15 | 6857.7139
2026 | 2008 | 5 | 24 | 16 | 8806.53
2026 | 2008 | 5 | 24 | 17 | 10769.57
2026 | 2008 | 5 | 24 | 18 | 14212.4595
2026 | 2008 | 5 | 24 | 19 | 16176.1487
2026 | 2008 | 5 | 24 | 20 | 17480.4528
2026 | 2008 | 5 | 24 | 21 | 19802.258
2026 | 2008 | 5 | 24 | 22 | 23413.1674
2026 | 2008 | 5 | 24 | 23 | 26103.0521
2026 | 2008 | 5 | 24 | 24 | 26707.7417
2026 | 2008 | 5 | 25 | 1 | 26355.8698
2026 | 2008 | 5 | 25 | 2 | 25869.468
2026 | 2008 | 5 | 25 | 3 | 24961.2058
2026 | 2008 | 5 | 25 | 4 | 23911.5834
2026 | 2008 | 5 | 25 | 5 | 22269.3659
2026 | 2008 | 5 | 25 | 6 | 20873.9039
2026 | 2008 | 5 | 25 | 7 | 20229.9845
2026 | 2008 | 5 | 25 | 8 | 20194.9523
2026 | 2008 | 5 | 25 | 9 | 22459.6622
2026 | 2008 | 5 | 25 | 10 | 23657.7126
2026 | 2008 | 5 | 25 | 11 | 25295.1797
2026 | 2008 | 5 | 25 | 12 | 25724.3084
2026 | 2008 | 5 | 25 | 13 | 25491.3515
2026 | 2008 | 5 | 25 | 14 | 25851.0863
2026 | 2008 | 5 | 25 | 15 | 25051.0327
2026 | 2008 | 5 | 25 | 16 | 24825.9816
2026 | 2008 | 5 | 25 | 17 | 25854.9608
2026 | 2008 | 5 | 25 | 18 | 26667.5873
2026 | 2008 | 5 | 25 | 19 | 27618.8065
2026 | 2008 | 5 | 25 | 20 | 26800.8381
2026 | 2008 | 5 | 25 | 21 | 26541.9109
2026 | 2008 | 5 | 25 | 22 | 26408.1415
2026 | 2008 | 5 | 25 | 23 | 26596.7315
2026 | 2008 | 5 | 25 | 24 | 26966.3634
2026 | 2008 | 5 | 26 | 1 | 27467.9951
2026 | 2008 | 5 | 26 | 2 | 28067.5668
2026 | 2008 | 5 | 26 | 3 | 28721.2194
2026 | 2008 | 5 | 26 | 4 | 27593.6293
2026 | 2008 | 5 | 26 | 5 | 27283.2689
2026 | 2008 | 5 | 26 | 6 | 27498.4364
2026 | 2008 | 5 | 26 | 7 | 26917.8458
2026 | 2008 | 5 | 26 | 8 | 27891.6725
2026 | 2008 | 5 | 26 | 9 | 30473.347
2026 | 2008 | 5 | 26 | 10 | 30914.5379
2026 | 2008 | 5 | 26 | 11 | 30839.3293
2026 | 2008 | 5 | 26 | 12 | 29563.6042
2026 | 2008 | 5 | 26 | 13 | 28678.6093
2026 | 2008 | 5 | 26 | 14 | 28328.8613
2026 | 2008 | 5 | 26 | 15 | 27329.9963
2026 | 2008 | 5 | 26 | 16 | 27236.9725
2026 | 2008 | 5 | 26 | 17 | 28026.2798
2026 | 2008 | 5 | 26 | 18 | 29121.0982
2026 | 2008 | 5 | 26 | 19 | 29892.9655
2026 | 2008 | 5 | 26 | 20 | 29640.3577
2026 | 2008 | 5 | 26 | 21 | 28939.4613
2026 | 2008 | 5 | 26 | 22 | 29306.5396
2026 | 2008 | 5 | 26 | 23 | 29989.6752
2026 | 2008 | 5 | 26 | 24 | 30341.044
2026 | 2008 | 5 | 27 | 1 | 29351.7782
2026 | 2008 | 5 | 27 | 2 | 28009.0064
2026 | 2008 | 5 | 27 | 3 | 25722.7597
2026 | 2008 | 5 | 27 | 4 | 24587.7163
2026 | 2008 | 5 | 27 | 5 | 23755.3749
2026 | 2008 | 5 | 27 | 6 | 23362.9338
2026 | 2008 | 5 | 27 | 7 | 23393.966
2026 | 2008 | 5 | 27 | 8 | 24013.2104
2026 | 2008 | 5 | 27 | 9 | 25973.3495
2026 | 2008 | 5 | 27 | 10 | 26880.3009
2026 | 2008 | 5 | 27 | 11 | 26059.8972
2026 | 2008 | 5 | 27 | 12 | 23521.3415
2026 | 2008 | 5 | 27 | 13 | 20598.78
2026 | 2008 | 5 | 27 | 14 | 18629.2035
2026 | 2008 | 5 | 27 | 15 | 16997.7197
2026 | 2008 | 5 | 27 | 16 | 16519.8645
2026 | 2008 | 5 | 27 | 17 | 17184.8636
2026 | 2008 | 5 | 27 | 18 | 17961.697
2026 | 2008 | 5 | 27 | 19 | 18585.714
2026 | 2008 | 5 | 27 | 20 | 18753.3267
2026 | 2008 | 5 | 27 | 21 | 20216.8028
2026 | 2008 | 5 | 27 | 22 | 19280.1785
2026 | 2008 | 5 | 27 | 23 | 19011.3041
2026 | 2008 | 5 | 27 | 24 | 18788.527
2026 | 2008 | 5 | 28 | 1 | 16873.8133
2026 | 2008 | 5 | 28 | 2 | 15717.5574
2026 | 2008 | 5 | 28 | 3 | 14237.4282
2026 | 2008 | 5 | 28 | 4 | 12099.2855
2026 | 2008 | 5 | 28 | 5 | 11562.2326
2026 | 2008 | 5 | 28 | 6 | 9764.8642
2026 | 2008 | 5 | 28 | 7 | 8498.9937
2026 | 2008 | 5 | 28 | 8 | 6994.0031
2026 | 2008 | 5 | 28 | 9 | 6751.4163
2026 | 2008 | 5 | 28 | 10 | 5866.6418
2026 | 2008 | 5 | 28 | 11 | 4989.1038
2026 | 2008 | 5 | 28 | 12 | 4917.5507
2026 | 2008 | 5 | 28 | 13 | 4700.4825
2026 | 2008 | 5 | 28 | 14 | 5863.1781
2026 | 2008 | 5 | 28 | 15 | 6522.3405
2026 | 2008 | 5 | 28 | 16 | 7567.9119
2026 | 2008 | 5 | 28 | 17 | 8822.9106
2026 | 2008 | 5 | 28 | 18 | 9951.9894
2026 | 2008 | 5 | 28 | 19 | 10330.973
2026 | 2008 | 5 | 28 | 20 | 11506.0416
2026 | 2008 | 5 | 28 | 21 | 13960.7491
2026 | 2008 | 5 | 28 | 22 | 16624.0672
2026 | 2008 | 5 | 28 | 23 | 18810.6695
2026 | 2008 | 5 | 28 | 24 | 19497.1162
2026 | 2008 | 5 | 29 | 1 | 20154.74
2026 | 2008 | 5 | 29 | 2 | 20280.2445
2026 | 2008 | 5 | 29 | 3 | 19557.0877
2026 | 2008 | 5 | 29 | 4 | 18235.5538
2026 | 2008 | 5 | 29 | 5 | 17896.8367
2026 | 2008 | 5 | 29 | 6 | 17221.0001
2026 | 2008 | 5 | 29 | 7 | 17247.4623
2026 | 2008 | 5 | 29 | 8 | 16064.6903
2026 | 2008 | 5 | 29 | 9 | 15815.4701
2026 | 2008 | 5 | 29 | 10 | 19418.0208
2026 | 2008 | 5 | 29 | 11 | 19671.7735
2026 | 2008 | 5 | 29 | 12 | 19605.9419
2026 | 2008 | 5 | 29 | 13 | 20226.4397
2026 | 2008 | 5 | 29 | 14 | 21388.0095
2026 | 2008 | 5 | 29 | 15 | 21585.731
2026 | 2008 | 5 | 29 | 16 | 22268.1911
2026 | 2008 | 5 | 29 | 17 | 23411.7772
2026 | 2008 | 5 | 29 | 18 | 24632.3886
2026 | 2008 | 5 | 29 | 19 | 24190.8078
2026 | 2008 | 5 | 29 | 20 | 24278.9119
2026 | 2008 | 5 | 29 | 21 | 24850.527
2026 | 2008 | 5 | 29 | 22 | 26196.5315
2026 | 2008 | 5 | 29 | 23 | 27514.7331
2026 | 2008 | 5 | 29 | 24 | 28310.288
2026 | 2008 | 5 | 30 | 1 | 28574.4109
2026 | 2008 | 5 | 30 | 2 | 28657.4043
2026 | 2008 | 5 | 30 | 3 | 28299.6056
2026 | 2008 | 5 | 30 | 4 | 27814.5305
2026 | 2008 | 5 | 30 | 5 | 26900.6108
2026 | 2008 | 5 | 30 | 6 | 26262.0381
2026 | 2008 | 5 | 30 | 7 | 25244.2247
2026 | 2008 | 5 | 30 | 8 | 24501.7609
2026 | 2008 | 5 | 30 | 9 | 25213.2444
2026 | 2008 | 5 | 30 | 10 | 26095.892
2026 | 2008 | 5 | 30 | 11 | 22998.8493
2026 | 2008 | 5 | 30 | 12 | 20314.7483
2026 | 2008 | 5 | 30 | 13 | 19110.13
2026 | 2008 | 5 | 30 | 14 | 18726.2209
2026 | 2008 | 5 | 30 | 15 | 17834.3763
2026 | 2008 | 5 | 30 | 16 | 18891.2872
2026 | 2008 | 5 | 30 | 17 | 20057.987
2026 | 2008 | 5 | 30 | 18 | 21821.6869
2026 | 2008 | 5 | 30 | 19 | 22924.5506
2026 | 2008 | 5 | 30 | 20 | 24406.6227
2026 | 2008 | 5 | 30 | 21 | 26305.8414
2026 | 2008 | 5 | 30 | 22 | 28415.4411
2026 | 2008 | 5 | 30 | 23 | 28769.2667
2026 | 2008 | 5 | 30 | 24 | 28960.9306
2026 | 2008 | 5 | 31 | 1 | 29010.597
2026 | 2008 | 5 | 31 | 2 | 28950.9523
2026 | 2008 | 5 | 31 | 3 | 28783.5475
2026 | 2008 | 5 | 31 | 4 | 27990.2324
2026 | 2008 | 5 | 31 | 5 | 26261.3185
2026 | 2008 | 5 | 31 | 6 | 24703.0488
2026 | 2008 | 5 | 31 | 7 | 23097.4911
2026 | 2008 | 5 | 31 | 8 | 21142.4924
2026 | 2008 | 5 | 31 | 9 | 20532.1582
2026 | 2008 | 5 | 31 | 10 | 20842.9043
2026 | 2008 | 5 | 31 | 11 | 19034.7749
2026 | 2008 | 5 | 31 | 12 | 18341.7831
2026 | 2008 | 5 | 31 | 13 | 18505.5175
2026 | 2008 | 5 | 31 | 14 | 19310.236
2026 | 2008 | 5 | 31 | 15 | 20528.3087
2026 | 2008 | 5 | 31 | 16 | 21824.083
2026 | 2008 | 5 | 31 | 17 | 23278.8972
2026 | 2008 | 5 | 31 | 18 | 24718.1069
2026 | 2008 | 5 | 31 | 19 | 26383.5017
2026 | 2008 | 5 | 31 | 20 | 27497.547
2026 | 2008 | 5 | 31 | 21 | 27372.5448
2026 | 2008 | 5 | 31 | 22 | 28348.9988
2026 | 2008 | 5 | 31 | 23 | 28221.2054
2026 | 2008 | 5 | 31 | 24 | 28461.012
2027 | 2008 | 5 | 1 | 1 | 36251.4905
2027 | 2008 | 5 | 1 | 2 | 35824.0382
2027 | 2008 | 5 | 1 | 3 | 35129.4053
2027 | 2008 | 5 | 1 | 4 | 33885.0904
2027 | 2008 | 5 | 1 | 5 | 33300.0075
2027 | 2008 | 5 | 1 | 6 | 33135.8185
2027 | 2008 | 5 | 1 | 7 | 31916.2047
2027 | 2008 | 5 | 1 | 8 | 30076.6392
2027 | 2008 | 5 | 1 | 9 | 29661.0118
2027 | 2008 | 5 | 1 | 10 | 29605.5476
2027 | 2008 | 5 | 1 | 11 | 29465.0328
2027 | 2008 | 5 | 1 | 12 | 28380.0726
2027 | 2008 | 5 | 1 | 13 | 27489.4389
2027 | 2008 | 5 | 1 | 14 | 26893.4347
2027 | 2008 | 5 | 1 | 15 | 26475.2182
2027 | 2008 | 5 | 1 | 16 | 25842.7632
2027 | 2008 | 5 | 1 | 17 | 27579.2647
2027 | 2008 | 5 | 1 | 18 | 27960.6306
2027 | 2008 | 5 | 1 | 19 | 29361.1102
2027 | 2008 | 5 | 1 | 20 | 29750.0543
2027 | 2008 | 5 | 1 | 21 | 30761.9715
2027 | 2008 | 5 | 1 | 22 | 32280.8797
2027 | 2008 | 5 | 1 | 23 | 32178.1963
2027 | 2008 | 5 | 1 | 24 | 31975.3329
2027 | 2008 | 5 | 2 | 1 | 32366.8989
2027 | 2008 | 5 | 2 | 2 | 31146.1291
2027 | 2008 | 5 | 2 | 3 | 31260.8367
2027 | 2008 | 5 | 2 | 4 | 30974.5749
2027 | 2008 | 5 | 2 | 5 | 30469.5012
2027 | 2008 | 5 | 2 | 6 | 28795.674
2027 | 2008 | 5 | 2 | 7 | 26675.0124
2027 | 2008 | 5 | 2 | 8 | 20084.1023
2027 | 2008 | 5 | 2 | 9 | 14449.6467
2027 | 2008 | 5 | 2 | 10 | 11183.0379
2027 | 2008 | 5 | 2 | 11 | 7516.6359
2027 | 2008 | 5 | 2 | 12 | 7290.4292
2027 | 2008 | 5 | 2 | 13 | 9183.4384
2027 | 2008 | 5 | 2 | 14 | 11709.6203
2027 | 2008 | 5 | 2 | 15 | 14415.9814
2027 | 2008 | 5 | 2 | 16 | 15287.051
2027 | 2008 | 5 | 2 | 17 | 15527.5361
2027 | 2008 | 5 | 2 | 18 | 14641.3022
2027 | 2008 | 5 | 2 | 19 | 11740.4023
2027 | 2008 | 5 | 2 | 20 | 10241.5173
2027 | 2008 | 5 | 2 | 21 | 10087.4629
2027 | 2008 | 5 | 2 | 22 | 11320.304
2027 | 2008 | 5 | 2 | 23 | 13109.5111
2027 | 2008 | 5 | 2 | 24 | 16177.5667
2027 | 2008 | 5 | 3 | 1 | 20023.1473
2027 | 2008 | 5 | 3 | 2 | 22304.4449
2027 | 2008 | 5 | 3 | 3 | 23425.4118
2027 | 2008 | 5 | 3 | 4 | 24603.5515
2027 | 2008 | 5 | 3 | 5 | 25211.2499
2027 | 2008 | 5 | 3 | 6 | 25299.4202
2027 | 2008 | 5 | 3 | 7 | 24275.6783
2027 | 2008 | 5 | 3 | 8 | 23885.7385
2027 | 2008 | 5 | 3 | 9 | 25002.3217
2027 | 2008 | 5 | 3 | 10 | 24130.6234
2027 | 2008 | 5 | 3 | 11 | 19206.2337
2027 | 2008 | 5 | 3 | 12 | 15364.2158
2027 | 2008 | 5 | 3 | 13 | 13380.8893
2027 | 2008 | 5 | 3 | 14 | 12022.9553
2027 | 2008 | 5 | 3 | 15 | 10961.2735
2027 | 2008 | 5 | 3 | 16 | 9996.2206
2027 | 2008 | 5 | 3 | 17 | 9735.7616
2027 | 2008 | 5 | 3 | 18 | 9798.7528
2027 | 2008 | 5 | 3 | 19 | 9284.9892
2027 | 2008 | 5 | 3 | 20 | 9066.649
2027 | 2008 | 5 | 3 | 21 | 9655.7422
2027 | 2008 | 5 | 3 | 22 | 10435.3253
2027 | 2008 | 5 | 3 | 23 | 12344.0295
2027 | 2008 | 5 | 3 | 24 | 12948.0732
2027 | 2008 | 5 | 4 | 1 | 13140.1068
2027 | 2008 | 5 | 4 | 2 | 13229.9777
2027 | 2008 | 5 | 4 | 3 | 13016.9737
2027 | 2008 | 5 | 4 | 4 | 12842.8272
2027 | 2008 | 5 | 4 | 5 | 13155.2591
2027 | 2008 | 5 | 4 | 6 | 13136.6439
2027 | 2008 | 5 | 4 | 7 | 13652.5238
2027 | 2008 | 5 | 4 | 8 | 10992.2573
2027 | 2008 | 5 | 4 | 9 | 10470.1946
2027 | 2008 | 5 | 4 | 10 | 12399.8139
2027 | 2008 | 5 | 4 | 11 | 13899.0854
2027 | 2008 | 5 | 4 | 12 | 14497.3864
2027 | 2008 | 5 | 4 | 13 | 15509.6861
2027 | 2008 | 5 | 4 | 14 | 16482.6601
2027 | 2008 | 5 | 4 | 15 | 17105.4917
2027 | 2008 | 5 | 4 | 16 | 17572.6027
2027 | 2008 | 5 | 4 | 17 | 19393.7802
2027 | 2008 | 5 | 4 | 18 | 20902.1134
2027 | 2008 | 5 | 4 | 19 | 22201.1617
2027 | 2008 | 5 | 4 | 20 | 21657.3385
2027 | 2008 | 5 | 4 | 21 | 22340.8642
2027 | 2008 | 5 | 4 | 22 | 23311.1005
2027 | 2008 | 5 | 4 | 23 | 23032.145
2027 | 2008 | 5 | 4 | 24 | 21481.4204
2027 | 2008 | 5 | 5 | 1 | 20210.0451
2027 | 2008 | 5 | 5 | 2 | 19791.9856
2027 | 2008 | 5 | 5 | 3 | 19636.7234
2027 | 2008 | 5 | 5 | 4 | 18407.0292
2027 | 2008 | 5 | 5 | 5 | 16624.8089
2027 | 2008 | 5 | 5 | 6 | 15176.0453
2027 | 2008 | 5 | 5 | 7 | 13673.0513
2027 | 2008 | 5 | 5 | 8 | 14243.4305
2027 | 2008 | 5 | 5 | 9 | 17023.9456
2027 | 2008 | 5 | 5 | 10 | 18476.1483
2027 | 2008 | 5 | 5 | 11 | 19812.4574
2027 | 2008 | 5 | 5 | 12 | 20735.407
2027 | 2008 | 5 | 5 | 13 | 21115.4335
2027 | 2008 | 5 | 5 | 14 | 22089.2726
2027 | 2008 | 5 | 5 | 15 | 21514.0345
2027 | 2008 | 5 | 5 | 16 | 20702.7579
2027 | 2008 | 5 | 5 | 17 | 22785.009
2027 | 2008 | 5 | 5 | 18 | 24695.8929
2027 | 2008 | 5 | 5 | 19 | 26291.8574
2027 | 2008 | 5 | 5 | 20 | 28430.4549
2027 | 2008 | 5 | 5 | 21 | 29966.5855
2027 | 2008 | 5 | 5 | 22 | 30288.5737
2027 | 2008 | 5 | 5 | 23 | 29936.7276
2027 | 2008 | 5 | 5 | 24 | 28568.4966
2027 | 2008 | 5 | 6 | 1 | 26678.6031
2027 | 2008 | 5 | 6 | 2 | 23879.5776
2027 | 2008 | 5 | 6 | 3 | 20893.0594
2027 | 2008 | 5 | 6 | 4 | 18239.2949
2027 | 2008 | 5 | 6 | 5 | 18139.9022
2027 | 2008 | 5 | 6 | 6 | 19470.6462
2027 | 2008 | 5 | 6 | 7 | 20446.0162
2027 | 2008 | 5 | 6 | 8 | 22819.9516
2027 | 2008 | 5 | 6 | 9 | 26850.776
2027 | 2008 | 5 | 6 | 10 | 28444.0771
2027 | 2008 | 5 | 6 | 11 | 28227.5732
2027 | 2008 | 5 | 6 | 12 | 28649.099
2027 | 2008 | 5 | 6 | 13 | 30131.6923
2027 | 2008 | 5 | 6 | 14 | 31915.8333
2027 | 2008 | 5 | 6 | 15 | 32949.1354
2027 | 2008 | 5 | 6 | 16 | 33233.1787
2027 | 2008 | 5 | 6 | 17 | 32675.2568
2027 | 2008 | 5 | 6 | 18 | 32990.8397
2027 | 2008 | 5 | 6 | 19 | 31990.6049
2027 | 2008 | 5 | 6 | 20 | 32380.2634
2027 | 2008 | 5 | 6 | 21 | 31639.7852
2027 | 2008 | 5 | 6 | 22 | 32270.4787
2027 | 2008 | 5 | 6 | 23 | 32444.754
2027 | 2008 | 5 | 6 | 24 | 31203.4289
2027 | 2008 | 5 | 7 | 1 | 30313.1119
2027 | 2008 | 5 | 7 | 2 | 30038.9516
2027 | 2008 | 5 | 7 | 3 | 30154.9088
2027 | 2008 | 5 | 7 | 4 | 30099.0302
2027 | 2008 | 5 | 7 | 5 | 29907.3045
2027 | 2008 | 5 | 7 | 6 | 29910.7133
2027 | 2008 | 5 | 7 | 7 | 30039.1575
2027 | 2008 | 5 | 7 | 8 | 30279.2436
2027 | 2008 | 5 | 7 | 9 | 31254.4524
2027 | 2008 | 5 | 7 | 10 | 30539.3426
2027 | 2008 | 5 | 7 | 11 | 29872.2336
2027 | 2008 | 5 | 7 | 12 | 28251.1818
2027 | 2008 | 5 | 7 | 13 | 28157.3977
2027 | 2008 | 5 | 7 | 14 | 28836.2113
2027 | 2008 | 5 | 7 | 15 | 30298.0084
2027 | 2008 | 5 | 7 | 16 | 30684.6587
2027 | 2008 | 5 | 7 | 17 | 31327.902
2027 | 2008 | 5 | 7 | 18 | 30511.78
2027 | 2008 | 5 | 7 | 19 | 27261.868
2027 | 2008 | 5 | 7 | 20 | 26099.5057
2027 | 2008 | 5 | 7 | 21 | 23907.3287
2027 | 2008 | 5 | 7 | 22 | 21930.5659
2027 | 2008 | 5 | 7 | 23 | 21035.6763
2027 | 2008 | 5 | 7 | 24 | 19528.0388
2027 | 2008 | 5 | 8 | 1 | 17334.9655
2027 | 2008 | 5 | 8 | 2 | 16266.4796
2027 | 2008 | 5 | 8 | 3 | 13519.7964
2027 | 2008 | 5 | 8 | 4 | 11252.2081
2027 | 2008 | 5 | 8 | 5 | 9933.333
2027 | 2008 | 5 | 8 | 6 | 7935.6455
2027 | 2008 | 5 | 8 | 7 | 7014.1472
2027 | 2008 | 5 | 8 | 8 | 4903.1125
2027 | 2008 | 5 | 8 | 9 | 3832.2597
2027 | 2008 | 5 | 8 | 10 | 2917.1672
2027 | 2008 | 5 | 8 | 11 | 3148.5554
2027 | 2008 | 5 | 8 | 12 | 4097.3134
2027 | 2008 | 5 | 8 | 13 | 5708.8507
2027 | 2008 | 5 | 8 | 14 | 7756.7422
2027 | 2008 | 5 | 8 | 15 | 9426.5303
2027 | 2008 | 5 | 8 | 16 | 12149.4978
2027 | 2008 | 5 | 8 | 17 | 15425.6766
2027 | 2008 | 5 | 8 | 18 | 18869.2117
2027 | 2008 | 5 | 8 | 19 | 19291.1536
2027 | 2008 | 5 | 8 | 20 | 21681.9284
2027 | 2008 | 5 | 8 | 21 | 24439.0687
2027 | 2008 | 5 | 8 | 22 | 28272.7314
2027 | 2008 | 5 | 8 | 23 | 28775.0274
2027 | 2008 | 5 | 8 | 24 | 28357.4833
2027 | 2008 | 5 | 9 | 1 | 29506.5038
2027 | 2008 | 5 | 9 | 2 | 28597.0185
2027 | 2008 | 5 | 9 | 3 | 28101.5997
2027 | 2008 | 5 | 9 | 4 | 26241.4728
2027 | 2008 | 5 | 9 | 5 | 24517.485
2027 | 2008 | 5 | 9 | 6 | 22591.4221
2027 | 2008 | 5 | 9 | 7 | 18550.8148
2027 | 2008 | 5 | 9 | 8 | 13129.1016
2027 | 2008 | 5 | 9 | 9 | 9101.9875
2027 | 2008 | 5 | 9 | 10 | 7474.1412
2027 | 2008 | 5 | 9 | 11 | 6932.6936
2027 | 2008 | 5 | 9 | 12 | 6788.5654
2027 | 2008 | 5 | 9 | 13 | 6610.2922
2027 | 2008 | 5 | 9 | 14 | 6265.5589
2027 | 2008 | 5 | 9 | 15 | 5935.0774
2027 | 2008 | 5 | 9 | 16 | 6437.466
2027 | 2008 | 5 | 9 | 17 | 7387.5978
2027 | 2008 | 5 | 9 | 18 | 8427.0812
2027 | 2008 | 5 | 9 | 19 | 9201.1547
2027 | 2008 | 5 | 9 | 20 | 10809.0475
2027 | 2008 | 5 | 9 | 21 | 14194.0192
2027 | 2008 | 5 | 9 | 22 | 18067.4897
2027 | 2008 | 5 | 9 | 23 | 21334.3833
2027 | 2008 | 5 | 9 | 24 | 23108.057
2027 | 2008 | 5 | 10 | 1 | 24827.437
2027 | 2008 | 5 | 10 | 2 | 25102.2292
2027 | 2008 | 5 | 10 | 3 | 24460.1239
2027 | 2008 | 5 | 10 | 4 | 23829.4453
2027 | 2008 | 5 | 10 | 5 | 23668.8052
2027 | 2008 | 5 | 10 | 6 | 24137.2859
2027 | 2008 | 5 | 10 | 7 | 23297.5448
2027 | 2008 | 5 | 10 | 8 | 21835.8147
2027 | 2008 | 5 | 10 | 9 | 22020.1576
2027 | 2008 | 5 | 10 | 10 | 23111.5995
2027 | 2008 | 5 | 10 | 11 | 23255.9823
2027 | 2008 | 5 | 10 | 12 | 24940.2446
2027 | 2008 | 5 | 10 | 13 | 25857.6832
2027 | 2008 | 5 | 10 | 14 | 25106.2885
2027 | 2008 | 5 | 10 | 15 | 24342.5303
2027 | 2008 | 5 | 10 | 16 | 23336.3347
2027 | 2008 | 5 | 10 | 17 | 22377.9256
2027 | 2008 | 5 | 10 | 18 | 20747.7458
2027 | 2008 | 5 | 10 | 19 | 18475.9429
2027 | 2008 | 5 | 10 | 20 | 17589.0757
2027 | 2008 | 5 | 10 | 21 | 17417.2562
2027 | 2008 | 5 | 10 | 22 | 18366.5139
2027 | 2008 | 5 | 10 | 23 | 22066.8846
2027 | 2008 | 5 | 10 | 24 | 24509.995
2027 | 2008 | 5 | 11 | 1 | 26841.3712
2027 | 2008 | 5 | 11 | 2 | 27735.5601
2027 | 2008 | 5 | 11 | 3 | 27818.9519
2027 | 2008 | 5 | 11 | 4 | 26715.609
2027 | 2008 | 5 | 11 | 5 | 25430.7504
2027 | 2008 | 5 | 11 | 6 | 24087.2572
2027 | 2008 | 5 | 11 | 7 | 22423.4317
2027 | 2008 | 5 | 11 | 8 | 21274.2487
2027 | 2008 | 5 | 11 | 9 | 21641.905
2027 | 2008 | 5 | 11 | 10 | 19607.199
2027 | 2008 | 5 | 11 | 11 | 15550.0387
2027 | 2008 | 5 | 11 | 12 | 14517.1587
2027 | 2008 | 5 | 11 | 13 | 13928.4796
2027 | 2008 | 5 | 11 | 14 | 13392.5633
2027 | 2008 | 5 | 11 | 15 | 12778.6148
2027 | 2008 | 5 | 11 | 16 | 12042.0733
2027 | 2008 | 5 | 11 | 17 | 12060.5294
2027 | 2008 | 5 | 11 | 18 | 12062.2073
2027 | 2008 | 5 | 11 | 19 | 11919.7275
2027 | 2008 | 5 | 11 | 20 | 11896.919
2027 | 2008 | 5 | 11 | 21 | 13121.4962
2027 | 2008 | 5 | 11 | 22 | 14871.8582
2027 | 2008 | 5 | 11 | 23 | 16724.0758
2027 | 2008 | 5 | 11 | 24 | 17457.0201
2027 | 2008 | 5 | 12 | 1 | 19234.8574
2027 | 2008 | 5 | 12 | 2 | 20418.4953
2027 | 2008 | 5 | 12 | 3 | 20571.8982
2027 | 2008 | 5 | 12 | 4 | 21351.0749
2027 | 2008 | 5 | 12 | 5 | 22020.7267
2027 | 2008 | 5 | 12 | 6 | 23118.6544
2027 | 2008 | 5 | 12 | 7 | 23931.486
2027 | 2008 | 5 | 12 | 8 | 22819.0126
2027 | 2008 | 5 | 12 | 9 | 22683.0672
2027 | 2008 | 5 | 12 | 10 | 26415.0024
2027 | 2008 | 5 | 12 | 11 | 28056.9253
2027 | 2008 | 5 | 12 | 12 | 29373.8297
2027 | 2008 | 5 | 12 | 13 | 29964.9966
2027 | 2008 | 5 | 12 | 14 | 31382.8862
2027 | 2008 | 5 | 12 | 15 | 32052.9996
2027 | 2008 | 5 | 12 | 16 | 33414.3924
2027 | 2008 | 5 | 12 | 17 | 34324.7355
2027 | 2008 | 5 | 12 | 18 | 34918.6704
2027 | 2008 | 5 | 12 | 19 | 34618.3401
2027 | 2008 | 5 | 12 | 20 | 32929.737
2027 | 2008 | 5 | 12 | 21 | 31754.7623
2027 | 2008 | 5 | 12 | 22 | 32368.2378
2027 | 2008 | 5 | 12 | 23 | 32861.2853
2027 | 2008 | 5 | 12 | 24 | 33278.1494
2027 | 2008 | 5 | 13 | 1 | 33650.5023
2027 | 2008 | 5 | 13 | 2 | 33922.2856
2027 | 2008 | 5 | 13 | 3 | 33255.6916
2027 | 2008 | 5 | 13 | 4 | 31567.8178
2027 | 2008 | 5 | 13 | 5 | 30887.7518
2027 | 2008 | 5 | 13 | 6 | 29027.5449
2027 | 2008 | 5 | 13 | 7 | 27231.8267
2027 | 2008 | 5 | 13 | 8 | 25533.4174
2027 | 2008 | 5 | 13 | 9 | 24978.8145
2027 | 2008 | 5 | 13 | 10 | 22791.0658
2027 | 2008 | 5 | 13 | 11 | 18764.8448
2027 | 2008 | 5 | 13 | 12 | 15317.0408
2027 | 2008 | 5 | 13 | 13 | 13547.6127
2027 | 2008 | 5 | 13 | 14 | 12133.0736
2027 | 2008 | 5 | 13 | 15 | 11764.4736
2027 | 2008 | 5 | 13 | 16 | 12150.7886
2027 | 2008 | 5 | 13 | 17 | 13619.8579
2027 | 2008 | 5 | 13 | 18 | 15734.2768
2027 | 2008 | 5 | 13 | 19 | 19244.6093
2027 | 2008 | 5 | 13 | 20 | 21532.4232
2027 | 2008 | 5 | 13 | 21 | 25163.1402
2027 | 2008 | 5 | 13 | 22 | 24076.9868
2027 | 2008 | 5 | 13 | 23 | 24151.9646
2027 | 2008 | 5 | 13 | 24 | 24734.8597
2027 | 2008 | 5 | 14 | 1 | 24810.8206
2027 | 2008 | 5 | 14 | 2 | 23672.8353
2027 | 2008 | 5 | 14 | 3 | 21289.6701
2027 | 2008 | 5 | 14 | 4 | 19533.6319
2027 | 2008 | 5 | 14 | 5 | 18663.7827
2027 | 2008 | 5 | 14 | 6 | 17805.6345
2027 | 2008 | 5 | 14 | 7 | 18005.1538
2027 | 2008 | 5 | 14 | 8 | 17831.6576
2027 | 2008 | 5 | 14 | 9 | 19346.7589
2027 | 2008 | 5 | 14 | 10 | 19028.4356
2027 | 2008 | 5 | 14 | 11 | 17392.7416
2027 | 2008 | 5 | 14 | 12 | 15743.7194
2027 | 2008 | 5 | 14 | 13 | 13873.2816
2027 | 2008 | 5 | 14 | 14 | 12370.7429
2027 | 2008 | 5 | 14 | 15 | 12390.0933
2027 | 2008 | 5 | 14 | 16 | 12682.9519
2027 | 2008 | 5 | 14 | 17 | 12921.1542
2027 | 2008 | 5 | 14 | 18 | 14188.5117
2027 | 2008 | 5 | 14 | 19 | 14162.5357
2027 | 2008 | 5 | 14 | 20 | 12580.4991
2027 | 2008 | 5 | 14 | 21 | 13019.8179
2027 | 2008 | 5 | 14 | 22 | 12572.2724
2027 | 2008 | 5 | 14 | 23 | 10497.5537
2027 | 2008 | 5 | 14 | 24 | 7737.7154
2027 | 2008 | 5 | 15 | 1 | 6219.4617
2027 | 2008 | 5 | 15 | 2 | 4997.5473
2027 | 2008 | 5 | 15 | 3 | 5321.4682
2027 | 2008 | 5 | 15 | 4 | 6202.6053
2027 | 2008 | 5 | 15 | 5 | 6981.249
2027 | 2008 | 5 | 15 | 6 | 6934.5806
2027 | 2008 | 5 | 15 | 7 | 10185.1581
2027 | 2008 | 5 | 15 | 8 | 10463.9682
2027 | 2008 | 5 | 15 | 9 | 12655.1332
2027 | 2008 | 5 | 15 | 10 | 11824.5301
2027 | 2008 | 5 | 15 | 11 | 10024.3626
2027 | 2008 | 5 | 15 | 12 | 9071.8299
2027 | 2008 | 5 | 15 | 13 | 9402.7001
2027 | 2008 | 5 | 15 | 14 | 9027.242
2027 | 2008 | 5 | 15 | 15 | 7497.6009
2027 | 2008 | 5 | 15 | 16 | 7395.5989
2027 | 2008 | 5 | 15 | 17 | 7264.9379
2027 | 2008 | 5 | 15 | 18 | 7725.2971
2027 | 2008 | 5 | 15 | 19 | 9070.3056
2027 | 2008 | 5 | 15 | 20 | 10191.6415
2027 | 2008 | 5 | 15 | 21 | 12922.154
2027 | 2008 | 5 | 15 | 22 | 12401.3807
2027 | 2008 | 5 | 15 | 23 | 11355.9978
2027 | 2008 | 5 | 15 | 24 | 10660.5973
2027 | 2008 | 5 | 16 | 1 | 9579.219
2027 | 2008 | 5 | 16 | 2 | 8725.8646
2027 | 2008 | 5 | 16 | 3 | 8909.6021
2027 | 2008 | 5 | 16 | 4 | 9423.3496
2027 | 2008 | 5 | 16 | 5 | 10814.9285
2027 | 2008 | 5 | 16 | 6 | 12413.128
2027 | 2008 | 5 | 16 | 7 | 14702.4155
2027 | 2008 | 5 | 16 | 8 | 14676.1721
2027 | 2008 | 5 | 16 | 9 | 13638.7624
2027 | 2008 | 5 | 16 | 10 | 17863.5349
2027 | 2008 | 5 | 16 | 11 | 18510.8328
2027 | 2008 | 5 | 16 | 12 | 17583.0667
2027 | 2008 | 5 | 16 | 13 | 15665.3001
2027 | 2008 | 5 | 16 | 14 | 13339.4428
2027 | 2008 | 5 | 16 | 15 | 11510.6237
2027 | 2008 | 5 | 16 | 16 | 9996.8719
2027 | 2008 | 5 | 16 | 17 | 9519.7913
2027 | 2008 | 5 | 16 | 18 | 8438.0619
2027 | 2008 | 5 | 16 | 19 | 6577.1973
2027 | 2008 | 5 | 16 | 20 | 4297.0245
2027 | 2008 | 5 | 16 | 21 | 3117.3187
2027 | 2008 | 5 | 16 | 22 | 2457.0143
2027 | 2008 | 5 | 16 | 23 | 2305.4527
2027 | 2008 | 5 | 16 | 24 | 2659.033
2027 | 2008 | 5 | 17 | 1 | 3401.2689
2027 | 2008 | 5 | 17 | 2 | 4630.4354
2027 | 2008 | 5 | 17 | 3 | 6324.8799
2027 | 2008 | 5 | 17 | 4 | 8843.1713
2027 | 2008 | 5 | 17 | 5 | 10387.1272
2027 | 2008 | 5 | 17 | 6 | 10909.8165
2027 | 2008 | 5 | 17 | 7 | 10810.2681
2027 | 2008 | 5 | 17 | 8 | 8360.8678
2027 | 2008 | 5 | 17 | 9 | 7723.381
2027 | 2008 | 5 | 17 | 10 | 4795.3862
2027 | 2008 | 5 | 17 | 11 | 5302.3325
2027 | 2008 | 5 | 17 | 12 | 4273.1757
2027 | 2008 | 5 | 17 | 13 | 3600.1698
2027 | 2008 | 5 | 17 | 14 | 4112.2874
2027 | 2008 | 5 | 17 | 15 | 4199.0845
2027 | 2008 | 5 | 17 | 16 | 4093.5018
2027 | 2008 | 5 | 17 | 17 | 3788.3028
2027 | 2008 | 5 | 17 | 18 | 4151.452
2027 | 2008 | 5 | 17 | 19 | 4113.3951
2027 | 2008 | 5 | 17 | 20 | 3950.2759
2027 | 2008 | 5 | 17 | 21 | 5208.3588
2027 | 2008 | 5 | 17 | 22 | 6552.2484
2027 | 2008 | 5 | 17 | 23 | 8127.3927
2027 | 2008 | 5 | 17 | 24 | 8886.6031
2027 | 2008 | 5 | 18 | 1 | 10377.8672
2027 | 2008 | 5 | 18 | 2 | 11406.6056
2027 | 2008 | 5 | 18 | 3 | 13906.7066
2027 | 2008 | 5 | 18 | 4 | 15499.9732
2027 | 2008 | 5 | 18 | 5 | 17199.3777
2027 | 2008 | 5 | 18 | 6 | 18308.8506
2027 | 2008 | 5 | 18 | 7 | 19047.2203
2027 | 2008 | 5 | 18 | 8 | 14163.1364
2027 | 2008 | 5 | 18 | 9 | 10140.3027
2027 | 2008 | 5 | 18 | 10 | 6436.2122
2027 | 2008 | 5 | 18 | 11 | 6890.0846
2027 | 2008 | 5 | 18 | 12 | 6398.9074
2027 | 2008 | 5 | 18 | 13 | 5551.0612
2027 | 2008 | 5 | 18 | 14 | 4840.2304
2027 | 2008 | 5 | 18 | 15 | 3836.5141
2027 | 2008 | 5 | 18 | 16 | 3137.9586
2027 | 2008 | 5 | 18 | 17 | 2638.6414
2027 | 2008 | 5 | 18 | 18 | 2204.5494
2027 | 2008 | 5 | 18 | 19 | 1853.2453
2027 | 2008 | 5 | 18 | 20 | 2343.5433
2027 | 2008 | 5 | 18 | 21 | 3990.1457
2027 | 2008 | 5 | 18 | 22 | 8077.224
2027 | 2008 | 5 | 18 | 23 | 14002.9701
2027 | 2008 | 5 | 18 | 24 | 18984.6603
2027 | 2008 | 5 | 19 | 1 | 23232.3952
2027 | 2008 | 5 | 19 | 2 | 26443.0782
2027 | 2008 | 5 | 19 | 3 | 28127.5179
2027 | 2008 | 5 | 19 | 4 | 28585.549
2027 | 2008 | 5 | 19 | 5 | 28415.4087
2027 | 2008 | 5 | 19 | 6 | 27767.5083
2027 | 2008 | 5 | 19 | 7 | 26931.3439
2027 | 2008 | 5 | 19 | 8 | 23923.8783
2027 | 2008 | 5 | 19 | 9 | 21679.193
2027 | 2008 | 5 | 19 | 10 | 19252.9611
2027 | 2008 | 5 | 19 | 11 | 19938.843
2027 | 2008 | 5 | 19 | 12 | 19624.406
2027 | 2008 | 5 | 19 | 13 | 18111.2409
2027 | 2008 | 5 | 19 | 14 | 16837.29
2027 | 2008 | 5 | 19 | 15 | 14747.3833
2027 | 2008 | 5 | 19 | 16 | 14247.5228
2027 | 2008 | 5 | 19 | 17 | 14435.9042
2027 | 2008 | 5 | 19 | 18 | 14291.4605
2027 | 2008 | 5 | 19 | 19 | 13782.7129
2027 | 2008 | 5 | 19 | 20 | 15119.6713
2027 | 2008 | 5 | 19 | 21 | 17350.1372
2027 | 2008 | 5 | 19 | 22 | 21283.938
2027 | 2008 | 5 | 19 | 23 | 24157.2674
2027 | 2008 | 5 | 19 | 24 | 25399.2014
2027 | 2008 | 5 | 20 | 1 | 26193.8567
2027 | 2008 | 5 | 20 | 2 | 26111.4824
2027 | 2008 | 5 | 20 | 3 | 26316.5714
2027 | 2008 | 5 | 20 | 4 | 25567.0771
2027 | 2008 | 5 | 20 | 5 | 25475.9934
2027 | 2008 | 5 | 20 | 6 | 23507.7604
2027 | 2008 | 5 | 20 | 7 | 20422.79
2027 | 2008 | 5 | 20 | 8 | 15366.1316
2027 | 2008 | 5 | 20 | 9 | 12166.7017
2027 | 2008 | 5 | 20 | 10 | 11601.082
2027 | 2008 | 5 | 20 | 11 | 13330.7029
2027 | 2008 | 5 | 20 | 12 | 13960.9468
2027 | 2008 | 5 | 20 | 13 | 13949.9844
2027 | 2008 | 5 | 20 | 14 | 13719.4472
2027 | 2008 | 5 | 20 | 15 | 12853.3498
2027 | 2008 | 5 | 20 | 16 | 12419.2006
2027 | 2008 | 5 | 20 | 17 | 12982.6261
2027 | 2008 | 5 | 20 | 18 | 14864.6468
2027 | 2008 | 5 | 20 | 19 | 16539.4245
2027 | 2008 | 5 | 20 | 20 | 19201.5912
2027 | 2008 | 5 | 20 | 21 | 23301.3512
2027 | 2008 | 5 | 20 | 22 | 23945.1245
2027 | 2008 | 5 | 20 | 23 | 23886.8179
2027 | 2008 | 5 | 20 | 24 | 22433.2335
2027 | 2008 | 5 | 21 | 1 | 20162.4165
2027 | 2008 | 5 | 21 | 2 | 18898.9024
2027 | 2008 | 5 | 21 | 3 | 18879.6948
2027 | 2008 | 5 | 21 | 4 | 18803.6733
2027 | 2008 | 5 | 21 | 5 | 18757.3605
2027 | 2008 | 5 | 21 | 6 | 19316.4028
2027 | 2008 | 5 | 21 | 7 | 19763.6183
2027 | 2008 | 5 | 21 | 8 | 19204.0245
2027 | 2008 | 5 | 21 | 9 | 20369.1354
2027 | 2008 | 5 | 21 | 10 | 23657.7353
2027 | 2008 | 5 | 21 | 11 | 26238.8212
2027 | 2008 | 5 | 21 | 12 | 27826.811
2027 | 2008 | 5 | 21 | 13 | 29741.1895
2027 | 2008 | 5 | 21 | 14 | 31568.1578
2027 | 2008 | 5 | 21 | 15 | 32453.3814
2027 | 2008 | 5 | 21 | 16 | 32444.9219
2027 | 2008 | 5 | 21 | 17 | 32712.8776
2027 | 2008 | 5 | 21 | 18 | 32818.4575
2027 | 2008 | 5 | 21 | 19 | 32747.5905
2027 | 2008 | 5 | 21 | 20 | 33248.0685
2027 | 2008 | 5 | 21 | 21 | 33436.6886
2027 | 2008 | 5 | 21 | 22 | 33201.683
2027 | 2008 | 5 | 21 | 23 | 33463.3815
2027 | 2008 | 5 | 21 | 24 | 33975.796
2027 | 2008 | 5 | 22 | 1 | 34165.2168
2027 | 2008 | 5 | 22 | 2 | 34573.87
2027 | 2008 | 5 | 22 | 3 | 35089.5043
2027 | 2008 | 5 | 22 | 4 | 35139.7658
2027 | 2008 | 5 | 22 | 5 | 34654.3925
2027 | 2008 | 5 | 22 | 6 | 34169.7001
2027 | 2008 | 5 | 22 | 7 | 34191.9557
2027 | 2008 | 5 | 22 | 8 | 35218.026
2027 | 2008 | 5 | 22 | 9 | 36013.3661
2027 | 2008 | 5 | 22 | 10 | 36241.825
2027 | 2008 | 5 | 22 | 11 | 36070.7706
2027 | 2008 | 5 | 22 | 12 | 34986.5649
2027 | 2008 | 5 | 22 | 13 | 33450.0835
2027 | 2008 | 5 | 22 | 14 | 32107.2346
2027 | 2008 | 5 | 22 | 15 | 29645.9141
2027 | 2008 | 5 | 22 | 16 | 29044.8256
2027 | 2008 | 5 | 22 | 17 | 29851.8363
2027 | 2008 | 5 | 22 | 18 | 30487.4207
2027 | 2008 | 5 | 22 | 19 | 29199.3962
2027 | 2008 | 5 | 22 | 20 | 28287.4425
2027 | 2008 | 5 | 22 | 21 | 27174.0931
2027 | 2008 | 5 | 22 | 22 | 28562.8918
2027 | 2008 | 5 | 22 | 23 | 28896.5374
2027 | 2008 | 5 | 22 | 24 | 28731.2559
2027 | 2008 | 5 | 23 | 1 | 29185.8969
2027 | 2008 | 5 | 23 | 2 | 30448.9865
2027 | 2008 | 5 | 23 | 3 | 31178.2361
2027 | 2008 | 5 | 23 | 4 | 30138.86
2027 | 2008 | 5 | 23 | 5 | 29122.5884
2027 | 2008 | 5 | 23 | 6 | 27593.183
2027 | 2008 | 5 | 23 | 7 | 25256.2085
2027 | 2008 | 5 | 23 | 8 | 22862.1391
2027 | 2008 | 5 | 23 | 9 | 22802.5324
2027 | 2008 | 5 | 23 | 10 | 24830.1164
2027 | 2008 | 5 | 23 | 11 | 23215.1937
2027 | 2008 | 5 | 23 | 12 | 20995.8602
2027 | 2008 | 5 | 23 | 13 | 19855.8204
2027 | 2008 | 5 | 23 | 14 | 20374.9369
2027 | 2008 | 5 | 23 | 15 | 20966.4898
2027 | 2008 | 5 | 23 | 16 | 23005.2162
2027 | 2008 | 5 | 23 | 17 | 26072.5403
2027 | 2008 | 5 | 23 | 18 | 27184.9404
2027 | 2008 | 5 | 23 | 19 | 28474.4073
2027 | 2008 | 5 | 23 | 20 | 27783.5415
2027 | 2008 | 5 | 23 | 21 | 27445.7783
2027 | 2008 | 5 | 23 | 22 | 25477.7664
2027 | 2008 | 5 | 23 | 23 | 24561.347
2027 | 2008 | 5 | 23 | 24 | 25810.3705
2027 | 2008 | 5 | 24 | 1 | 25299.1968
2027 | 2008 | 5 | 24 | 2 | 24435.9191
2027 | 2008 | 5 | 24 | 3 | 22980.906
2027 | 2008 | 5 | 24 | 4 | 20498.6953
2027 | 2008 | 5 | 24 | 5 | 18495.6543
2027 | 2008 | 5 | 24 | 6 | 17539.975
2027 | 2008 | 5 | 24 | 7 | 15091.4826
2027 | 2008 | 5 | 24 | 8 | 10902.8225
2027 | 2008 | 5 | 24 | 9 | 9238.953
2027 | 2008 | 5 | 24 | 10 | 8749.9068
2027 | 2008 | 5 | 24 | 11 | 6824.9708
2027 | 2008 | 5 | 24 | 12 | 5962.6083
2027 | 2008 | 5 | 24 | 13 | 5796.5109
2027 | 2008 | 5 | 24 | 14 | 6623.9709
2027 | 2008 | 5 | 24 | 15 | 7436.2514
2027 | 2008 | 5 | 24 | 16 | 9470.8131
2027 | 2008 | 5 | 24 | 17 | 11608.7662
2027 | 2008 | 5 | 24 | 18 | 15148.4594
2027 | 2008 | 5 | 24 | 19 | 17235.4492
2027 | 2008 | 5 | 24 | 20 | 18751.1035
2027 | 2008 | 5 | 24 | 21 | 21124.1005
2027 | 2008 | 5 | 24 | 22 | 24877.8461
2027 | 2008 | 5 | 24 | 23 | 27577.0889
2027 | 2008 | 5 | 24 | 24 | 28198.3257
2027 | 2008 | 5 | 25 | 1 | 27813.9081
2027 | 2008 | 5 | 25 | 2 | 27389.3082
2027 | 2008 | 5 | 25 | 3 | 26489.3561
2027 | 2008 | 5 | 25 | 4 | 25269.7638
2027 | 2008 | 5 | 25 | 5 | 23453.0396
2027 | 2008 | 5 | 25 | 6 | 21973.6428
2027 | 2008 | 5 | 25 | 7 | 21264.4684
2027 | 2008 | 5 | 25 | 8 | 21301.0841
2027 | 2008 | 5 | 25 | 9 | 23581.5041
2027 | 2008 | 5 | 25 | 10 | 24888.1971
2027 | 2008 | 5 | 25 | 11 | 26467.8081
2027 | 2008 | 5 | 25 | 12 | 27027.8312
2027 | 2008 | 5 | 25 | 13 | 26661.9917
2027 | 2008 | 5 | 25 | 14 | 26917.9077
2027 | 2008 | 5 | 25 | 15 | 26090.9071
2027 | 2008 | 5 | 25 | 16 | 25827.8834
2027 | 2008 | 5 | 25 | 17 | 26967.4762
2027 | 2008 | 5 | 25 | 18 | 27785.0942
2027 | 2008 | 5 | 25 | 19 | 28882.6875
2027 | 2008 | 5 | 25 | 20 | 28210.0158
2027 | 2008 | 5 | 25 | 21 | 28067.6929
2027 | 2008 | 5 | 25 | 22 | 27915.2846
2027 | 2008 | 5 | 25 | 23 | 28028.2568
2027 | 2008 | 5 | 25 | 24 | 28331.2848
2027 | 2008 | 5 | 26 | 1 | 28841.7973
2027 | 2008 | 5 | 26 | 2 | 29432.2687
2027 | 2008 | 5 | 26 | 3 | 30094.9705
2027 | 2008 | 5 | 26 | 4 | 28981.6749
2027 | 2008 | 5 | 26 | 5 | 28663.9869
2027 | 2008 | 5 | 26 | 6 | 28816.6944
2027 | 2008 | 5 | 26 | 7 | 28390.8412
2027 | 2008 | 5 | 26 | 8 | 29293.0436
2027 | 2008 | 5 | 26 | 9 | 31958.6643
2027 | 2008 | 5 | 26 | 10 | 32419.6833
2027 | 2008 | 5 | 26 | 11 | 32324.133
2027 | 2008 | 5 | 26 | 12 | 31056.4474
2027 | 2008 | 5 | 26 | 13 | 30015.0757
2027 | 2008 | 5 | 26 | 14 | 29350.3388
2027 | 2008 | 5 | 26 | 15 | 28251.7595
2027 | 2008 | 5 | 26 | 16 | 28070.9187
2027 | 2008 | 5 | 26 | 17 | 29199.2776
2027 | 2008 | 5 | 26 | 18 | 30430.3613
2027 | 2008 | 5 | 26 | 19 | 31113.5384
2027 | 2008 | 5 | 26 | 20 | 31121.4116
2027 | 2008 | 5 | 26 | 21 | 30477.3282
2027 | 2008 | 5 | 26 | 22 | 30794.0707
2027 | 2008 | 5 | 26 | 23 | 31423.8781
2027 | 2008 | 5 | 26 | 24 | 31726.7543
2027 | 2008 | 5 | 27 | 1 | 30832.2415
2027 | 2008 | 5 | 27 | 2 | 29413.6486
2027 | 2008 | 5 | 27 | 3 | 27193.0066
2027 | 2008 | 5 | 27 | 4 | 26001.2743
2027 | 2008 | 5 | 27 | 5 | 25243.2591
2027 | 2008 | 5 | 27 | 6 | 24810.0501
2027 | 2008 | 5 | 27 | 7 | 24595.9021
2027 | 2008 | 5 | 27 | 8 | 25301.9166
2027 | 2008 | 5 | 27 | 9 | 27246.1749
2027 | 2008 | 5 | 27 | 10 | 28101.7041
2027 | 2008 | 5 | 27 | 11 | 27167.5385
2027 | 2008 | 5 | 27 | 12 | 24615.2387
2027 | 2008 | 5 | 27 | 13 | 21628.4522
2027 | 2008 | 5 | 27 | 14 | 19716.0363
2027 | 2008 | 5 | 27 | 15 | 18099.9958
2027 | 2008 | 5 | 27 | 16 | 17704.4437
2027 | 2008 | 5 | 27 | 17 | 18302.5774
2027 | 2008 | 5 | 27 | 18 | 19365.3878
2027 | 2008 | 5 | 27 | 19 | 19829.4141
2027 | 2008 | 5 | 27 | 20 | 20010.7452
2027 | 2008 | 5 | 27 | 21 | 21524.2585
2027 | 2008 | 5 | 27 | 22 | 20173.1682
2027 | 2008 | 5 | 27 | 23 | 19652.0876
2027 | 2008 | 5 | 27 | 24 | 19284.0315
2027 | 2008 | 5 | 28 | 1 | 17318.1512
2027 | 2008 | 5 | 28 | 2 | 16290.5373
2027 | 2008 | 5 | 28 | 3 | 14853.9012
2027 | 2008 | 5 | 28 | 4 | 12745.0627
2027 | 2008 | 5 | 28 | 5 | 12208.2693
2027 | 2008 | 5 | 28 | 6 | 10304.1293
2027 | 2008 | 5 | 28 | 7 | 8967.1787
2027 | 2008 | 5 | 28 | 8 | 7353.1585
2027 | 2008 | 5 | 28 | 9 | 7114.2078
2027 | 2008 | 5 | 28 | 10 | 6093.1334
2027 | 2008 | 5 | 28 | 11 | 5169.8116
2027 | 2008 | 5 | 28 | 12 | 5101.4527
2027 | 2008 | 5 | 28 | 13 | 4932
2027 | 2008 | 5 | 28 | 14 | 6155.1165
2027 | 2008 | 5 | 28 | 15 | 6859.1856
2027 | 2008 | 5 | 28 | 16 | 7913.9882
2027 | 2008 | 5 | 28 | 17 | 9168.8684
2027 | 2008 | 5 | 28 | 18 | 10412.7211
2027 | 2008 | 5 | 28 | 19 | 10791.6784
2027 | 2008 | 5 | 28 | 20 | 12099.175
2027 | 2008 | 5 | 28 | 21 | 14722.1795
2027 | 2008 | 5 | 28 | 22 | 17632.8478
2027 | 2008 | 5 | 28 | 23 | 19879.1578
2027 | 2008 | 5 | 28 | 24 | 20445.6126
2027 | 2008 | 5 | 29 | 1 | 21259.3974
2027 | 2008 | 5 | 29 | 2 | 21379.7543
2027 | 2008 | 5 | 29 | 3 | 20550.6203
2027 | 2008 | 5 | 29 | 4 | 19319.1177
2027 | 2008 | 5 | 29 | 5 | 18930.011
2027 | 2008 | 5 | 29 | 6 | 17943.7461
2027 | 2008 | 5 | 29 | 7 | 17840.7278
2027 | 2008 | 5 | 29 | 8 | 16536.0868
2027 | 2008 | 5 | 29 | 9 | 16211.6834
2027 | 2008 | 5 | 29 | 10 | 20117.205
2027 | 2008 | 5 | 29 | 11 | 20362.6531
2027 | 2008 | 5 | 29 | 12 | 20337.9138
2027 | 2008 | 5 | 29 | 13 | 20923.6594
2027 | 2008 | 5 | 29 | 14 | 22079.759
2027 | 2008 | 5 | 29 | 15 | 22318.0591
2027 | 2008 | 5 | 29 | 16 | 23019.5634
2027 | 2008 | 5 | 29 | 17 | 24277.2082
2027 | 2008 | 5 | 29 | 18 | 25456.1423
2027 | 2008 | 5 | 29 | 19 | 25143.9234
2027 | 2008 | 5 | 29 | 20 | 25351.2611
2027 | 2008 | 5 | 29 | 21 | 26064.104
2027 | 2008 | 5 | 29 | 22 | 27685.703
2027 | 2008 | 5 | 29 | 23 | 29033.0199
2027 | 2008 | 5 | 29 | 24 | 29714.9101
2027 | 2008 | 5 | 30 | 1 | 30118.7052
2027 | 2008 | 5 | 30 | 2 | 30241.0776
2027 | 2008 | 5 | 30 | 3 | 29777.1414
2027 | 2008 | 5 | 30 | 4 | 29307.5928
2027 | 2008 | 5 | 30 | 5 | 28394.1329
2027 | 2008 | 5 | 30 | 6 | 27694.3273
2027 | 2008 | 5 | 30 | 7 | 26600.8023
2027 | 2008 | 5 | 30 | 8 | 25769.2815
2027 | 2008 | 5 | 30 | 9 | 26370.4321
2027 | 2008 | 5 | 30 | 10 | 27295.7005
2027 | 2008 | 5 | 30 | 11 | 23983.7053
2027 | 2008 | 5 | 30 | 12 | 21106.7953
2027 | 2008 | 5 | 30 | 13 | 19809.904
2027 | 2008 | 5 | 30 | 14 | 19417.5873
2027 | 2008 | 5 | 30 | 15 | 18586.6174
2027 | 2008 | 5 | 30 | 16 | 19587.5566
2027 | 2008 | 5 | 30 | 17 | 20832.3684
2027 | 2008 | 5 | 30 | 18 | 22901.3692
2027 | 2008 | 5 | 30 | 19 | 24183.97
2027 | 2008 | 5 | 30 | 20 | 25682.0426
2027 | 2008 | 5 | 30 | 21 | 27602.109
2027 | 2008 | 5 | 30 | 22 | 29846.8305
2027 | 2008 | 5 | 30 | 23 | 30183.3135
2027 | 2008 | 5 | 30 | 24 | 30229.0729
2027 | 2008 | 5 | 31 | 1 | 30441.1262
2027 | 2008 | 5 | 31 | 2 | 30399.4636
2027 | 2008 | 5 | 31 | 3 | 30251.243
2027 | 2008 | 5 | 31 | 4 | 29482.9333
2027 | 2008 | 5 | 31 | 5 | 27699.6615
2027 | 2008 | 5 | 31 | 6 | 26128.0428
2027 | 2008 | 5 | 31 | 7 | 24337.4351
2027 | 2008 | 5 | 31 | 8 | 22271.1378
2027 | 2008 | 5 | 31 | 9 | 21549.7203
2027 | 2008 | 5 | 31 | 10 | 21924.8993
2027 | 2008 | 5 | 31 | 11 | 19671.7845
2027 | 2008 | 5 | 31 | 12 | 18935.1432
2027 | 2008 | 5 | 31 | 13 | 19153.3051
2027 | 2008 | 5 | 31 | 14 | 19904.1333
2027 | 2008 | 5 | 31 | 15 | 21075.6715
2027 | 2008 | 5 | 31 | 16 | 22323.6568
2027 | 2008 | 5 | 31 | 17 | 23865.5622
2027 | 2008 | 5 | 31 | 18 | 25381.6105
2027 | 2008 | 5 | 31 | 19 | 27333.1033
2027 | 2008 | 5 | 31 | 20 | 28669.9024
2027 | 2008 | 5 | 31 | 21 | 28674.291
2027 | 2008 | 5 | 31 | 22 | 29664.3229
2027 | 2008 | 5 | 31 | 23 | 29451.4938
2027 | 2008 | 5 | 31 | 24 | 29818.9165
2028 | 2008 | 5 | 1 | 1 | 38220.9563
2028 | 2008 | 5 | 1 | 2 | 37787.8419
2028 | 2008 | 5 | 1 | 3 | 37007.3039
2028 | 2008 | 5 | 1 | 4 | 35678.297
2028 | 2008 | 5 | 1 | 5 | 35165.9999
2028 | 2008 | 5 | 1 | 6 | 34977.5505
2028 | 2008 | 5 | 1 | 7 | 33745.649
2028 | 2008 | 5 | 1 | 8 | 31957.3819
2028 | 2008 | 5 | 1 | 9 | 31624.0711
2028 | 2008 | 5 | 1 | 10 | 31522.1803
2028 | 2008 | 5 | 1 | 11 | 31384.5934
2028 | 2008 | 5 | 1 | 12 | 30284.6606
2028 | 2008 | 5 | 1 | 13 | 29368.1639
2028 | 2008 | 5 | 1 | 14 | 28757.7872
2028 | 2008 | 5 | 1 | 15 | 28296.449
2028 | 2008 | 5 | 1 | 16 | 27712.0359
2028 | 2008 | 5 | 1 | 17 | 29449.3684
2028 | 2008 | 5 | 1 | 18 | 29829.0034
2028 | 2008 | 5 | 1 | 19 | 31230.152
2028 | 2008 | 5 | 1 | 20 | 31639.2453
2028 | 2008 | 5 | 1 | 21 | 32664.1658
2028 | 2008 | 5 | 1 | 22 | 34214.4923
2028 | 2008 | 5 | 1 | 23 | 34126.781
2028 | 2008 | 5 | 1 | 24 | 33833.5364
2028 | 2008 | 5 | 2 | 1 | 34294.5882
2028 | 2008 | 5 | 2 | 2 | 33140.1891
2028 | 2008 | 5 | 2 | 3 | 33038.6137
2028 | 2008 | 5 | 2 | 4 | 32871.4875
2028 | 2008 | 5 | 2 | 5 | 32325.9765
2028 | 2008 | 5 | 2 | 6 | 30490.2478
2028 | 2008 | 5 | 2 | 7 | 28323.9398
2028 | 2008 | 5 | 2 | 8 | 21474.4325
2028 | 2008 | 5 | 2 | 9 | 15412.9545
2028 | 2008 | 5 | 2 | 10 | 11956.303
2028 | 2008 | 5 | 2 | 11 | 8045.9221
2028 | 2008 | 5 | 2 | 12 | 7944.6113
2028 | 2008 | 5 | 2 | 13 | 10135.4971
2028 | 2008 | 5 | 2 | 14 | 13023.3595
2028 | 2008 | 5 | 2 | 15 | 15859.1994
2028 | 2008 | 5 | 2 | 16 | 16849.1507
2028 | 2008 | 5 | 2 | 17 | 16977.1525
2028 | 2008 | 5 | 2 | 18 | 15956.3333
2028 | 2008 | 5 | 2 | 19 | 12579.5869
2028 | 2008 | 5 | 2 | 20 | 10846.828
2028 | 2008 | 5 | 2 | 21 | 10594.4512
2028 | 2008 | 5 | 2 | 22 | 12173.9669
2028 | 2008 | 5 | 2 | 23 | 14490.1878
2028 | 2008 | 5 | 2 | 24 | 17600.878
2028 | 2008 | 5 | 3 | 1 | 21750.8162
2028 | 2008 | 5 | 3 | 2 | 24058.7996
2028 | 2008 | 5 | 3 | 3 | 25149.0495
2028 | 2008 | 5 | 3 | 4 | 26270.7593
2028 | 2008 | 5 | 3 | 5 | 26782.3094
2028 | 2008 | 5 | 3 | 6 | 26883.7315
2028 | 2008 | 5 | 3 | 7 | 25775.9133
2028 | 2008 | 5 | 3 | 8 | 25391.0143
2028 | 2008 | 5 | 3 | 9 | 26469.9707
2028 | 2008 | 5 | 3 | 10 | 25577.3645
2028 | 2008 | 5 | 3 | 11 | 20420.1515
2028 | 2008 | 5 | 3 | 12 | 16269.3087
2028 | 2008 | 5 | 3 | 13 | 14229.1794
2028 | 2008 | 5 | 3 | 14 | 12721.3294
2028 | 2008 | 5 | 3 | 15 | 11494.1936
2028 | 2008 | 5 | 3 | 16 | 10360.5633
2028 | 2008 | 5 | 3 | 17 | 10050.9536
2028 | 2008 | 5 | 3 | 18 | 10118.3507
2028 | 2008 | 5 | 3 | 19 | 9705.1793
2028 | 2008 | 5 | 3 | 20 | 9547.8173
2028 | 2008 | 5 | 3 | 21 | 10233.7195
2028 | 2008 | 5 | 3 | 22 | 11224.7026
2028 | 2008 | 5 | 3 | 23 | 13335.7008
2028 | 2008 | 5 | 3 | 24 | 13881.8286
2028 | 2008 | 5 | 4 | 1 | 14043.9308
2028 | 2008 | 5 | 4 | 2 | 14124.996
2028 | 2008 | 5 | 4 | 3 | 14088.0201
2028 | 2008 | 5 | 4 | 4 | 13998.9968
2028 | 2008 | 5 | 4 | 5 | 14230.4128
2028 | 2008 | 5 | 4 | 6 | 14238.1678
2028 | 2008 | 5 | 4 | 7 | 14819.5193
2028 | 2008 | 5 | 4 | 8 | 12022.8801
2028 | 2008 | 5 | 4 | 9 | 11418.5789
2028 | 2008 | 5 | 4 | 10 | 13573.0814
2028 | 2008 | 5 | 4 | 11 | 14978.551
2028 | 2008 | 5 | 4 | 12 | 15540.5772
2028 | 2008 | 5 | 4 | 13 | 16639.6103
2028 | 2008 | 5 | 4 | 14 | 17705.1728
2028 | 2008 | 5 | 4 | 15 | 18270.9454
2028 | 2008 | 5 | 4 | 16 | 18789.661
2028 | 2008 | 5 | 4 | 17 | 20804.4494
2028 | 2008 | 5 | 4 | 18 | 22463.7432
2028 | 2008 | 5 | 4 | 19 | 23789.8397
2028 | 2008 | 5 | 4 | 20 | 23253.4556
2028 | 2008 | 5 | 4 | 21 | 23910.646
2028 | 2008 | 5 | 4 | 22 | 24881.571
2028 | 2008 | 5 | 4 | 23 | 24511.7045
2028 | 2008 | 5 | 4 | 24 | 23035.6939
2028 | 2008 | 5 | 5 | 1 | 21675.4544
2028 | 2008 | 5 | 5 | 2 | 21108.087
2028 | 2008 | 5 | 5 | 3 | 20916.866
2028 | 2008 | 5 | 5 | 4 | 19384.754
2028 | 2008 | 5 | 5 | 5 | 17415.5531
2028 | 2008 | 5 | 5 | 6 | 16415.1053
2028 | 2008 | 5 | 5 | 7 | 14515.434
2028 | 2008 | 5 | 5 | 8 | 15286.8703
2028 | 2008 | 5 | 5 | 9 | 18316.9406
2028 | 2008 | 5 | 5 | 10 | 19889.7038
2028 | 2008 | 5 | 5 | 11 | 21068.9216
2028 | 2008 | 5 | 5 | 12 | 21921.8073
2028 | 2008 | 5 | 5 | 13 | 22121.5879
2028 | 2008 | 5 | 5 | 14 | 22953.4723
2028 | 2008 | 5 | 5 | 15 | 22586.0335
2028 | 2008 | 5 | 5 | 16 | 22386.6686
2028 | 2008 | 5 | 5 | 17 | 24472.7207
2028 | 2008 | 5 | 5 | 18 | 26486.2212
2028 | 2008 | 5 | 5 | 19 | 27997.9272
2028 | 2008 | 5 | 5 | 20 | 30067.3669
2028 | 2008 | 5 | 5 | 21 | 31606.2509
2028 | 2008 | 5 | 5 | 22 | 31963.6256
2028 | 2008 | 5 | 5 | 23 | 31574.615
2028 | 2008 | 5 | 5 | 24 | 30210.5706
2028 | 2008 | 5 | 6 | 1 | 28143.3394
2028 | 2008 | 5 | 6 | 2 | 25054.9808
2028 | 2008 | 5 | 6 | 3 | 22041.2432
2028 | 2008 | 5 | 6 | 4 | 19427.1869
2028 | 2008 | 5 | 6 | 5 | 19308.4772
2028 | 2008 | 5 | 6 | 6 | 20840.9175
2028 | 2008 | 5 | 6 | 7 | 21882.71
2028 | 2008 | 5 | 6 | 8 | 24205.9338
2028 | 2008 | 5 | 6 | 9 | 28467.7083
2028 | 2008 | 5 | 6 | 10 | 30196.9507
2028 | 2008 | 5 | 6 | 11 | 29998.0111
2028 | 2008 | 5 | 6 | 12 | 30278.3208
2028 | 2008 | 5 | 6 | 13 | 31731.1096
2028 | 2008 | 5 | 6 | 14 | 33524.7132
2028 | 2008 | 5 | 6 | 15 | 34581.2273
2028 | 2008 | 5 | 6 | 16 | 35094.3697
2028 | 2008 | 5 | 6 | 17 | 34491.3821
2028 | 2008 | 5 | 6 | 18 | 34893.3885
2028 | 2008 | 5 | 6 | 19 | 33893.6689
2028 | 2008 | 5 | 6 | 20 | 34284.2799
2028 | 2008 | 5 | 6 | 21 | 33412.5867
2028 | 2008 | 5 | 6 | 22 | 34104.4158
2028 | 2008 | 5 | 6 | 23 | 34322.1652
2028 | 2008 | 5 | 6 | 24 | 32958.5508
2028 | 2008 | 5 | 7 | 1 | 31920.0252
2028 | 2008 | 5 | 7 | 2 | 31502.8389
2028 | 2008 | 5 | 7 | 3 | 31656.8233
2028 | 2008 | 5 | 7 | 4 | 31771.4749
2028 | 2008 | 5 | 7 | 5 | 31747.9222
2028 | 2008 | 5 | 7 | 6 | 31897.4401
2028 | 2008 | 5 | 7 | 7 | 32026.103
2028 | 2008 | 5 | 7 | 8 | 32203.5425
2028 | 2008 | 5 | 7 | 9 | 33251.2756
2028 | 2008 | 5 | 7 | 10 | 32534.3505
2028 | 2008 | 5 | 7 | 11 | 31899.27
2028 | 2008 | 5 | 7 | 12 | 30182.1539
2028 | 2008 | 5 | 7 | 13 | 29953.646
2028 | 2008 | 5 | 7 | 14 | 29728.371
2028 | 2008 | 5 | 7 | 15 | 32242.0559
2028 | 2008 | 5 | 7 | 16 | 32648.2636
2028 | 2008 | 5 | 7 | 17 | 33231.8237
2028 | 2008 | 5 | 7 | 18 | 32451.4029
2028 | 2008 | 5 | 7 | 19 | 29164.9129
2028 | 2008 | 5 | 7 | 20 | 27947.3626
2028 | 2008 | 5 | 7 | 21 | 25496.7507
2028 | 2008 | 5 | 7 | 22 | 23500.6622
2028 | 2008 | 5 | 7 | 23 | 22597.0249
2028 | 2008 | 5 | 7 | 24 | 21028.9589
2028 | 2008 | 5 | 8 | 1 | 18676.361
2028 | 2008 | 5 | 8 | 2 | 17546.1791
2028 | 2008 | 5 | 8 | 3 | 14882.4765
2028 | 2008 | 5 | 8 | 4 | 12359.3001
2028 | 2008 | 5 | 8 | 5 | 11158.5357
2028 | 2008 | 5 | 8 | 6 | 9094.326
2028 | 2008 | 5 | 8 | 7 | 8067.5376
2028 | 2008 | 5 | 8 | 8 | 5661.5957
2028 | 2008 | 5 | 8 | 9 | 4529.3329
2028 | 2008 | 5 | 8 | 10 | 3488.4192
2028 | 2008 | 5 | 8 | 11 | 3832.6148
2028 | 2008 | 5 | 8 | 12 | 4707.4723
2028 | 2008 | 5 | 8 | 13 | 6188.3747
2028 | 2008 | 5 | 8 | 14 | 8305.609
2028 | 2008 | 5 | 8 | 15 | 10237.3229
2028 | 2008 | 5 | 8 | 16 | 13132.8263
2028 | 2008 | 5 | 8 | 17 | 16650.7533
2028 | 2008 | 5 | 8 | 18 | 20363.5454
2028 | 2008 | 5 | 8 | 19 | 20821.8185
2028 | 2008 | 5 | 8 | 20 | 23130.8336
2028 | 2008 | 5 | 8 | 21 | 25993.5533
2028 | 2008 | 5 | 8 | 22 | 29854.8522
2028 | 2008 | 5 | 8 | 23 | 30204.4519
2028 | 2008 | 5 | 8 | 24 | 29861.0557
2028 | 2008 | 5 | 9 | 1 | 30995.2945
2028 | 2008 | 5 | 9 | 2 | 30179.2889
2028 | 2008 | 5 | 9 | 3 | 29650.1293
2028 | 2008 | 5 | 9 | 4 | 27550.1592
2028 | 2008 | 5 | 9 | 5 | 25669.5985
2028 | 2008 | 5 | 9 | 6 | 23803.7372
2028 | 2008 | 5 | 9 | 7 | 19687.1645
2028 | 2008 | 5 | 9 | 8 | 13906.3422
2028 | 2008 | 5 | 9 | 9 | 9645.3602
2028 | 2008 | 5 | 9 | 10 | 8113.3323
2028 | 2008 | 5 | 9 | 11 | 7528.5876
2028 | 2008 | 5 | 9 | 12 | 7439.1148
2028 | 2008 | 5 | 9 | 13 | 7162.5351
2028 | 2008 | 5 | 9 | 14 | 6779.4845
2028 | 2008 | 5 | 9 | 15 | 6426.1822
2028 | 2008 | 5 | 9 | 16 | 6839.5399
2028 | 2008 | 5 | 9 | 17 | 7728.7467
2028 | 2008 | 5 | 9 | 18 | 8623.0402
2028 | 2008 | 5 | 9 | 19 | 9452.4526
2028 | 2008 | 5 | 9 | 20 | 11197.1213
2028 | 2008 | 5 | 9 | 21 | 14898.4761
2028 | 2008 | 5 | 9 | 22 | 18724.9759
2028 | 2008 | 5 | 9 | 23 | 22361.0248
2028 | 2008 | 5 | 9 | 24 | 24570.8682
2028 | 2008 | 5 | 10 | 1 | 26391.9502
2028 | 2008 | 5 | 10 | 2 | 26687.0673
2028 | 2008 | 5 | 10 | 3 | 26090.7494
2028 | 2008 | 5 | 10 | 4 | 25493.7907
2028 | 2008 | 5 | 10 | 5 | 25176.3695
2028 | 2008 | 5 | 10 | 6 | 25500.0044
2028 | 2008 | 5 | 10 | 7 | 24967.0618
2028 | 2008 | 5 | 10 | 8 | 23545.1263
2028 | 2008 | 5 | 10 | 9 | 23524.3516
2028 | 2008 | 5 | 10 | 10 | 24803.3223
2028 | 2008 | 5 | 10 | 11 | 25062.1221
2028 | 2008 | 5 | 10 | 12 | 26724.7998
2028 | 2008 | 5 | 10 | 13 | 27640.1086
2028 | 2008 | 5 | 10 | 14 | 26871.9543
2028 | 2008 | 5 | 10 | 15 | 26110.366
2028 | 2008 | 5 | 10 | 16 | 25072.2704
2028 | 2008 | 5 | 10 | 17 | 24087.4002
2028 | 2008 | 5 | 10 | 18 | 22456.0075
2028 | 2008 | 5 | 10 | 19 | 19919.6607
2028 | 2008 | 5 | 10 | 20 | 19082.2148
2028 | 2008 | 5 | 10 | 21 | 18936.4323
2028 | 2008 | 5 | 10 | 22 | 19834.0576
2028 | 2008 | 5 | 10 | 23 | 23426.9033
2028 | 2008 | 5 | 10 | 24 | 26036.8667
2028 | 2008 | 5 | 11 | 1 | 28644.7855
2028 | 2008 | 5 | 11 | 2 | 29589.2307
2028 | 2008 | 5 | 11 | 3 | 29607.939
2028 | 2008 | 5 | 11 | 4 | 28137.8135
2028 | 2008 | 5 | 11 | 5 | 27200.2345
2028 | 2008 | 5 | 11 | 6 | 26073.0522
2028 | 2008 | 5 | 11 | 7 | 24364.2765
2028 | 2008 | 5 | 11 | 8 | 22992.8635
2028 | 2008 | 5 | 11 | 9 | 23335.4809
2028 | 2008 | 5 | 11 | 10 | 21026.3277
2028 | 2008 | 5 | 11 | 11 | 16599.6667
2028 | 2008 | 5 | 11 | 12 | 15375.0939
2028 | 2008 | 5 | 11 | 13 | 14566.4454
2028 | 2008 | 5 | 11 | 14 | 13919.511
2028 | 2008 | 5 | 11 | 15 | 13263.5041
2028 | 2008 | 5 | 11 | 16 | 12513.9859
2028 | 2008 | 5 | 11 | 17 | 12476.7963
2028 | 2008 | 5 | 11 | 18 | 12468.1859
2028 | 2008 | 5 | 11 | 19 | 12496.7202
2028 | 2008 | 5 | 11 | 20 | 12590.7479
2028 | 2008 | 5 | 11 | 21 | 14012.3056
2028 | 2008 | 5 | 11 | 22 | 15868.2818
2028 | 2008 | 5 | 11 | 23 | 17686.2732
2028 | 2008 | 5 | 11 | 24 | 18495.4297
2028 | 2008 | 5 | 12 | 1 | 20403.9353
2028 | 2008 | 5 | 12 | 2 | 21811.8597
2028 | 2008 | 5 | 12 | 3 | 22202.7369
2028 | 2008 | 5 | 12 | 4 | 23128.3937
2028 | 2008 | 5 | 12 | 5 | 23759.9769
2028 | 2008 | 5 | 12 | 6 | 24950.3374
2028 | 2008 | 5 | 12 | 7 | 25777.7505
2028 | 2008 | 5 | 12 | 8 | 24595.869
2028 | 2008 | 5 | 12 | 9 | 24310.6673
2028 | 2008 | 5 | 12 | 10 | 27891.068
2028 | 2008 | 5 | 12 | 11 | 29695.2047
2028 | 2008 | 5 | 12 | 12 | 31016.6562
2028 | 2008 | 5 | 12 | 13 | 31671.2689
2028 | 2008 | 5 | 12 | 14 | 33061.3119
2028 | 2008 | 5 | 12 | 15 | 33663.3367
2028 | 2008 | 5 | 12 | 16 | 34969.1332
2028 | 2008 | 5 | 12 | 17 | 35613.0232
2028 | 2008 | 5 | 12 | 18 | 36237.9633
2028 | 2008 | 5 | 12 | 19 | 36192.8603
2028 | 2008 | 5 | 12 | 20 | 34584.2864
2028 | 2008 | 5 | 12 | 21 | 33482.2839
2028 | 2008 | 5 | 12 | 22 | 34183.7254
2028 | 2008 | 5 | 12 | 23 | 34751.5973
2028 | 2008 | 5 | 12 | 24 | 35190.6625
2028 | 2008 | 5 | 13 | 1 | 35554.0974
2028 | 2008 | 5 | 13 | 2 | 35848.2227
2028 | 2008 | 5 | 13 | 3 | 35225.8016
2028 | 2008 | 5 | 13 | 4 | 33526.7454
2028 | 2008 | 5 | 13 | 5 | 32685.96
2028 | 2008 | 5 | 13 | 6 | 30746.3991
2028 | 2008 | 5 | 13 | 7 | 28958.967
2028 | 2008 | 5 | 13 | 8 | 27133.8296
2028 | 2008 | 5 | 13 | 9 | 26454.934
2028 | 2008 | 5 | 13 | 10 | 24225.5726
2028 | 2008 | 5 | 13 | 11 | 20174.9992
2028 | 2008 | 5 | 13 | 12 | 16499.903
2028 | 2008 | 5 | 13 | 13 | 14557.7123
2028 | 2008 | 5 | 13 | 14 | 13002.2463
2028 | 2008 | 5 | 13 | 15 | 12543.4797
2028 | 2008 | 5 | 13 | 16 | 12852.536
2028 | 2008 | 5 | 13 | 17 | 14346.1844
2028 | 2008 | 5 | 13 | 18 | 16424.6649
2028 | 2008 | 5 | 13 | 19 | 20035.0353
2028 | 2008 | 5 | 13 | 20 | 22471.9358
2028 | 2008 | 5 | 13 | 21 | 26501.0592
2028 | 2008 | 5 | 13 | 22 | 25083.1889
2028 | 2008 | 5 | 13 | 23 | 24988.2002
2028 | 2008 | 5 | 13 | 24 | 25617.1887
2028 | 2008 | 5 | 14 | 1 | 25778.9564
2028 | 2008 | 5 | 14 | 2 | 24682.7056
2028 | 2008 | 5 | 14 | 3 | 22492.0429
2028 | 2008 | 5 | 14 | 4 | 20718.2249
2028 | 2008 | 5 | 14 | 5 | 19995.6083
2028 | 2008 | 5 | 14 | 6 | 19124.1302
2028 | 2008 | 5 | 14 | 7 | 19212.0496
2028 | 2008 | 5 | 14 | 8 | 19115.3493
2028 | 2008 | 5 | 14 | 9 | 20758.3365
2028 | 2008 | 5 | 14 | 10 | 20519.8996
2028 | 2008 | 5 | 14 | 11 | 18784.5115
2028 | 2008 | 5 | 14 | 12 | 17099.0056
2028 | 2008 | 5 | 14 | 13 | 15081.4862
2028 | 2008 | 5 | 14 | 14 | 13427.0189
2028 | 2008 | 5 | 14 | 15 | 13576.1792
2028 | 2008 | 5 | 14 | 16 | 14036.5979
2028 | 2008 | 5 | 14 | 17 | 14511.4094
2028 | 2008 | 5 | 14 | 18 | 15941.6961
2028 | 2008 | 5 | 14 | 19 | 15784.0727
2028 | 2008 | 5 | 14 | 20 | 13908.3164
2028 | 2008 | 5 | 14 | 21 | 14122.6476
2028 | 2008 | 5 | 14 | 22 | 13383.6684
2028 | 2008 | 5 | 14 | 23 | 11585.2389
2028 | 2008 | 5 | 14 | 24 | 8516.7149
2028 | 2008 | 5 | 15 | 1 | 7003.9589
2028 | 2008 | 5 | 15 | 2 | 5688.3006
2028 | 2008 | 5 | 15 | 3 | 5947.8496
2028 | 2008 | 5 | 15 | 4 | 6731.392
2028 | 2008 | 5 | 15 | 5 | 7402.7487
2028 | 2008 | 5 | 15 | 6 | 7475.9396
2028 | 2008 | 5 | 15 | 7 | 10897.6323
2028 | 2008 | 5 | 15 | 8 | 11320.999
2028 | 2008 | 5 | 15 | 9 | 13709.7015
2028 | 2008 | 5 | 15 | 10 | 12797.1558
2028 | 2008 | 5 | 15 | 11 | 10865.876
2028 | 2008 | 5 | 15 | 12 | 9955.1333
2028 | 2008 | 5 | 15 | 13 | 10282.3399
2028 | 2008 | 5 | 15 | 14 | 9823.7871
2028 | 2008 | 5 | 15 | 15 | 8176.0808
2028 | 2008 | 5 | 15 | 16 | 7965.5761
2028 | 2008 | 5 | 15 | 17 | 7712.5033
2028 | 2008 | 5 | 15 | 18 | 8319.9329
2028 | 2008 | 5 | 15 | 19 | 9574.0713
2028 | 2008 | 5 | 15 | 20 | 10630.3324
2028 | 2008 | 5 | 15 | 21 | 13483.7894
2028 | 2008 | 5 | 15 | 22 | 12993.072
2028 | 2008 | 5 | 15 | 23 | 11983.5926
2028 | 2008 | 5 | 15 | 24 | 11190.3568
2028 | 2008 | 5 | 16 | 1 | 10165.8582
2028 | 2008 | 5 | 16 | 2 | 9189.3844
2028 | 2008 | 5 | 16 | 3 | 9443.7657
2028 | 2008 | 5 | 16 | 4 | 10274.2808
2028 | 2008 | 5 | 16 | 5 | 11644.6475
2028 | 2008 | 5 | 16 | 6 | 13379.1732
2028 | 2008 | 5 | 16 | 7 | 15913.6445
2028 | 2008 | 5 | 16 | 8 | 15518.7726
2028 | 2008 | 5 | 16 | 9 | 14386.6178
2028 | 2008 | 5 | 16 | 10 | 19036.4825
2028 | 2008 | 5 | 16 | 11 | 19698.1813
2028 | 2008 | 5 | 16 | 12 | 18684.1541
2028 | 2008 | 5 | 16 | 13 | 16742.6651
2028 | 2008 | 5 | 16 | 14 | 14314.6611
2028 | 2008 | 5 | 16 | 15 | 12252.5975
2028 | 2008 | 5 | 16 | 16 | 10709.7615
2028 | 2008 | 5 | 16 | 17 | 10160.8704
2028 | 2008 | 5 | 16 | 18 | 8911.8834
2028 | 2008 | 5 | 16 | 19 | 6975.6803
2028 | 2008 | 5 | 16 | 20 | 4608.4004
2028 | 2008 | 5 | 16 | 21 | 3423.7341
2028 | 2008 | 5 | 16 | 22 | 2731.2022
2028 | 2008 | 5 | 16 | 23 | 2628.1276
2028 | 2008 | 5 | 16 | 24 | 3079.5055
2028 | 2008 | 5 | 17 | 1 | 3775.0572
2028 | 2008 | 5 | 17 | 2 | 5032.7112
2028 | 2008 | 5 | 17 | 3 | 6805.1344
2028 | 2008 | 5 | 17 | 4 | 9504.4902
2028 | 2008 | 5 | 17 | 5 | 11475.0053
2028 | 2008 | 5 | 17 | 6 | 12002.9364
2028 | 2008 | 5 | 17 | 7 | 11916.0812
2028 | 2008 | 5 | 17 | 8 | 9225.6589
2028 | 2008 | 5 | 17 | 9 | 8575.1629
2028 | 2008 | 5 | 17 | 10 | 5169.8102
2028 | 2008 | 5 | 17 | 11 | 5606.0982
2028 | 2008 | 5 | 17 | 12 | 4580.7746
2028 | 2008 | 5 | 17 | 13 | 3799.7077
2028 | 2008 | 5 | 17 | 14 | 4258.007
2028 | 2008 | 5 | 17 | 15 | 4338.9276
2028 | 2008 | 5 | 17 | 16 | 4343.3039
2028 | 2008 | 5 | 17 | 17 | 3883.1223
2028 | 2008 | 5 | 17 | 18 | 4208.1862
2028 | 2008 | 5 | 17 | 19 | 4159.2534
2028 | 2008 | 5 | 17 | 20 | 4039.5193
2028 | 2008 | 5 | 17 | 21 | 5404.3641
2028 | 2008 | 5 | 17 | 22 | 7035.4259
2028 | 2008 | 5 | 17 | 23 | 8746.5503
2028 | 2008 | 5 | 17 | 24 | 9583.1392
2028 | 2008 | 5 | 18 | 1 | 11173.6799
2028 | 2008 | 5 | 18 | 2 | 12440.7639
2028 | 2008 | 5 | 18 | 3 | 15214.1489
2028 | 2008 | 5 | 18 | 4 | 17004.9386
2028 | 2008 | 5 | 18 | 5 | 18839.5617
2028 | 2008 | 5 | 18 | 6 | 20019.7793
2028 | 2008 | 5 | 18 | 7 | 20750.2155
2028 | 2008 | 5 | 18 | 8 | 15712.6132
2028 | 2008 | 5 | 18 | 9 | 11410.1047
2028 | 2008 | 5 | 18 | 10 | 7275.3253
2028 | 2008 | 5 | 18 | 11 | 7848.9223
2028 | 2008 | 5 | 18 | 12 | 7231.9575
2028 | 2008 | 5 | 18 | 13 | 6388.3968
2028 | 2008 | 5 | 18 | 14 | 5480.215
2028 | 2008 | 5 | 18 | 15 | 4380.3431
2028 | 2008 | 5 | 18 | 16 | 3446.7733
2028 | 2008 | 5 | 18 | 17 | 2920.6243
2028 | 2008 | 5 | 18 | 18 | 2433.9258
2028 | 2008 | 5 | 18 | 19 | 2055.7505
2028 | 2008 | 5 | 18 | 20 | 2604.8579
2028 | 2008 | 5 | 18 | 21 | 4360.6614
2028 | 2008 | 5 | 18 | 22 | 8800.2658
2028 | 2008 | 5 | 18 | 23 | 15138.0913
2028 | 2008 | 5 | 18 | 24 | 20017.3779
2028 | 2008 | 5 | 19 | 1 | 24700.2274
2028 | 2008 | 5 | 19 | 2 | 28077.0765
2028 | 2008 | 5 | 19 | 3 | 29937.7781
2028 | 2008 | 5 | 19 | 4 | 30462.4529
2028 | 2008 | 5 | 19 | 5 | 30348.2893
2028 | 2008 | 5 | 19 | 6 | 29647.7624
2028 | 2008 | 5 | 19 | 7 | 28702.4176
2028 | 2008 | 5 | 19 | 8 | 25533.3136
2028 | 2008 | 5 | 19 | 9 | 23277.613
2028 | 2008 | 5 | 19 | 10 | 20737.3566
2028 | 2008 | 5 | 19 | 11 | 21380.9883
2028 | 2008 | 5 | 19 | 12 | 21101.8649
2028 | 2008 | 5 | 19 | 13 | 19671.8085
2028 | 2008 | 5 | 19 | 14 | 18400.5996
2028 | 2008 | 5 | 19 | 15 | 16246.6499
2028 | 2008 | 5 | 19 | 16 | 15639.8352
2028 | 2008 | 5 | 19 | 17 | 15862.3226
2028 | 2008 | 5 | 19 | 18 | 15720.5887
2028 | 2008 | 5 | 19 | 19 | 14922.2618
2028 | 2008 | 5 | 19 | 20 | 16012.896
2028 | 2008 | 5 | 19 | 21 | 18248.8445
2028 | 2008 | 5 | 19 | 22 | 22338.6071
2028 | 2008 | 5 | 19 | 23 | 25643.1054
2028 | 2008 | 5 | 19 | 24 | 27272.7437
2028 | 2008 | 5 | 20 | 1 | 28096.4901
2028 | 2008 | 5 | 20 | 2 | 27748.0922
2028 | 2008 | 5 | 20 | 3 | 27919.8386
2028 | 2008 | 5 | 20 | 4 | 27292.6755
2028 | 2008 | 5 | 20 | 5 | 27274.1071
2028 | 2008 | 5 | 20 | 6 | 25118.7995
2028 | 2008 | 5 | 20 | 7 | 21708.2531
2028 | 2008 | 5 | 20 | 8 | 16300.5313
2028 | 2008 | 5 | 20 | 9 | 13009.5496
2028 | 2008 | 5 | 20 | 10 | 12501.1224
2028 | 2008 | 5 | 20 | 11 | 14634.0558
2028 | 2008 | 5 | 20 | 12 | 15322.5589
2028 | 2008 | 5 | 20 | 13 | 15284.3838
2028 | 2008 | 5 | 20 | 14 | 15047.2749
2028 | 2008 | 5 | 20 | 15 | 14232.7788
2028 | 2008 | 5 | 20 | 16 | 13649.8115
2028 | 2008 | 5 | 20 | 17 | 14223.0501
2028 | 2008 | 5 | 20 | 18 | 16193.0374
2028 | 2008 | 5 | 20 | 19 | 17849.7766
2028 | 2008 | 5 | 20 | 20 | 20749.2541
2028 | 2008 | 5 | 20 | 21 | 24997.174
2028 | 2008 | 5 | 20 | 22 | 25590.2466
2028 | 2008 | 5 | 20 | 23 | 25437.0175
2028 | 2008 | 5 | 20 | 24 | 24037.4628
2028 | 2008 | 5 | 21 | 1 | 21593.8891
2028 | 2008 | 5 | 21 | 2 | 20304.4759
2028 | 2008 | 5 | 21 | 3 | 20533.1955
2028 | 2008 | 5 | 21 | 4 | 20583.3109
2028 | 2008 | 5 | 21 | 5 | 20551.0563
2028 | 2008 | 5 | 21 | 6 | 21060.6959
2028 | 2008 | 5 | 21 | 7 | 21479.717
2028 | 2008 | 5 | 21 | 8 | 20836.9834
2028 | 2008 | 5 | 21 | 9 | 21923.1028
2028 | 2008 | 5 | 21 | 10 | 25227.3091
2028 | 2008 | 5 | 21 | 11 | 27789.6041
2028 | 2008 | 5 | 21 | 12 | 29367.9545
2028 | 2008 | 5 | 21 | 13 | 31373.5753
2028 | 2008 | 5 | 21 | 14 | 33234.7366
2028 | 2008 | 5 | 21 | 15 | 34015.848
2028 | 2008 | 5 | 21 | 16 | 33927.146
2028 | 2008 | 5 | 21 | 17 | 34291.0267
2028 | 2008 | 5 | 21 | 18 | 34444.6473
2028 | 2008 | 5 | 21 | 19 | 34373.1701
2028 | 2008 | 5 | 21 | 20 | 34886.3936
2028 | 2008 | 5 | 21 | 21 | 35082.4525
2028 | 2008 | 5 | 21 | 22 | 34875.4881
2028 | 2008 | 5 | 21 | 23 | 35155.8024
2028 | 2008 | 5 | 21 | 24 | 35731.112
2028 | 2008 | 5 | 22 | 1 | 35924.5859
2028 | 2008 | 5 | 22 | 2 | 36374.6733
2028 | 2008 | 5 | 22 | 3 | 36835.6438
2028 | 2008 | 5 | 22 | 4 | 36906.5587
2028 | 2008 | 5 | 22 | 5 | 36376.8696
2028 | 2008 | 5 | 22 | 6 | 35915.1346
2028 | 2008 | 5 | 22 | 7 | 35812.4938
2028 | 2008 | 5 | 22 | 8 | 36928.2599
2028 | 2008 | 5 | 22 | 9 | 37838.1181
2028 | 2008 | 5 | 22 | 10 | 38065.0494
2028 | 2008 | 5 | 22 | 11 | 37864.657
2028 | 2008 | 5 | 22 | 12 | 36649.2114
2028 | 2008 | 5 | 22 | 13 | 35109.526
2028 | 2008 | 5 | 22 | 14 | 33711.8151
2028 | 2008 | 5 | 22 | 15 | 31182.9076
2028 | 2008 | 5 | 22 | 16 | 30560.2096
2028 | 2008 | 5 | 22 | 17 | 31425.9992
2028 | 2008 | 5 | 22 | 18 | 32334.4899
2028 | 2008 | 5 | 22 | 19 | 30944.7266
2028 | 2008 | 5 | 22 | 20 | 29965.0473
2028 | 2008 | 5 | 22 | 21 | 28729.8891
2028 | 2008 | 5 | 22 | 22 | 30399.5106
2028 | 2008 | 5 | 22 | 23 | 30742.8982
2028 | 2008 | 5 | 22 | 24 | 30592.1921
2028 | 2008 | 5 | 23 | 1 | 31056.3529
2028 | 2008 | 5 | 23 | 2 | 32253.812
2028 | 2008 | 5 | 23 | 3 | 32933.7143
2028 | 2008 | 5 | 23 | 4 | 31854.5031
2028 | 2008 | 5 | 23 | 5 | 30747.1523
2028 | 2008 | 5 | 23 | 6 | 29337.039
2028 | 2008 | 5 | 23 | 7 | 27169.7399
2028 | 2008 | 5 | 23 | 8 | 24572.5308
2028 | 2008 | 5 | 23 | 9 | 24377.6794
2028 | 2008 | 5 | 23 | 10 | 26481.0398
2028 | 2008 | 5 | 23 | 11 | 24870.1657
2028 | 2008 | 5 | 23 | 12 | 22677.4951
2028 | 2008 | 5 | 23 | 13 | 21639.1003
2028 | 2008 | 5 | 23 | 14 | 22118.3578
2028 | 2008 | 5 | 23 | 15 | 22518.7224
2028 | 2008 | 5 | 23 | 16 | 24435.3163
2028 | 2008 | 5 | 23 | 17 | 27693.5363
2028 | 2008 | 5 | 23 | 18 | 28786.868
2028 | 2008 | 5 | 23 | 19 | 30000.6434
2028 | 2008 | 5 | 23 | 20 | 29171.0935
2028 | 2008 | 5 | 23 | 21 | 28875.706
2028 | 2008 | 5 | 23 | 22 | 26815.2726
2028 | 2008 | 5 | 23 | 23 | 26099.2313
2028 | 2008 | 5 | 23 | 24 | 27184.9347
2028 | 2008 | 5 | 24 | 1 | 26825.7376
2028 | 2008 | 5 | 24 | 2 | 26047.1066
2028 | 2008 | 5 | 24 | 3 | 24798.9963
2028 | 2008 | 5 | 24 | 4 | 21865.4679
2028 | 2008 | 5 | 24 | 5 | 19648.4572
2028 | 2008 | 5 | 24 | 6 | 18737.6516
2028 | 2008 | 5 | 24 | 7 | 16351.2257
2028 | 2008 | 5 | 24 | 8 | 11979.8532
2028 | 2008 | 5 | 24 | 9 | 10026.6815
2028 | 2008 | 5 | 24 | 10 | 9555.5822
2028 | 2008 | 5 | 24 | 11 | 7244.7229
2028 | 2008 | 5 | 24 | 12 | 6132.9581
2028 | 2008 | 5 | 24 | 13 | 6015.0809
2028 | 2008 | 5 | 24 | 14 | 6887.883
2028 | 2008 | 5 | 24 | 15 | 7808.4324
2028 | 2008 | 5 | 24 | 16 | 9916.328
2028 | 2008 | 5 | 24 | 17 | 12220.6152
2028 | 2008 | 5 | 24 | 18 | 15979.7391
2028 | 2008 | 5 | 24 | 19 | 17943.6157
2028 | 2008 | 5 | 24 | 20 | 19731.9525
2028 | 2008 | 5 | 24 | 21 | 22268.3556
2028 | 2008 | 5 | 24 | 22 | 26454.4193
2028 | 2008 | 5 | 24 | 23 | 29225.9698
2028 | 2008 | 5 | 24 | 24 | 29894.8299
2028 | 2008 | 5 | 25 | 1 | 29480.7587
2028 | 2008 | 5 | 25 | 2 | 29052.8466
2028 | 2008 | 5 | 25 | 3 | 28204.5882
2028 | 2008 | 5 | 25 | 4 | 26973.2541
2028 | 2008 | 5 | 25 | 5 | 25043.0822
2028 | 2008 | 5 | 25 | 6 | 23454.2759
2028 | 2008 | 5 | 25 | 7 | 22546.034
2028 | 2008 | 5 | 25 | 8 | 22671.2968
2028 | 2008 | 5 | 25 | 9 | 25105.2147
2028 | 2008 | 5 | 25 | 10 | 26407.8887
2028 | 2008 | 5 | 25 | 11 | 28013.6237
2028 | 2008 | 5 | 25 | 12 | 28691.8658
2028 | 2008 | 5 | 25 | 13 | 28361.3273
2028 | 2008 | 5 | 25 | 14 | 28634.837
2028 | 2008 | 5 | 25 | 15 | 27735.2455
2028 | 2008 | 5 | 25 | 16 | 27258.3741
2028 | 2008 | 5 | 25 | 17 | 28395.4525
2028 | 2008 | 5 | 25 | 18 | 29287.1641
2028 | 2008 | 5 | 25 | 19 | 30436.7502
2028 | 2008 | 5 | 25 | 20 | 29777.9292
2028 | 2008 | 5 | 25 | 21 | 29647.7543
2028 | 2008 | 5 | 25 | 22 | 29475.5986
2028 | 2008 | 5 | 25 | 23 | 29673.7964
2028 | 2008 | 5 | 25 | 24 | 30086.7991
2028 | 2008 | 5 | 26 | 1 | 30640.4521
2028 | 2008 | 5 | 26 | 2 | 31249.1926
2028 | 2008 | 5 | 26 | 3 | 31930.0553
2028 | 2008 | 5 | 26 | 4 | 30799.2456
2028 | 2008 | 5 | 26 | 5 | 30427.2923
2028 | 2008 | 5 | 26 | 6 | 30492.7648
2028 | 2008 | 5 | 26 | 7 | 29920.0801
2028 | 2008 | 5 | 26 | 8 | 31031.2868
2028 | 2008 | 5 | 26 | 9 | 33754.6622
2028 | 2008 | 5 | 26 | 10 | 34302.4899
2028 | 2008 | 5 | 26 | 11 | 34220.819
2028 | 2008 | 5 | 26 | 12 | 32805.9261
2028 | 2008 | 5 | 26 | 13 | 31592.2343
2028 | 2008 | 5 | 26 | 14 | 30820.5597
2028 | 2008 | 5 | 26 | 15 | 29614.1108
2028 | 2008 | 5 | 26 | 16 | 29338.333
2028 | 2008 | 5 | 26 | 17 | 30647.2266
2028 | 2008 | 5 | 26 | 18 | 31813.5664
2028 | 2008 | 5 | 26 | 19 | 32315.7586
2028 | 2008 | 5 | 26 | 20 | 32438.056
2028 | 2008 | 5 | 26 | 21 | 31924.0326
2028 | 2008 | 5 | 26 | 22 | 32431.4569
2028 | 2008 | 5 | 26 | 23 | 33146.4592
2028 | 2008 | 5 | 26 | 24 | 33470.7104
2028 | 2008 | 5 | 27 | 1 | 32578.4655
2028 | 2008 | 5 | 27 | 2 | 30999.6075
2028 | 2008 | 5 | 27 | 3 | 28748.4438
2028 | 2008 | 5 | 27 | 4 | 27496.6766
2028 | 2008 | 5 | 27 | 5 | 26607.3557
2028 | 2008 | 5 | 27 | 6 | 26185.333
2028 | 2008 | 5 | 27 | 7 | 26071.4667
2028 | 2008 | 5 | 27 | 8 | 26680.8939
2028 | 2008 | 5 | 27 | 9 | 28820.539
2028 | 2008 | 5 | 27 | 10 | 29695.4616
2028 | 2008 | 5 | 27 | 11 | 28699.6076
2028 | 2008 | 5 | 27 | 12 | 25921.6756
2028 | 2008 | 5 | 27 | 13 | 22759.5573
2028 | 2008 | 5 | 27 | 14 | 20949.1239
2028 | 2008 | 5 | 27 | 15 | 19206.761
2028 | 2008 | 5 | 27 | 16 | 18436.3255
2028 | 2008 | 5 | 27 | 17 | 18699.2745
2028 | 2008 | 5 | 27 | 18 | 20089.5208
2028 | 2008 | 5 | 27 | 19 | 20769.6285
2028 | 2008 | 5 | 27 | 20 | 20879.0442
2028 | 2008 | 5 | 27 | 21 | 22452.9998
2028 | 2008 | 5 | 27 | 22 | 21295.0113
2028 | 2008 | 5 | 27 | 23 | 20817.9745
2028 | 2008 | 5 | 27 | 24 | 20509.1692
2028 | 2008 | 5 | 28 | 1 | 18282.4939
2028 | 2008 | 5 | 28 | 2 | 17092.8375
2028 | 2008 | 5 | 28 | 3 | 15860.9193
2028 | 2008 | 5 | 28 | 4 | 13680.9449
2028 | 2008 | 5 | 28 | 5 | 12997.2227
2028 | 2008 | 5 | 28 | 6 | 10960.6749
2028 | 2008 | 5 | 28 | 7 | 9448.5611
2028 | 2008 | 5 | 28 | 8 | 7765.5396
2028 | 2008 | 5 | 28 | 9 | 7572.932
2028 | 2008 | 5 | 28 | 10 | 6639.6653
2028 | 2008 | 5 | 28 | 11 | 5655.3539
2028 | 2008 | 5 | 28 | 12 | 5533.7644
2028 | 2008 | 5 | 28 | 13 | 5303.0021
2028 | 2008 | 5 | 28 | 14 | 6732.9346
2028 | 2008 | 5 | 28 | 15 | 7424.8561
2028 | 2008 | 5 | 28 | 16 | 8458.063
2028 | 2008 | 5 | 28 | 17 | 9676.9228
2028 | 2008 | 5 | 28 | 18 | 10939.0023
2028 | 2008 | 5 | 28 | 19 | 11413.3191
2028 | 2008 | 5 | 28 | 20 | 12847.4807
2028 | 2008 | 5 | 28 | 21 | 15735.2269
2028 | 2008 | 5 | 28 | 22 | 18633.3113
2028 | 2008 | 5 | 28 | 23 | 21119.9196
2028 | 2008 | 5 | 28 | 24 | 21854.6179
2028 | 2008 | 5 | 29 | 1 | 22676.1072
2028 | 2008 | 5 | 29 | 2 | 22834.8878
2028 | 2008 | 5 | 29 | 3 | 21726.7015
2028 | 2008 | 5 | 29 | 4 | 20565.9209
2028 | 2008 | 5 | 29 | 5 | 20130.4348
2028 | 2008 | 5 | 29 | 6 | 19152.3315
2028 | 2008 | 5 | 29 | 7 | 19027.7658
2028 | 2008 | 5 | 29 | 8 | 17612.9446
2028 | 2008 | 5 | 29 | 9 | 17235.0133
2028 | 2008 | 5 | 29 | 10 | 21349.7872
2028 | 2008 | 5 | 29 | 11 | 21605.3741
2028 | 2008 | 5 | 29 | 12 | 21706.1774
2028 | 2008 | 5 | 29 | 13 | 22569.0006
2028 | 2008 | 5 | 29 | 14 | 23919.9179
2028 | 2008 | 5 | 29 | 15 | 24018.8122
2028 | 2008 | 5 | 29 | 16 | 24629.5488
2028 | 2008 | 5 | 29 | 17 | 25866.7456
2028 | 2008 | 5 | 29 | 18 | 27022.0439
2028 | 2008 | 5 | 29 | 19 | 26653.6961
2028 | 2008 | 5 | 29 | 20 | 26890.7169
2028 | 2008 | 5 | 29 | 21 | 27621.6826
2028 | 2008 | 5 | 29 | 22 | 29209.6326
2028 | 2008 | 5 | 29 | 23 | 30661.8088
2028 | 2008 | 5 | 29 | 24 | 31324.0937
2028 | 2008 | 5 | 30 | 1 | 31711.2371
2028 | 2008 | 5 | 30 | 2 | 31813.1843
2028 | 2008 | 5 | 30 | 3 | 31342.0271
2028 | 2008 | 5 | 30 | 4 | 30866.8218
2028 | 2008 | 5 | 30 | 5 | 29976.0509
2028 | 2008 | 5 | 30 | 6 | 29323.6601
2028 | 2008 | 5 | 30 | 7 | 28213.5137
2028 | 2008 | 5 | 30 | 8 | 27351.9497
2028 | 2008 | 5 | 30 | 9 | 27923.7219
2028 | 2008 | 5 | 30 | 10 | 28950.9629
2028 | 2008 | 5 | 30 | 11 | 25621.2522
2028 | 2008 | 5 | 30 | 12 | 22629.6373
2028 | 2008 | 5 | 30 | 13 | 21260.808
2028 | 2008 | 5 | 30 | 14 | 20843.1662
2028 | 2008 | 5 | 30 | 15 | 19877.8585
2028 | 2008 | 5 | 30 | 16 | 20799.4855
2028 | 2008 | 5 | 30 | 17 | 21995.2869
2028 | 2008 | 5 | 30 | 18 | 24091.9331
2028 | 2008 | 5 | 30 | 19 | 25491.7983
2028 | 2008 | 5 | 30 | 20 | 27137.1525
2028 | 2008 | 5 | 30 | 21 | 29119.7116
2028 | 2008 | 5 | 30 | 22 | 31404.5134
2028 | 2008 | 5 | 30 | 23 | 31770.9097
2028 | 2008 | 5 | 30 | 24 | 31851.3799
2028 | 2008 | 5 | 31 | 1 | 32062.7984
2028 | 2008 | 5 | 31 | 2 | 32039.926
2028 | 2008 | 5 | 31 | 3 | 31907.4252
2028 | 2008 | 5 | 31 | 4 | 31156.6155
2028 | 2008 | 5 | 31 | 5 | 29382.5651
2028 | 2008 | 5 | 31 | 6 | 27774.6341
2028 | 2008 | 5 | 31 | 7 | 25856.9737
2028 | 2008 | 5 | 31 | 8 | 23742.5202
2028 | 2008 | 5 | 31 | 9 | 22961.9952
2028 | 2008 | 5 | 31 | 10 | 23431.5243
2028 | 2008 | 5 | 31 | 11 | 21096.0213
2028 | 2008 | 5 | 31 | 12 | 20241.165
2028 | 2008 | 5 | 31 | 13 | 20400.544
2028 | 2008 | 5 | 31 | 14 | 21078.499
2028 | 2008 | 5 | 31 | 15 | 22228.7579
2028 | 2008 | 5 | 31 | 16 | 23437.4619
2028 | 2008 | 5 | 31 | 17 | 24951.197
2028 | 2008 | 5 | 31 | 18 | 26601.6542
2028 | 2008 | 5 | 31 | 19 | 28844.6104
2028 | 2008 | 5 | 31 | 20 | 30195.4628
2028 | 2008 | 5 | 31 | 21 | 30233.5136
2028 | 2008 | 5 | 31 | 22 | 31242.1158
2028 | 2008 | 5 | 31 | 23 | 31049.5306
2028 | 2008 | 5 | 31 | 24 | 31435.7172
2029 | 2008 | 5 | 1 | 1 | 38220.9563
2029 | 2008 | 5 | 1 | 2 | 37787.8419
2029 | 2008 | 5 | 1 | 3 | 37007.3039
2029 | 2008 | 5 | 1 | 4 | 35678.297
2029 | 2008 | 5 | 1 | 5 | 35165.9999
2029 | 2008 | 5 | 1 | 6 | 34977.5505
2029 | 2008 | 5 | 1 | 7 | 33745.649
2029 | 2008 | 5 | 1 | 8 | 31957.3819
2029 | 2008 | 5 | 1 | 9 | 31624.0711
2029 | 2008 | 5 | 1 | 10 | 31522.1803
2029 | 2008 | 5 | 1 | 11 | 31384.5934
2029 | 2008 | 5 | 1 | 12 | 30284.6606
2029 | 2008 | 5 | 1 | 13 | 29368.1639
2029 | 2008 | 5 | 1 | 14 | 28757.7872
2029 | 2008 | 5 | 1 | 15 | 28296.449
2029 | 2008 | 5 | 1 | 16 | 27712.0359
2029 | 2008 | 5 | 1 | 17 | 29449.3684
2029 | 2008 | 5 | 1 | 18 | 29829.0034
2029 | 2008 | 5 | 1 | 19 | 31230.152
2029 | 2008 | 5 | 1 | 20 | 31639.2453
2029 | 2008 | 5 | 1 | 21 | 32664.1658
2029 | 2008 | 5 | 1 | 22 | 34214.4923
2029 | 2008 | 5 | 1 | 23 | 34126.781
2029 | 2008 | 5 | 1 | 24 | 33833.5364
2029 | 2008 | 5 | 2 | 1 | 34294.5882
2029 | 2008 | 5 | 2 | 2 | 33140.1891
2029 | 2008 | 5 | 2 | 3 | 33038.6137
2029 | 2008 | 5 | 2 | 4 | 32871.4875
2029 | 2008 | 5 | 2 | 5 | 32325.9765
2029 | 2008 | 5 | 2 | 6 | 30490.2478
2029 | 2008 | 5 | 2 | 7 | 28323.9398
2029 | 2008 | 5 | 2 | 8 | 21474.4325
2029 | 2008 | 5 | 2 | 9 | 15412.9545
2029 | 2008 | 5 | 2 | 10 | 11956.303
2029 | 2008 | 5 | 2 | 11 | 8045.9221
2029 | 2008 | 5 | 2 | 12 | 7944.6113
2029 | 2008 | 5 | 2 | 13 | 10135.4971
2029 | 2008 | 5 | 2 | 14 | 13023.3595
2029 | 2008 | 5 | 2 | 15 | 15859.1994
2029 | 2008 | 5 | 2 | 16 | 16849.1507
2029 | 2008 | 5 | 2 | 17 | 16977.1525
2029 | 2008 | 5 | 2 | 18 | 15956.3333
2029 | 2008 | 5 | 2 | 19 | 12579.5869
2029 | 2008 | 5 | 2 | 20 | 10846.828
2029 | 2008 | 5 | 2 | 21 | 10594.4512
2029 | 2008 | 5 | 2 | 22 | 12173.9669
2029 | 2008 | 5 | 2 | 23 | 14490.1878
2029 | 2008 | 5 | 2 | 24 | 17600.878
2029 | 2008 | 5 | 3 | 1 | 21750.8162
2029 | 2008 | 5 | 3 | 2 | 24058.7996
2029 | 2008 | 5 | 3 | 3 | 25149.0495
2029 | 2008 | 5 | 3 | 4 | 26270.7593
2029 | 2008 | 5 | 3 | 5 | 26782.3094
2029 | 2008 | 5 | 3 | 6 | 26883.7315
2029 | 2008 | 5 | 3 | 7 | 25775.9133
2029 | 2008 | 5 | 3 | 8 | 25391.0143
2029 | 2008 | 5 | 3 | 9 | 26469.9707
2029 | 2008 | 5 | 3 | 10 | 25577.3645
2029 | 2008 | 5 | 3 | 11 | 20420.1515
2029 | 2008 | 5 | 3 | 12 | 16269.3087
2029 | 2008 | 5 | 3 | 13 | 14229.1794
2029 | 2008 | 5 | 3 | 14 | 12721.3294
2029 | 2008 | 5 | 3 | 15 | 11494.1936
2029 | 2008 | 5 | 3 | 16 | 10360.5633
2029 | 2008 | 5 | 3 | 17 | 10050.9536
2029 | 2008 | 5 | 3 | 18 | 10118.3507
2029 | 2008 | 5 | 3 | 19 | 9705.1793
2029 | 2008 | 5 | 3 | 20 | 9547.8173
2029 | 2008 | 5 | 3 | 21 | 10233.7195
2029 | 2008 | 5 | 3 | 22 | 11224.7026
2029 | 2008 | 5 | 3 | 23 | 13335.7008
2029 | 2008 | 5 | 3 | 24 | 13881.8286
2029 | 2008 | 5 | 4 | 1 | 14043.9308
2029 | 2008 | 5 | 4 | 2 | 14124.996
2029 | 2008 | 5 | 4 | 3 | 14088.0201
2029 | 2008 | 5 | 4 | 4 | 13998.9968
2029 | 2008 | 5 | 4 | 5 | 14230.4128
2029 | 2008 | 5 | 4 | 6 | 14238.1678
2029 | 2008 | 5 | 4 | 7 | 14819.5193
2029 | 2008 | 5 | 4 | 8 | 12022.8801
2029 | 2008 | 5 | 4 | 9 | 11418.5789
2029 | 2008 | 5 | 4 | 10 | 13573.0814
2029 | 2008 | 5 | 4 | 11 | 14978.551
2029 | 2008 | 5 | 4 | 12 | 15540.5772
2029 | 2008 | 5 | 4 | 13 | 16639.6103
2029 | 2008 | 5 | 4 | 14 | 17705.1728
2029 | 2008 | 5 | 4 | 15 | 18270.9454
2029 | 2008 | 5 | 4 | 16 | 18789.661
2029 | 2008 | 5 | 4 | 17 | 20804.4494
2029 | 2008 | 5 | 4 | 18 | 22463.7432
2029 | 2008 | 5 | 4 | 19 | 23789.8397
2029 | 2008 | 5 | 4 | 20 | 23253.4556
2029 | 2008 | 5 | 4 | 21 | 23910.646
2029 | 2008 | 5 | 4 | 22 | 24881.571
2029 | 2008 | 5 | 4 | 23 | 24511.7045
2029 | 2008 | 5 | 4 | 24 | 23035.6939
2029 | 2008 | 5 | 5 | 1 | 21675.4544
2029 | 2008 | 5 | 5 | 2 | 21108.087
2029 | 2008 | 5 | 5 | 3 | 20916.866
2029 | 2008 | 5 | 5 | 4 | 19384.754
2029 | 2008 | 5 | 5 | 5 | 17415.5531
2029 | 2008 | 5 | 5 | 6 | 16415.1053
2029 | 2008 | 5 | 5 | 7 | 14515.434
2029 | 2008 | 5 | 5 | 8 | 15286.8703
2029 | 2008 | 5 | 5 | 9 | 18316.9406
2029 | 2008 | 5 | 5 | 10 | 19889.7038
2029 | 2008 | 5 | 5 | 11 | 21068.9216
2029 | 2008 | 5 | 5 | 12 | 21921.8073
2029 | 2008 | 5 | 5 | 13 | 22121.5879
2029 | 2008 | 5 | 5 | 14 | 22953.4723
2029 | 2008 | 5 | 5 | 15 | 22586.0335
2029 | 2008 | 5 | 5 | 16 | 22386.6686
2029 | 2008 | 5 | 5 | 17 | 24472.7207
2029 | 2008 | 5 | 5 | 18 | 26486.2212
2029 | 2008 | 5 | 5 | 19 | 27997.9272
2029 | 2008 | 5 | 5 | 20 | 30067.3669
2029 | 2008 | 5 | 5 | 21 | 31606.2509
2029 | 2008 | 5 | 5 | 22 | 31963.6256
2029 | 2008 | 5 | 5 | 23 | 31574.615
2029 | 2008 | 5 | 5 | 24 | 30210.5706
2029 | 2008 | 5 | 6 | 1 | 28143.3394
2029 | 2008 | 5 | 6 | 2 | 25054.9808
2029 | 2008 | 5 | 6 | 3 | 22041.2432
2029 | 2008 | 5 | 6 | 4 | 19427.1869
2029 | 2008 | 5 | 6 | 5 | 19308.4772
2029 | 2008 | 5 | 6 | 6 | 20840.9175
2029 | 2008 | 5 | 6 | 7 | 21882.71
2029 | 2008 | 5 | 6 | 8 | 24205.9338
2029 | 2008 | 5 | 6 | 9 | 28467.7083
2029 | 2008 | 5 | 6 | 10 | 30196.9507
2029 | 2008 | 5 | 6 | 11 | 29998.0111
2029 | 2008 | 5 | 6 | 12 | 30278.3208
2029 | 2008 | 5 | 6 | 13 | 31731.1096
2029 | 2008 | 5 | 6 | 14 | 33524.7132
2029 | 2008 | 5 | 6 | 15 | 34581.2273
2029 | 2008 | 5 | 6 | 16 | 35094.3697
2029 | 2008 | 5 | 6 | 17 | 34491.3821
2029 | 2008 | 5 | 6 | 18 | 34893.3885
2029 | 2008 | 5 | 6 | 19 | 33893.6689
2029 | 2008 | 5 | 6 | 20 | 34284.2799
2029 | 2008 | 5 | 6 | 21 | 33412.5867
2029 | 2008 | 5 | 6 | 22 | 34104.4158
2029 | 2008 | 5 | 6 | 23 | 34322.1652
2029 | 2008 | 5 | 6 | 24 | 32958.5508
2029 | 2008 | 5 | 7 | 1 | 31920.0252
2029 | 2008 | 5 | 7 | 2 | 31502.8389
2029 | 2008 | 5 | 7 | 3 | 31656.8233
2029 | 2008 | 5 | 7 | 4 | 31771.4749
2029 | 2008 | 5 | 7 | 5 | 31747.9222
2029 | 2008 | 5 | 7 | 6 | 31897.4401
2029 | 2008 | 5 | 7 | 7 | 32026.103
2029 | 2008 | 5 | 7 | 8 | 32203.5425
2029 | 2008 | 5 | 7 | 9 | 33251.2756
2029 | 2008 | 5 | 7 | 10 | 32534.3505
2029 | 2008 | 5 | 7 | 11 | 31899.27
2029 | 2008 | 5 | 7 | 12 | 30182.1539
2029 | 2008 | 5 | 7 | 13 | 29953.646
2029 | 2008 | 5 | 7 | 14 | 29728.371
2029 | 2008 | 5 | 7 | 15 | 32242.0559
2029 | 2008 | 5 | 7 | 16 | 32648.2636
2029 | 2008 | 5 | 7 | 17 | 33231.8237
2029 | 2008 | 5 | 7 | 18 | 32451.4029
2029 | 2008 | 5 | 7 | 19 | 29164.9129
2029 | 2008 | 5 | 7 | 20 | 27947.3626
2029 | 2008 | 5 | 7 | 21 | 25496.7507
2029 | 2008 | 5 | 7 | 22 | 23500.6622
2029 | 2008 | 5 | 7 | 23 | 22597.0249
2029 | 2008 | 5 | 7 | 24 | 21028.9589
2029 | 2008 | 5 | 8 | 1 | 18676.361
2029 | 2008 | 5 | 8 | 2 | 17546.1791
2029 | 2008 | 5 | 8 | 3 | 14882.4765
2029 | 2008 | 5 | 8 | 4 | 12359.3001
2029 | 2008 | 5 | 8 | 5 | 11158.5357
2029 | 2008 | 5 | 8 | 6 | 9094.326
2029 | 2008 | 5 | 8 | 7 | 8067.5376
2029 | 2008 | 5 | 8 | 8 | 5661.5957
2029 | 2008 | 5 | 8 | 9 | 4529.3329
2029 | 2008 | 5 | 8 | 10 | 3488.4192
2029 | 2008 | 5 | 8 | 11 | 3832.6148
2029 | 2008 | 5 | 8 | 12 | 4707.4723
2029 | 2008 | 5 | 8 | 13 | 6188.3747
2029 | 2008 | 5 | 8 | 14 | 8305.609
2029 | 2008 | 5 | 8 | 15 | 10237.3229
2029 | 2008 | 5 | 8 | 16 | 13132.8263
2029 | 2008 | 5 | 8 | 17 | 16650.7533
2029 | 2008 | 5 | 8 | 18 | 20363.5454
2029 | 2008 | 5 | 8 | 19 | 20821.8185
2029 | 2008 | 5 | 8 | 20 | 23130.8336
2029 | 2008 | 5 | 8 | 21 | 25993.5533
2029 | 2008 | 5 | 8 | 22 | 29854.8522
2029 | 2008 | 5 | 8 | 23 | 30204.4519
2029 | 2008 | 5 | 8 | 24 | 29861.0557
2029 | 2008 | 5 | 9 | 1 | 30995.2945
2029 | 2008 | 5 | 9 | 2 | 30179.2889
2029 | 2008 | 5 | 9 | 3 | 29650.1293
2029 | 2008 | 5 | 9 | 4 | 27550.1592
2029 | 2008 | 5 | 9 | 5 | 25669.5985
2029 | 2008 | 5 | 9 | 6 | 23803.7372
2029 | 2008 | 5 | 9 | 7 | 19687.1645
2029 | 2008 | 5 | 9 | 8 | 13906.3422
2029 | 2008 | 5 | 9 | 9 | 9645.3602
2029 | 2008 | 5 | 9 | 10 | 8113.3323
2029 | 2008 | 5 | 9 | 11 | 7528.5876
2029 | 2008 | 5 | 9 | 12 | 7439.1148
2029 | 2008 | 5 | 9 | 13 | 7162.5351
2029 | 2008 | 5 | 9 | 14 | 6779.4845
2029 | 2008 | 5 | 9 | 15 | 6426.1822
2029 | 2008 | 5 | 9 | 16 | 6839.5399
2029 | 2008 | 5 | 9 | 17 | 7728.7467
2029 | 2008 | 5 | 9 | 18 | 8623.0402
2029 | 2008 | 5 | 9 | 19 | 9452.4526
2029 | 2008 | 5 | 9 | 20 | 11197.1213
2029 | 2008 | 5 | 9 | 21 | 14898.4761
2029 | 2008 | 5 | 9 | 22 | 18724.9759
2029 | 2008 | 5 | 9 | 23 | 22361.0248
2029 | 2008 | 5 | 9 | 24 | 24570.8682
2029 | 2008 | 5 | 10 | 1 | 26391.9502
2029 | 2008 | 5 | 10 | 2 | 26687.0673
2029 | 2008 | 5 | 10 | 3 | 26090.7494
2029 | 2008 | 5 | 10 | 4 | 25493.7907
2029 | 2008 | 5 | 10 | 5 | 25176.3695
2029 | 2008 | 5 | 10 | 6 | 25500.0044
2029 | 2008 | 5 | 10 | 7 | 24967.0618
2029 | 2008 | 5 | 10 | 8 | 23545.1263
2029 | 2008 | 5 | 10 | 9 | 23524.3516
2029 | 2008 | 5 | 10 | 10 | 24803.3223
2029 | 2008 | 5 | 10 | 11 | 25062.1221
2029 | 2008 | 5 | 10 | 12 | 26724.7998
2029 | 2008 | 5 | 10 | 13 | 27640.1086
2029 | 2008 | 5 | 10 | 14 | 26871.9543
2029 | 2008 | 5 | 10 | 15 | 26110.366
2029 | 2008 | 5 | 10 | 16 | 25072.2704
2029 | 2008 | 5 | 10 | 17 | 24087.4002
2029 | 2008 | 5 | 10 | 18 | 22456.0075
2029 | 2008 | 5 | 10 | 19 | 19919.6607
2029 | 2008 | 5 | 10 | 20 | 19082.2148
2029 | 2008 | 5 | 10 | 21 | 18936.4323
2029 | 2008 | 5 | 10 | 22 | 19834.0576
2029 | 2008 | 5 | 10 | 23 | 23426.9033
2029 | 2008 | 5 | 10 | 24 | 26036.8667
2029 | 2008 | 5 | 11 | 1 | 28644.7855
2029 | 2008 | 5 | 11 | 2 | 29589.2307
2029 | 2008 | 5 | 11 | 3 | 29607.939
2029 | 2008 | 5 | 11 | 4 | 28137.8135
2029 | 2008 | 5 | 11 | 5 | 27200.2345
2029 | 2008 | 5 | 11 | 6 | 26073.0522
2029 | 2008 | 5 | 11 | 7 | 24364.2765
2029 | 2008 | 5 | 11 | 8 | 22992.8635
2029 | 2008 | 5 | 11 | 9 | 23335.4809
2029 | 2008 | 5 | 11 | 10 | 21026.3277
2029 | 2008 | 5 | 11 | 11 | 16599.6667
2029 | 2008 | 5 | 11 | 12 | 15375.0939
2029 | 2008 | 5 | 11 | 13 | 14566.4454
2029 | 2008 | 5 | 11 | 14 | 13919.511
2029 | 2008 | 5 | 11 | 15 | 13263.5041
2029 | 2008 | 5 | 11 | 16 | 12513.9859
2029 | 2008 | 5 | 11 | 17 | 12476.7963
2029 | 2008 | 5 | 11 | 18 | 12468.1859
2029 | 2008 | 5 | 11 | 19 | 12496.7202
2029 | 2008 | 5 | 11 | 20 | 12590.7479
2029 | 2008 | 5 | 11 | 21 | 14012.3056
2029 | 2008 | 5 | 11 | 22 | 15868.2818
2029 | 2008 | 5 | 11 | 23 | 17686.2732
2029 | 2008 | 5 | 11 | 24 | 18495.4297
2029 | 2008 | 5 | 12 | 1 | 20403.9353
2029 | 2008 | 5 | 12 | 2 | 21811.8597
2029 | 2008 | 5 | 12 | 3 | 22202.7369
2029 | 2008 | 5 | 12 | 4 | 23128.3937
2029 | 2008 | 5 | 12 | 5 | 23759.9769
2029 | 2008 | 5 | 12 | 6 | 24950.3374
2029 | 2008 | 5 | 12 | 7 | 25777.7505
2029 | 2008 | 5 | 12 | 8 | 24595.869
2029 | 2008 | 5 | 12 | 9 | 24310.6673
2029 | 2008 | 5 | 12 | 10 | 27891.068
2029 | 2008 | 5 | 12 | 11 | 29695.2047
2029 | 2008 | 5 | 12 | 12 | 31016.6562
2029 | 2008 | 5 | 12 | 13 | 31671.2689
2029 | 2008 | 5 | 12 | 14 | 33061.3119
2029 | 2008 | 5 | 12 | 15 | 33663.3367
2029 | 2008 | 5 | 12 | 16 | 34969.1332
2029 | 2008 | 5 | 12 | 17 | 35613.0232
2029 | 2008 | 5 | 12 | 18 | 36237.9633
2029 | 2008 | 5 | 12 | 19 | 36192.8603
2029 | 2008 | 5 | 12 | 20 | 34584.2864
2029 | 2008 | 5 | 12 | 21 | 33482.2839
2029 | 2008 | 5 | 12 | 22 | 34183.7254
2029 | 2008 | 5 | 12 | 23 | 34751.5973
2029 | 2008 | 5 | 12 | 24 | 35190.6625
2029 | 2008 | 5 | 13 | 1 | 35554.0974
2029 | 2008 | 5 | 13 | 2 | 35848.2227
2029 | 2008 | 5 | 13 | 3 | 35225.8016
2029 | 2008 | 5 | 13 | 4 | 33526.7454
2029 | 2008 | 5 | 13 | 5 | 32685.96
2029 | 2008 | 5 | 13 | 6 | 30746.3991
2029 | 2008 | 5 | 13 | 7 | 28958.967
2029 | 2008 | 5 | 13 | 8 | 27133.8296
2029 | 2008 | 5 | 13 | 9 | 26454.934
2029 | 2008 | 5 | 13 | 10 | 24225.5726
2029 | 2008 | 5 | 13 | 11 | 20174.9992
2029 | 2008 | 5 | 13 | 12 | 16499.903
2029 | 2008 | 5 | 13 | 13 | 14557.7123
2029 | 2008 | 5 | 13 | 14 | 13002.2463
2029 | 2008 | 5 | 13 | 15 | 12543.4797
2029 | 2008 | 5 | 13 | 16 | 12852.536
2029 | 2008 | 5 | 13 | 17 | 14346.1844
2029 | 2008 | 5 | 13 | 18 | 16424.6649
2029 | 2008 | 5 | 13 | 19 | 20035.0353
2029 | 2008 | 5 | 13 | 20 | 22471.9358
2029 | 2008 | 5 | 13 | 21 | 26501.0592
2029 | 2008 | 5 | 13 | 22 | 25083.1889
2029 | 2008 | 5 | 13 | 23 | 24988.2002
2029 | 2008 | 5 | 13 | 24 | 25617.1887
2029 | 2008 | 5 | 14 | 1 | 25778.9564
2029 | 2008 | 5 | 14 | 2 | 24682.7056
2029 | 2008 | 5 | 14 | 3 | 22492.0429
2029 | 2008 | 5 | 14 | 4 | 20718.2249
2029 | 2008 | 5 | 14 | 5 | 19995.6083
2029 | 2008 | 5 | 14 | 6 | 19124.1302
2029 | 2008 | 5 | 14 | 7 | 19212.0496
2029 | 2008 | 5 | 14 | 8 | 19115.3493
2029 | 2008 | 5 | 14 | 9 | 20758.3365
2029 | 2008 | 5 | 14 | 10 | 20519.8996
2029 | 2008 | 5 | 14 | 11 | 18784.5115
2029 | 2008 | 5 | 14 | 12 | 17099.0056
2029 | 2008 | 5 | 14 | 13 | 15081.4862
2029 | 2008 | 5 | 14 | 14 | 13427.0189
2029 | 2008 | 5 | 14 | 15 | 13576.1792
2029 | 2008 | 5 | 14 | 16 | 14036.5979
2029 | 2008 | 5 | 14 | 17 | 14511.4094
2029 | 2008 | 5 | 14 | 18 | 15941.6961
2029 | 2008 | 5 | 14 | 19 | 15784.0727
2029 | 2008 | 5 | 14 | 20 | 13908.3164
2029 | 2008 | 5 | 14 | 21 | 14122.6476
2029 | 2008 | 5 | 14 | 22 | 13383.6684
2029 | 2008 | 5 | 14 | 23 | 11585.2389
2029 | 2008 | 5 | 14 | 24 | 8516.7149
2029 | 2008 | 5 | 15 | 1 | 7003.9589
2029 | 2008 | 5 | 15 | 2 | 5688.3006
2029 | 2008 | 5 | 15 | 3 | 5947.8496
2029 | 2008 | 5 | 15 | 4 | 6731.392
2029 | 2008 | 5 | 15 | 5 | 7402.7487
2029 | 2008 | 5 | 15 | 6 | 7475.9396
2029 | 2008 | 5 | 15 | 7 | 10897.6323
2029 | 2008 | 5 | 15 | 8 | 11320.999
2029 | 2008 | 5 | 15 | 9 | 13709.7015
2029 | 2008 | 5 | 15 | 10 | 12797.1558
2029 | 2008 | 5 | 15 | 11 | 10865.876
2029 | 2008 | 5 | 15 | 12 | 9955.1333
2029 | 2008 | 5 | 15 | 13 | 10282.3399
2029 | 2008 | 5 | 15 | 14 | 9823.7871
2029 | 2008 | 5 | 15 | 15 | 8176.0808
2029 | 2008 | 5 | 15 | 16 | 7965.5761
2029 | 2008 | 5 | 15 | 17 | 7712.5033
2029 | 2008 | 5 | 15 | 18 | 8319.9329
2029 | 2008 | 5 | 15 | 19 | 9574.0713
2029 | 2008 | 5 | 15 | 20 | 10630.3324
2029 | 2008 | 5 | 15 | 21 | 13483.7894
2029 | 2008 | 5 | 15 | 22 | 12993.072
2029 | 2008 | 5 | 15 | 23 | 11983.5926
2029 | 2008 | 5 | 15 | 24 | 11190.3568
2029 | 2008 | 5 | 16 | 1 | 10165.8582
2029 | 2008 | 5 | 16 | 2 | 9189.3844
2029 | 2008 | 5 | 16 | 3 | 9443.7657
2029 | 2008 | 5 | 16 | 4 | 10274.2808
2029 | 2008 | 5 | 16 | 5 | 11644.6475
2029 | 2008 | 5 | 16 | 6 | 13379.1732
2029 | 2008 | 5 | 16 | 7 | 15913.6445
2029 | 2008 | 5 | 16 | 8 | 15518.7726
2029 | 2008 | 5 | 16 | 9 | 14386.6178
2029 | 2008 | 5 | 16 | 10 | 19036.4825
2029 | 2008 | 5 | 16 | 11 | 19698.1813
2029 | 2008 | 5 | 16 | 12 | 18684.1541
2029 | 2008 | 5 | 16 | 13 | 16742.6651
2029 | 2008 | 5 | 16 | 14 | 14314.6611
2029 | 2008 | 5 | 16 | 15 | 12252.5975
2029 | 2008 | 5 | 16 | 16 | 10709.7615
2029 | 2008 | 5 | 16 | 17 | 10160.8704
2029 | 2008 | 5 | 16 | 18 | 8911.8834
2029 | 2008 | 5 | 16 | 19 | 6975.6803
2029 | 2008 | 5 | 16 | 20 | 4608.4004
2029 | 2008 | 5 | 16 | 21 | 3423.7341
2029 | 2008 | 5 | 16 | 22 | 2731.2022
2029 | 2008 | 5 | 16 | 23 | 2628.1276
2029 | 2008 | 5 | 16 | 24 | 3079.5055
2029 | 2008 | 5 | 17 | 1 | 3775.0572
2029 | 2008 | 5 | 17 | 2 | 5032.7112
2029 | 2008 | 5 | 17 | 3 | 6805.1344
2029 | 2008 | 5 | 17 | 4 | 9504.4902
2029 | 2008 | 5 | 17 | 5 | 11475.0053
2029 | 2008 | 5 | 17 | 6 | 12002.9364
2029 | 2008 | 5 | 17 | 7 | 11916.0812
2029 | 2008 | 5 | 17 | 8 | 9225.6589
2029 | 2008 | 5 | 17 | 9 | 8575.1629
2029 | 2008 | 5 | 17 | 10 | 5169.8102
2029 | 2008 | 5 | 17 | 11 | 5606.0982
2029 | 2008 | 5 | 17 | 12 | 4580.7746
2029 | 2008 | 5 | 17 | 13 | 3799.7077
2029 | 2008 | 5 | 17 | 14 | 4258.007
2029 | 2008 | 5 | 17 | 15 | 4338.9276
2029 | 2008 | 5 | 17 | 16 | 4343.3039
2029 | 2008 | 5 | 17 | 17 | 3883.1223
2029 | 2008 | 5 | 17 | 18 | 4208.1862
2029 | 2008 | 5 | 17 | 19 | 4159.2534
2029 | 2008 | 5 | 17 | 20 | 4039.5193
2029 | 2008 | 5 | 17 | 21 | 5404.3641
2029 | 2008 | 5 | 17 | 22 | 7035.4259
2029 | 2008 | 5 | 17 | 23 | 8746.5503
2029 | 2008 | 5 | 17 | 24 | 9583.1392
2029 | 2008 | 5 | 18 | 1 | 11173.6799
2029 | 2008 | 5 | 18 | 2 | 12440.7639
2029 | 2008 | 5 | 18 | 3 | 15214.1489
2029 | 2008 | 5 | 18 | 4 | 17004.9386
2029 | 2008 | 5 | 18 | 5 | 18839.5617
2029 | 2008 | 5 | 18 | 6 | 20019.7793
2029 | 2008 | 5 | 18 | 7 | 20750.2155
2029 | 2008 | 5 | 18 | 8 | 15712.6132
2029 | 2008 | 5 | 18 | 9 | 11410.1047
2029 | 2008 | 5 | 18 | 10 | 7275.3253
2029 | 2008 | 5 | 18 | 11 | 7848.9223
2029 | 2008 | 5 | 18 | 12 | 7231.9575
2029 | 2008 | 5 | 18 | 13 | 6388.3968
2029 | 2008 | 5 | 18 | 14 | 5480.215
2029 | 2008 | 5 | 18 | 15 | 4380.3431
2029 | 2008 | 5 | 18 | 16 | 3446.7733
2029 | 2008 | 5 | 18 | 17 | 2920.6243
2029 | 2008 | 5 | 18 | 18 | 2433.9258
2029 | 2008 | 5 | 18 | 19 | 2055.7505
2029 | 2008 | 5 | 18 | 20 | 2604.8579
2029 | 2008 | 5 | 18 | 21 | 4360.6614
2029 | 2008 | 5 | 18 | 22 | 8800.2658
2029 | 2008 | 5 | 18 | 23 | 15138.0913
2029 | 2008 | 5 | 18 | 24 | 20017.3779
2029 | 2008 | 5 | 19 | 1 | 24700.2274
2029 | 2008 | 5 | 19 | 2 | 28077.0765
2029 | 2008 | 5 | 19 | 3 | 29937.7781
2029 | 2008 | 5 | 19 | 4 | 30462.4529
2029 | 2008 | 5 | 19 | 5 | 30348.2893
2029 | 2008 | 5 | 19 | 6 | 29647.7624
2029 | 2008 | 5 | 19 | 7 | 28702.4176
2029 | 2008 | 5 | 19 | 8 | 25533.3136
2029 | 2008 | 5 | 19 | 9 | 23277.613
2029 | 2008 | 5 | 19 | 10 | 20737.3566
2029 | 2008 | 5 | 19 | 11 | 21380.9883
2029 | 2008 | 5 | 19 | 12 | 21101.8649
2029 | 2008 | 5 | 19 | 13 | 19671.8085
2029 | 2008 | 5 | 19 | 14 | 18400.5996
2029 | 2008 | 5 | 19 | 15 | 16246.6499
2029 | 2008 | 5 | 19 | 16 | 15639.8352
2029 | 2008 | 5 | 19 | 17 | 15862.3226
2029 | 2008 | 5 | 19 | 18 | 15720.5887
2029 | 2008 | 5 | 19 | 19 | 14922.2618
2029 | 2008 | 5 | 19 | 20 | 16012.896
2029 | 2008 | 5 | 19 | 21 | 18248.8445
2029 | 2008 | 5 | 19 | 22 | 22338.6071
2029 | 2008 | 5 | 19 | 23 | 25643.1054
2029 | 2008 | 5 | 19 | 24 | 27272.7437
2029 | 2008 | 5 | 20 | 1 | 28096.4901
2029 | 2008 | 5 | 20 | 2 | 27748.0922
2029 | 2008 | 5 | 20 | 3 | 27919.8386
2029 | 2008 | 5 | 20 | 4 | 27292.6755
2029 | 2008 | 5 | 20 | 5 | 27274.1071
2029 | 2008 | 5 | 20 | 6 | 25118.7995
2029 | 2008 | 5 | 20 | 7 | 21708.2531
2029 | 2008 | 5 | 20 | 8 | 16300.5313
2029 | 2008 | 5 | 20 | 9 | 13009.5496
2029 | 2008 | 5 | 20 | 10 | 12501.1224
2029 | 2008 | 5 | 20 | 11 | 14634.0558
2029 | 2008 | 5 | 20 | 12 | 15322.5589
2029 | 2008 | 5 | 20 | 13 | 15284.3838
2029 | 2008 | 5 | 20 | 14 | 15047.2749
2029 | 2008 | 5 | 20 | 15 | 14232.7788
2029 | 2008 | 5 | 20 | 16 | 13649.8115
2029 | 2008 | 5 | 20 | 17 | 14223.0501
2029 | 2008 | 5 | 20 | 18 | 16193.0374
2029 | 2008 | 5 | 20 | 19 | 17849.7766
2029 | 2008 | 5 | 20 | 20 | 20749.2541
2029 | 2008 | 5 | 20 | 21 | 24997.174
2029 | 2008 | 5 | 20 | 22 | 25590.2466
2029 | 2008 | 5 | 20 | 23 | 25437.0175
2029 | 2008 | 5 | 20 | 24 | 24037.4628
2029 | 2008 | 5 | 21 | 1 | 21593.8891
2029 | 2008 | 5 | 21 | 2 | 20304.4759
2029 | 2008 | 5 | 21 | 3 | 20533.1955
2029 | 2008 | 5 | 21 | 4 | 20583.3109
2029 | 2008 | 5 | 21 | 5 | 20551.0563
2029 | 2008 | 5 | 21 | 6 | 21060.6959
2029 | 2008 | 5 | 21 | 7 | 21479.717
2029 | 2008 | 5 | 21 | 8 | 20836.9834
2029 | 2008 | 5 | 21 | 9 | 21923.1028
2029 | 2008 | 5 | 21 | 10 | 25227.3091
2029 | 2008 | 5 | 21 | 11 | 27789.6041
2029 | 2008 | 5 | 21 | 12 | 29367.9545
2029 | 2008 | 5 | 21 | 13 | 31373.5753
2029 | 2008 | 5 | 21 | 14 | 33234.7366
2029 | 2008 | 5 | 21 | 15 | 34015.848
2029 | 2008 | 5 | 21 | 16 | 33927.146
2029 | 2008 | 5 | 21 | 17 | 34291.0267
2029 | 2008 | 5 | 21 | 18 | 34444.6473
2029 | 2008 | 5 | 21 | 19 | 34373.1701
2029 | 2008 | 5 | 21 | 20 | 34886.3936
2029 | 2008 | 5 | 21 | 21 | 35082.4525
2029 | 2008 | 5 | 21 | 22 | 34875.4881
2029 | 2008 | 5 | 21 | 23 | 35155.8024
2029 | 2008 | 5 | 21 | 24 | 35731.112
2029 | 2008 | 5 | 22 | 1 | 35924.5859
2029 | 2008 | 5 | 22 | 2 | 36374.6733
2029 | 2008 | 5 | 22 | 3 | 36835.6438
2029 | 2008 | 5 | 22 | 4 | 36906.5587
2029 | 2008 | 5 | 22 | 5 | 36376.8696
2029 | 2008 | 5 | 22 | 6 | 35915.1346
2029 | 2008 | 5 | 22 | 7 | 35812.4938
2029 | 2008 | 5 | 22 | 8 | 36928.2599
2029 | 2008 | 5 | 22 | 9 | 37838.1181
2029 | 2008 | 5 | 22 | 10 | 38065.0494
2029 | 2008 | 5 | 22 | 11 | 37864.657
2029 | 2008 | 5 | 22 | 12 | 36649.2114
2029 | 2008 | 5 | 22 | 13 | 35109.526
2029 | 2008 | 5 | 22 | 14 | 33711.8151
2029 | 2008 | 5 | 22 | 15 | 31182.9076
2029 | 2008 | 5 | 22 | 16 | 30560.2096
2029 | 2008 | 5 | 22 | 17 | 31425.9992
2029 | 2008 | 5 | 22 | 18 | 32334.4899
2029 | 2008 | 5 | 22 | 19 | 30944.7266
2029 | 2008 | 5 | 22 | 20 | 29965.0473
2029 | 2008 | 5 | 22 | 21 | 28729.8891
2029 | 2008 | 5 | 22 | 22 | 30399.5106
2029 | 2008 | 5 | 22 | 23 | 30742.8982
2029 | 2008 | 5 | 22 | 24 | 30592.1921
2029 | 2008 | 5 | 23 | 1 | 31056.3529
2029 | 2008 | 5 | 23 | 2 | 32253.812
2029 | 2008 | 5 | 23 | 3 | 32933.7143
2029 | 2008 | 5 | 23 | 4 | 31854.5031
2029 | 2008 | 5 | 23 | 5 | 30747.1523
2029 | 2008 | 5 | 23 | 6 | 29337.039
2029 | 2008 | 5 | 23 | 7 | 27169.7399
2029 | 2008 | 5 | 23 | 8 | 24572.5308
2029 | 2008 | 5 | 23 | 9 | 24377.6794
2029 | 2008 | 5 | 23 | 10 | 26481.0398
2029 | 2008 | 5 | 23 | 11 | 24870.1657
2029 | 2008 | 5 | 23 | 12 | 22677.4951
2029 | 2008 | 5 | 23 | 13 | 21639.1003
2029 | 2008 | 5 | 23 | 14 | 22118.3578
2029 | 2008 | 5 | 23 | 15 | 22518.7224
2029 | 2008 | 5 | 23 | 16 | 24435.3163
2029 | 2008 | 5 | 23 | 17 | 27693.5363
2029 | 2008 | 5 | 23 | 18 | 28786.868
2029 | 2008 | 5 | 23 | 19 | 30000.6434
2029 | 2008 | 5 | 23 | 20 | 29171.0935
2029 | 2008 | 5 | 23 | 21 | 28875.706
2029 | 2008 | 5 | 23 | 22 | 26815.2726
2029 | 2008 | 5 | 23 | 23 | 26099.2313
2029 | 2008 | 5 | 23 | 24 | 27184.9347
2029 | 2008 | 5 | 24 | 1 | 26825.7376
2029 | 2008 | 5 | 24 | 2 | 26047.1066
2029 | 2008 | 5 | 24 | 3 | 24798.9963
2029 | 2008 | 5 | 24 | 4 | 21865.4679
2029 | 2008 | 5 | 24 | 5 | 19648.4572
2029 | 2008 | 5 | 24 | 6 | 18737.6516
2029 | 2008 | 5 | 24 | 7 | 16351.2257
2029 | 2008 | 5 | 24 | 8 | 11979.8532
2029 | 2008 | 5 | 24 | 9 | 10026.6815
2029 | 2008 | 5 | 24 | 10 | 9555.5822
2029 | 2008 | 5 | 24 | 11 | 7244.7229
2029 | 2008 | 5 | 24 | 12 | 6132.9581
2029 | 2008 | 5 | 24 | 13 | 6015.0809
2029 | 2008 | 5 | 24 | 14 | 6887.883
2029 | 2008 | 5 | 24 | 15 | 7808.4324
2029 | 2008 | 5 | 24 | 16 | 9916.328
2029 | 2008 | 5 | 24 | 17 | 12220.6152
2029 | 2008 | 5 | 24 | 18 | 15979.7391
2029 | 2008 | 5 | 24 | 19 | 17943.6157
2029 | 2008 | 5 | 24 | 20 | 19731.9525
2029 | 2008 | 5 | 24 | 21 | 22268.3556
2029 | 2008 | 5 | 24 | 22 | 26454.4193
2029 | 2008 | 5 | 24 | 23 | 29225.9698
2029 | 2008 | 5 | 24 | 24 | 29894.8299
2029 | 2008 | 5 | 25 | 1 | 29480.7587
2029 | 2008 | 5 | 25 | 2 | 29052.8466
2029 | 2008 | 5 | 25 | 3 | 28204.5882
2029 | 2008 | 5 | 25 | 4 | 26973.2541
2029 | 2008 | 5 | 25 | 5 | 25043.0822
2029 | 2008 | 5 | 25 | 6 | 23454.2759
2029 | 2008 | 5 | 25 | 7 | 22546.034
2029 | 2008 | 5 | 25 | 8 | 22671.2968
2029 | 2008 | 5 | 25 | 9 | 25105.2147
2029 | 2008 | 5 | 25 | 10 | 26407.8887
2029 | 2008 | 5 | 25 | 11 | 28013.6237
2029 | 2008 | 5 | 25 | 12 | 28691.8658
2029 | 2008 | 5 | 25 | 13 | 28361.3273
2029 | 2008 | 5 | 25 | 14 | 28634.837
2029 | 2008 | 5 | 25 | 15 | 27735.2455
2029 | 2008 | 5 | 25 | 16 | 27258.3741
2029 | 2008 | 5 | 25 | 17 | 28395.4525
2029 | 2008 | 5 | 25 | 18 | 29287.1641
2029 | 2008 | 5 | 25 | 19 | 30436.7502
2029 | 2008 | 5 | 25 | 20 | 29777.9292
2029 | 2008 | 5 | 25 | 21 | 29647.7543
2029 | 2008 | 5 | 25 | 22 | 29475.5986
2029 | 2008 | 5 | 25 | 23 | 29673.7964
2029 | 2008 | 5 | 25 | 24 | 30086.7991
2029 | 2008 | 5 | 26 | 1 | 30640.4521
2029 | 2008 | 5 | 26 | 2 | 31249.1926
2029 | 2008 | 5 | 26 | 3 | 31930.0553
2029 | 2008 | 5 | 26 | 4 | 30799.2456
2029 | 2008 | 5 | 26 | 5 | 30427.2923
2029 | 2008 | 5 | 26 | 6 | 30492.7648
2029 | 2008 | 5 | 26 | 7 | 29920.0801
2029 | 2008 | 5 | 26 | 8 | 31031.2868
2029 | 2008 | 5 | 26 | 9 | 33754.6622
2029 | 2008 | 5 | 26 | 10 | 34302.4899
2029 | 2008 | 5 | 26 | 11 | 34220.819
2029 | 2008 | 5 | 26 | 12 | 32805.9261
2029 | 2008 | 5 | 26 | 13 | 31592.2343
2029 | 2008 | 5 | 26 | 14 | 30820.5597
2029 | 2008 | 5 | 26 | 15 | 29614.1108
2029 | 2008 | 5 | 26 | 16 | 29338.333
2029 | 2008 | 5 | 26 | 17 | 30647.2266
2029 | 2008 | 5 | 26 | 18 | 31813.5664
2029 | 2008 | 5 | 26 | 19 | 32315.7586
2029 | 2008 | 5 | 26 | 20 | 32438.056
2029 | 2008 | 5 | 26 | 21 | 31924.0326
2029 | 2008 | 5 | 26 | 22 | 32431.4569
2029 | 2008 | 5 | 26 | 23 | 33146.4592
2029 | 2008 | 5 | 26 | 24 | 33470.7104
2029 | 2008 | 5 | 27 | 1 | 32578.4655
2029 | 2008 | 5 | 27 | 2 | 30999.6075
2029 | 2008 | 5 | 27 | 3 | 28748.4438
2029 | 2008 | 5 | 27 | 4 | 27496.6766
2029 | 2008 | 5 | 27 | 5 | 26607.3557
2029 | 2008 | 5 | 27 | 6 | 26185.333
2029 | 2008 | 5 | 27 | 7 | 26071.4667
2029 | 2008 | 5 | 27 | 8 | 26680.8939
2029 | 2008 | 5 | 27 | 9 | 28820.539
2029 | 2008 | 5 | 27 | 10 | 29695.4616
2029 | 2008 | 5 | 27 | 11 | 28699.6076
2029 | 2008 | 5 | 27 | 12 | 25921.6756
2029 | 2008 | 5 | 27 | 13 | 22759.5573
2029 | 2008 | 5 | 27 | 14 | 20949.1239
2029 | 2008 | 5 | 27 | 15 | 19206.761
2029 | 2008 | 5 | 27 | 16 | 18436.3255
2029 | 2008 | 5 | 27 | 17 | 18699.2745
2029 | 2008 | 5 | 27 | 18 | 20089.5208
2029 | 2008 | 5 | 27 | 19 | 20769.6285
2029 | 2008 | 5 | 27 | 20 | 20879.0442
2029 | 2008 | 5 | 27 | 21 | 22452.9998
2029 | 2008 | 5 | 27 | 22 | 21295.0113
2029 | 2008 | 5 | 27 | 23 | 20817.9745
2029 | 2008 | 5 | 27 | 24 | 20509.1692
2029 | 2008 | 5 | 28 | 1 | 18282.4939
2029 | 2008 | 5 | 28 | 2 | 17092.8375
2029 | 2008 | 5 | 28 | 3 | 15860.9193
2029 | 2008 | 5 | 28 | 4 | 13680.9449
2029 | 2008 | 5 | 28 | 5 | 12997.2227
2029 | 2008 | 5 | 28 | 6 | 10960.6749
2029 | 2008 | 5 | 28 | 7 | 9448.5611
2029 | 2008 | 5 | 28 | 8 | 7765.5396
2029 | 2008 | 5 | 28 | 9 | 7572.932
2029 | 2008 | 5 | 28 | 10 | 6639.6653
2029 | 2008 | 5 | 28 | 11 | 5655.3539
2029 | 2008 | 5 | 28 | 12 | 5533.7644
2029 | 2008 | 5 | 28 | 13 | 5303.0021
2029 | 2008 | 5 | 28 | 14 | 6732.9346
2029 | 2008 | 5 | 28 | 15 | 7424.8561
2029 | 2008 | 5 | 28 | 16 | 8458.063
2029 | 2008 | 5 | 28 | 17 | 9676.9228
2029 | 2008 | 5 | 28 | 18 | 10939.0023
2029 | 2008 | 5 | 28 | 19 | 11413.3191
2029 | 2008 | 5 | 28 | 20 | 12847.4807
2029 | 2008 | 5 | 28 | 21 | 15735.2269
2029 | 2008 | 5 | 28 | 22 | 18633.3113
2029 | 2008 | 5 | 28 | 23 | 21119.9196
2029 | 2008 | 5 | 28 | 24 | 21854.6179
2029 | 2008 | 5 | 29 | 1 | 22676.1072
2029 | 2008 | 5 | 29 | 2 | 22834.8878
2029 | 2008 | 5 | 29 | 3 | 21726.7015
2029 | 2008 | 5 | 29 | 4 | 20565.9209
2029 | 2008 | 5 | 29 | 5 | 20130.4348
2029 | 2008 | 5 | 29 | 6 | 19152.3315
2029 | 2008 | 5 | 29 | 7 | 19027.7658
2029 | 2008 | 5 | 29 | 8 | 17612.9446
2029 | 2008 | 5 | 29 | 9 | 17235.0133
2029 | 2008 | 5 | 29 | 10 | 21349.7872
2029 | 2008 | 5 | 29 | 11 | 21605.3741
2029 | 2008 | 5 | 29 | 12 | 21706.1774
2029 | 2008 | 5 | 29 | 13 | 22569.0006
2029 | 2008 | 5 | 29 | 14 | 23919.9179
2029 | 2008 | 5 | 29 | 15 | 24018.8122
2029 | 2008 | 5 | 29 | 16 | 24629.5488
2029 | 2008 | 5 | 29 | 17 | 25866.7456
2029 | 2008 | 5 | 29 | 18 | 27022.0439
2029 | 2008 | 5 | 29 | 19 | 26653.6961
2029 | 2008 | 5 | 29 | 20 | 26890.7169
2029 | 2008 | 5 | 29 | 21 | 27621.6826
2029 | 2008 | 5 | 29 | 22 | 29209.6326
2029 | 2008 | 5 | 29 | 23 | 30661.8088
2029 | 2008 | 5 | 29 | 24 | 31324.0937
2029 | 2008 | 5 | 30 | 1 | 31711.2371
2029 | 2008 | 5 | 30 | 2 | 31813.1843
2029 | 2008 | 5 | 30 | 3 | 31342.0271
2029 | 2008 | 5 | 30 | 4 | 30866.8218
2029 | 2008 | 5 | 30 | 5 | 29976.0509
2029 | 2008 | 5 | 30 | 6 | 29323.6601
2029 | 2008 | 5 | 30 | 7 | 28213.5137
2029 | 2008 | 5 | 30 | 8 | 27351.9497
2029 | 2008 | 5 | 30 | 9 | 27923.7219
2029 | 2008 | 5 | 30 | 10 | 28950.9629
2029 | 2008 | 5 | 30 | 11 | 25621.2522
2029 | 2008 | 5 | 30 | 12 | 22629.6373
2029 | 2008 | 5 | 30 | 13 | 21260.808
2029 | 2008 | 5 | 30 | 14 | 20843.1662
2029 | 2008 | 5 | 30 | 15 | 19877.8585
2029 | 2008 | 5 | 30 | 16 | 20799.4855
2029 | 2008 | 5 | 30 | 17 | 21995.2869
2029 | 2008 | 5 | 30 | 18 | 24091.9331
2029 | 2008 | 5 | 30 | 19 | 25491.7983
2029 | 2008 | 5 | 30 | 20 | 27137.1525
2029 | 2008 | 5 | 30 | 21 | 29119.7116
2029 | 2008 | 5 | 30 | 22 | 31404.5134
2029 | 2008 | 5 | 30 | 23 | 31770.9097
2029 | 2008 | 5 | 30 | 24 | 31851.3799
2029 | 2008 | 5 | 31 | 1 | 32062.7984
2029 | 2008 | 5 | 31 | 2 | 32039.926
2029 | 2008 | 5 | 31 | 3 | 31907.4252
2029 | 2008 | 5 | 31 | 4 | 31156.6155
2029 | 2008 | 5 | 31 | 5 | 29382.5651
2029 | 2008 | 5 | 31 | 6 | 27774.6341
2029 | 2008 | 5 | 31 | 7 | 25856.9737
2029 | 2008 | 5 | 31 | 8 | 23742.5202
2029 | 2008 | 5 | 31 | 9 | 22961.9952
2029 | 2008 | 5 | 31 | 10 | 23431.5243
2029 | 2008 | 5 | 31 | 11 | 21096.0213
2029 | 2008 | 5 | 31 | 12 | 20241.165
2029 | 2008 | 5 | 31 | 13 | 20400.544
2029 | 2008 | 5 | 31 | 14 | 21078.499
2029 | 2008 | 5 | 31 | 15 | 22228.7579
2029 | 2008 | 5 | 31 | 16 | 23437.4619
2029 | 2008 | 5 | 31 | 17 | 24951.197
2029 | 2008 | 5 | 31 | 18 | 26601.6542
2029 | 2008 | 5 | 31 | 19 | 28844.6104
2029 | 2008 | 5 | 31 | 20 | 30195.4628
2029 | 2008 | 5 | 31 | 21 | 30233.5136
2029 | 2008 | 5 | 31 | 22 | 31242.1158
2029 | 2008 | 5 | 31 | 23 | 31049.5306
2029 | 2008 | 5 | 31 | 24 | 31435.7172
2030 | 2008 | 5 | 1 | 1 | 38220.9563
2030 | 2008 | 5 | 1 | 2 | 37787.8419
2030 | 2008 | 5 | 1 | 3 | 37007.3039
2030 | 2008 | 5 | 1 | 4 | 35678.297
2030 | 2008 | 5 | 1 | 5 | 35165.9999
2030 | 2008 | 5 | 1 | 6 | 34977.5505
2030 | 2008 | 5 | 1 | 7 | 33745.649
2030 | 2008 | 5 | 1 | 8 | 31957.3819
2030 | 2008 | 5 | 1 | 9 | 31624.0711
2030 | 2008 | 5 | 1 | 10 | 31522.1803
2030 | 2008 | 5 | 1 | 11 | 31384.5934
2030 | 2008 | 5 | 1 | 12 | 30284.6606
2030 | 2008 | 5 | 1 | 13 | 29368.1639
2030 | 2008 | 5 | 1 | 14 | 28757.7872
2030 | 2008 | 5 | 1 | 15 | 28296.449
2030 | 2008 | 5 | 1 | 16 | 27712.0359
2030 | 2008 | 5 | 1 | 17 | 29449.3684
2030 | 2008 | 5 | 1 | 18 | 29829.0034
2030 | 2008 | 5 | 1 | 19 | 31230.152
2030 | 2008 | 5 | 1 | 20 | 31639.2453
2030 | 2008 | 5 | 1 | 21 | 32664.1658
2030 | 2008 | 5 | 1 | 22 | 34214.4923
2030 | 2008 | 5 | 1 | 23 | 34126.781
2030 | 2008 | 5 | 1 | 24 | 33833.5364
2030 | 2008 | 5 | 2 | 1 | 34294.5882
2030 | 2008 | 5 | 2 | 2 | 33140.1891
2030 | 2008 | 5 | 2 | 3 | 33038.6137
2030 | 2008 | 5 | 2 | 4 | 32871.4875
2030 | 2008 | 5 | 2 | 5 | 32325.9765
2030 | 2008 | 5 | 2 | 6 | 30490.2478
2030 | 2008 | 5 | 2 | 7 | 28323.9398
2030 | 2008 | 5 | 2 | 8 | 21474.4325
2030 | 2008 | 5 | 2 | 9 | 15412.9545
2030 | 2008 | 5 | 2 | 10 | 11956.303
2030 | 2008 | 5 | 2 | 11 | 8045.9221
2030 | 2008 | 5 | 2 | 12 | 7944.6113
2030 | 2008 | 5 | 2 | 13 | 10135.4971
2030 | 2008 | 5 | 2 | 14 | 13023.3595
2030 | 2008 | 5 | 2 | 15 | 15859.1994
2030 | 2008 | 5 | 2 | 16 | 16849.1507
2030 | 2008 | 5 | 2 | 17 | 16977.1525
2030 | 2008 | 5 | 2 | 18 | 15956.3333
2030 | 2008 | 5 | 2 | 19 | 12579.5869
2030 | 2008 | 5 | 2 | 20 | 10846.828
2030 | 2008 | 5 | 2 | 21 | 10594.4512
2030 | 2008 | 5 | 2 | 22 | 12173.9669
2030 | 2008 | 5 | 2 | 23 | 14490.1878
2030 | 2008 | 5 | 2 | 24 | 17600.878
2030 | 2008 | 5 | 3 | 1 | 21750.8162
2030 | 2008 | 5 | 3 | 2 | 24058.7996
2030 | 2008 | 5 | 3 | 3 | 25149.0495
2030 | 2008 | 5 | 3 | 4 | 26270.7593
2030 | 2008 | 5 | 3 | 5 | 26782.3094
2030 | 2008 | 5 | 3 | 6 | 26883.7315
2030 | 2008 | 5 | 3 | 7 | 25775.9133
2030 | 2008 | 5 | 3 | 8 | 25391.0143
2030 | 2008 | 5 | 3 | 9 | 26469.9707
2030 | 2008 | 5 | 3 | 10 | 25577.3645
2030 | 2008 | 5 | 3 | 11 | 20420.1515
2030 | 2008 | 5 | 3 | 12 | 16269.3087
2030 | 2008 | 5 | 3 | 13 | 14229.1794
2030 | 2008 | 5 | 3 | 14 | 12721.3294
2030 | 2008 | 5 | 3 | 15 | 11494.1936
2030 | 2008 | 5 | 3 | 16 | 10360.5633
2030 | 2008 | 5 | 3 | 17 | 10050.9536
2030 | 2008 | 5 | 3 | 18 | 10118.3507
2030 | 2008 | 5 | 3 | 19 | 9705.1793
2030 | 2008 | 5 | 3 | 20 | 9547.8173
2030 | 2008 | 5 | 3 | 21 | 10233.7195
2030 | 2008 | 5 | 3 | 22 | 11224.7026
2030 | 2008 | 5 | 3 | 23 | 13335.7008
2030 | 2008 | 5 | 3 | 24 | 13881.8286
2030 | 2008 | 5 | 4 | 1 | 14043.9308
2030 | 2008 | 5 | 4 | 2 | 14124.996
2030 | 2008 | 5 | 4 | 3 | 14088.0201
2030 | 2008 | 5 | 4 | 4 | 13998.9968
2030 | 2008 | 5 | 4 | 5 | 14230.4128
2030 | 2008 | 5 | 4 | 6 | 14238.1678
2030 | 2008 | 5 | 4 | 7 | 14819.5193
2030 | 2008 | 5 | 4 | 8 | 12022.8801
2030 | 2008 | 5 | 4 | 9 | 11418.5789
2030 | 2008 | 5 | 4 | 10 | 13573.0814
2030 | 2008 | 5 | 4 | 11 | 14978.551
2030 | 2008 | 5 | 4 | 12 | 15540.5772
2030 | 2008 | 5 | 4 | 13 | 16639.6103
2030 | 2008 | 5 | 4 | 14 | 17705.1728
2030 | 2008 | 5 | 4 | 15 | 18270.9454
2030 | 2008 | 5 | 4 | 16 | 18789.661
2030 | 2008 | 5 | 4 | 17 | 20804.4494
2030 | 2008 | 5 | 4 | 18 | 22463.7432
2030 | 2008 | 5 | 4 | 19 | 23789.8397
2030 | 2008 | 5 | 4 | 20 | 23253.4556
2030 | 2008 | 5 | 4 | 21 | 23910.646
2030 | 2008 | 5 | 4 | 22 | 24881.571
2030 | 2008 | 5 | 4 | 23 | 24511.7045
2030 | 2008 | 5 | 4 | 24 | 23035.6939
2030 | 2008 | 5 | 5 | 1 | 21675.4544
2030 | 2008 | 5 | 5 | 2 | 21108.087
2030 | 2008 | 5 | 5 | 3 | 20916.866
2030 | 2008 | 5 | 5 | 4 | 19384.754
2030 | 2008 | 5 | 5 | 5 | 17415.5531
2030 | 2008 | 5 | 5 | 6 | 16415.1053
2030 | 2008 | 5 | 5 | 7 | 14515.434
2030 | 2008 | 5 | 5 | 8 | 15286.8703
2030 | 2008 | 5 | 5 | 9 | 18316.9406
2030 | 2008 | 5 | 5 | 10 | 19889.7038
2030 | 2008 | 5 | 5 | 11 | 21068.9216
2030 | 2008 | 5 | 5 | 12 | 21921.8073
2030 | 2008 | 5 | 5 | 13 | 22121.5879
2030 | 2008 | 5 | 5 | 14 | 22953.4723
2030 | 2008 | 5 | 5 | 15 | 22586.0335
2030 | 2008 | 5 | 5 | 16 | 22386.6686
2030 | 2008 | 5 | 5 | 17 | 24472.7207
2030 | 2008 | 5 | 5 | 18 | 26486.2212
2030 | 2008 | 5 | 5 | 19 | 27997.9272
2030 | 2008 | 5 | 5 | 20 | 30067.3669
2030 | 2008 | 5 | 5 | 21 | 31606.2509
2030 | 2008 | 5 | 5 | 22 | 31963.6256
2030 | 2008 | 5 | 5 | 23 | 31574.615
2030 | 2008 | 5 | 5 | 24 | 30210.5706
2030 | 2008 | 5 | 6 | 1 | 28143.3394
2030 | 2008 | 5 | 6 | 2 | 25054.9808
2030 | 2008 | 5 | 6 | 3 | 22041.2432
2030 | 2008 | 5 | 6 | 4 | 19427.1869
2030 | 2008 | 5 | 6 | 5 | 19308.4772
2030 | 2008 | 5 | 6 | 6 | 20840.9175
2030 | 2008 | 5 | 6 | 7 | 21882.71
2030 | 2008 | 5 | 6 | 8 | 24205.9338
2030 | 2008 | 5 | 6 | 9 | 28467.7083
2030 | 2008 | 5 | 6 | 10 | 30196.9507
2030 | 2008 | 5 | 6 | 11 | 29998.0111
2030 | 2008 | 5 | 6 | 12 | 30278.3208
2030 | 2008 | 5 | 6 | 13 | 31731.1096
2030 | 2008 | 5 | 6 | 14 | 33524.7132
2030 | 2008 | 5 | 6 | 15 | 34581.2273
2030 | 2008 | 5 | 6 | 16 | 35094.3697
2030 | 2008 | 5 | 6 | 17 | 34491.3821
2030 | 2008 | 5 | 6 | 18 | 34893.3885
2030 | 2008 | 5 | 6 | 19 | 33893.6689
2030 | 2008 | 5 | 6 | 20 | 34284.2799
2030 | 2008 | 5 | 6 | 21 | 33412.5867
2030 | 2008 | 5 | 6 | 22 | 34104.4158
2030 | 2008 | 5 | 6 | 23 | 34322.1652
2030 | 2008 | 5 | 6 | 24 | 32958.5508
2030 | 2008 | 5 | 7 | 1 | 31920.0252
2030 | 2008 | 5 | 7 | 2 | 31502.8389
2030 | 2008 | 5 | 7 | 3 | 31656.8233
2030 | 2008 | 5 | 7 | 4 | 31771.4749
2030 | 2008 | 5 | 7 | 5 | 31747.9222
2030 | 2008 | 5 | 7 | 6 | 31897.4401
2030 | 2008 | 5 | 7 | 7 | 32026.103
2030 | 2008 | 5 | 7 | 8 | 32203.5425
2030 | 2008 | 5 | 7 | 9 | 33251.2756
2030 | 2008 | 5 | 7 | 10 | 32534.3505
2030 | 2008 | 5 | 7 | 11 | 31899.27
2030 | 2008 | 5 | 7 | 12 | 30182.1539
2030 | 2008 | 5 | 7 | 13 | 29953.646
2030 | 2008 | 5 | 7 | 14 | 29728.371
2030 | 2008 | 5 | 7 | 15 | 32242.0559
2030 | 2008 | 5 | 7 | 16 | 32648.2636
2030 | 2008 | 5 | 7 | 17 | 33231.8237
2030 | 2008 | 5 | 7 | 18 | 32451.4029
2030 | 2008 | 5 | 7 | 19 | 29164.9129
2030 | 2008 | 5 | 7 | 20 | 27947.3626
2030 | 2008 | 5 | 7 | 21 | 25496.7507
2030 | 2008 | 5 | 7 | 22 | 23500.6622
2030 | 2008 | 5 | 7 | 23 | 22597.0249
2030 | 2008 | 5 | 7 | 24 | 21028.9589
2030 | 2008 | 5 | 8 | 1 | 18676.361
2030 | 2008 | 5 | 8 | 2 | 17546.1791
2030 | 2008 | 5 | 8 | 3 | 14882.4765
2030 | 2008 | 5 | 8 | 4 | 12359.3001
2030 | 2008 | 5 | 8 | 5 | 11158.5357
2030 | 2008 | 5 | 8 | 6 | 9094.326
2030 | 2008 | 5 | 8 | 7 | 8067.5376
2030 | 2008 | 5 | 8 | 8 | 5661.5957
2030 | 2008 | 5 | 8 | 9 | 4529.3329
2030 | 2008 | 5 | 8 | 10 | 3488.4192
2030 | 2008 | 5 | 8 | 11 | 3832.6148
2030 | 2008 | 5 | 8 | 12 | 4707.4723
2030 | 2008 | 5 | 8 | 13 | 6188.3747
2030 | 2008 | 5 | 8 | 14 | 8305.609
2030 | 2008 | 5 | 8 | 15 | 10237.3229
2030 | 2008 | 5 | 8 | 16 | 13132.8263
2030 | 2008 | 5 | 8 | 17 | 16650.7533
2030 | 2008 | 5 | 8 | 18 | 20363.5454
2030 | 2008 | 5 | 8 | 19 | 20821.8185
2030 | 2008 | 5 | 8 | 20 | 23130.8336
2030 | 2008 | 5 | 8 | 21 | 25993.5533
2030 | 2008 | 5 | 8 | 22 | 29854.8522
2030 | 2008 | 5 | 8 | 23 | 30204.4519
2030 | 2008 | 5 | 8 | 24 | 29861.0557
2030 | 2008 | 5 | 9 | 1 | 30995.2945
2030 | 2008 | 5 | 9 | 2 | 30179.2889
2030 | 2008 | 5 | 9 | 3 | 29650.1293
2030 | 2008 | 5 | 9 | 4 | 27550.1592
2030 | 2008 | 5 | 9 | 5 | 25669.5985
2030 | 2008 | 5 | 9 | 6 | 23803.7372
2030 | 2008 | 5 | 9 | 7 | 19687.1645
2030 | 2008 | 5 | 9 | 8 | 13906.3422
2030 | 2008 | 5 | 9 | 9 | 9645.3602
2030 | 2008 | 5 | 9 | 10 | 8113.3323
2030 | 2008 | 5 | 9 | 11 | 7528.5876
2030 | 2008 | 5 | 9 | 12 | 7439.1148
2030 | 2008 | 5 | 9 | 13 | 7162.5351
2030 | 2008 | 5 | 9 | 14 | 6779.4845
2030 | 2008 | 5 | 9 | 15 | 6426.1822
2030 | 2008 | 5 | 9 | 16 | 6839.5399
2030 | 2008 | 5 | 9 | 17 | 7728.7467
2030 | 2008 | 5 | 9 | 18 | 8623.0402
2030 | 2008 | 5 | 9 | 19 | 9452.4526
2030 | 2008 | 5 | 9 | 20 | 11197.1213
2030 | 2008 | 5 | 9 | 21 | 14898.4761
2030 | 2008 | 5 | 9 | 22 | 18724.9759
2030 | 2008 | 5 | 9 | 23 | 22361.0248
2030 | 2008 | 5 | 9 | 24 | 24570.8682
2030 | 2008 | 5 | 10 | 1 | 26391.9502
2030 | 2008 | 5 | 10 | 2 | 26687.0673
2030 | 2008 | 5 | 10 | 3 | 26090.7494
2030 | 2008 | 5 | 10 | 4 | 25493.7907
2030 | 2008 | 5 | 10 | 5 | 25176.3695
2030 | 2008 | 5 | 10 | 6 | 25500.0044
2030 | 2008 | 5 | 10 | 7 | 24967.0618
2030 | 2008 | 5 | 10 | 8 | 23545.1263
2030 | 2008 | 5 | 10 | 9 | 23524.3516
2030 | 2008 | 5 | 10 | 10 | 24803.3223
2030 | 2008 | 5 | 10 | 11 | 25062.1221
2030 | 2008 | 5 | 10 | 12 | 26724.7998
2030 | 2008 | 5 | 10 | 13 | 27640.1086
2030 | 2008 | 5 | 10 | 14 | 26871.9543
2030 | 2008 | 5 | 10 | 15 | 26110.366
2030 | 2008 | 5 | 10 | 16 | 25072.2704
2030 | 2008 | 5 | 10 | 17 | 24087.4002
2030 | 2008 | 5 | 10 | 18 | 22456.0075
2030 | 2008 | 5 | 10 | 19 | 19919.6607
2030 | 2008 | 5 | 10 | 20 | 19082.2148
2030 | 2008 | 5 | 10 | 21 | 18936.4323
2030 | 2008 | 5 | 10 | 22 | 19834.0576
2030 | 2008 | 5 | 10 | 23 | 23426.9033
2030 | 2008 | 5 | 10 | 24 | 26036.8667
2030 | 2008 | 5 | 11 | 1 | 28644.7855
2030 | 2008 | 5 | 11 | 2 | 29589.2307
2030 | 2008 | 5 | 11 | 3 | 29607.939
2030 | 2008 | 5 | 11 | 4 | 28137.8135
2030 | 2008 | 5 | 11 | 5 | 27200.2345
2030 | 2008 | 5 | 11 | 6 | 26073.0522
2030 | 2008 | 5 | 11 | 7 | 24364.2765
2030 | 2008 | 5 | 11 | 8 | 22992.8635
2030 | 2008 | 5 | 11 | 9 | 23335.4809
2030 | 2008 | 5 | 11 | 10 | 21026.3277
2030 | 2008 | 5 | 11 | 11 | 16599.6667
2030 | 2008 | 5 | 11 | 12 | 15375.0939
2030 | 2008 | 5 | 11 | 13 | 14566.4454
2030 | 2008 | 5 | 11 | 14 | 13919.511
2030 | 2008 | 5 | 11 | 15 | 13263.5041
2030 | 2008 | 5 | 11 | 16 | 12513.9859
2030 | 2008 | 5 | 11 | 17 | 12476.7963
2030 | 2008 | 5 | 11 | 18 | 12468.1859
2030 | 2008 | 5 | 11 | 19 | 12496.7202
2030 | 2008 | 5 | 11 | 20 | 12590.7479
2030 | 2008 | 5 | 11 | 21 | 14012.3056
2030 | 2008 | 5 | 11 | 22 | 15868.2818
2030 | 2008 | 5 | 11 | 23 | 17686.2732
2030 | 2008 | 5 | 11 | 24 | 18495.4297
2030 | 2008 | 5 | 12 | 1 | 20403.9353
2030 | 2008 | 5 | 12 | 2 | 21811.8597
2030 | 2008 | 5 | 12 | 3 | 22202.7369
2030 | 2008 | 5 | 12 | 4 | 23128.3937
2030 | 2008 | 5 | 12 | 5 | 23759.9769
2030 | 2008 | 5 | 12 | 6 | 24950.3374
2030 | 2008 | 5 | 12 | 7 | 25777.7505
2030 | 2008 | 5 | 12 | 8 | 24595.869
2030 | 2008 | 5 | 12 | 9 | 24310.6673
2030 | 2008 | 5 | 12 | 10 | 27891.068
2030 | 2008 | 5 | 12 | 11 | 29695.2047
2030 | 2008 | 5 | 12 | 12 | 31016.6562
2030 | 2008 | 5 | 12 | 13 | 31671.2689
2030 | 2008 | 5 | 12 | 14 | 33061.3119
2030 | 2008 | 5 | 12 | 15 | 33663.3367
2030 | 2008 | 5 | 12 | 16 | 34969.1332
2030 | 2008 | 5 | 12 | 17 | 35613.0232
2030 | 2008 | 5 | 12 | 18 | 36237.9633
2030 | 2008 | 5 | 12 | 19 | 36192.8603
2030 | 2008 | 5 | 12 | 20 | 34584.2864
2030 | 2008 | 5 | 12 | 21 | 33482.2839
2030 | 2008 | 5 | 12 | 22 | 34183.7254
2030 | 2008 | 5 | 12 | 23 | 34751.5973
2030 | 2008 | 5 | 12 | 24 | 35190.6625
2030 | 2008 | 5 | 13 | 1 | 35554.0974
2030 | 2008 | 5 | 13 | 2 | 35848.2227
2030 | 2008 | 5 | 13 | 3 | 35225.8016
2030 | 2008 | 5 | 13 | 4 | 33526.7454
2030 | 2008 | 5 | 13 | 5 | 32685.96
2030 | 2008 | 5 | 13 | 6 | 30746.3991
2030 | 2008 | 5 | 13 | 7 | 28958.967
2030 | 2008 | 5 | 13 | 8 | 27133.8296
2030 | 2008 | 5 | 13 | 9 | 26454.934
2030 | 2008 | 5 | 13 | 10 | 24225.5726
2030 | 2008 | 5 | 13 | 11 | 20174.9992
2030 | 2008 | 5 | 13 | 12 | 16499.903
2030 | 2008 | 5 | 13 | 13 | 14557.7123
2030 | 2008 | 5 | 13 | 14 | 13002.2463
2030 | 2008 | 5 | 13 | 15 | 12543.4797
2030 | 2008 | 5 | 13 | 16 | 12852.536
2030 | 2008 | 5 | 13 | 17 | 14346.1844
2030 | 2008 | 5 | 13 | 18 | 16424.6649
2030 | 2008 | 5 | 13 | 19 | 20035.0353
2030 | 2008 | 5 | 13 | 20 | 22471.9358
2030 | 2008 | 5 | 13 | 21 | 26501.0592
2030 | 2008 | 5 | 13 | 22 | 25083.1889
2030 | 2008 | 5 | 13 | 23 | 24988.2002
2030 | 2008 | 5 | 13 | 24 | 25617.1887
2030 | 2008 | 5 | 14 | 1 | 25778.9564
2030 | 2008 | 5 | 14 | 2 | 24682.7056
2030 | 2008 | 5 | 14 | 3 | 22492.0429
2030 | 2008 | 5 | 14 | 4 | 20718.2249
2030 | 2008 | 5 | 14 | 5 | 19995.6083
2030 | 2008 | 5 | 14 | 6 | 19124.1302
2030 | 2008 | 5 | 14 | 7 | 19212.0496
2030 | 2008 | 5 | 14 | 8 | 19115.3493
2030 | 2008 | 5 | 14 | 9 | 20758.3365
2030 | 2008 | 5 | 14 | 10 | 20519.8996
2030 | 2008 | 5 | 14 | 11 | 18784.5115
2030 | 2008 | 5 | 14 | 12 | 17099.0056
2030 | 2008 | 5 | 14 | 13 | 15081.4862
2030 | 2008 | 5 | 14 | 14 | 13427.0189
2030 | 2008 | 5 | 14 | 15 | 13576.1792
2030 | 2008 | 5 | 14 | 16 | 14036.5979
2030 | 2008 | 5 | 14 | 17 | 14511.4094
2030 | 2008 | 5 | 14 | 18 | 15941.6961
2030 | 2008 | 5 | 14 | 19 | 15784.0727
2030 | 2008 | 5 | 14 | 20 | 13908.3164
2030 | 2008 | 5 | 14 | 21 | 14122.6476
2030 | 2008 | 5 | 14 | 22 | 13383.6684
2030 | 2008 | 5 | 14 | 23 | 11585.2389
2030 | 2008 | 5 | 14 | 24 | 8516.7149
2030 | 2008 | 5 | 15 | 1 | 7003.9589
2030 | 2008 | 5 | 15 | 2 | 5688.3006
2030 | 2008 | 5 | 15 | 3 | 5947.8496
2030 | 2008 | 5 | 15 | 4 | 6731.392
2030 | 2008 | 5 | 15 | 5 | 7402.7487
2030 | 2008 | 5 | 15 | 6 | 7475.9396
2030 | 2008 | 5 | 15 | 7 | 10897.6323
2030 | 2008 | 5 | 15 | 8 | 11320.999
2030 | 2008 | 5 | 15 | 9 | 13709.7015
2030 | 2008 | 5 | 15 | 10 | 12797.1558
2030 | 2008 | 5 | 15 | 11 | 10865.876
2030 | 2008 | 5 | 15 | 12 | 9955.1333
2030 | 2008 | 5 | 15 | 13 | 10282.3399
2030 | 2008 | 5 | 15 | 14 | 9823.7871
2030 | 2008 | 5 | 15 | 15 | 8176.0808
2030 | 2008 | 5 | 15 | 16 | 7965.5761
2030 | 2008 | 5 | 15 | 17 | 7712.5033
2030 | 2008 | 5 | 15 | 18 | 8319.9329
2030 | 2008 | 5 | 15 | 19 | 9574.0713
2030 | 2008 | 5 | 15 | 20 | 10630.3324
2030 | 2008 | 5 | 15 | 21 | 13483.7894
2030 | 2008 | 5 | 15 | 22 | 12993.072
2030 | 2008 | 5 | 15 | 23 | 11983.5926
2030 | 2008 | 5 | 15 | 24 | 11190.3568
2030 | 2008 | 5 | 16 | 1 | 10165.8582
2030 | 2008 | 5 | 16 | 2 | 9189.3844
2030 | 2008 | 5 | 16 | 3 | 9443.7657
2030 | 2008 | 5 | 16 | 4 | 10274.2808
2030 | 2008 | 5 | 16 | 5 | 11644.6475
2030 | 2008 | 5 | 16 | 6 | 13379.1732
2030 | 2008 | 5 | 16 | 7 | 15913.6445
2030 | 2008 | 5 | 16 | 8 | 15518.7726
2030 | 2008 | 5 | 16 | 9 | 14386.6178
2030 | 2008 | 5 | 16 | 10 | 19036.4825
2030 | 2008 | 5 | 16 | 11 | 19698.1813
2030 | 2008 | 5 | 16 | 12 | 18684.1541
2030 | 2008 | 5 | 16 | 13 | 16742.6651
2030 | 2008 | 5 | 16 | 14 | 14314.6611
2030 | 2008 | 5 | 16 | 15 | 12252.5975
2030 | 2008 | 5 | 16 | 16 | 10709.7615
2030 | 2008 | 5 | 16 | 17 | 10160.8704
2030 | 2008 | 5 | 16 | 18 | 8911.8834
2030 | 2008 | 5 | 16 | 19 | 6975.6803
2030 | 2008 | 5 | 16 | 20 | 4608.4004
2030 | 2008 | 5 | 16 | 21 | 3423.7341
2030 | 2008 | 5 | 16 | 22 | 2731.2022
2030 | 2008 | 5 | 16 | 23 | 2628.1276
2030 | 2008 | 5 | 16 | 24 | 3079.5055
2030 | 2008 | 5 | 17 | 1 | 3775.0572
2030 | 2008 | 5 | 17 | 2 | 5032.7112
2030 | 2008 | 5 | 17 | 3 | 6805.1344
2030 | 2008 | 5 | 17 | 4 | 9504.4902
2030 | 2008 | 5 | 17 | 5 | 11475.0053
2030 | 2008 | 5 | 17 | 6 | 12002.9364
2030 | 2008 | 5 | 17 | 7 | 11916.0812
2030 | 2008 | 5 | 17 | 8 | 9225.6589
2030 | 2008 | 5 | 17 | 9 | 8575.1629
2030 | 2008 | 5 | 17 | 10 | 5169.8102
2030 | 2008 | 5 | 17 | 11 | 5606.0982
2030 | 2008 | 5 | 17 | 12 | 4580.7746
2030 | 2008 | 5 | 17 | 13 | 3799.7077
2030 | 2008 | 5 | 17 | 14 | 4258.007
2030 | 2008 | 5 | 17 | 15 | 4338.9276
2030 | 2008 | 5 | 17 | 16 | 4343.3039
2030 | 2008 | 5 | 17 | 17 | 3883.1223
2030 | 2008 | 5 | 17 | 18 | 4208.1862
2030 | 2008 | 5 | 17 | 19 | 4159.2534
2030 | 2008 | 5 | 17 | 20 | 4039.5193
2030 | 2008 | 5 | 17 | 21 | 5404.3641
2030 | 2008 | 5 | 17 | 22 | 7035.4259
2030 | 2008 | 5 | 17 | 23 | 8746.5503
2030 | 2008 | 5 | 17 | 24 | 9583.1392
2030 | 2008 | 5 | 18 | 1 | 11173.6799
2030 | 2008 | 5 | 18 | 2 | 12440.7639
2030 | 2008 | 5 | 18 | 3 | 15214.1489
2030 | 2008 | 5 | 18 | 4 | 17004.9386
2030 | 2008 | 5 | 18 | 5 | 18839.5617
2030 | 2008 | 5 | 18 | 6 | 20019.7793
2030 | 2008 | 5 | 18 | 7 | 20750.2155
2030 | 2008 | 5 | 18 | 8 | 15712.6132
2030 | 2008 | 5 | 18 | 9 | 11410.1047
2030 | 2008 | 5 | 18 | 10 | 7275.3253
2030 | 2008 | 5 | 18 | 11 | 7848.9223
2030 | 2008 | 5 | 18 | 12 | 7231.9575
2030 | 2008 | 5 | 18 | 13 | 6388.3968
2030 | 2008 | 5 | 18 | 14 | 5480.215
2030 | 2008 | 5 | 18 | 15 | 4380.3431
2030 | 2008 | 5 | 18 | 16 | 3446.7733
2030 | 2008 | 5 | 18 | 17 | 2920.6243
2030 | 2008 | 5 | 18 | 18 | 2433.9258
2030 | 2008 | 5 | 18 | 19 | 2055.7505
2030 | 2008 | 5 | 18 | 20 | 2604.8579
2030 | 2008 | 5 | 18 | 21 | 4360.6614
2030 | 2008 | 5 | 18 | 22 | 8800.2658
2030 | 2008 | 5 | 18 | 23 | 15138.0913
2030 | 2008 | 5 | 18 | 24 | 20017.3779
2030 | 2008 | 5 | 19 | 1 | 24700.2274
2030 | 2008 | 5 | 19 | 2 | 28077.0765
2030 | 2008 | 5 | 19 | 3 | 29937.7781
2030 | 2008 | 5 | 19 | 4 | 30462.4529
2030 | 2008 | 5 | 19 | 5 | 30348.2893
2030 | 2008 | 5 | 19 | 6 | 29647.7624
2030 | 2008 | 5 | 19 | 7 | 28702.4176
2030 | 2008 | 5 | 19 | 8 | 25533.3136
2030 | 2008 | 5 | 19 | 9 | 23277.613
2030 | 2008 | 5 | 19 | 10 | 20737.3566
2030 | 2008 | 5 | 19 | 11 | 21380.9883
2030 | 2008 | 5 | 19 | 12 | 21101.8649
2030 | 2008 | 5 | 19 | 13 | 19671.8085
2030 | 2008 | 5 | 19 | 14 | 18400.5996
2030 | 2008 | 5 | 19 | 15 | 16246.6499
2030 | 2008 | 5 | 19 | 16 | 15639.8352
2030 | 2008 | 5 | 19 | 17 | 15862.3226
2030 | 2008 | 5 | 19 | 18 | 15720.5887
2030 | 2008 | 5 | 19 | 19 | 14922.2618
2030 | 2008 | 5 | 19 | 20 | 16012.896
2030 | 2008 | 5 | 19 | 21 | 18248.8445
2030 | 2008 | 5 | 19 | 22 | 22338.6071
2030 | 2008 | 5 | 19 | 23 | 25643.1054
2030 | 2008 | 5 | 19 | 24 | 27272.7437
2030 | 2008 | 5 | 20 | 1 | 28096.4901
2030 | 2008 | 5 | 20 | 2 | 27748.0922
2030 | 2008 | 5 | 20 | 3 | 27919.8386
2030 | 2008 | 5 | 20 | 4 | 27292.6755
2030 | 2008 | 5 | 20 | 5 | 27274.1071
2030 | 2008 | 5 | 20 | 6 | 25118.7995
2030 | 2008 | 5 | 20 | 7 | 21708.2531
2030 | 2008 | 5 | 20 | 8 | 16300.5313
2030 | 2008 | 5 | 20 | 9 | 13009.5496
2030 | 2008 | 5 | 20 | 10 | 12501.1224
2030 | 2008 | 5 | 20 | 11 | 14634.0558
2030 | 2008 | 5 | 20 | 12 | 15322.5589
2030 | 2008 | 5 | 20 | 13 | 15284.3838
2030 | 2008 | 5 | 20 | 14 | 15047.2749
2030 | 2008 | 5 | 20 | 15 | 14232.7788
2030 | 2008 | 5 | 20 | 16 | 13649.8115
2030 | 2008 | 5 | 20 | 17 | 14223.0501
2030 | 2008 | 5 | 20 | 18 | 16193.0374
2030 | 2008 | 5 | 20 | 19 | 17849.7766
2030 | 2008 | 5 | 20 | 20 | 20749.2541
2030 | 2008 | 5 | 20 | 21 | 24997.174
2030 | 2008 | 5 | 20 | 22 | 25590.2466
2030 | 2008 | 5 | 20 | 23 | 25437.0175
2030 | 2008 | 5 | 20 | 24 | 24037.4628
2030 | 2008 | 5 | 21 | 1 | 21593.8891
2030 | 2008 | 5 | 21 | 2 | 20304.4759
2030 | 2008 | 5 | 21 | 3 | 20533.1955
2030 | 2008 | 5 | 21 | 4 | 20583.3109
2030 | 2008 | 5 | 21 | 5 | 20551.0563
2030 | 2008 | 5 | 21 | 6 | 21060.6959
2030 | 2008 | 5 | 21 | 7 | 21479.717
2030 | 2008 | 5 | 21 | 8 | 20836.9834
2030 | 2008 | 5 | 21 | 9 | 21923.1028
2030 | 2008 | 5 | 21 | 10 | 25227.3091
2030 | 2008 | 5 | 21 | 11 | 27789.6041
2030 | 2008 | 5 | 21 | 12 | 29367.9545
2030 | 2008 | 5 | 21 | 13 | 31373.5753
2030 | 2008 | 5 | 21 | 14 | 33234.7366
2030 | 2008 | 5 | 21 | 15 | 34015.848
2030 | 2008 | 5 | 21 | 16 | 33927.146
2030 | 2008 | 5 | 21 | 17 | 34291.0267
2030 | 2008 | 5 | 21 | 18 | 34444.6473
2030 | 2008 | 5 | 21 | 19 | 34373.1701
2030 | 2008 | 5 | 21 | 20 | 34886.3936
2030 | 2008 | 5 | 21 | 21 | 35082.4525
2030 | 2008 | 5 | 21 | 22 | 34875.4881
2030 | 2008 | 5 | 21 | 23 | 35155.8024
2030 | 2008 | 5 | 21 | 24 | 35731.112
2030 | 2008 | 5 | 22 | 1 | 35924.5859
2030 | 2008 | 5 | 22 | 2 | 36374.6733
2030 | 2008 | 5 | 22 | 3 | 36835.6438
2030 | 2008 | 5 | 22 | 4 | 36906.5587
2030 | 2008 | 5 | 22 | 5 | 36376.8696
2030 | 2008 | 5 | 22 | 6 | 35915.1346
2030 | 2008 | 5 | 22 | 7 | 35812.4938
2030 | 2008 | 5 | 22 | 8 | 36928.2599
2030 | 2008 | 5 | 22 | 9 | 37838.1181
2030 | 2008 | 5 | 22 | 10 | 38065.0494
2030 | 2008 | 5 | 22 | 11 | 37864.657
2030 | 2008 | 5 | 22 | 12 | 36649.2114
2030 | 2008 | 5 | 22 | 13 | 35109.526
2030 | 2008 | 5 | 22 | 14 | 33711.8151
2030 | 2008 | 5 | 22 | 15 | 31182.9076
2030 | 2008 | 5 | 22 | 16 | 30560.2096
2030 | 2008 | 5 | 22 | 17 | 31425.9992
2030 | 2008 | 5 | 22 | 18 | 32334.4899
2030 | 2008 | 5 | 22 | 19 | 30944.7266
2030 | 2008 | 5 | 22 | 20 | 29965.0473
2030 | 2008 | 5 | 22 | 21 | 28729.8891
2030 | 2008 | 5 | 22 | 22 | 30399.5106
2030 | 2008 | 5 | 22 | 23 | 30742.8982
2030 | 2008 | 5 | 22 | 24 | 30592.1921
2030 | 2008 | 5 | 23 | 1 | 31056.3529
2030 | 2008 | 5 | 23 | 2 | 32253.812
2030 | 2008 | 5 | 23 | 3 | 32933.7143
2030 | 2008 | 5 | 23 | 4 | 31854.5031
2030 | 2008 | 5 | 23 | 5 | 30747.1523
2030 | 2008 | 5 | 23 | 6 | 29337.039
2030 | 2008 | 5 | 23 | 7 | 27169.7399
2030 | 2008 | 5 | 23 | 8 | 24572.5308
2030 | 2008 | 5 | 23 | 9 | 24377.6794
2030 | 2008 | 5 | 23 | 10 | 26481.0398
2030 | 2008 | 5 | 23 | 11 | 24870.1657
2030 | 2008 | 5 | 23 | 12 | 22677.4951
2030 | 2008 | 5 | 23 | 13 | 21639.1003
2030 | 2008 | 5 | 23 | 14 | 22118.3578
2030 | 2008 | 5 | 23 | 15 | 22518.7224
2030 | 2008 | 5 | 23 | 16 | 24435.3163
2030 | 2008 | 5 | 23 | 17 | 27693.5363
2030 | 2008 | 5 | 23 | 18 | 28786.868
2030 | 2008 | 5 | 23 | 19 | 30000.6434
2030 | 2008 | 5 | 23 | 20 | 29171.0935
2030 | 2008 | 5 | 23 | 21 | 28875.706
2030 | 2008 | 5 | 23 | 22 | 26815.2726
2030 | 2008 | 5 | 23 | 23 | 26099.2313
2030 | 2008 | 5 | 23 | 24 | 27184.9347
2030 | 2008 | 5 | 24 | 1 | 26825.7376
2030 | 2008 | 5 | 24 | 2 | 26047.1066
2030 | 2008 | 5 | 24 | 3 | 24798.9963
2030 | 2008 | 5 | 24 | 4 | 21865.4679
2030 | 2008 | 5 | 24 | 5 | 19648.4572
2030 | 2008 | 5 | 24 | 6 | 18737.6516
2030 | 2008 | 5 | 24 | 7 | 16351.2257
2030 | 2008 | 5 | 24 | 8 | 11979.8532
2030 | 2008 | 5 | 24 | 9 | 10026.6815
2030 | 2008 | 5 | 24 | 10 | 9555.5822
2030 | 2008 | 5 | 24 | 11 | 7244.7229
2030 | 2008 | 5 | 24 | 12 | 6132.9581
2030 | 2008 | 5 | 24 | 13 | 6015.0809
2030 | 2008 | 5 | 24 | 14 | 6887.883
2030 | 2008 | 5 | 24 | 15 | 7808.4324
2030 | 2008 | 5 | 24 | 16 | 9916.328
2030 | 2008 | 5 | 24 | 17 | 12220.6152
2030 | 2008 | 5 | 24 | 18 | 15979.7391
2030 | 2008 | 5 | 24 | 19 | 17943.6157
2030 | 2008 | 5 | 24 | 20 | 19731.9525
2030 | 2008 | 5 | 24 | 21 | 22268.3556
2030 | 2008 | 5 | 24 | 22 | 26454.4193
2030 | 2008 | 5 | 24 | 23 | 29225.9698
2030 | 2008 | 5 | 24 | 24 | 29894.8299
2030 | 2008 | 5 | 25 | 1 | 29480.7587
2030 | 2008 | 5 | 25 | 2 | 29052.8466
2030 | 2008 | 5 | 25 | 3 | 28204.5882
2030 | 2008 | 5 | 25 | 4 | 26973.2541
2030 | 2008 | 5 | 25 | 5 | 25043.0822
2030 | 2008 | 5 | 25 | 6 | 23454.2759
2030 | 2008 | 5 | 25 | 7 | 22546.034
2030 | 2008 | 5 | 25 | 8 | 22671.2968
2030 | 2008 | 5 | 25 | 9 | 25105.2147
2030 | 2008 | 5 | 25 | 10 | 26407.8887
2030 | 2008 | 5 | 25 | 11 | 28013.6237
2030 | 2008 | 5 | 25 | 12 | 28691.8658
2030 | 2008 | 5 | 25 | 13 | 28361.3273
2030 | 2008 | 5 | 25 | 14 | 28634.837
2030 | 2008 | 5 | 25 | 15 | 27735.2455
2030 | 2008 | 5 | 25 | 16 | 27258.3741
2030 | 2008 | 5 | 25 | 17 | 28395.4525
2030 | 2008 | 5 | 25 | 18 | 29287.1641
2030 | 2008 | 5 | 25 | 19 | 30436.7502
2030 | 2008 | 5 | 25 | 20 | 29777.9292
2030 | 2008 | 5 | 25 | 21 | 29647.7543
2030 | 2008 | 5 | 25 | 22 | 29475.5986
2030 | 2008 | 5 | 25 | 23 | 29673.7964
2030 | 2008 | 5 | 25 | 24 | 30086.7991
2030 | 2008 | 5 | 26 | 1 | 30640.4521
2030 | 2008 | 5 | 26 | 2 | 31249.1926
2030 | 2008 | 5 | 26 | 3 | 31930.0553
2030 | 2008 | 5 | 26 | 4 | 30799.2456
2030 | 2008 | 5 | 26 | 5 | 30427.2923
2030 | 2008 | 5 | 26 | 6 | 30492.7648
2030 | 2008 | 5 | 26 | 7 | 29920.0801
2030 | 2008 | 5 | 26 | 8 | 31031.2868
2030 | 2008 | 5 | 26 | 9 | 33754.6622
2030 | 2008 | 5 | 26 | 10 | 34302.4899
2030 | 2008 | 5 | 26 | 11 | 34220.819
2030 | 2008 | 5 | 26 | 12 | 32805.9261
2030 | 2008 | 5 | 26 | 13 | 31592.2343
2030 | 2008 | 5 | 26 | 14 | 30820.5597
2030 | 2008 | 5 | 26 | 15 | 29614.1108
2030 | 2008 | 5 | 26 | 16 | 29338.333
2030 | 2008 | 5 | 26 | 17 | 30647.2266
2030 | 2008 | 5 | 26 | 18 | 31813.5664
2030 | 2008 | 5 | 26 | 19 | 32315.7586
2030 | 2008 | 5 | 26 | 20 | 32438.056
2030 | 2008 | 5 | 26 | 21 | 31924.0326
2030 | 2008 | 5 | 26 | 22 | 32431.4569
2030 | 2008 | 5 | 26 | 23 | 33146.4592
2030 | 2008 | 5 | 26 | 24 | 33470.7104
2030 | 2008 | 5 | 27 | 1 | 32578.4655
2030 | 2008 | 5 | 27 | 2 | 30999.6075
2030 | 2008 | 5 | 27 | 3 | 28748.4438
2030 | 2008 | 5 | 27 | 4 | 27496.6766
2030 | 2008 | 5 | 27 | 5 | 26607.3557
2030 | 2008 | 5 | 27 | 6 | 26185.333
2030 | 2008 | 5 | 27 | 7 | 26071.4667
2030 | 2008 | 5 | 27 | 8 | 26680.8939
2030 | 2008 | 5 | 27 | 9 | 28820.539
2030 | 2008 | 5 | 27 | 10 | 29695.4616
2030 | 2008 | 5 | 27 | 11 | 28699.6076
2030 | 2008 | 5 | 27 | 12 | 25921.6756
2030 | 2008 | 5 | 27 | 13 | 22759.5573
2030 | 2008 | 5 | 27 | 14 | 20949.1239
2030 | 2008 | 5 | 27 | 15 | 19206.761
2030 | 2008 | 5 | 27 | 16 | 18436.3255
2030 | 2008 | 5 | 27 | 17 | 18699.2745
2030 | 2008 | 5 | 27 | 18 | 20089.5208
2030 | 2008 | 5 | 27 | 19 | 20769.6285
2030 | 2008 | 5 | 27 | 20 | 20879.0442
2030 | 2008 | 5 | 27 | 21 | 22452.9998
2030 | 2008 | 5 | 27 | 22 | 21295.0113
2030 | 2008 | 5 | 27 | 23 | 20817.9745
2030 | 2008 | 5 | 27 | 24 | 20509.1692
2030 | 2008 | 5 | 28 | 1 | 18282.4939
2030 | 2008 | 5 | 28 | 2 | 17092.8375
2030 | 2008 | 5 | 28 | 3 | 15860.9193
2030 | 2008 | 5 | 28 | 4 | 13680.9449
2030 | 2008 | 5 | 28 | 5 | 12997.2227
2030 | 2008 | 5 | 28 | 6 | 10960.6749
2030 | 2008 | 5 | 28 | 7 | 9448.5611
2030 | 2008 | 5 | 28 | 8 | 7765.5396
2030 | 2008 | 5 | 28 | 9 | 7572.932
2030 | 2008 | 5 | 28 | 10 | 6639.6653
2030 | 2008 | 5 | 28 | 11 | 5655.3539
2030 | 2008 | 5 | 28 | 12 | 5533.7644
2030 | 2008 | 5 | 28 | 13 | 5303.0021
2030 | 2008 | 5 | 28 | 14 | 6732.9346
2030 | 2008 | 5 | 28 | 15 | 7424.8561
2030 | 2008 | 5 | 28 | 16 | 8458.063
2030 | 2008 | 5 | 28 | 17 | 9676.9228
2030 | 2008 | 5 | 28 | 18 | 10939.0023
2030 | 2008 | 5 | 28 | 19 | 11413.3191
2030 | 2008 | 5 | 28 | 20 | 12847.4807
2030 | 2008 | 5 | 28 | 21 | 15735.2269
2030 | 2008 | 5 | 28 | 22 | 18633.3113
2030 | 2008 | 5 | 28 | 23 | 21119.9196
2030 | 2008 | 5 | 28 | 24 | 21854.6179
2030 | 2008 | 5 | 29 | 1 | 22676.1072
2030 | 2008 | 5 | 29 | 2 | 22834.8878
2030 | 2008 | 5 | 29 | 3 | 21726.7015
2030 | 2008 | 5 | 29 | 4 | 20565.9209
2030 | 2008 | 5 | 29 | 5 | 20130.4348
2030 | 2008 | 5 | 29 | 6 | 19152.3315
2030 | 2008 | 5 | 29 | 7 | 19027.7658
2030 | 2008 | 5 | 29 | 8 | 17612.9446
2030 | 2008 | 5 | 29 | 9 | 17235.0133
2030 | 2008 | 5 | 29 | 10 | 21349.7872
2030 | 2008 | 5 | 29 | 11 | 21605.3741
2030 | 2008 | 5 | 29 | 12 | 21706.1774
2030 | 2008 | 5 | 29 | 13 | 22569.0006
2030 | 2008 | 5 | 29 | 14 | 23919.9179
2030 | 2008 | 5 | 29 | 15 | 24018.8122
2030 | 2008 | 5 | 29 | 16 | 24629.5488
2030 | 2008 | 5 | 29 | 17 | 25866.7456
2030 | 2008 | 5 | 29 | 18 | 27022.0439
2030 | 2008 | 5 | 29 | 19 | 26653.6961
2030 | 2008 | 5 | 29 | 20 | 26890.7169
2030 | 2008 | 5 | 29 | 21 | 27621.6826
2030 | 2008 | 5 | 29 | 22 | 29209.6326
2030 | 2008 | 5 | 29 | 23 | 30661.8088
2030 | 2008 | 5 | 29 | 24 | 31324.0937
2030 | 2008 | 5 | 30 | 1 | 31711.2371
2030 | 2008 | 5 | 30 | 2 | 31813.1843
2030 | 2008 | 5 | 30 | 3 | 31342.0271
2030 | 2008 | 5 | 30 | 4 | 30866.8218
2030 | 2008 | 5 | 30 | 5 | 29976.0509
2030 | 2008 | 5 | 30 | 6 | 29323.6601
2030 | 2008 | 5 | 30 | 7 | 28213.5137
2030 | 2008 | 5 | 30 | 8 | 27351.9497
2030 | 2008 | 5 | 30 | 9 | 27923.7219
2030 | 2008 | 5 | 30 | 10 | 28950.9629
2030 | 2008 | 5 | 30 | 11 | 25621.2522
2030 | 2008 | 5 | 30 | 12 | 22629.6373
2030 | 2008 | 5 | 30 | 13 | 21260.808
2030 | 2008 | 5 | 30 | 14 | 20843.1662
2030 | 2008 | 5 | 30 | 15 | 19877.8585
2030 | 2008 | 5 | 30 | 16 | 20799.4855
2030 | 2008 | 5 | 30 | 17 | 21995.2869
2030 | 2008 | 5 | 30 | 18 | 24091.9331
2030 | 2008 | 5 | 30 | 19 | 25491.7983
2030 | 2008 | 5 | 30 | 20 | 27137.1525
2030 | 2008 | 5 | 30 | 21 | 29119.7116
2030 | 2008 | 5 | 30 | 22 | 31404.5134
2030 | 2008 | 5 | 30 | 23 | 31770.9097
2030 | 2008 | 5 | 30 | 24 | 31851.3799
2030 | 2008 | 5 | 31 | 1 | 32062.7984
2030 | 2008 | 5 | 31 | 2 | 32039.926
2030 | 2008 | 5 | 31 | 3 | 31907.4252
2030 | 2008 | 5 | 31 | 4 | 31156.6155
2030 | 2008 | 5 | 31 | 5 | 29382.5651
2030 | 2008 | 5 | 31 | 6 | 27774.6341
2030 | 2008 | 5 | 31 | 7 | 25856.9737
2030 | 2008 | 5 | 31 | 8 | 23742.5202
2030 | 2008 | 5 | 31 | 9 | 22961.9952
2030 | 2008 | 5 | 31 | 10 | 23431.5243
2030 | 2008 | 5 | 31 | 11 | 21096.0213
2030 | 2008 | 5 | 31 | 12 | 20241.165
2030 | 2008 | 5 | 31 | 13 | 20400.544
2030 | 2008 | 5 | 31 | 14 | 21078.499
2030 | 2008 | 5 | 31 | 15 | 22228.7579
2030 | 2008 | 5 | 31 | 16 | 23437.4619
2030 | 2008 | 5 | 31 | 17 | 24951.197
2030 | 2008 | 5 | 31 | 18 | 26601.6542
2030 | 2008 | 5 | 31 | 19 | 28844.6104
2030 | 2008 | 5 | 31 | 20 | 30195.4628
2030 | 2008 | 5 | 31 | 21 | 30233.5136
2030 | 2008 | 5 | 31 | 22 | 31242.1158
2030 | 2008 | 5 | 31 | 23 | 31049.5306
2030 | 2008 | 5 | 31 | 24 | 31435.7172
2026 | 2008 | 10 | 1 | 1 | 5928.2856
2026 | 2008 | 10 | 1 | 2 | 5958.4081
2026 | 2008 | 10 | 1 | 3 | 5503.822
2026 | 2008 | 10 | 1 | 4 | 5837.2311
2026 | 2008 | 10 | 1 | 5 | 5909.4036
2026 | 2008 | 10 | 1 | 6 | 5186.7232
2026 | 2008 | 10 | 1 | 7 | 4570.5824
2026 | 2008 | 10 | 1 | 8 | 3954.1275
2026 | 2008 | 10 | 1 | 9 | 3280.2955
2026 | 2008 | 10 | 1 | 10 | 1579.5631
2026 | 2008 | 10 | 1 | 11 | 1662.6172
2026 | 2008 | 10 | 1 | 12 | 1469.3099
2026 | 2008 | 10 | 1 | 13 | 1463.7978
2026 | 2008 | 10 | 1 | 14 | 1390.091
2026 | 2008 | 10 | 1 | 15 | 1196.5643
2026 | 2008 | 10 | 1 | 16 | 1011.999
2026 | 2008 | 10 | 1 | 17 | 1004.4246
2026 | 2008 | 10 | 1 | 18 | 1563.0929
2026 | 2008 | 10 | 1 | 19 | 3750.122
2026 | 2008 | 10 | 1 | 20 | 4212.6558
2026 | 2008 | 10 | 1 | 21 | 5648.1358
2026 | 2008 | 10 | 1 | 22 | 7692.5839
2026 | 2008 | 10 | 1 | 23 | 8355.7663
2026 | 2008 | 10 | 1 | 24 | 8451.2627
2026 | 2008 | 10 | 2 | 1 | 8535.4836
2026 | 2008 | 10 | 2 | 2 | 9015.0712
2026 | 2008 | 10 | 2 | 3 | 9196.4232
2026 | 2008 | 10 | 2 | 4 | 9007.106
2026 | 2008 | 10 | 2 | 5 | 8651.6194
2026 | 2008 | 10 | 2 | 6 | 8005.8264
2026 | 2008 | 10 | 2 | 7 | 7880.9776
2026 | 2008 | 10 | 2 | 8 | 6725.32
2026 | 2008 | 10 | 2 | 9 | 5662.3619
2026 | 2008 | 10 | 2 | 10 | 3350.8792
2026 | 2008 | 10 | 2 | 11 | 4153.7853
2026 | 2008 | 10 | 2 | 12 | 3810.1858
2026 | 2008 | 10 | 2 | 13 | 3706.6983
2026 | 2008 | 10 | 2 | 14 | 3862.6951
2026 | 2008 | 10 | 2 | 15 | 4238.3853
2026 | 2008 | 10 | 2 | 16 | 4390.2723
2026 | 2008 | 10 | 2 | 17 | 4931.7549
2026 | 2008 | 10 | 2 | 18 | 6148.3318
2026 | 2008 | 10 | 2 | 19 | 8197.0723
2026 | 2008 | 10 | 2 | 20 | 11628.4271
2026 | 2008 | 10 | 2 | 21 | 16140.8293
2026 | 2008 | 10 | 2 | 22 | 19723.1782
2026 | 2008 | 10 | 2 | 23 | 22088.7815
2026 | 2008 | 10 | 2 | 24 | 23865.5603
2026 | 2008 | 10 | 3 | 1 | 24676.7058
2026 | 2008 | 10 | 3 | 2 | 24932.5028
2026 | 2008 | 10 | 3 | 3 | 25419.6585
2026 | 2008 | 10 | 3 | 4 | 25528.7531
2026 | 2008 | 10 | 3 | 5 | 24770.0157
2026 | 2008 | 10 | 3 | 6 | 24292.2314
2026 | 2008 | 10 | 3 | 7 | 23282.119
2026 | 2008 | 10 | 3 | 8 | 20971.5897
2026 | 2008 | 10 | 3 | 9 | 17564.4363
2026 | 2008 | 10 | 3 | 10 | 12704.6802
2026 | 2008 | 10 | 3 | 11 | 13816.6074
2026 | 2008 | 10 | 3 | 12 | 15100.7287
2026 | 2008 | 10 | 3 | 13 | 15791.0071
2026 | 2008 | 10 | 3 | 14 | 16965.1578
2026 | 2008 | 10 | 3 | 15 | 18474.778
2026 | 2008 | 10 | 3 | 16 | 18832.9744
2026 | 2008 | 10 | 3 | 17 | 20203.8242
2026 | 2008 | 10 | 3 | 18 | 20668.6468
2026 | 2008 | 10 | 3 | 19 | 22774.0389
2026 | 2008 | 10 | 3 | 20 | 27840.5487
2026 | 2008 | 10 | 3 | 21 | 30498.9096
2026 | 2008 | 10 | 3 | 22 | 30728.6942
2026 | 2008 | 10 | 3 | 23 | 30158.5979
2026 | 2008 | 10 | 3 | 24 | 30308.4945
2026 | 2008 | 10 | 4 | 1 | 30321.345
2026 | 2008 | 10 | 4 | 2 | 30489.1007
2026 | 2008 | 10 | 4 | 3 | 30611.484
2026 | 2008 | 10 | 4 | 4 | 30067.5661
2026 | 2008 | 10 | 4 | 5 | 29643.1578
2026 | 2008 | 10 | 4 | 6 | 28754.7536
2026 | 2008 | 10 | 4 | 7 | 28523.3926
2026 | 2008 | 10 | 4 | 8 | 26722.6524
2026 | 2008 | 10 | 4 | 9 | 23667.8178
2026 | 2008 | 10 | 4 | 10 | 24802.2926
2026 | 2008 | 10 | 4 | 11 | 27418.5011
2026 | 2008 | 10 | 4 | 12 | 28020.2992
2026 | 2008 | 10 | 4 | 13 | 28867.9528
2026 | 2008 | 10 | 4 | 14 | 29748.198
2026 | 2008 | 10 | 4 | 15 | 31016.9101
2026 | 2008 | 10 | 4 | 16 | 32142.7132
2026 | 2008 | 10 | 4 | 17 | 32615.5849
2026 | 2008 | 10 | 4 | 18 | 32925.5208
2026 | 2008 | 10 | 4 | 19 | 32202.5288
2026 | 2008 | 10 | 4 | 20 | 32505.7103
2026 | 2008 | 10 | 4 | 21 | 32427.7101
2026 | 2008 | 10 | 4 | 22 | 32279.9262
2026 | 2008 | 10 | 4 | 23 | 32161.1925
2026 | 2008 | 10 | 4 | 24 | 31809.8787
2026 | 2008 | 10 | 5 | 1 | 31606.9374
2026 | 2008 | 10 | 5 | 2 | 31380.2742
2026 | 2008 | 10 | 5 | 3 | 30956.7004
2026 | 2008 | 10 | 5 | 4 | 30691.5465
2026 | 2008 | 10 | 5 | 5 | 30170.0097
2026 | 2008 | 10 | 5 | 6 | 29757.447
2026 | 2008 | 10 | 5 | 7 | 28791.2188
2026 | 2008 | 10 | 5 | 8 | 26749.1158
2026 | 2008 | 10 | 5 | 9 | 23452.9608
2026 | 2008 | 10 | 5 | 10 | 27646.2324
2026 | 2008 | 10 | 5 | 11 | 30279.839
2026 | 2008 | 10 | 5 | 12 | 30569.5709
2026 | 2008 | 10 | 5 | 13 | 31160.7031
2026 | 2008 | 10 | 5 | 14 | 30303.0217
2026 | 2008 | 10 | 5 | 15 | 30679.577
2026 | 2008 | 10 | 5 | 16 | 30291.0934
2026 | 2008 | 10 | 5 | 17 | 30481.5734
2026 | 2008 | 10 | 5 | 18 | 30372.8769
2026 | 2008 | 10 | 5 | 19 | 29118.4762
2026 | 2008 | 10 | 5 | 20 | 29397.3485
2026 | 2008 | 10 | 5 | 21 | 29294.0382
2026 | 2008 | 10 | 5 | 22 | 28469.7347
2026 | 2008 | 10 | 5 | 23 | 27519.6232
2026 | 2008 | 10 | 5 | 24 | 26322.7007
2026 | 2008 | 10 | 6 | 1 | 26015.2172
2026 | 2008 | 10 | 6 | 2 | 26385.3903
2026 | 2008 | 10 | 6 | 3 | 25727.4738
2026 | 2008 | 10 | 6 | 4 | 25887.0498
2026 | 2008 | 10 | 6 | 5 | 25929.6351
2026 | 2008 | 10 | 6 | 6 | 24497.0797
2026 | 2008 | 10 | 6 | 7 | 23893.5094
2026 | 2008 | 10 | 6 | 8 | 22400.6459
2026 | 2008 | 10 | 6 | 9 | 19907.3231
2026 | 2008 | 10 | 6 | 10 | 23004.9931
2026 | 2008 | 10 | 6 | 11 | 24037.6742
2026 | 2008 | 10 | 6 | 12 | 23466.6302
2026 | 2008 | 10 | 6 | 13 | 22492.7708
2026 | 2008 | 10 | 6 | 14 | 20977.9092
2026 | 2008 | 10 | 6 | 15 | 19427.7089
2026 | 2008 | 10 | 6 | 16 | 17617.3498
2026 | 2008 | 10 | 6 | 17 | 14819.0426
2026 | 2008 | 10 | 6 | 18 | 11938.555
2026 | 2008 | 10 | 6 | 19 | 10601.1358
2026 | 2008 | 10 | 6 | 20 | 12527.1363
2026 | 2008 | 10 | 6 | 21 | 14987.944
2026 | 2008 | 10 | 6 | 22 | 16256.9625
2026 | 2008 | 10 | 6 | 23 | 14852.9484
2026 | 2008 | 10 | 6 | 24 | 14705.0542
2026 | 2008 | 10 | 7 | 1 | 14702.9226
2026 | 2008 | 10 | 7 | 2 | 15371.5822
2026 | 2008 | 10 | 7 | 3 | 15810.395
2026 | 2008 | 10 | 7 | 4 | 16609.0255
2026 | 2008 | 10 | 7 | 5 | 17325.9072
2026 | 2008 | 10 | 7 | 6 | 17610.2406
2026 | 2008 | 10 | 7 | 7 | 18394.6427
2026 | 2008 | 10 | 7 | 8 | 17873.1539
2026 | 2008 | 10 | 7 | 9 | 15888.047
2026 | 2008 | 10 | 7 | 10 | 14862.1384
2026 | 2008 | 10 | 7 | 11 | 17321.1921
2026 | 2008 | 10 | 7 | 12 | 16333.4009
2026 | 2008 | 10 | 7 | 13 | 15580.3314
2026 | 2008 | 10 | 7 | 14 | 15082.9026
2026 | 2008 | 10 | 7 | 15 | 15402.9571
2026 | 2008 | 10 | 7 | 16 | 13971.475
2026 | 2008 | 10 | 7 | 17 | 12548.2983
2026 | 2008 | 10 | 7 | 18 | 9792.6421
2026 | 2008 | 10 | 7 | 19 | 7264.3395
2026 | 2008 | 10 | 7 | 20 | 6136.1928
2026 | 2008 | 10 | 7 | 21 | 5646.6508
2026 | 2008 | 10 | 7 | 22 | 6056.1766
2026 | 2008 | 10 | 7 | 23 | 7006.7042
2026 | 2008 | 10 | 7 | 24 | 7849.1711
2026 | 2008 | 10 | 8 | 1 | 9656.6158
2026 | 2008 | 10 | 8 | 2 | 11672.7744
2026 | 2008 | 10 | 8 | 3 | 13996.6515
2026 | 2008 | 10 | 8 | 4 | 15458.2349
2026 | 2008 | 10 | 8 | 5 | 16394.9317
2026 | 2008 | 10 | 8 | 6 | 15597.1105
2026 | 2008 | 10 | 8 | 7 | 15950.799
2026 | 2008 | 10 | 8 | 8 | 14866.1519
2026 | 2008 | 10 | 8 | 9 | 12892.5756
2026 | 2008 | 10 | 8 | 10 | 8165.2389
2026 | 2008 | 10 | 8 | 11 | 7896.1144
2026 | 2008 | 10 | 8 | 12 | 7784.9077
2026 | 2008 | 10 | 8 | 13 | 6918.0267
2026 | 2008 | 10 | 8 | 14 | 5939.3739
2026 | 2008 | 10 | 8 | 15 | 5493.4322
2026 | 2008 | 10 | 8 | 16 | 5121.8851
2026 | 2008 | 10 | 8 | 17 | 4987.8431
2026 | 2008 | 10 | 8 | 18 | 5532.034
2026 | 2008 | 10 | 8 | 19 | 7445.7099
2026 | 2008 | 10 | 8 | 20 | 10751.3641
2026 | 2008 | 10 | 8 | 21 | 15338.9298
2026 | 2008 | 10 | 8 | 22 | 19091.7576
2026 | 2008 | 10 | 8 | 23 | 21344.1149
2026 | 2008 | 10 | 8 | 24 | 22832.1543
2026 | 2008 | 10 | 9 | 1 | 22376.1883
2026 | 2008 | 10 | 9 | 2 | 21787.174
2026 | 2008 | 10 | 9 | 3 | 21120.5172
2026 | 2008 | 10 | 9 | 4 | 20360.0862
2026 | 2008 | 10 | 9 | 5 | 19663.5041
2026 | 2008 | 10 | 9 | 6 | 19602.9686
2026 | 2008 | 10 | 9 | 7 | 19183.351
2026 | 2008 | 10 | 9 | 8 | 18452.0814
2026 | 2008 | 10 | 9 | 9 | 16034.5617
2026 | 2008 | 10 | 9 | 10 | 10195.6164
2026 | 2008 | 10 | 9 | 11 | 13388.3031
2026 | 2008 | 10 | 9 | 12 | 17099.8022
2026 | 2008 | 10 | 9 | 13 | 18381.4436
2026 | 2008 | 10 | 9 | 14 | 19309.1171
2026 | 2008 | 10 | 9 | 15 | 19843.466
2026 | 2008 | 10 | 9 | 16 | 20538.6521
2026 | 2008 | 10 | 9 | 17 | 20337.3581
2026 | 2008 | 10 | 9 | 18 | 20551.6179
2026 | 2008 | 10 | 9 | 19 | 22914.0445
2026 | 2008 | 10 | 9 | 20 | 26657.4919
2026 | 2008 | 10 | 9 | 21 | 29061.5034
2026 | 2008 | 10 | 9 | 22 | 29267.6762
2026 | 2008 | 10 | 9 | 23 | 29279.3571
2026 | 2008 | 10 | 9 | 24 | 29017.6991
2026 | 2008 | 10 | 10 | 1 | 28537.7192
2026 | 2008 | 10 | 10 | 2 | 28318.3316
2026 | 2008 | 10 | 10 | 3 | 28170.5404
2026 | 2008 | 10 | 10 | 4 | 27636.4046
2026 | 2008 | 10 | 10 | 5 | 27338.1903
2026 | 2008 | 10 | 10 | 6 | 27149.4161
2026 | 2008 | 10 | 10 | 7 | 26610.0501
2026 | 2008 | 10 | 10 | 8 | 24853.2551
2026 | 2008 | 10 | 10 | 9 | 21168.9584
2026 | 2008 | 10 | 10 | 10 | 18632.1677
2026 | 2008 | 10 | 10 | 11 | 20047.5602
2026 | 2008 | 10 | 10 | 12 | 19640.2462
2026 | 2008 | 10 | 10 | 13 | 19687.0113
2026 | 2008 | 10 | 10 | 14 | 20231.0203
2026 | 2008 | 10 | 10 | 15 | 20917.5234
2026 | 2008 | 10 | 10 | 16 | 21996.7468
2026 | 2008 | 10 | 10 | 17 | 22974.1272
2026 | 2008 | 10 | 10 | 18 | 24211.8219
2026 | 2008 | 10 | 10 | 19 | 26123.466
2026 | 2008 | 10 | 10 | 20 | 28946.8665
2026 | 2008 | 10 | 10 | 21 | 30604.126
2026 | 2008 | 10 | 10 | 22 | 30597.4755
2026 | 2008 | 10 | 10 | 23 | 29907.9629
2026 | 2008 | 10 | 10 | 24 | 29040.4425
2026 | 2008 | 10 | 11 | 1 | 28521.8547
2026 | 2008 | 10 | 11 | 2 | 27489.9474
2026 | 2008 | 10 | 11 | 3 | 26945.1391
2026 | 2008 | 10 | 11 | 4 | 25706.907
2026 | 2008 | 10 | 11 | 5 | 24504.4354
2026 | 2008 | 10 | 11 | 6 | 22813.6478
2026 | 2008 | 10 | 11 | 7 | 20862.1273
2026 | 2008 | 10 | 11 | 8 | 18722.0068
2026 | 2008 | 10 | 11 | 9 | 15469.8588
2026 | 2008 | 10 | 11 | 10 | 17164.4416
2026 | 2008 | 10 | 11 | 11 | 18519.175
2026 | 2008 | 10 | 11 | 12 | 19137.7879
2026 | 2008 | 10 | 11 | 13 | 20779.631
2026 | 2008 | 10 | 11 | 14 | 22398.3059
2026 | 2008 | 10 | 11 | 15 | 24919.9026
2026 | 2008 | 10 | 11 | 16 | 27162.9386
2026 | 2008 | 10 | 11 | 17 | 28264.6108
2026 | 2008 | 10 | 11 | 18 | 30084.096
2026 | 2008 | 10 | 11 | 19 | 30081.2266
2026 | 2008 | 10 | 11 | 20 | 31204.0753
2026 | 2008 | 10 | 11 | 21 | 31742.0635
2026 | 2008 | 10 | 11 | 22 | 31462.2407
2026 | 2008 | 10 | 11 | 23 | 31239.3628
2026 | 2008 | 10 | 11 | 24 | 30614.1757
2026 | 2008 | 10 | 12 | 1 | 30477.0127
2026 | 2008 | 10 | 12 | 2 | 30488.2486
2026 | 2008 | 10 | 12 | 3 | 30512.1113
2026 | 2008 | 10 | 12 | 4 | 30211.5134
2026 | 2008 | 10 | 12 | 5 | 29143.5562
2026 | 2008 | 10 | 12 | 6 | 28784.3956
2026 | 2008 | 10 | 12 | 7 | 28034.5627
2026 | 2008 | 10 | 12 | 8 | 26501.6768
2026 | 2008 | 10 | 12 | 9 | 23877.9673
2026 | 2008 | 10 | 12 | 10 | 28468.3714
2026 | 2008 | 10 | 12 | 11 | 29884.9402
2026 | 2008 | 10 | 12 | 12 | 30212.8707
2026 | 2008 | 10 | 12 | 13 | 31211.4379
2026 | 2008 | 10 | 12 | 14 | 31491.1547
2026 | 2008 | 10 | 12 | 15 | 31646.0223
2026 | 2008 | 10 | 12 | 16 | 31753.9699
2026 | 2008 | 10 | 12 | 17 | 30454.942
2026 | 2008 | 10 | 12 | 18 | 29304.85
2026 | 2008 | 10 | 12 | 19 | 28056.1802
2026 | 2008 | 10 | 12 | 20 | 29367.21
2026 | 2008 | 10 | 12 | 21 | 30307.1282
2026 | 2008 | 10 | 12 | 22 | 30443.6573
2026 | 2008 | 10 | 12 | 23 | 29745.6167
2026 | 2008 | 10 | 12 | 24 | 29334.2007
2026 | 2008 | 10 | 13 | 1 | 27210.076
2026 | 2008 | 10 | 13 | 2 | 25359.4713
2026 | 2008 | 10 | 13 | 3 | 23380.787
2026 | 2008 | 10 | 13 | 4 | 21403.8654
2026 | 2008 | 10 | 13 | 5 | 19670.4737
2026 | 2008 | 10 | 13 | 6 | 18898.6548
2026 | 2008 | 10 | 13 | 7 | 18343.8348
2026 | 2008 | 10 | 13 | 8 | 17869.6289
2026 | 2008 | 10 | 13 | 9 | 16282.1571
2026 | 2008 | 10 | 13 | 10 | 19718.3445
2026 | 2008 | 10 | 13 | 11 | 20489.5385
2026 | 2008 | 10 | 13 | 12 | 19295.9077
2026 | 2008 | 10 | 13 | 13 | 18346.0426
2026 | 2008 | 10 | 13 | 14 | 17599.4993
2026 | 2008 | 10 | 13 | 15 | 17047.216
2026 | 2008 | 10 | 13 | 16 | 16829.8551
2026 | 2008 | 10 | 13 | 17 | 17498.3035
2026 | 2008 | 10 | 13 | 18 | 18993.2663
2026 | 2008 | 10 | 13 | 19 | 19598.8566
2026 | 2008 | 10 | 13 | 20 | 20282.198
2026 | 2008 | 10 | 13 | 21 | 20860.2045
2026 | 2008 | 10 | 13 | 22 | 20432.6554
2026 | 2008 | 10 | 13 | 23 | 18768.7663
2026 | 2008 | 10 | 13 | 24 | 17064.0933
2026 | 2008 | 10 | 14 | 1 | 14693.8257
2026 | 2008 | 10 | 14 | 2 | 13462.719
2026 | 2008 | 10 | 14 | 3 | 12475.5311
2026 | 2008 | 10 | 14 | 4 | 10874.2399
2026 | 2008 | 10 | 14 | 5 | 9075.0611
2026 | 2008 | 10 | 14 | 6 | 7225.3132
2026 | 2008 | 10 | 14 | 7 | 6366.4742
2026 | 2008 | 10 | 14 | 8 | 5768.2985
2026 | 2008 | 10 | 14 | 9 | 4666.8698
2026 | 2008 | 10 | 14 | 10 | 5624.8664
2026 | 2008 | 10 | 14 | 11 | 6054.7112
2026 | 2008 | 10 | 14 | 12 | 6271.8592
2026 | 2008 | 10 | 14 | 13 | 6829.0084
2026 | 2008 | 10 | 14 | 14 | 7833.7791
2026 | 2008 | 10 | 14 | 15 | 8834.7816
2026 | 2008 | 10 | 14 | 16 | 9088.6599
2026 | 2008 | 10 | 14 | 17 | 8889.0544
2026 | 2008 | 10 | 14 | 18 | 8612.0923
2026 | 2008 | 10 | 14 | 19 | 8627.4869
2026 | 2008 | 10 | 14 | 20 | 8447.1626
2026 | 2008 | 10 | 14 | 21 | 9150.0631
2026 | 2008 | 10 | 14 | 22 | 8520.568
2026 | 2008 | 10 | 14 | 23 | 7413.5714
2026 | 2008 | 10 | 14 | 24 | 6523.8833
2026 | 2008 | 10 | 15 | 1 | 6333.5742
2026 | 2008 | 10 | 15 | 2 | 7078.9029
2026 | 2008 | 10 | 15 | 3 | 7469.0918
2026 | 2008 | 10 | 15 | 4 | 8451.6121
2026 | 2008 | 10 | 15 | 5 | 9198.1759
2026 | 2008 | 10 | 15 | 6 | 9631.9307
2026 | 2008 | 10 | 15 | 7 | 10364.0085
2026 | 2008 | 10 | 15 | 8 | 10151.8887
2026 | 2008 | 10 | 15 | 9 | 8867.3858
2026 | 2008 | 10 | 15 | 10 | 10713.405
2026 | 2008 | 10 | 15 | 11 | 10980.7809
2026 | 2008 | 10 | 15 | 12 | 9756.2572
2026 | 2008 | 10 | 15 | 13 | 8836.9497
2026 | 2008 | 10 | 15 | 14 | 9068.257
2026 | 2008 | 10 | 15 | 15 | 9977.2043
2026 | 2008 | 10 | 15 | 16 | 10888.1606
2026 | 2008 | 10 | 15 | 17 | 11726.4486
2026 | 2008 | 10 | 15 | 18 | 11509.3757
2026 | 2008 | 10 | 15 | 19 | 11871.9484
2026 | 2008 | 10 | 15 | 20 | 13112.6701
2026 | 2008 | 10 | 15 | 21 | 14406.5235
2026 | 2008 | 10 | 15 | 22 | 13825.2177
2026 | 2008 | 10 | 15 | 23 | 12303.5286
2026 | 2008 | 10 | 15 | 24 | 12286.1848
2026 | 2008 | 10 | 16 | 1 | 11986.1723
2026 | 2008 | 10 | 16 | 2 | 12516.2127
2026 | 2008 | 10 | 16 | 3 | 13303.2303
2026 | 2008 | 10 | 16 | 4 | 14510.5106
2026 | 2008 | 10 | 16 | 5 | 14366.1067
2026 | 2008 | 10 | 16 | 6 | 14725.6864
2026 | 2008 | 10 | 16 | 7 | 15000.7388
2026 | 2008 | 10 | 16 | 8 | 15138.3185
2026 | 2008 | 10 | 16 | 9 | 13881.6331
2026 | 2008 | 10 | 16 | 10 | 17394.1478
2026 | 2008 | 10 | 16 | 11 | 17534.6655
2026 | 2008 | 10 | 16 | 12 | 15964.0818
2026 | 2008 | 10 | 16 | 13 | 14035.399
2026 | 2008 | 10 | 16 | 14 | 12440.9793
2026 | 2008 | 10 | 16 | 15 | 11292.3221
2026 | 2008 | 10 | 16 | 16 | 9853.9507
2026 | 2008 | 10 | 16 | 17 | 8133.9871
2026 | 2008 | 10 | 16 | 18 | 6695.134
2026 | 2008 | 10 | 16 | 19 | 5507.9725
2026 | 2008 | 10 | 16 | 20 | 5247.7706
2026 | 2008 | 10 | 16 | 21 | 5217.6724
2026 | 2008 | 10 | 16 | 22 | 5326.9932
2026 | 2008 | 10 | 16 | 23 | 5168.4398
2026 | 2008 | 10 | 16 | 24 | 5084.0445
2026 | 2008 | 10 | 17 | 1 | 5065.4636
2026 | 2008 | 10 | 17 | 2 | 5112.5832
2026 | 2008 | 10 | 17 | 3 | 5372.4461
2026 | 2008 | 10 | 17 | 4 | 6039.3315
2026 | 2008 | 10 | 17 | 5 | 6691.7547
2026 | 2008 | 10 | 17 | 6 | 6809.1407
2026 | 2008 | 10 | 17 | 7 | 6626.0825
2026 | 2008 | 10 | 17 | 8 | 5542.7179
2026 | 2008 | 10 | 17 | 9 | 5233.3544
2026 | 2008 | 10 | 17 | 10 | 5239.1259
2026 | 2008 | 10 | 17 | 11 | 4971.9642
2026 | 2008 | 10 | 17 | 12 | 4987.4251
2026 | 2008 | 10 | 17 | 13 | 4678.3167
2026 | 2008 | 10 | 17 | 14 | 4594.8444
2026 | 2008 | 10 | 17 | 15 | 4308.2524
2026 | 2008 | 10 | 17 | 16 | 3804.8709
2026 | 2008 | 10 | 17 | 17 | 3322.9807
2026 | 2008 | 10 | 17 | 18 | 3078.4033
2026 | 2008 | 10 | 17 | 19 | 3004.8148
2026 | 2008 | 10 | 17 | 20 | 2725.878
2026 | 2008 | 10 | 17 | 21 | 2544.8327
2026 | 2008 | 10 | 17 | 22 | 2563.4848
2026 | 2008 | 10 | 17 | 23 | 2660.7448
2026 | 2008 | 10 | 17 | 24 | 3130.5269
2026 | 2008 | 10 | 18 | 1 | 3310.0736
2026 | 2008 | 10 | 18 | 2 | 3704.9181
2026 | 2008 | 10 | 18 | 3 | 3952.8589
2026 | 2008 | 10 | 18 | 4 | 4369.107
2026 | 2008 | 10 | 18 | 5 | 4725.4793
2026 | 2008 | 10 | 18 | 6 | 5283.0242
2026 | 2008 | 10 | 18 | 7 | 5880.7433
2026 | 2008 | 10 | 18 | 8 | 5004.3525
2026 | 2008 | 10 | 18 | 9 | 4054.2539
2026 | 2008 | 10 | 18 | 10 | 4197.6596
2026 | 2008 | 10 | 18 | 11 | 4330.3805
2026 | 2008 | 10 | 18 | 12 | 5093.4739
2026 | 2008 | 10 | 18 | 13 | 5619.8835
2026 | 2008 | 10 | 18 | 14 | 6320.1083
2026 | 2008 | 10 | 18 | 15 | 6953.7975
2026 | 2008 | 10 | 18 | 16 | 7145.8052
2026 | 2008 | 10 | 18 | 17 | 7055.2485
2026 | 2008 | 10 | 18 | 18 | 6996.4282
2026 | 2008 | 10 | 18 | 19 | 7488.7811
2026 | 2008 | 10 | 18 | 20 | 9067.9538
2026 | 2008 | 10 | 18 | 21 | 10616.4057
2026 | 2008 | 10 | 18 | 22 | 12295.0522
2026 | 2008 | 10 | 18 | 23 | 13763.6902
2026 | 2008 | 10 | 18 | 24 | 15721.5022
2026 | 2008 | 10 | 19 | 1 | 17592.8143
2026 | 2008 | 10 | 19 | 2 | 18606.5295
2026 | 2008 | 10 | 19 | 3 | 19241.6852
2026 | 2008 | 10 | 19 | 4 | 19024.2141
2026 | 2008 | 10 | 19 | 5 | 18665.2062
2026 | 2008 | 10 | 19 | 6 | 18516.5016
2026 | 2008 | 10 | 19 | 7 | 17683.9321
2026 | 2008 | 10 | 19 | 8 | 17252.9689
2026 | 2008 | 10 | 19 | 9 | 15317.2993
2026 | 2008 | 10 | 19 | 10 | 9619.4732
2026 | 2008 | 10 | 19 | 11 | 12380.5666
2026 | 2008 | 10 | 19 | 12 | 13491.5663
2026 | 2008 | 10 | 19 | 13 | 12683.4905
2026 | 2008 | 10 | 19 | 14 | 12049.4334
2026 | 2008 | 10 | 19 | 15 | 12130.2811
2026 | 2008 | 10 | 19 | 16 | 12139.5674
2026 | 2008 | 10 | 19 | 17 | 12066.0334
2026 | 2008 | 10 | 19 | 18 | 11928.8794
2026 | 2008 | 10 | 19 | 19 | 14688.5924
2026 | 2008 | 10 | 19 | 20 | 19073.7113
2026 | 2008 | 10 | 19 | 21 | 23065.5872
2026 | 2008 | 10 | 19 | 22 | 25103.0836
2026 | 2008 | 10 | 19 | 23 | 25180.7416
2026 | 2008 | 10 | 19 | 24 | 25112.8499
2026 | 2008 | 10 | 20 | 1 | 24865.7642
2026 | 2008 | 10 | 20 | 2 | 24239.9053
2026 | 2008 | 10 | 20 | 3 | 22831.9299
2026 | 2008 | 10 | 20 | 4 | 21600.5376
2026 | 2008 | 10 | 20 | 5 | 19388.5416
2026 | 2008 | 10 | 20 | 6 | 17753.6976
2026 | 2008 | 10 | 20 | 7 | 16368.7765
2026 | 2008 | 10 | 20 | 8 | 14372.507
2026 | 2008 | 10 | 20 | 9 | 11229.4534
2026 | 2008 | 10 | 20 | 10 | 6449.2754
2026 | 2008 | 10 | 20 | 11 | 5727.9037
2026 | 2008 | 10 | 20 | 12 | 4644.336
2026 | 2008 | 10 | 20 | 13 | 3784.552
2026 | 2008 | 10 | 20 | 14 | 3444.3038
2026 | 2008 | 10 | 20 | 15 | 3466.7529
2026 | 2008 | 10 | 20 | 16 | 3657.3448
2026 | 2008 | 10 | 20 | 17 | 3885.2671
2026 | 2008 | 10 | 20 | 18 | 5151.2904
2026 | 2008 | 10 | 20 | 19 | 7872.6564
2026 | 2008 | 10 | 20 | 20 | 10491.3247
2026 | 2008 | 10 | 20 | 21 | 13851.6042
2026 | 2008 | 10 | 20 | 22 | 15115.0642
2026 | 2008 | 10 | 20 | 23 | 15585.4979
2026 | 2008 | 10 | 20 | 24 | 14774.4366
2026 | 2008 | 10 | 21 | 1 | 13703.9785
2026 | 2008 | 10 | 21 | 2 | 13009.2296
2026 | 2008 | 10 | 21 | 3 | 12341.3155
2026 | 2008 | 10 | 21 | 4 | 10948.2558
2026 | 2008 | 10 | 21 | 5 | 9229.1385
2026 | 2008 | 10 | 21 | 6 | 7834.1314
2026 | 2008 | 10 | 21 | 7 | 5512.2729
2026 | 2008 | 10 | 21 | 8 | 5754.5717
2026 | 2008 | 10 | 21 | 9 | 4830.3436
2026 | 2008 | 10 | 21 | 10 | 4443.3153
2026 | 2008 | 10 | 21 | 11 | 5447.7559
2026 | 2008 | 10 | 21 | 12 | 7192.6308
2026 | 2008 | 10 | 21 | 13 | 10107.1054
2026 | 2008 | 10 | 21 | 14 | 12301.2484
2026 | 2008 | 10 | 21 | 15 | 14295.9455
2026 | 2008 | 10 | 21 | 16 | 16274.6382
2026 | 2008 | 10 | 21 | 17 | 17100.5094
2026 | 2008 | 10 | 21 | 18 | 17673.7377
2026 | 2008 | 10 | 21 | 19 | 20544.794
2026 | 2008 | 10 | 21 | 20 | 24679.5894
2026 | 2008 | 10 | 21 | 21 | 27073.4227
2026 | 2008 | 10 | 21 | 22 | 28000.836
2026 | 2008 | 10 | 21 | 23 | 28076.71
2026 | 2008 | 10 | 21 | 24 | 29068.974
2026 | 2008 | 10 | 22 | 1 | 28872.8426
2026 | 2008 | 10 | 22 | 2 | 27586.8319
2026 | 2008 | 10 | 22 | 3 | 27948.2185
2026 | 2008 | 10 | 22 | 4 | 26861.1276
2026 | 2008 | 10 | 22 | 5 | 25223.161
2026 | 2008 | 10 | 22 | 6 | 23550.4631
2026 | 2008 | 10 | 22 | 7 | 21291.2527
2026 | 2008 | 10 | 22 | 8 | 20024.0881
2026 | 2008 | 10 | 22 | 9 | 17561.2348
2026 | 2008 | 10 | 22 | 10 | 19970.2441
2026 | 2008 | 10 | 22 | 11 | 22493.0783
2026 | 2008 | 10 | 22 | 12 | 23337.0087
2026 | 2008 | 10 | 22 | 13 | 24663.1663
2026 | 2008 | 10 | 22 | 14 | 25230.087
2026 | 2008 | 10 | 22 | 15 | 24718.6306
2026 | 2008 | 10 | 22 | 16 | 24990.5227
2026 | 2008 | 10 | 22 | 17 | 25316.3318
2026 | 2008 | 10 | 22 | 18 | 24789.9636
2026 | 2008 | 10 | 22 | 19 | 22423.5278
2026 | 2008 | 10 | 22 | 20 | 21744.7132
2026 | 2008 | 10 | 22 | 21 | 20135.074
2026 | 2008 | 10 | 22 | 22 | 17856.9839
2026 | 2008 | 10 | 22 | 23 | 15700.3117
2026 | 2008 | 10 | 22 | 24 | 13785.9573
2026 | 2008 | 10 | 23 | 1 | 12410.738
2026 | 2008 | 10 | 23 | 2 | 13698.839
2026 | 2008 | 10 | 23 | 3 | 14719.0149
2026 | 2008 | 10 | 23 | 4 | 15306.413
2026 | 2008 | 10 | 23 | 5 | 15813.2859
2026 | 2008 | 10 | 23 | 6 | 16743.2635
2026 | 2008 | 10 | 23 | 7 | 17022.1207
2026 | 2008 | 10 | 23 | 8 | 17167.8663
2026 | 2008 | 10 | 23 | 9 | 16008.1306
2026 | 2008 | 10 | 23 | 10 | 15119.8227
2026 | 2008 | 10 | 23 | 11 | 14390.2637
2026 | 2008 | 10 | 23 | 12 | 15441.163
2026 | 2008 | 10 | 23 | 13 | 14947.8249
2026 | 2008 | 10 | 23 | 14 | 15840.2937
2026 | 2008 | 10 | 23 | 15 | 16453.892
2026 | 2008 | 10 | 23 | 16 | 15718.6338
2026 | 2008 | 10 | 23 | 17 | 14235.1347
2026 | 2008 | 10 | 23 | 18 | 10431.344
2026 | 2008 | 10 | 23 | 19 | 6887.6975
2026 | 2008 | 10 | 23 | 20 | 6160.4826
2026 | 2008 | 10 | 23 | 21 | 5435.1816
2026 | 2008 | 10 | 23 | 22 | 7726.1879
2026 | 2008 | 10 | 23 | 23 | 8684.8398
2026 | 2008 | 10 | 23 | 24 | 9032.6862
2026 | 2008 | 10 | 24 | 1 | 10561.0427
2026 | 2008 | 10 | 24 | 2 | 10681.5329
2026 | 2008 | 10 | 24 | 3 | 9496.2922
2026 | 2008 | 10 | 24 | 4 | 8974.0985
2026 | 2008 | 10 | 24 | 5 | 8289.3715
2026 | 2008 | 10 | 24 | 6 | 7570.1829
2026 | 2008 | 10 | 24 | 7 | 7151.1709
2026 | 2008 | 10 | 24 | 8 | 6390.2733
2026 | 2008 | 10 | 24 | 9 | 5432.4565
2026 | 2008 | 10 | 24 | 10 | 3288.658
2026 | 2008 | 10 | 24 | 11 | 2721.7022
2026 | 2008 | 10 | 24 | 12 | 2693.0718
2026 | 2008 | 10 | 24 | 13 | 2341.7704
2026 | 2008 | 10 | 24 | 14 | 2415.9913
2026 | 2008 | 10 | 24 | 15 | 2083.7117
2026 | 2008 | 10 | 24 | 16 | 1639.2364
2026 | 2008 | 10 | 24 | 17 | 1196.9025
2026 | 2008 | 10 | 24 | 18 | 1412.7785
2026 | 2008 | 10 | 24 | 19 | 2257.8358
2026 | 2008 | 10 | 24 | 20 | 3279.0502
2026 | 2008 | 10 | 24 | 21 | 5067.8116
2026 | 2008 | 10 | 24 | 22 | 7470.9975
2026 | 2008 | 10 | 24 | 23 | 8439.4235
2026 | 2008 | 10 | 24 | 24 | 8872.4205
2026 | 2008 | 10 | 25 | 1 | 8753.3921
2026 | 2008 | 10 | 25 | 2 | 8423.8415
2026 | 2008 | 10 | 25 | 3 | 7402.9969
2026 | 2008 | 10 | 25 | 4 | 6426.8958
2026 | 2008 | 10 | 25 | 5 | 5469.0769
2026 | 2008 | 10 | 25 | 6 | 4671.4167
2026 | 2008 | 10 | 25 | 7 | 4265.6067
2026 | 2008 | 10 | 25 | 8 | 4152.2202
2026 | 2008 | 10 | 25 | 9 | 3888.666
2026 | 2008 | 10 | 25 | 10 | 3551.5817
2026 | 2008 | 10 | 25 | 11 | 2858.8651
2026 | 2008 | 10 | 25 | 12 | 3646.6026
2026 | 2008 | 10 | 25 | 13 | 3872.2429
2026 | 2008 | 10 | 25 | 14 | 4532.9738
2026 | 2008 | 10 | 25 | 15 | 5465.2698
2026 | 2008 | 10 | 25 | 16 | 6339.3062
2026 | 2008 | 10 | 25 | 17 | 6330.1802
2026 | 2008 | 10 | 25 | 18 | 6436.8509
2026 | 2008 | 10 | 25 | 19 | 7612.7548
2026 | 2008 | 10 | 25 | 20 | 11252.7609
2026 | 2008 | 10 | 25 | 21 | 15979.9409
2026 | 2008 | 10 | 25 | 22 | 20506.6979
2026 | 2008 | 10 | 25 | 23 | 23046.0521
2026 | 2008 | 10 | 25 | 24 | 24948.5165
2026 | 2008 | 10 | 26 | 1 | 25549.4072
2026 | 2008 | 10 | 26 | 2 | 25599.2257
2026 | 2008 | 10 | 26 | 3 | 25431.8255
2026 | 2008 | 10 | 26 | 4 | 24133.2015
2026 | 2008 | 10 | 26 | 5 | 23799.6835
2026 | 2008 | 10 | 26 | 6 | 23782.3351
2026 | 2008 | 10 | 26 | 7 | 22212.9211
2026 | 2008 | 10 | 26 | 8 | 19875.4221
2026 | 2008 | 10 | 26 | 9 | 16204.1417
2026 | 2008 | 10 | 26 | 10 | 12359.6757
2026 | 2008 | 10 | 26 | 11 | 10967.503
2026 | 2008 | 10 | 26 | 12 | 9342.6379
2026 | 2008 | 10 | 26 | 13 | 8610.3716
2026 | 2008 | 10 | 26 | 14 | 9307.6477
2026 | 2008 | 10 | 26 | 15 | 12104.0719
2026 | 2008 | 10 | 26 | 16 | 15507.3334
2026 | 2008 | 10 | 26 | 17 | 18834.306
2026 | 2008 | 10 | 26 | 18 | 22302.0733
2026 | 2008 | 10 | 26 | 19 | 24530.052
2026 | 2008 | 10 | 26 | 20 | 27037.2522
2026 | 2008 | 10 | 26 | 21 | 28942.2476
2026 | 2008 | 10 | 26 | 22 | 29231.9143
2026 | 2008 | 10 | 26 | 23 | 28340.2165
2026 | 2008 | 10 | 26 | 24 | 27197.2255
2026 | 2008 | 10 | 27 | 1 | 25716.701
2026 | 2008 | 10 | 27 | 2 | 24049.9032
2026 | 2008 | 10 | 27 | 3 | 22602.0571
2026 | 2008 | 10 | 27 | 4 | 21565.7185
2026 | 2008 | 10 | 27 | 5 | 20686.9092
2026 | 2008 | 10 | 27 | 6 | 20509.8826
2026 | 2008 | 10 | 27 | 7 | 19934.2391
2026 | 2008 | 10 | 27 | 8 | 18747.3359
2026 | 2008 | 10 | 27 | 9 | 15942.9125
2026 | 2008 | 10 | 27 | 10 | 14298.8053
2026 | 2008 | 10 | 27 | 11 | 15430.6954
2026 | 2008 | 10 | 27 | 12 | 13385.836
2026 | 2008 | 10 | 27 | 13 | 12720.9092
2026 | 2008 | 10 | 27 | 14 | 11589.4591
2026 | 2008 | 10 | 27 | 15 | 10827.8635
2026 | 2008 | 10 | 27 | 16 | 9993.2734
2026 | 2008 | 10 | 27 | 17 | 8770.5336
2026 | 2008 | 10 | 27 | 18 | 7387.8594
2026 | 2008 | 10 | 27 | 19 | 6503.8219
2026 | 2008 | 10 | 27 | 20 | 7003.5703
2026 | 2008 | 10 | 27 | 21 | 7815.5172
2026 | 2008 | 10 | 27 | 22 | 8707.2851
2026 | 2008 | 10 | 27 | 23 | 9679.9945
2026 | 2008 | 10 | 27 | 24 | 10901.7353
2026 | 2008 | 10 | 28 | 1 | 11051.9041
2026 | 2008 | 10 | 28 | 2 | 11543.1578
2026 | 2008 | 10 | 28 | 3 | 11973.5626
2026 | 2008 | 10 | 28 | 4 | 12272.8684
2026 | 2008 | 10 | 28 | 5 | 13170.9652
2026 | 2008 | 10 | 28 | 6 | 14189.0672
2026 | 2008 | 10 | 28 | 7 | 15351.1291
2026 | 2008 | 10 | 28 | 8 | 15605.4013
2026 | 2008 | 10 | 28 | 9 | 14474.9947
2026 | 2008 | 10 | 28 | 10 | 8710.2867
2026 | 2008 | 10 | 28 | 11 | 9333.6413
2026 | 2008 | 10 | 28 | 12 | 10181.9378
2026 | 2008 | 10 | 28 | 13 | 9602.7005
2026 | 2008 | 10 | 28 | 14 | 9349.9722
2026 | 2008 | 10 | 28 | 15 | 9439.6227
2026 | 2008 | 10 | 28 | 16 | 9664.0922
2026 | 2008 | 10 | 28 | 17 | 9909.8725
2026 | 2008 | 10 | 28 | 18 | 10810.2476
2026 | 2008 | 10 | 28 | 19 | 14056.6478
2026 | 2008 | 10 | 28 | 20 | 18349.9744
2026 | 2008 | 10 | 28 | 21 | 22278.6547
2026 | 2008 | 10 | 28 | 22 | 23653.4863
2026 | 2008 | 10 | 28 | 23 | 23871.157
2026 | 2008 | 10 | 28 | 24 | 24079.3833
2026 | 2008 | 10 | 29 | 1 | 24069.0024
2026 | 2008 | 10 | 29 | 2 | 23545.6311
2026 | 2008 | 10 | 29 | 3 | 22918.3098
2026 | 2008 | 10 | 29 | 4 | 21951.5228
2026 | 2008 | 10 | 29 | 5 | 21026.8467
2026 | 2008 | 10 | 29 | 6 | 19734.6203
2026 | 2008 | 10 | 29 | 7 | 18458.1449
2026 | 2008 | 10 | 29 | 8 | 16869.5123
2026 | 2008 | 10 | 29 | 9 | 14077.1197
2026 | 2008 | 10 | 29 | 10 | 8859.1961
2026 | 2008 | 10 | 29 | 11 | 8855.9059
2026 | 2008 | 10 | 29 | 12 | 8348.5034
2026 | 2008 | 10 | 29 | 13 | 7591.8702
2026 | 2008 | 10 | 29 | 14 | 7287.6284
2026 | 2008 | 10 | 29 | 15 | 7395.7066
2026 | 2008 | 10 | 29 | 16 | 7775.6784
2026 | 2008 | 10 | 29 | 17 | 8181.2678
2026 | 2008 | 10 | 29 | 18 | 9352.5241
2026 | 2008 | 10 | 29 | 19 | 12010.4601
2026 | 2008 | 10 | 29 | 20 | 16473.7403
2026 | 2008 | 10 | 29 | 21 | 21796.0104
2026 | 2008 | 10 | 29 | 22 | 25214.3552
2026 | 2008 | 10 | 29 | 23 | 26578.3179
2026 | 2008 | 10 | 29 | 24 | 27004.3926
2026 | 2008 | 10 | 30 | 1 | 27189.3722
2026 | 2008 | 10 | 30 | 2 | 26868.8191
2026 | 2008 | 10 | 30 | 3 | 26679.091
2026 | 2008 | 10 | 30 | 4 | 26192.7902
2026 | 2008 | 10 | 30 | 5 | 26036.9618
2026 | 2008 | 10 | 30 | 6 | 23018.1389
2026 | 2008 | 10 | 30 | 7 | 22837.5483
2026 | 2008 | 10 | 30 | 8 | 21985.4032
2026 | 2008 | 10 | 30 | 9 | 19775.4648
2026 | 2008 | 10 | 30 | 10 | 17720.753
2026 | 2008 | 10 | 30 | 11 | 17114.3532
2026 | 2008 | 10 | 30 | 12 | 17408.3055
2026 | 2008 | 10 | 30 | 13 | 16959.4169
2026 | 2008 | 10 | 30 | 14 | 17643.4379
2026 | 2008 | 10 | 30 | 15 | 17992.587
2026 | 2008 | 10 | 30 | 16 | 17805.6125
2026 | 2008 | 10 | 30 | 17 | 17476.6171
2026 | 2008 | 10 | 30 | 18 | 17638.2527
2026 | 2008 | 10 | 30 | 19 | 20351.4075
2026 | 2008 | 10 | 30 | 20 | 23014.5433
2026 | 2008 | 10 | 30 | 21 | 24532.2171
2026 | 2008 | 10 | 30 | 22 | 24319.3066
2026 | 2008 | 10 | 30 | 23 | 24192.4562
2026 | 2008 | 10 | 30 | 24 | 26746.6566
2026 | 2008 | 10 | 31 | 1 | 25596.7394
2026 | 2008 | 10 | 31 | 2 | 24525.3291
2026 | 2008 | 10 | 31 | 3 | 23521.4489
2026 | 2008 | 10 | 31 | 4 | 22278.4731
2026 | 2008 | 10 | 31 | 5 | 20067.7519
2026 | 2008 | 10 | 31 | 6 | 18505.6961
2026 | 2008 | 10 | 31 | 7 | 16350.9671
2026 | 2008 | 10 | 31 | 8 | 14736.1154
2026 | 2008 | 10 | 31 | 9 | 12117.6195
2026 | 2008 | 10 | 31 | 10 | 11929.7551
2026 | 2008 | 10 | 31 | 11 | 11176.6083
2026 | 2008 | 10 | 31 | 12 | 9919.4259
2026 | 2008 | 10 | 31 | 13 | 9083.7153
2026 | 2008 | 10 | 31 | 14 | 7816.7655
2026 | 2008 | 10 | 31 | 15 | 6741.297
2026 | 2008 | 10 | 31 | 16 | 5305.8457
2026 | 2008 | 10 | 31 | 17 | 4784.6908
2026 | 2008 | 10 | 31 | 18 | 5018.2745
2026 | 2008 | 10 | 31 | 19 | 7709.123
2026 | 2008 | 10 | 31 | 20 | 9752.3145
2026 | 2008 | 10 | 31 | 21 | 11583.0456
2026 | 2008 | 10 | 31 | 22 | 12787.8685
2026 | 2008 | 10 | 31 | 23 | 13137.5777
2026 | 2008 | 10 | 31 | 24 | 12877.2309
2027 | 2008 | 10 | 1 | 1 | 6620.3856
2027 | 2008 | 10 | 1 | 2 | 6766.3434
2027 | 2008 | 10 | 1 | 3 | 6422.3402
2027 | 2008 | 10 | 1 | 4 | 6805.0874
2027 | 2008 | 10 | 1 | 5 | 6866.4046
2027 | 2008 | 10 | 1 | 6 | 5988.2616
2027 | 2008 | 10 | 1 | 7 | 5321.4634
2027 | 2008 | 10 | 1 | 8 | 4518.0676
2027 | 2008 | 10 | 1 | 9 | 3609.6301
2027 | 2008 | 10 | 1 | 10 | 1722.6032
2027 | 2008 | 10 | 1 | 11 | 1824.9271
2027 | 2008 | 10 | 1 | 12 | 1645.4733
2027 | 2008 | 10 | 1 | 13 | 1609.2633
2027 | 2008 | 10 | 1 | 14 | 1529.6245
2027 | 2008 | 10 | 1 | 15 | 1320.7679
2027 | 2008 | 10 | 1 | 16 | 1144.628
2027 | 2008 | 10 | 1 | 17 | 1139.0741
2027 | 2008 | 10 | 1 | 18 | 1686.2299
2027 | 2008 | 10 | 1 | 19 | 3974.6129
2027 | 2008 | 10 | 1 | 20 | 4421.2259
2027 | 2008 | 10 | 1 | 21 | 5905.9393
2027 | 2008 | 10 | 1 | 22 | 8144.6727
2027 | 2008 | 10 | 1 | 23 | 8987.3333
2027 | 2008 | 10 | 1 | 24 | 9064.9207
2027 | 2008 | 10 | 2 | 1 | 9055.0176
2027 | 2008 | 10 | 2 | 2 | 9544.7463
2027 | 2008 | 10 | 2 | 3 | 9891.3163
2027 | 2008 | 10 | 2 | 4 | 9959.7761
2027 | 2008 | 10 | 2 | 5 | 9592.4933
2027 | 2008 | 10 | 2 | 6 | 8760.3085
2027 | 2008 | 10 | 2 | 7 | 8573.8879
2027 | 2008 | 10 | 2 | 8 | 7234.8699
2027 | 2008 | 10 | 2 | 9 | 6092.7401
2027 | 2008 | 10 | 2 | 10 | 3625.8202
2027 | 2008 | 10 | 2 | 11 | 4493.5121
2027 | 2008 | 10 | 2 | 12 | 4085.3933
2027 | 2008 | 10 | 2 | 13 | 3914.6863
2027 | 2008 | 10 | 2 | 14 | 4032.9696
2027 | 2008 | 10 | 2 | 15 | 4412.7398
2027 | 2008 | 10 | 2 | 16 | 4578.7814
2027 | 2008 | 10 | 2 | 17 | 5142.7077
2027 | 2008 | 10 | 2 | 18 | 6416.9116
2027 | 2008 | 10 | 2 | 19 | 8811.0839
2027 | 2008 | 10 | 2 | 20 | 12643.9093
2027 | 2008 | 10 | 2 | 21 | 17489.1774
2027 | 2008 | 10 | 2 | 22 | 21271.7419
2027 | 2008 | 10 | 2 | 23 | 23863.2305
2027 | 2008 | 10 | 2 | 24 | 26103.923
2027 | 2008 | 10 | 3 | 1 | 26925.9546
2027 | 2008 | 10 | 3 | 2 | 27133.7199
2027 | 2008 | 10 | 3 | 3 | 27554.418
2027 | 2008 | 10 | 3 | 4 | 27557.5809
2027 | 2008 | 10 | 3 | 5 | 26696.2552
2027 | 2008 | 10 | 3 | 6 | 26224.2919
2027 | 2008 | 10 | 3 | 7 | 25160.5032
2027 | 2008 | 10 | 3 | 8 | 22795.0783
2027 | 2008 | 10 | 3 | 9 | 19043.4594
2027 | 2008 | 10 | 3 | 10 | 13746.8398
2027 | 2008 | 10 | 3 | 11 | 15013.2297
2027 | 2008 | 10 | 3 | 12 | 16301.1675
2027 | 2008 | 10 | 3 | 13 | 17055.7313
2027 | 2008 | 10 | 3 | 14 | 18250.6081
2027 | 2008 | 10 | 3 | 15 | 19759.0089
2027 | 2008 | 10 | 3 | 16 | 20225.2228
2027 | 2008 | 10 | 3 | 17 | 21690.7053
2027 | 2008 | 10 | 3 | 18 | 22508.3921
2027 | 2008 | 10 | 3 | 19 | 24700.2687
2027 | 2008 | 10 | 3 | 20 | 29921.3021
2027 | 2008 | 10 | 3 | 21 | 32665.2017
2027 | 2008 | 10 | 3 | 22 | 33073.3264
2027 | 2008 | 10 | 3 | 23 | 32480.7393
2027 | 2008 | 10 | 3 | 24 | 32691.536
2027 | 2008 | 10 | 4 | 1 | 32798.2217
2027 | 2008 | 10 | 4 | 2 | 32996.3628
2027 | 2008 | 10 | 4 | 3 | 33107.8467
2027 | 2008 | 10 | 4 | 4 | 32578.7144
2027 | 2008 | 10 | 4 | 5 | 32094.245
2027 | 2008 | 10 | 4 | 6 | 31171.8911
2027 | 2008 | 10 | 4 | 7 | 30870.4711
2027 | 2008 | 10 | 4 | 8 | 28904.4852
2027 | 2008 | 10 | 4 | 9 | 25565.8921
2027 | 2008 | 10 | 4 | 10 | 26552.0547
2027 | 2008 | 10 | 4 | 11 | 29389.8946
2027 | 2008 | 10 | 4 | 12 | 30051.903
2027 | 2008 | 10 | 4 | 13 | 30991.1189
2027 | 2008 | 10 | 4 | 14 | 31943.4006
2027 | 2008 | 10 | 4 | 15 | 33250.5451
2027 | 2008 | 10 | 4 | 16 | 34470.1696
2027 | 2008 | 10 | 4 | 17 | 34880.2792
2027 | 2008 | 10 | 4 | 18 | 35218.5662
2027 | 2008 | 10 | 4 | 19 | 34514.1885
2027 | 2008 | 10 | 4 | 20 | 34856.9267
2027 | 2008 | 10 | 4 | 21 | 34839.2502
2027 | 2008 | 10 | 4 | 22 | 34704.5544
2027 | 2008 | 10 | 4 | 23 | 34611.8831
2027 | 2008 | 10 | 4 | 24 | 34293.7723
2027 | 2008 | 10 | 5 | 1 | 34105.9985
2027 | 2008 | 10 | 5 | 2 | 33904.0285
2027 | 2008 | 10 | 5 | 3 | 33393.794
2027 | 2008 | 10 | 5 | 4 | 33114.4637
2027 | 2008 | 10 | 5 | 5 | 32604.7531
2027 | 2008 | 10 | 5 | 6 | 32150.3599
2027 | 2008 | 10 | 5 | 7 | 31113.2783
2027 | 2008 | 10 | 5 | 8 | 28997.686
2027 | 2008 | 10 | 5 | 9 | 25514.068
2027 | 2008 | 10 | 5 | 10 | 29684.5768
2027 | 2008 | 10 | 5 | 11 | 32664.9633
2027 | 2008 | 10 | 5 | 12 | 32889.4792
2027 | 2008 | 10 | 5 | 13 | 33530.1402
2027 | 2008 | 10 | 5 | 14 | 32671.2541
2027 | 2008 | 10 | 5 | 15 | 33110.7686
2027 | 2008 | 10 | 5 | 16 | 32652.9767
2027 | 2008 | 10 | 5 | 17 | 32849.8403
2027 | 2008 | 10 | 5 | 18 | 32716.5861
2027 | 2008 | 10 | 5 | 19 | 31435.3569
2027 | 2008 | 10 | 5 | 20 | 31685.0369
2027 | 2008 | 10 | 5 | 21 | 31507.1824
2027 | 2008 | 10 | 5 | 22 | 29782.8304
2027 | 2008 | 10 | 5 | 23 | 29918.2986
2027 | 2008 | 10 | 5 | 24 | 28590.1877
2027 | 2008 | 10 | 6 | 1 | 28387.3592
2027 | 2008 | 10 | 6 | 2 | 28847.172
2027 | 2008 | 10 | 6 | 3 | 28200.2197
2027 | 2008 | 10 | 6 | 4 | 28142.782
2027 | 2008 | 10 | 6 | 5 | 28225.8473
2027 | 2008 | 10 | 6 | 6 | 26733.1086
2027 | 2008 | 10 | 6 | 7 | 25819.8982
2027 | 2008 | 10 | 6 | 8 | 24308.203
2027 | 2008 | 10 | 6 | 9 | 21739.7466
2027 | 2008 | 10 | 6 | 10 | 25055.643
2027 | 2008 | 10 | 6 | 11 | 26198.1735
2027 | 2008 | 10 | 6 | 12 | 25596.8223
2027 | 2008 | 10 | 6 | 13 | 24453.8326
2027 | 2008 | 10 | 6 | 14 | 22889.0758
2027 | 2008 | 10 | 6 | 15 | 21392.1458
2027 | 2008 | 10 | 6 | 16 | 19540.8996
2027 | 2008 | 10 | 6 | 17 | 16253.6168
2027 | 2008 | 10 | 6 | 18 | 13021.5337
2027 | 2008 | 10 | 6 | 19 | 11230.8493
2027 | 2008 | 10 | 6 | 20 | 13544.2323
2027 | 2008 | 10 | 6 | 21 | 16337.6521
2027 | 2008 | 10 | 6 | 22 | 18199.5068
2027 | 2008 | 10 | 6 | 23 | 16559.0827
2027 | 2008 | 10 | 6 | 24 | 16435.2719
2027 | 2008 | 10 | 7 | 1 | 16234.2465
2027 | 2008 | 10 | 7 | 2 | 17083.9228
2027 | 2008 | 10 | 7 | 3 | 17575.2017
2027 | 2008 | 10 | 7 | 4 | 18487.9285
2027 | 2008 | 10 | 7 | 5 | 19151.6233
2027 | 2008 | 10 | 7 | 6 | 19334.5546
2027 | 2008 | 10 | 7 | 7 | 20132.4246
2027 | 2008 | 10 | 7 | 8 | 19555.1071
2027 | 2008 | 10 | 7 | 9 | 17394.0006
2027 | 2008 | 10 | 7 | 10 | 16246.5536
2027 | 2008 | 10 | 7 | 11 | 18834.3232
2027 | 2008 | 10 | 7 | 12 | 17945.0802
2027 | 2008 | 10 | 7 | 13 | 17115.6761
2027 | 2008 | 10 | 7 | 14 | 16778.5293
2027 | 2008 | 10 | 7 | 15 | 17050.696
2027 | 2008 | 10 | 7 | 16 | 15522.8467
2027 | 2008 | 10 | 7 | 17 | 14055.682
2027 | 2008 | 10 | 7 | 18 | 11052.015
2027 | 2008 | 10 | 7 | 19 | 8213.2039
2027 | 2008 | 10 | 7 | 20 | 7053.3535
2027 | 2008 | 10 | 7 | 21 | 6595.2007
2027 | 2008 | 10 | 7 | 22 | 6974.9855
2027 | 2008 | 10 | 7 | 23 | 7684.7843
2027 | 2008 | 10 | 7 | 24 | 8551.4575
2027 | 2008 | 10 | 8 | 1 | 10398.8832
2027 | 2008 | 10 | 8 | 2 | 12220.9585
2027 | 2008 | 10 | 8 | 3 | 14673.704
2027 | 2008 | 10 | 8 | 4 | 16229.2637
2027 | 2008 | 10 | 8 | 5 | 17340.533
2027 | 2008 | 10 | 8 | 6 | 16328.0517
2027 | 2008 | 10 | 8 | 7 | 16676.8709
2027 | 2008 | 10 | 8 | 8 | 15575.6375
2027 | 2008 | 10 | 8 | 9 | 13561.5753
2027 | 2008 | 10 | 8 | 10 | 8594.5492
2027 | 2008 | 10 | 8 | 11 | 8380.8948
2027 | 2008 | 10 | 8 | 12 | 8289.6149
2027 | 2008 | 10 | 8 | 13 | 7503.7602
2027 | 2008 | 10 | 8 | 14 | 6557.1002
2027 | 2008 | 10 | 8 | 15 | 6044.1197
2027 | 2008 | 10 | 8 | 16 | 5658.4177
2027 | 2008 | 10 | 8 | 17 | 5435.6459
2027 | 2008 | 10 | 8 | 18 | 5937.2573
2027 | 2008 | 10 | 8 | 19 | 7803.3546
2027 | 2008 | 10 | 8 | 20 | 11279.7779
2027 | 2008 | 10 | 8 | 21 | 16689.7932
2027 | 2008 | 10 | 8 | 22 | 20589.681
2027 | 2008 | 10 | 8 | 23 | 22972.9981
2027 | 2008 | 10 | 8 | 24 | 24731.5632
2027 | 2008 | 10 | 9 | 1 | 24329.3603
2027 | 2008 | 10 | 9 | 2 | 23718.7141
2027 | 2008 | 10 | 9 | 3 | 23067.2378
2027 | 2008 | 10 | 9 | 4 | 22206.5251
2027 | 2008 | 10 | 9 | 5 | 21476.5304
2027 | 2008 | 10 | 9 | 6 | 21316.4984
2027 | 2008 | 10 | 9 | 7 | 20785.0717
2027 | 2008 | 10 | 9 | 8 | 19998.4086
2027 | 2008 | 10 | 9 | 9 | 17397.799
2027 | 2008 | 10 | 9 | 10 | 11262.1837
2027 | 2008 | 10 | 9 | 11 | 14342.2201
2027 | 2008 | 10 | 9 | 12 | 18291.905
2027 | 2008 | 10 | 9 | 13 | 19695.8249
2027 | 2008 | 10 | 9 | 14 | 20686.5378
2027 | 2008 | 10 | 9 | 15 | 21136.7764
2027 | 2008 | 10 | 9 | 16 | 21922.136
2027 | 2008 | 10 | 9 | 17 | 21755.1828
2027 | 2008 | 10 | 9 | 18 | 22172.3756
2027 | 2008 | 10 | 9 | 19 | 24625.4839
2027 | 2008 | 10 | 9 | 20 | 28527.0195
2027 | 2008 | 10 | 9 | 21 | 31037.5378
2027 | 2008 | 10 | 9 | 22 | 31288.6848
2027 | 2008 | 10 | 9 | 23 | 31329.0893
2027 | 2008 | 10 | 9 | 24 | 31100.6533
2027 | 2008 | 10 | 10 | 1 | 30604.8908
2027 | 2008 | 10 | 10 | 2 | 30383.0777
2027 | 2008 | 10 | 10 | 3 | 30215.5458
2027 | 2008 | 10 | 10 | 4 | 29663.022
2027 | 2008 | 10 | 10 | 5 | 29429.6853
2027 | 2008 | 10 | 10 | 6 | 29279.0799
2027 | 2008 | 10 | 10 | 7 | 28716.9179
2027 | 2008 | 10 | 10 | 8 | 26879.5543
2027 | 2008 | 10 | 10 | 9 | 23095.1529
2027 | 2008 | 10 | 10 | 10 | 20340.4448
2027 | 2008 | 10 | 10 | 11 | 21660.1496
2027 | 2008 | 10 | 10 | 12 | 21130.7729
2027 | 2008 | 10 | 10 | 13 | 21252.5392
2027 | 2008 | 10 | 10 | 14 | 21803.4762
2027 | 2008 | 10 | 10 | 15 | 22483.2036
2027 | 2008 | 10 | 10 | 16 | 23574.616
2027 | 2008 | 10 | 10 | 17 | 24521.2933
2027 | 2008 | 10 | 10 | 18 | 25996.1473
2027 | 2008 | 10 | 10 | 19 | 28229.1831
2027 | 2008 | 10 | 10 | 20 | 31117.3527
2027 | 2008 | 10 | 10 | 21 | 32821.1387
2027 | 2008 | 10 | 10 | 22 | 32922.2811
2027 | 2008 | 10 | 10 | 23 | 32239.8474
2027 | 2008 | 10 | 10 | 24 | 31360.1103
2027 | 2008 | 10 | 11 | 1 | 30813.2473
2027 | 2008 | 10 | 11 | 2 | 29776.5192
2027 | 2008 | 10 | 11 | 3 | 29110.1144
2027 | 2008 | 10 | 11 | 4 | 27792.4009
2027 | 2008 | 10 | 11 | 5 | 26500.9823
2027 | 2008 | 10 | 11 | 6 | 24670.701
2027 | 2008 | 10 | 11 | 7 | 22702.8183
2027 | 2008 | 10 | 11 | 8 | 20646.1927
2027 | 2008 | 10 | 11 | 9 | 17295.7743
2027 | 2008 | 10 | 11 | 10 | 18632.4902
2027 | 2008 | 10 | 11 | 11 | 20054.93
2027 | 2008 | 10 | 11 | 12 | 20677.2031
2027 | 2008 | 10 | 11 | 13 | 22532.6283
2027 | 2008 | 10 | 11 | 14 | 24185.0053
2027 | 2008 | 10 | 11 | 15 | 26929.8476
2027 | 2008 | 10 | 11 | 16 | 29313.6976
2027 | 2008 | 10 | 11 | 17 | 30363.5391
2027 | 2008 | 10 | 11 | 18 | 32262.4455
2027 | 2008 | 10 | 11 | 19 | 32192.3034
2027 | 2008 | 10 | 11 | 20 | 33359.2448
2027 | 2008 | 10 | 11 | 21 | 33925.7279
2027 | 2008 | 10 | 11 | 22 | 33535.5381
2027 | 2008 | 10 | 11 | 23 | 33521.0208
2027 | 2008 | 10 | 11 | 24 | 32901.6666
2027 | 2008 | 10 | 12 | 1 | 32776.4783
2027 | 2008 | 10 | 12 | 2 | 32778.4766
2027 | 2008 | 10 | 12 | 3 | 32805.3441
2027 | 2008 | 10 | 12 | 4 | 32514.2848
2027 | 2008 | 10 | 12 | 5 | 31372.6397
2027 | 2008 | 10 | 12 | 6 | 31087.4893
2027 | 2008 | 10 | 12 | 7 | 30270.5429
2027 | 2008 | 10 | 12 | 8 | 28700.5393
2027 | 2008 | 10 | 12 | 9 | 25837.1476
2027 | 2008 | 10 | 12 | 10 | 30611.7773
2027 | 2008 | 10 | 12 | 11 | 32310.0397
2027 | 2008 | 10 | 12 | 12 | 32595.1022
2027 | 2008 | 10 | 12 | 13 | 33648.9892
2027 | 2008 | 10 | 12 | 14 | 33892.0194
2027 | 2008 | 10 | 12 | 15 | 34111.1395
2027 | 2008 | 10 | 12 | 16 | 34258.5836
2027 | 2008 | 10 | 12 | 17 | 32839.0048
2027 | 2008 | 10 | 12 | 18 | 31558.9278
2027 | 2008 | 10 | 12 | 19 | 30292.4897
2027 | 2008 | 10 | 12 | 20 | 31680.3527
2027 | 2008 | 10 | 12 | 21 | 32616.784
2027 | 2008 | 10 | 12 | 22 | 32808.4915
2027 | 2008 | 10 | 12 | 23 | 32193.4082
2027 | 2008 | 10 | 12 | 24 | 31830.9532
2027 | 2008 | 10 | 13 | 1 | 29686.2997
2027 | 2008 | 10 | 13 | 2 | 27802.3034
2027 | 2008 | 10 | 13 | 3 | 25760.8353
2027 | 2008 | 10 | 13 | 4 | 23810.7206
2027 | 2008 | 10 | 13 | 5 | 22064.2044
2027 | 2008 | 10 | 13 | 6 | 21117.9349
2027 | 2008 | 10 | 13 | 7 | 20377.8001
2027 | 2008 | 10 | 13 | 8 | 19931.8178
2027 | 2008 | 10 | 13 | 9 | 18260.569
2027 | 2008 | 10 | 13 | 10 | 21867.8301
2027 | 2008 | 10 | 13 | 11 | 22671.6608
2027 | 2008 | 10 | 13 | 12 | 21392.0388
2027 | 2008 | 10 | 13 | 13 | 20301.5084
2027 | 2008 | 10 | 13 | 14 | 19498.8111
2027 | 2008 | 10 | 13 | 15 | 18699.6739
2027 | 2008 | 10 | 13 | 16 | 18117.0806
2027 | 2008 | 10 | 13 | 17 | 18689.7178
2027 | 2008 | 10 | 13 | 18 | 20074.2598
2027 | 2008 | 10 | 13 | 19 | 20928.7921
2027 | 2008 | 10 | 13 | 20 | 21672.3662
2027 | 2008 | 10 | 13 | 21 | 22298.8294
2027 | 2008 | 10 | 13 | 22 | 21796.5857
2027 | 2008 | 10 | 13 | 23 | 20266.2562
2027 | 2008 | 10 | 13 | 24 | 18693.2183
2027 | 2008 | 10 | 14 | 1 | 16126.9222
2027 | 2008 | 10 | 14 | 2 | 14896.6518
2027 | 2008 | 10 | 14 | 3 | 13746.5359
2027 | 2008 | 10 | 14 | 4 | 11986.9175
2027 | 2008 | 10 | 14 | 5 | 10081.0692
2027 | 2008 | 10 | 14 | 6 | 8236.8051
2027 | 2008 | 10 | 14 | 7 | 7293.9482
2027 | 2008 | 10 | 14 | 8 | 6391.1276
2027 | 2008 | 10 | 14 | 9 | 5035.346
2027 | 2008 | 10 | 14 | 10 | 6153.4475
2027 | 2008 | 10 | 14 | 11 | 6456.309
2027 | 2008 | 10 | 14 | 12 | 6811.4429
2027 | 2008 | 10 | 14 | 13 | 7425.0816
2027 | 2008 | 10 | 14 | 14 | 8484.9639
2027 | 2008 | 10 | 14 | 15 | 9520.4684
2027 | 2008 | 10 | 14 | 16 | 9960.7597
2027 | 2008 | 10 | 14 | 17 | 9441.9564
2027 | 2008 | 10 | 14 | 18 | 9162.7699
2027 | 2008 | 10 | 14 | 19 | 9221.4021
2027 | 2008 | 10 | 14 | 20 | 9138.0328
2027 | 2008 | 10 | 14 | 21 | 9973.7757
2027 | 2008 | 10 | 14 | 22 | 9379.9055
2027 | 2008 | 10 | 14 | 23 | 8175.4567
2027 | 2008 | 10 | 14 | 24 | 7164.76
2027 | 2008 | 10 | 15 | 1 | 6968.2827
2027 | 2008 | 10 | 15 | 2 | 7882.2054
2027 | 2008 | 10 | 15 | 3 | 8574.4773
2027 | 2008 | 10 | 15 | 4 | 9687.3319
2027 | 2008 | 10 | 15 | 5 | 10594.6191
2027 | 2008 | 10 | 15 | 6 | 11044.1699
2027 | 2008 | 10 | 15 | 7 | 11814.3701
2027 | 2008 | 10 | 15 | 8 | 11536.6356
2027 | 2008 | 10 | 15 | 9 | 10006.263
2027 | 2008 | 10 | 15 | 10 | 11880.1727
2027 | 2008 | 10 | 15 | 11 | 12204.8834
2027 | 2008 | 10 | 15 | 12 | 10657.8259
2027 | 2008 | 10 | 15 | 13 | 9622.6087
2027 | 2008 | 10 | 15 | 14 | 10297.7606
2027 | 2008 | 10 | 15 | 15 | 11287.4762
2027 | 2008 | 10 | 15 | 16 | 12211.8986
2027 | 2008 | 10 | 15 | 17 | 12867.452
2027 | 2008 | 10 | 15 | 18 | 12506.8533
2027 | 2008 | 10 | 15 | 19 | 13010.8066
2027 | 2008 | 10 | 15 | 20 | 14364.3206
2027 | 2008 | 10 | 15 | 21 | 15752.7019
2027 | 2008 | 10 | 15 | 22 | 15166.463
2027 | 2008 | 10 | 15 | 23 | 13600.1895
2027 | 2008 | 10 | 15 | 24 | 13542.8744
2027 | 2008 | 10 | 16 | 1 | 13331.4755
2027 | 2008 | 10 | 16 | 2 | 14007.3989
2027 | 2008 | 10 | 16 | 3 | 14800.0809
2027 | 2008 | 10 | 16 | 4 | 16017.864
2027 | 2008 | 10 | 16 | 5 | 15789.3524
2027 | 2008 | 10 | 16 | 6 | 16410.719
2027 | 2008 | 10 | 16 | 7 | 16657.3644
2027 | 2008 | 10 | 16 | 8 | 16724.954
2027 | 2008 | 10 | 16 | 9 | 15176.6202
2027 | 2008 | 10 | 16 | 10 | 19035.2869
2027 | 2008 | 10 | 16 | 11 | 19151.4044
2027 | 2008 | 10 | 16 | 12 | 17313.8576
2027 | 2008 | 10 | 16 | 13 | 15255.7236
2027 | 2008 | 10 | 16 | 14 | 13400.1665
2027 | 2008 | 10 | 16 | 15 | 12176.5324
2027 | 2008 | 10 | 16 | 16 | 10649.7481
2027 | 2008 | 10 | 16 | 17 | 8656.9024
2027 | 2008 | 10 | 16 | 18 | 7085.9834
2027 | 2008 | 10 | 16 | 19 | 5871.4027
2027 | 2008 | 10 | 16 | 20 | 5570.8995
2027 | 2008 | 10 | 16 | 21 | 5545.5251
2027 | 2008 | 10 | 16 | 22 | 5548.3914
2027 | 2008 | 10 | 16 | 23 | 5304.1082
2027 | 2008 | 10 | 16 | 24 | 5213.3993
2027 | 2008 | 10 | 17 | 1 | 5269.0749
2027 | 2008 | 10 | 17 | 2 | 5336.7525
2027 | 2008 | 10 | 17 | 3 | 5621.4011
2027 | 2008 | 10 | 17 | 4 | 6300.8011
2027 | 2008 | 10 | 17 | 5 | 6945.2604
2027 | 2008 | 10 | 17 | 6 | 7069.8732
2027 | 2008 | 10 | 17 | 7 | 6881.3838
2027 | 2008 | 10 | 17 | 8 | 5762.296
2027 | 2008 | 10 | 17 | 9 | 5423.8781
2027 | 2008 | 10 | 17 | 10 | 5535.3504
2027 | 2008 | 10 | 17 | 11 | 5275.3982
2027 | 2008 | 10 | 17 | 12 | 5348.1464
2027 | 2008 | 10 | 17 | 13 | 5025.8737
2027 | 2008 | 10 | 17 | 14 | 4829.4649
2027 | 2008 | 10 | 17 | 15 | 4513.226
2027 | 2008 | 10 | 17 | 16 | 4019.2171
2027 | 2008 | 10 | 17 | 17 | 3436.7196
2027 | 2008 | 10 | 17 | 18 | 3169.6301
2027 | 2008 | 10 | 17 | 19 | 3094.3149
2027 | 2008 | 10 | 17 | 20 | 2817.1583
2027 | 2008 | 10 | 17 | 21 | 2713.9603
2027 | 2008 | 10 | 17 | 22 | 2763.5157
2027 | 2008 | 10 | 17 | 23 | 2941.8648
2027 | 2008 | 10 | 17 | 24 | 3551.4498
2027 | 2008 | 10 | 18 | 1 | 3688.5953
2027 | 2008 | 10 | 18 | 2 | 4155.2181
2027 | 2008 | 10 | 18 | 3 | 4379.3408
2027 | 2008 | 10 | 18 | 4 | 4827.0259
2027 | 2008 | 10 | 18 | 5 | 5183.891
2027 | 2008 | 10 | 18 | 6 | 5741.2147
2027 | 2008 | 10 | 18 | 7 | 6314.5429
2027 | 2008 | 10 | 18 | 8 | 5359.4519
2027 | 2008 | 10 | 18 | 9 | 4354.2741
2027 | 2008 | 10 | 18 | 10 | 4340.1724
2027 | 2008 | 10 | 18 | 11 | 4599.2498
2027 | 2008 | 10 | 18 | 12 | 5394.2137
2027 | 2008 | 10 | 18 | 13 | 5986.2149
2027 | 2008 | 10 | 18 | 14 | 6748.7631
2027 | 2008 | 10 | 18 | 15 | 7406.683
2027 | 2008 | 10 | 18 | 16 | 7561.8252
2027 | 2008 | 10 | 18 | 17 | 7411.0585
2027 | 2008 | 10 | 18 | 18 | 7348.6318
2027 | 2008 | 10 | 18 | 19 | 7869.2721
2027 | 2008 | 10 | 18 | 20 | 9642.6813
2027 | 2008 | 10 | 18 | 21 | 11378.9371
2027 | 2008 | 10 | 18 | 22 | 13276.0187
2027 | 2008 | 10 | 18 | 23 | 14851.7182
2027 | 2008 | 10 | 18 | 24 | 16982.1228
2027 | 2008 | 10 | 19 | 1 | 19185.2874
2027 | 2008 | 10 | 19 | 2 | 20361.5691
2027 | 2008 | 10 | 19 | 3 | 20892.4418
2027 | 2008 | 10 | 19 | 4 | 20769.04
2027 | 2008 | 10 | 19 | 5 | 20397.085
2027 | 2008 | 10 | 19 | 6 | 20327.5036
2027 | 2008 | 10 | 19 | 7 | 19512.4932
2027 | 2008 | 10 | 19 | 8 | 18993.8891
2027 | 2008 | 10 | 19 | 9 | 16891.8242
2027 | 2008 | 10 | 19 | 10 | 10603.4147
2027 | 2008 | 10 | 19 | 11 | 13364.6137
2027 | 2008 | 10 | 19 | 12 | 14657.4765
2027 | 2008 | 10 | 19 | 13 | 13781.9775
2027 | 2008 | 10 | 19 | 14 | 13105.4273
2027 | 2008 | 10 | 19 | 15 | 13233.8145
2027 | 2008 | 10 | 19 | 16 | 13301.0058
2027 | 2008 | 10 | 19 | 17 | 13142.6918
2027 | 2008 | 10 | 19 | 18 | 12959.2567
2027 | 2008 | 10 | 19 | 19 | 15844.0994
2027 | 2008 | 10 | 19 | 20 | 20537.2438
2027 | 2008 | 10 | 19 | 21 | 25189.8326
2027 | 2008 | 10 | 19 | 22 | 27291.7647
2027 | 2008 | 10 | 19 | 23 | 27338.8637
2027 | 2008 | 10 | 19 | 24 | 27165.2659
2027 | 2008 | 10 | 20 | 1 | 26954.9814
2027 | 2008 | 10 | 20 | 2 | 26349.0649
2027 | 2008 | 10 | 20 | 3 | 24994.9429
2027 | 2008 | 10 | 20 | 4 | 23807.281
2027 | 2008 | 10 | 20 | 5 | 21578.3422
2027 | 2008 | 10 | 20 | 6 | 19873.0259
2027 | 2008 | 10 | 20 | 7 | 18455.1868
2027 | 2008 | 10 | 20 | 8 | 16348.1822
2027 | 2008 | 10 | 20 | 9 | 12769.8174
2027 | 2008 | 10 | 20 | 10 | 7008.6383
2027 | 2008 | 10 | 20 | 11 | 6156.8035
2027 | 2008 | 10 | 20 | 12 | 4932.6749
2027 | 2008 | 10 | 20 | 13 | 3899.5763
2027 | 2008 | 10 | 20 | 14 | 3495.2407
2027 | 2008 | 10 | 20 | 15 | 3545.4008
2027 | 2008 | 10 | 20 | 16 | 3737.8355
2027 | 2008 | 10 | 20 | 17 | 4006.7432
2027 | 2008 | 10 | 20 | 18 | 5376.1065
2027 | 2008 | 10 | 20 | 19 | 8439.0105
2027 | 2008 | 10 | 20 | 20 | 11417.354
2027 | 2008 | 10 | 20 | 21 | 15116.0032
2027 | 2008 | 10 | 20 | 22 | 16515.5674
2027 | 2008 | 10 | 20 | 23 | 16987.4356
2027 | 2008 | 10 | 20 | 24 | 16143.9264
2027 | 2008 | 10 | 21 | 1 | 15223.6751
2027 | 2008 | 10 | 21 | 2 | 14489.377
2027 | 2008 | 10 | 21 | 3 | 13907.5692
2027 | 2008 | 10 | 21 | 4 | 12539.872
2027 | 2008 | 10 | 21 | 5 | 10585.8267
2027 | 2008 | 10 | 21 | 6 | 9242.4708
2027 | 2008 | 10 | 21 | 7 | 5925.4169
2027 | 2008 | 10 | 21 | 8 | 6617.6096
2027 | 2008 | 10 | 21 | 9 | 5629.211
2027 | 2008 | 10 | 21 | 10 | 5088.0931
2027 | 2008 | 10 | 21 | 11 | 6114.0866
2027 | 2008 | 10 | 21 | 12 | 8063.1332
2027 | 2008 | 10 | 21 | 13 | 11134.5218
2027 | 2008 | 10 | 21 | 14 | 13555.152
2027 | 2008 | 10 | 21 | 15 | 15607.6915
2027 | 2008 | 10 | 21 | 16 | 17676.2131
2027 | 2008 | 10 | 21 | 17 | 18509.4818
2027 | 2008 | 10 | 21 | 18 | 18943.7634
2027 | 2008 | 10 | 21 | 19 | 22236.7748
2027 | 2008 | 10 | 21 | 20 | 26645.6263
2027 | 2008 | 10 | 21 | 21 | 29264.6196
2027 | 2008 | 10 | 21 | 22 | 30321.4856
2027 | 2008 | 10 | 21 | 23 | 30449.6315
2027 | 2008 | 10 | 21 | 24 | 31442.2598
2027 | 2008 | 10 | 22 | 1 | 31191.2773
2027 | 2008 | 10 | 22 | 2 | 29876.8348
2027 | 2008 | 10 | 22 | 3 | 30220.9045
2027 | 2008 | 10 | 22 | 4 | 29123.4893
2027 | 2008 | 10 | 22 | 5 | 27419.7046
2027 | 2008 | 10 | 22 | 6 | 25684.6751
2027 | 2008 | 10 | 22 | 7 | 22954.4638
2027 | 2008 | 10 | 22 | 8 | 21805.9766
2027 | 2008 | 10 | 22 | 9 | 19238.6026
2027 | 2008 | 10 | 22 | 10 | 21908.3607
2027 | 2008 | 10 | 22 | 11 | 24244.0316
2027 | 2008 | 10 | 22 | 12 | 25193.2974
2027 | 2008 | 10 | 22 | 13 | 26551.5701
2027 | 2008 | 10 | 22 | 14 | 27186.5584
2027 | 2008 | 10 | 22 | 15 | 26526.7195
2027 | 2008 | 10 | 22 | 16 | 26925.5889
2027 | 2008 | 10 | 22 | 17 | 27269.2948
2027 | 2008 | 10 | 22 | 18 | 26772.5609
2027 | 2008 | 10 | 22 | 19 | 24423.3062
2027 | 2008 | 10 | 22 | 20 | 23728.4003
2027 | 2008 | 10 | 22 | 21 | 21958.0454
2027 | 2008 | 10 | 22 | 22 | 19402.7409
2027 | 2008 | 10 | 22 | 23 | 16925.6226
2027 | 2008 | 10 | 22 | 24 | 14767.7873
2027 | 2008 | 10 | 23 | 1 | 13269.6605
2027 | 2008 | 10 | 23 | 2 | 14519.1386
2027 | 2008 | 10 | 23 | 3 | 15819.8335
2027 | 2008 | 10 | 23 | 4 | 16614.9176
2027 | 2008 | 10 | 23 | 5 | 17332.2434
2027 | 2008 | 10 | 23 | 6 | 18397.9756
2027 | 2008 | 10 | 23 | 7 | 18730.4599
2027 | 2008 | 10 | 23 | 8 | 18783.0182
2027 | 2008 | 10 | 23 | 9 | 17513.1327
2027 | 2008 | 10 | 23 | 10 | 16498.0256
2027 | 2008 | 10 | 23 | 11 | 15514.2064
2027 | 2008 | 10 | 23 | 12 | 16801.2494
2027 | 2008 | 10 | 23 | 13 | 16463.949
2027 | 2008 | 10 | 23 | 14 | 17420.8543
2027 | 2008 | 10 | 23 | 15 | 18072.6708
2027 | 2008 | 10 | 23 | 16 | 17348.215
2027 | 2008 | 10 | 23 | 17 | 15708.1402
2027 | 2008 | 10 | 23 | 18 | 11797.6135
2027 | 2008 | 10 | 23 | 19 | 8122.4553
2027 | 2008 | 10 | 23 | 20 | 7336.1282
2027 | 2008 | 10 | 23 | 21 | 6369.8723
2027 | 2008 | 10 | 23 | 22 | 8588.583
2027 | 2008 | 10 | 23 | 23 | 9467.0858
2027 | 2008 | 10 | 23 | 24 | 9588.7308
2027 | 2008 | 10 | 24 | 1 | 11519.3158
2027 | 2008 | 10 | 24 | 2 | 11845.4094
2027 | 2008 | 10 | 24 | 3 | 10551.5047
2027 | 2008 | 10 | 24 | 4 | 10026.0511
2027 | 2008 | 10 | 24 | 5 | 9282.4007
2027 | 2008 | 10 | 24 | 6 | 8371.5462
2027 | 2008 | 10 | 24 | 7 | 7742.6382
2027 | 2008 | 10 | 24 | 8 | 6780.7561
2027 | 2008 | 10 | 24 | 9 | 5694.0907
2027 | 2008 | 10 | 24 | 10 | 3426.9337
2027 | 2008 | 10 | 24 | 11 | 2767.5345
2027 | 2008 | 10 | 24 | 12 | 2796.1573
2027 | 2008 | 10 | 24 | 13 | 2478.5862
2027 | 2008 | 10 | 24 | 14 | 2562.3166
2027 | 2008 | 10 | 24 | 15 | 2212.532
2027 | 2008 | 10 | 24 | 16 | 1739.7473
2027 | 2008 | 10 | 24 | 17 | 1235.9358
2027 | 2008 | 10 | 24 | 18 | 1445.0958
2027 | 2008 | 10 | 24 | 19 | 2326.3911
2027 | 2008 | 10 | 24 | 20 | 3452.6218
2027 | 2008 | 10 | 24 | 21 | 5357.2635
2027 | 2008 | 10 | 24 | 22 | 7870.9644
2027 | 2008 | 10 | 24 | 23 | 8939.151
2027 | 2008 | 10 | 24 | 24 | 9475.1608
2027 | 2008 | 10 | 25 | 1 | 9522.0818
2027 | 2008 | 10 | 25 | 2 | 9123.9095
2027 | 2008 | 10 | 25 | 3 | 8044.5658
2027 | 2008 | 10 | 25 | 4 | 7020.2952
2027 | 2008 | 10 | 25 | 5 | 6084.0246
2027 | 2008 | 10 | 25 | 6 | 5188.3156
2027 | 2008 | 10 | 25 | 7 | 4713.4261
2027 | 2008 | 10 | 25 | 8 | 4480.861
2027 | 2008 | 10 | 25 | 9 | 4093.5285
2027 | 2008 | 10 | 25 | 10 | 3684.4045
2027 | 2008 | 10 | 25 | 11 | 2997.4646
2027 | 2008 | 10 | 25 | 12 | 3743.9498
2027 | 2008 | 10 | 25 | 13 | 3955.4368
2027 | 2008 | 10 | 25 | 14 | 4683.5282
2027 | 2008 | 10 | 25 | 15 | 5760.5999
2027 | 2008 | 10 | 25 | 16 | 6688.563
2027 | 2008 | 10 | 25 | 17 | 6649.2178
2027 | 2008 | 10 | 25 | 18 | 6678.7465
2027 | 2008 | 10 | 25 | 19 | 7914.4304
2027 | 2008 | 10 | 25 | 20 | 11909.7927
2027 | 2008 | 10 | 25 | 21 | 17012.8221
2027 | 2008 | 10 | 25 | 22 | 21772.1811
2027 | 2008 | 10 | 25 | 23 | 24833.1354
2027 | 2008 | 10 | 25 | 24 | 27034.3674
2027 | 2008 | 10 | 26 | 1 | 27915.2141
2027 | 2008 | 10 | 26 | 2 | 27976.7672
2027 | 2008 | 10 | 26 | 3 | 27740.0892
2027 | 2008 | 10 | 26 | 4 | 26220.737
2027 | 2008 | 10 | 26 | 5 | 25918.2046
2027 | 2008 | 10 | 26 | 6 | 25802.0385
2027 | 2008 | 10 | 26 | 7 | 24020.4569
2027 | 2008 | 10 | 26 | 8 | 21577.7404
2027 | 2008 | 10 | 26 | 9 | 17710.0444
2027 | 2008 | 10 | 26 | 10 | 13382.1451
2027 | 2008 | 10 | 26 | 11 | 11483.7422
2027 | 2008 | 10 | 26 | 12 | 9848.992
2027 | 2008 | 10 | 26 | 13 | 9138.8028
2027 | 2008 | 10 | 26 | 14 | 9900.1781
2027 | 2008 | 10 | 26 | 15 | 13215.1069
2027 | 2008 | 10 | 26 | 16 | 16731.6873
2027 | 2008 | 10 | 26 | 17 | 20154.3553
2027 | 2008 | 10 | 26 | 18 | 24018.1747
2027 | 2008 | 10 | 26 | 19 | 26411.5752
2027 | 2008 | 10 | 26 | 20 | 29104.8527
2027 | 2008 | 10 | 26 | 21 | 31165.9281
2027 | 2008 | 10 | 26 | 22 | 31418.4638
2027 | 2008 | 10 | 26 | 23 | 30492.0285
2027 | 2008 | 10 | 26 | 24 | 29334.0359
2027 | 2008 | 10 | 27 | 1 | 27899.5508
2027 | 2008 | 10 | 27 | 2 | 26166.223
2027 | 2008 | 10 | 27 | 3 | 24801.1829
2027 | 2008 | 10 | 27 | 4 | 23683.0708
2027 | 2008 | 10 | 27 | 5 | 22639.1559
2027 | 2008 | 10 | 27 | 6 | 22686.6031
2027 | 2008 | 10 | 27 | 7 | 22070.5927
2027 | 2008 | 10 | 27 | 8 | 20705.9388
2027 | 2008 | 10 | 27 | 9 | 17482.0126
2027 | 2008 | 10 | 27 | 10 | 15475.1555
2027 | 2008 | 10 | 27 | 11 | 16782.9169
2027 | 2008 | 10 | 27 | 12 | 14547.0929
2027 | 2008 | 10 | 27 | 13 | 13844.6442
2027 | 2008 | 10 | 27 | 14 | 12605.1693
2027 | 2008 | 10 | 27 | 15 | 11841.6447
2027 | 2008 | 10 | 27 | 16 | 10965.7706
2027 | 2008 | 10 | 27 | 17 | 9513.3017
2027 | 2008 | 10 | 27 | 18 | 7989.7277
2027 | 2008 | 10 | 27 | 19 | 6958.7912
2027 | 2008 | 10 | 27 | 20 | 7416.2656
2027 | 2008 | 10 | 27 | 21 | 8188.9596
2027 | 2008 | 10 | 27 | 22 | 9105.5611
2027 | 2008 | 10 | 27 | 23 | 10077.8562
2027 | 2008 | 10 | 27 | 24 | 11362.3656
2027 | 2008 | 10 | 28 | 1 | 11736.4491
2027 | 2008 | 10 | 28 | 2 | 12316.9537
2027 | 2008 | 10 | 28 | 3 | 12884.3122
2027 | 2008 | 10 | 28 | 4 | 13321.2152
2027 | 2008 | 10 | 28 | 5 | 14356.4396
2027 | 2008 | 10 | 28 | 6 | 15585.7001
2027 | 2008 | 10 | 28 | 7 | 16816.3586
2027 | 2008 | 10 | 28 | 8 | 17123.5217
2027 | 2008 | 10 | 28 | 9 | 15802.7263
2027 | 2008 | 10 | 28 | 10 | 9708.3467
2027 | 2008 | 10 | 28 | 11 | 10330.419
2027 | 2008 | 10 | 28 | 12 | 11341.5558
2027 | 2008 | 10 | 28 | 13 | 10667.0528
2027 | 2008 | 10 | 28 | 14 | 10149.5586
2027 | 2008 | 10 | 28 | 15 | 10280.473
2027 | 2008 | 10 | 28 | 16 | 10492.7882
2027 | 2008 | 10 | 28 | 17 | 10768.4367
2027 | 2008 | 10 | 28 | 18 | 11840.7855
2027 | 2008 | 10 | 28 | 19 | 15613.9454
2027 | 2008 | 10 | 28 | 20 | 20064.5187
2027 | 2008 | 10 | 28 | 21 | 24167.5624
2027 | 2008 | 10 | 28 | 22 | 25718.5279
2027 | 2008 | 10 | 28 | 23 | 25994.6545
2027 | 2008 | 10 | 28 | 24 | 26217.9817
2027 | 2008 | 10 | 29 | 1 | 26216.1018
2027 | 2008 | 10 | 29 | 2 | 25751.4843
2027 | 2008 | 10 | 29 | 3 | 25123.3129
2027 | 2008 | 10 | 29 | 4 | 24110.6627
2027 | 2008 | 10 | 29 | 5 | 23037.3984
2027 | 2008 | 10 | 29 | 6 | 21613.3455
2027 | 2008 | 10 | 29 | 7 | 20248.5432
2027 | 2008 | 10 | 29 | 8 | 18445.2638
2027 | 2008 | 10 | 29 | 9 | 15287.11
2027 | 2008 | 10 | 29 | 10 | 9718.0846
2027 | 2008 | 10 | 29 | 11 | 9509.8063
2027 | 2008 | 10 | 29 | 12 | 8991.4098
2027 | 2008 | 10 | 29 | 13 | 8221.7835
2027 | 2008 | 10 | 29 | 14 | 7841.3935
2027 | 2008 | 10 | 29 | 15 | 7949.2513
2027 | 2008 | 10 | 29 | 16 | 8349.5905
2027 | 2008 | 10 | 29 | 17 | 8760.2557
2027 | 2008 | 10 | 29 | 18 | 9977.3172
2027 | 2008 | 10 | 29 | 19 | 12865.0331
2027 | 2008 | 10 | 29 | 20 | 17836.8177
2027 | 2008 | 10 | 29 | 21 | 23645.4993
2027 | 2008 | 10 | 29 | 22 | 27031.4303
2027 | 2008 | 10 | 29 | 23 | 28508.0481
2027 | 2008 | 10 | 29 | 24 | 29241.2177
2027 | 2008 | 10 | 30 | 1 | 29532.2363
2027 | 2008 | 10 | 30 | 2 | 29144.2881
2027 | 2008 | 10 | 30 | 3 | 28838.6046
2027 | 2008 | 10 | 30 | 4 | 28437.5075
2027 | 2008 | 10 | 30 | 5 | 28310.0891
2027 | 2008 | 10 | 30 | 6 | 25279.6437
2027 | 2008 | 10 | 30 | 7 | 25008.6428
2027 | 2008 | 10 | 30 | 8 | 24172.9949
2027 | 2008 | 10 | 30 | 9 | 21970.6246
2027 | 2008 | 10 | 30 | 10 | 19844.5819
2027 | 2008 | 10 | 30 | 11 | 18767.6737
2027 | 2008 | 10 | 30 | 12 | 19074.6008
2027 | 2008 | 10 | 30 | 13 | 18647.6874
2027 | 2008 | 10 | 30 | 14 | 19325.4852
2027 | 2008 | 10 | 30 | 15 | 19795.0838
2027 | 2008 | 10 | 30 | 16 | 19576.8604
2027 | 2008 | 10 | 30 | 17 | 19080.6343
2027 | 2008 | 10 | 30 | 18 | 19271.0804
2027 | 2008 | 10 | 30 | 19 | 22211.2022
2027 | 2008 | 10 | 30 | 20 | 25127.7897
2027 | 2008 | 10 | 30 | 21 | 26833.2312
2027 | 2008 | 10 | 30 | 22 | 26529.8397
2027 | 2008 | 10 | 30 | 23 | 26525.4739
2027 | 2008 | 10 | 30 | 24 | 29105.2863
2027 | 2008 | 10 | 31 | 1 | 27962.0861
2027 | 2008 | 10 | 31 | 2 | 26846.2373
2027 | 2008 | 10 | 31 | 3 | 25709.2261
2027 | 2008 | 10 | 31 | 4 | 24462.2031
2027 | 2008 | 10 | 31 | 5 | 22128.0465
2027 | 2008 | 10 | 31 | 6 | 20441.7901
2027 | 2008 | 10 | 31 | 7 | 18068.5316
2027 | 2008 | 10 | 31 | 8 | 16364.0359
2027 | 2008 | 10 | 31 | 9 | 13343.175
2027 | 2008 | 10 | 31 | 10 | 13223.6351
2027 | 2008 | 10 | 31 | 11 | 12708.4181
2027 | 2008 | 10 | 31 | 12 | 11312.9114
2027 | 2008 | 10 | 31 | 13 | 10217.111
2027 | 2008 | 10 | 31 | 14 | 8795.2467
2027 | 2008 | 10 | 31 | 15 | 7423.7185
2027 | 2008 | 10 | 31 | 16 | 5814.6051
2027 | 2008 | 10 | 31 | 17 | 5086.8127
2027 | 2008 | 10 | 31 | 18 | 5285.8673
2027 | 2008 | 10 | 31 | 19 | 8285.7459
2027 | 2008 | 10 | 31 | 20 | 10588.9004
2027 | 2008 | 10 | 31 | 21 | 12657.5852
2027 | 2008 | 10 | 31 | 22 | 14145.58
2027 | 2008 | 10 | 31 | 23 | 14533.6227
2027 | 2008 | 10 | 31 | 24 | 14356.325
2028 | 2008 | 10 | 1 | 1 | 6636.2232
2028 | 2008 | 10 | 1 | 2 | 6793.4699
2028 | 2008 | 10 | 1 | 3 | 6483.7449
2028 | 2008 | 10 | 1 | 4 | 6866.2229
2028 | 2008 | 10 | 1 | 5 | 6913.4056
2028 | 2008 | 10 | 1 | 6 | 6030.0329
2028 | 2008 | 10 | 1 | 7 | 5354.816
2028 | 2008 | 10 | 1 | 8 | 4531.3852
2028 | 2008 | 10 | 1 | 9 | 3619.7301
2028 | 2008 | 10 | 1 | 10 | 1724.774
2028 | 2008 | 10 | 1 | 11 | 1825.7456
2028 | 2008 | 10 | 1 | 12 | 1646.1095
2028 | 2008 | 10 | 1 | 13 | 1611.5497
2028 | 2008 | 10 | 1 | 14 | 1538.4372
2028 | 2008 | 10 | 1 | 15 | 1330.7201
2028 | 2008 | 10 | 1 | 16 | 1156.9454
2028 | 2008 | 10 | 1 | 17 | 1143.4801
2028 | 2008 | 10 | 1 | 18 | 1696.7147
2028 | 2008 | 10 | 1 | 19 | 3998.0427
2028 | 2008 | 10 | 1 | 20 | 4455.5466
2028 | 2008 | 10 | 1 | 21 | 5943.1331
2028 | 2008 | 10 | 1 | 22 | 8190.8845
2028 | 2008 | 10 | 1 | 23 | 9035.999
2028 | 2008 | 10 | 1 | 24 | 9095.889
2028 | 2008 | 10 | 2 | 1 | 9080.3685
2028 | 2008 | 10 | 2 | 2 | 9585.8682
2028 | 2008 | 10 | 2 | 3 | 9923.3821
2028 | 2008 | 10 | 2 | 4 | 9987.3566
2028 | 2008 | 10 | 2 | 5 | 9629.0262
2028 | 2008 | 10 | 2 | 6 | 8790.8909
2028 | 2008 | 10 | 2 | 7 | 8605.9336
2028 | 2008 | 10 | 2 | 8 | 7262.5895
2028 | 2008 | 10 | 2 | 9 | 6117.0074
2028 | 2008 | 10 | 2 | 10 | 3634.0899
2028 | 2008 | 10 | 2 | 11 | 4498.781
2028 | 2008 | 10 | 2 | 12 | 4092.8002
2028 | 2008 | 10 | 2 | 13 | 3917.1993
2028 | 2008 | 10 | 2 | 14 | 4034.2207
2028 | 2008 | 10 | 2 | 15 | 4414.9342
2028 | 2008 | 10 | 2 | 16 | 4578.8078
2028 | 2008 | 10 | 2 | 17 | 5151.2776
2028 | 2008 | 10 | 2 | 18 | 6439.3635
2028 | 2008 | 10 | 2 | 19 | 8884.4476
2028 | 2008 | 10 | 2 | 20 | 12713.7602
2028 | 2008 | 10 | 2 | 21 | 17558.6533
2028 | 2008 | 10 | 2 | 22 | 21363.5713
2028 | 2008 | 10 | 2 | 23 | 23952.398
2028 | 2008 | 10 | 2 | 24 | 26162.6489
2028 | 2008 | 10 | 3 | 1 | 26985.9552
2028 | 2008 | 10 | 3 | 2 | 27219.6708
2028 | 2008 | 10 | 3 | 3 | 27629.214
2028 | 2008 | 10 | 3 | 4 | 27645.7884
2028 | 2008 | 10 | 3 | 5 | 26789.6976
2028 | 2008 | 10 | 3 | 6 | 26286.1544
2028 | 2008 | 10 | 3 | 7 | 25205.9229
2028 | 2008 | 10 | 3 | 8 | 22831.5824
2028 | 2008 | 10 | 3 | 9 | 19071.7801
2028 | 2008 | 10 | 3 | 10 | 13769.7881
2028 | 2008 | 10 | 3 | 11 | 15050.6593
2028 | 2008 | 10 | 3 | 12 | 16339.2649
2028 | 2008 | 10 | 3 | 13 | 17090.7658
2028 | 2008 | 10 | 3 | 14 | 18273.7877
2028 | 2008 | 10 | 3 | 15 | 19788.9793
2028 | 2008 | 10 | 3 | 16 | 20276.8318
2028 | 2008 | 10 | 3 | 17 | 21749.9702
2028 | 2008 | 10 | 3 | 18 | 22604.3417
2028 | 2008 | 10 | 3 | 19 | 24800.7222
2028 | 2008 | 10 | 3 | 20 | 30017.705
2028 | 2008 | 10 | 3 | 21 | 32769.5982
2028 | 2008 | 10 | 3 | 22 | 33165.3963
2028 | 2008 | 10 | 3 | 23 | 32555.9914
2028 | 2008 | 10 | 3 | 24 | 32749.5815
2028 | 2008 | 10 | 4 | 1 | 32843.657
2028 | 2008 | 10 | 4 | 2 | 33037.0746
2028 | 2008 | 10 | 4 | 3 | 33145.3367
2028 | 2008 | 10 | 4 | 4 | 32608.1021
2028 | 2008 | 10 | 4 | 5 | 32119.1617
2028 | 2008 | 10 | 4 | 6 | 31185.3152
2028 | 2008 | 10 | 4 | 7 | 30873.1136
2028 | 2008 | 10 | 4 | 8 | 28905.0047
2028 | 2008 | 10 | 4 | 9 | 25565.9554
2028 | 2008 | 10 | 4 | 10 | 26552.2365
2028 | 2008 | 10 | 4 | 11 | 29408.2476
2028 | 2008 | 10 | 4 | 12 | 30080.7068
2028 | 2008 | 10 | 4 | 13 | 31026.9196
2028 | 2008 | 10 | 4 | 14 | 31994.4781
2028 | 2008 | 10 | 4 | 15 | 33309.458
2028 | 2008 | 10 | 4 | 16 | 34530.4664
2028 | 2008 | 10 | 4 | 17 | 35005.9899
2028 | 2008 | 10 | 4 | 18 | 35305.9884
2028 | 2008 | 10 | 4 | 19 | 34637.9188
2028 | 2008 | 10 | 4 | 20 | 34953.149
2028 | 2008 | 10 | 4 | 21 | 34938.2398
2028 | 2008 | 10 | 4 | 22 | 34805.1718
2028 | 2008 | 10 | 4 | 23 | 34699.8052
2028 | 2008 | 10 | 4 | 24 | 34368.1426
2028 | 2008 | 10 | 5 | 1 | 34174.5426
2028 | 2008 | 10 | 5 | 2 | 33971.0747
2028 | 2008 | 10 | 5 | 3 | 33452.8352
2028 | 2008 | 10 | 5 | 4 | 33155.96
2028 | 2008 | 10 | 5 | 5 | 32643.9014
2028 | 2008 | 10 | 5 | 6 | 32202.964
2028 | 2008 | 10 | 5 | 7 | 31171.2294
2028 | 2008 | 10 | 5 | 8 | 29058.9486
2028 | 2008 | 10 | 5 | 9 | 25585.6209
2028 | 2008 | 10 | 5 | 10 | 29779.1466
2028 | 2008 | 10 | 5 | 11 | 32788.6498
2028 | 2008 | 10 | 5 | 12 | 33012.0544
2028 | 2008 | 10 | 5 | 13 | 33651.832
2028 | 2008 | 10 | 5 | 14 | 32801.242
2028 | 2008 | 10 | 5 | 15 | 33240.3498
2028 | 2008 | 10 | 5 | 16 | 32782.6488
2028 | 2008 | 10 | 5 | 17 | 32979.9046
2028 | 2008 | 10 | 5 | 18 | 32847.159
2028 | 2008 | 10 | 5 | 19 | 31566.926
2028 | 2008 | 10 | 5 | 20 | 31817.0012
2028 | 2008 | 10 | 5 | 21 | 31620.9795
2028 | 2008 | 10 | 5 | 22 | 29882.8652
2028 | 2008 | 10 | 5 | 23 | 29998.6165
2028 | 2008 | 10 | 5 | 24 | 28672.9732
2028 | 2008 | 10 | 6 | 1 | 28486.3132
2028 | 2008 | 10 | 6 | 2 | 28964.5578
2028 | 2008 | 10 | 6 | 3 | 28331.1296
2028 | 2008 | 10 | 6 | 4 | 28278.2596
2028 | 2008 | 10 | 6 | 5 | 28361.5613
2028 | 2008 | 10 | 6 | 6 | 26868.8036
2028 | 2008 | 10 | 6 | 7 | 25955.748
2028 | 2008 | 10 | 6 | 8 | 24408.5645
2028 | 2008 | 10 | 6 | 9 | 21792.6141
2028 | 2008 | 10 | 6 | 10 | 25125.4537
2028 | 2008 | 10 | 6 | 11 | 26308.0448
2028 | 2008 | 10 | 6 | 12 | 25703.8826
2028 | 2008 | 10 | 6 | 13 | 24552.6439
2028 | 2008 | 10 | 6 | 14 | 23011.2525
2028 | 2008 | 10 | 6 | 15 | 21511.015
2028 | 2008 | 10 | 6 | 16 | 19656.5522
2028 | 2008 | 10 | 6 | 17 | 16349.6608
2028 | 2008 | 10 | 6 | 18 | 13131.0145
2028 | 2008 | 10 | 6 | 19 | 11338.3427
2028 | 2008 | 10 | 6 | 20 | 13618.4599
2028 | 2008 | 10 | 6 | 21 | 16402.8198
2028 | 2008 | 10 | 6 | 22 | 18232.4803
2028 | 2008 | 10 | 6 | 23 | 16596.881
2028 | 2008 | 10 | 6 | 24 | 16476.0671
2028 | 2008 | 10 | 7 | 1 | 16272.5699
2028 | 2008 | 10 | 7 | 2 | 17106.7619
2028 | 2008 | 10 | 7 | 3 | 17591.0457
2028 | 2008 | 10 | 7 | 4 | 18510.0566
2028 | 2008 | 10 | 7 | 5 | 19176.2403
2028 | 2008 | 10 | 7 | 6 | 19341.3748
2028 | 2008 | 10 | 7 | 7 | 20139.9046
2028 | 2008 | 10 | 7 | 8 | 19560.6969
2028 | 2008 | 10 | 7 | 9 | 17395.0498
2028 | 2008 | 10 | 7 | 10 | 16246.5536
2028 | 2008 | 10 | 7 | 11 | 18834.3255
2028 | 2008 | 10 | 7 | 12 | 17959.6473
2028 | 2008 | 10 | 7 | 13 | 17142.9977
2028 | 2008 | 10 | 7 | 14 | 16812.4634
2028 | 2008 | 10 | 7 | 15 | 17118.5706
2028 | 2008 | 10 | 7 | 16 | 15582.3342
2028 | 2008 | 10 | 7 | 17 | 14142.8114
2028 | 2008 | 10 | 7 | 18 | 11094.3598
2028 | 2008 | 10 | 7 | 19 | 8240.3517
2028 | 2008 | 10 | 7 | 20 | 7062.6741
2028 | 2008 | 10 | 7 | 21 | 6595.226
2028 | 2008 | 10 | 7 | 22 | 6974.9855
2028 | 2008 | 10 | 7 | 23 | 7684.7843
2028 | 2008 | 10 | 7 | 24 | 8551.7026
2028 | 2008 | 10 | 8 | 1 | 10408.2141
2028 | 2008 | 10 | 8 | 2 | 12234.4119
2028 | 2008 | 10 | 8 | 3 | 14693.2931
2028 | 2008 | 10 | 8 | 4 | 16249.2589
2028 | 2008 | 10 | 8 | 5 | 17360.7347
2028 | 2008 | 10 | 8 | 6 | 16361.8875
2028 | 2008 | 10 | 8 | 7 | 16710.698
2028 | 2008 | 10 | 8 | 8 | 15632.5987
2028 | 2008 | 10 | 8 | 9 | 13610.5338
2028 | 2008 | 10 | 8 | 10 | 8598.9305
2028 | 2008 | 10 | 8 | 11 | 8380.8948
2028 | 2008 | 10 | 8 | 12 | 8289.6149
2028 | 2008 | 10 | 8 | 13 | 7503.7602
2028 | 2008 | 10 | 8 | 14 | 6557.1002
2028 | 2008 | 10 | 8 | 15 | 6044.1197
2028 | 2008 | 10 | 8 | 16 | 5658.4177
2028 | 2008 | 10 | 8 | 17 | 5435.6459
2028 | 2008 | 10 | 8 | 18 | 5944.0706
2028 | 2008 | 10 | 8 | 19 | 7840.4477
2028 | 2008 | 10 | 8 | 20 | 11313.7184
2028 | 2008 | 10 | 8 | 21 | 16716.1772
2028 | 2008 | 10 | 8 | 22 | 20613.0756
2028 | 2008 | 10 | 8 | 23 | 22992.8495
2028 | 2008 | 10 | 8 | 24 | 24743.2404
2028 | 2008 | 10 | 9 | 1 | 24343.9233
2028 | 2008 | 10 | 9 | 2 | 23730.5978
2028 | 2008 | 10 | 9 | 3 | 23078.8943
2028 | 2008 | 10 | 9 | 4 | 22214.8436
2028 | 2008 | 10 | 9 | 5 | 21482.4987
2028 | 2008 | 10 | 9 | 6 | 21319.0943
2028 | 2008 | 10 | 9 | 7 | 20785.2345
2028 | 2008 | 10 | 9 | 8 | 19998.4086
2028 | 2008 | 10 | 9 | 9 | 17397.799
2028 | 2008 | 10 | 9 | 10 | 11262.1837
2028 | 2008 | 10 | 9 | 11 | 14342.2201
2028 | 2008 | 10 | 9 | 12 | 18301.2486
2028 | 2008 | 10 | 9 | 13 | 19702.4202
2028 | 2008 | 10 | 9 | 14 | 20695.7468
2028 | 2008 | 10 | 9 | 15 | 21142.3444
2028 | 2008 | 10 | 9 | 16 | 21933.7523
2028 | 2008 | 10 | 9 | 17 | 21772.6966
2028 | 2008 | 10 | 9 | 18 | 22202.2442
2028 | 2008 | 10 | 9 | 19 | 24678.6338
2028 | 2008 | 10 | 9 | 20 | 28589.0874
2028 | 2008 | 10 | 9 | 21 | 31104.19
2028 | 2008 | 10 | 9 | 22 | 31348.1021
2028 | 2008 | 10 | 9 | 23 | 31375.667
2028 | 2008 | 10 | 9 | 24 | 31151.3908
2028 | 2008 | 10 | 10 | 1 | 30646.1571
2028 | 2008 | 10 | 10 | 2 | 30423.2333
2028 | 2008 | 10 | 10 | 3 | 30250.6349
2028 | 2008 | 10 | 10 | 4 | 29697.3939
2028 | 2008 | 10 | 10 | 5 | 29476.5994
2028 | 2008 | 10 | 10 | 6 | 29338.4242
2028 | 2008 | 10 | 10 | 7 | 28767.4306
2028 | 2008 | 10 | 10 | 8 | 26931.36
2028 | 2008 | 10 | 10 | 9 | 23141.4125
2028 | 2008 | 10 | 10 | 10 | 20395.268
2028 | 2008 | 10 | 10 | 11 | 21698.1625
2028 | 2008 | 10 | 10 | 12 | 21161.3427
2028 | 2008 | 10 | 10 | 13 | 21277.5099
2028 | 2008 | 10 | 10 | 14 | 21827.2178
2028 | 2008 | 10 | 10 | 15 | 22518.5884
2028 | 2008 | 10 | 10 | 16 | 23610.5225
2028 | 2008 | 10 | 10 | 17 | 24576.6922
2028 | 2008 | 10 | 10 | 18 | 26096.7526
2028 | 2008 | 10 | 10 | 19 | 28338.1911
2028 | 2008 | 10 | 10 | 20 | 31214.3354
2028 | 2008 | 10 | 10 | 21 | 32920.218
2028 | 2008 | 10 | 10 | 22 | 33029.1016
2028 | 2008 | 10 | 10 | 23 | 32319.6562
2028 | 2008 | 10 | 10 | 24 | 31429.9986
2028 | 2008 | 10 | 11 | 1 | 30858.7131
2028 | 2008 | 10 | 11 | 2 | 29821.0669
2028 | 2008 | 10 | 11 | 3 | 29149.1316
2028 | 2008 | 10 | 11 | 4 | 27848.6466
2028 | 2008 | 10 | 11 | 5 | 26569.2669
2028 | 2008 | 10 | 11 | 6 | 24749.4475
2028 | 2008 | 10 | 11 | 7 | 22745.3062
2028 | 2008 | 10 | 11 | 8 | 20677.784
2028 | 2008 | 10 | 11 | 9 | 17312.5001
2028 | 2008 | 10 | 11 | 10 | 18658.8236
2028 | 2008 | 10 | 11 | 11 | 20106.7748
2028 | 2008 | 10 | 11 | 12 | 20732.533
2028 | 2008 | 10 | 11 | 13 | 22602.1238
2028 | 2008 | 10 | 11 | 14 | 24291.35
2028 | 2008 | 10 | 11 | 15 | 27053.9644
2028 | 2008 | 10 | 11 | 16 | 29439.2259
2028 | 2008 | 10 | 11 | 17 | 30490.0832
2028 | 2008 | 10 | 11 | 18 | 32389.8128
2028 | 2008 | 10 | 11 | 19 | 32321.1524
2028 | 2008 | 10 | 11 | 20 | 33487.644
2028 | 2008 | 10 | 11 | 21 | 34046.0167
2028 | 2008 | 10 | 11 | 22 | 33640.1325
2028 | 2008 | 10 | 11 | 23 | 33605.3364
2028 | 2008 | 10 | 11 | 24 | 32981.6607
2028 | 2008 | 10 | 12 | 1 | 32873.9419
2028 | 2008 | 10 | 12 | 2 | 32888.4865
2028 | 2008 | 10 | 12 | 3 | 32932.0062
2028 | 2008 | 10 | 12 | 4 | 32639.2466
2028 | 2008 | 10 | 12 | 5 | 31496.1083
2028 | 2008 | 10 | 12 | 6 | 31217.3903
2028 | 2008 | 10 | 12 | 7 | 30385.1539
2028 | 2008 | 10 | 12 | 8 | 28792.2181
2028 | 2008 | 10 | 12 | 9 | 25913.9878
2028 | 2008 | 10 | 12 | 10 | 30733.45
2028 | 2008 | 10 | 12 | 11 | 32435.9666
2028 | 2008 | 10 | 12 | 12 | 32720.4442
2028 | 2008 | 10 | 12 | 13 | 33771.9044
2028 | 2008 | 10 | 12 | 14 | 34014.0343
2028 | 2008 | 10 | 12 | 15 | 34233.7234
2028 | 2008 | 10 | 12 | 16 | 34381.5178
2028 | 2008 | 10 | 12 | 17 | 32965.4316
2028 | 2008 | 10 | 12 | 18 | 31686.4273
2028 | 2008 | 10 | 12 | 19 | 30421.284
2028 | 2008 | 10 | 12 | 20 | 31810.0858
2028 | 2008 | 10 | 12 | 21 | 32746.0408
2028 | 2008 | 10 | 12 | 22 | 32937.708
2028 | 2008 | 10 | 12 | 23 | 32317.2616
2028 | 2008 | 10 | 12 | 24 | 31925.7104
2028 | 2008 | 10 | 13 | 1 | 29751.4283
2028 | 2008 | 10 | 13 | 2 | 27873.1903
2028 | 2008 | 10 | 13 | 3 | 25846.3967
2028 | 2008 | 10 | 13 | 4 | 23897.8702
2028 | 2008 | 10 | 13 | 5 | 22144.7231
2028 | 2008 | 10 | 13 | 6 | 21193.7859
2028 | 2008 | 10 | 13 | 7 | 20450.4339
2028 | 2008 | 10 | 13 | 8 | 20003.6423
2028 | 2008 | 10 | 13 | 9 | 18327.9783
2028 | 2008 | 10 | 13 | 10 | 21951.9939
2028 | 2008 | 10 | 13 | 11 | 22765.9084
2028 | 2008 | 10 | 13 | 12 | 21470.7789
2028 | 2008 | 10 | 13 | 13 | 20359.0684
2028 | 2008 | 10 | 13 | 14 | 19555.881
2028 | 2008 | 10 | 13 | 15 | 18781.3671
2028 | 2008 | 10 | 13 | 16 | 18202.0795
2028 | 2008 | 10 | 13 | 17 | 18767.7119
2028 | 2008 | 10 | 13 | 18 | 20179.6468
2028 | 2008 | 10 | 13 | 19 | 21015.2647
2028 | 2008 | 10 | 13 | 20 | 21752.2441
2028 | 2008 | 10 | 13 | 21 | 22379.5368
2028 | 2008 | 10 | 13 | 22 | 21883.6698
2028 | 2008 | 10 | 13 | 23 | 20332.205
2028 | 2008 | 10 | 13 | 24 | 18742.2216
2028 | 2008 | 10 | 14 | 1 | 16169.6667
2028 | 2008 | 10 | 14 | 2 | 14926.1223
2028 | 2008 | 10 | 14 | 3 | 13768.0336
2028 | 2008 | 10 | 14 | 4 | 11991.6652
2028 | 2008 | 10 | 14 | 5 | 10082.364
2028 | 2008 | 10 | 14 | 6 | 8237.4412
2028 | 2008 | 10 | 14 | 7 | 7293.9482
2028 | 2008 | 10 | 14 | 8 | 6391.1276
2028 | 2008 | 10 | 14 | 9 | 5035.346
2028 | 2008 | 10 | 14 | 10 | 6153.4475
2028 | 2008 | 10 | 14 | 11 | 6457.3403
2028 | 2008 | 10 | 14 | 12 | 6815.8122
2028 | 2008 | 10 | 14 | 13 | 7446.0604
2028 | 2008 | 10 | 14 | 14 | 8503.8489
2028 | 2008 | 10 | 14 | 15 | 9553.0819
2028 | 2008 | 10 | 14 | 16 | 9996.94
2028 | 2008 | 10 | 14 | 17 | 9475.8497
2028 | 2008 | 10 | 14 | 18 | 9194.8467
2028 | 2008 | 10 | 14 | 19 | 9254.3158
2028 | 2008 | 10 | 14 | 20 | 9171.3578
2028 | 2008 | 10 | 14 | 21 | 10002.0722
2028 | 2008 | 10 | 14 | 22 | 9395.6839
2028 | 2008 | 10 | 14 | 23 | 8185.1805
2028 | 2008 | 10 | 14 | 24 | 7168.4418
2028 | 2008 | 10 | 15 | 1 | 6968.6606
2028 | 2008 | 10 | 15 | 2 | 7882.2761
2028 | 2008 | 10 | 15 | 3 | 8574.6774
2028 | 2008 | 10 | 15 | 4 | 9687.3319
2028 | 2008 | 10 | 15 | 5 | 10594.6191
2028 | 2008 | 10 | 15 | 6 | 11044.1699
2028 | 2008 | 10 | 15 | 7 | 11814.3701
2028 | 2008 | 10 | 15 | 8 | 11536.6356
2028 | 2008 | 10 | 15 | 9 | 10006.263
2028 | 2008 | 10 | 15 | 10 | 11880.1727
2028 | 2008 | 10 | 15 | 11 | 12204.8834
2028 | 2008 | 10 | 15 | 12 | 10657.8259
2028 | 2008 | 10 | 15 | 13 | 9622.6087
2028 | 2008 | 10 | 15 | 14 | 10297.7629
2028 | 2008 | 10 | 15 | 15 | 11300.565
2028 | 2008 | 10 | 15 | 16 | 12234.2706
2028 | 2008 | 10 | 15 | 17 | 12896.4871
2028 | 2008 | 10 | 15 | 18 | 12522.298
2028 | 2008 | 10 | 15 | 19 | 13022.6742
2028 | 2008 | 10 | 15 | 20 | 14369.6505
2028 | 2008 | 10 | 15 | 21 | 15757.4019
2028 | 2008 | 10 | 15 | 22 | 15169.9999
2028 | 2008 | 10 | 15 | 23 | 13601.5389
2028 | 2008 | 10 | 15 | 24 | 13542.8744
2028 | 2008 | 10 | 16 | 1 | 13331.4755
2028 | 2008 | 10 | 16 | 2 | 14007.3989
2028 | 2008 | 10 | 16 | 3 | 14800.0809
2028 | 2008 | 10 | 16 | 4 | 16017.864
2028 | 2008 | 10 | 16 | 5 | 15789.3524
2028 | 2008 | 10 | 16 | 6 | 16412.6229
2028 | 2008 | 10 | 16 | 7 | 16664.2289
2028 | 2008 | 10 | 16 | 8 | 16738.5449
2028 | 2008 | 10 | 16 | 9 | 15186.5292
2028 | 2008 | 10 | 16 | 10 | 19063.9562
2028 | 2008 | 10 | 16 | 11 | 19271.0208
2028 | 2008 | 10 | 16 | 12 | 17423.0099
2028 | 2008 | 10 | 16 | 13 | 15383.0557
2028 | 2008 | 10 | 16 | 14 | 13535.2548
2028 | 2008 | 10 | 16 | 15 | 12311.3962
2028 | 2008 | 10 | 16 | 16 | 10776.7633
2028 | 2008 | 10 | 16 | 17 | 8770.1939
2028 | 2008 | 10 | 16 | 18 | 7182.3006
2028 | 2008 | 10 | 16 | 19 | 5940.8291
2028 | 2008 | 10 | 16 | 20 | 5629.8273
2028 | 2008 | 10 | 16 | 21 | 5594.0475
2028 | 2008 | 10 | 16 | 22 | 5586.1886
2028 | 2008 | 10 | 16 | 23 | 5346.331
2028 | 2008 | 10 | 16 | 24 | 5255.132
2028 | 2008 | 10 | 17 | 1 | 5304.2221
2028 | 2008 | 10 | 17 | 2 | 5364.6763
2028 | 2008 | 10 | 17 | 3 | 5638.9368
2028 | 2008 | 10 | 17 | 4 | 6318.1394
2028 | 2008 | 10 | 17 | 5 | 6970.7263
2028 | 2008 | 10 | 17 | 6 | 7108.0736
2028 | 2008 | 10 | 17 | 7 | 6934.5469
2028 | 2008 | 10 | 17 | 8 | 5802.4165
2028 | 2008 | 10 | 17 | 9 | 5449.9412
2028 | 2008 | 10 | 17 | 10 | 5593.4309
2028 | 2008 | 10 | 17 | 11 | 5358.7296
2028 | 2008 | 10 | 17 | 12 | 5415.4463
2028 | 2008 | 10 | 17 | 13 | 5117.9643
2028 | 2008 | 10 | 17 | 14 | 4935.5525
2028 | 2008 | 10 | 17 | 15 | 4610.8115
2028 | 2008 | 10 | 17 | 16 | 4065.6349
2028 | 2008 | 10 | 17 | 17 | 3472.2908
2028 | 2008 | 10 | 17 | 18 | 3213.8655
2028 | 2008 | 10 | 17 | 19 | 3143.4217
2028 | 2008 | 10 | 17 | 20 | 2863.9419
2028 | 2008 | 10 | 17 | 21 | 2769.747
2028 | 2008 | 10 | 17 | 22 | 2814.9044
2028 | 2008 | 10 | 17 | 23 | 2988.8934
2028 | 2008 | 10 | 17 | 24 | 3592.0465
2028 | 2008 | 10 | 18 | 1 | 3745.3167
2028 | 2008 | 10 | 18 | 2 | 4233.2594
2028 | 2008 | 10 | 18 | 3 | 4439.5502
2028 | 2008 | 10 | 18 | 4 | 4907.8552
2028 | 2008 | 10 | 18 | 5 | 5274.6092
2028 | 2008 | 10 | 18 | 6 | 5853.3442
2028 | 2008 | 10 | 18 | 7 | 6444.7787
2028 | 2008 | 10 | 18 | 8 | 5447.7732
2028 | 2008 | 10 | 18 | 9 | 4411.466
2028 | 2008 | 10 | 18 | 10 | 4436.9981
2028 | 2008 | 10 | 18 | 11 | 4702.9578
2028 | 2008 | 10 | 18 | 12 | 5485.9235
2028 | 2008 | 10 | 18 | 13 | 6051.8433
2028 | 2008 | 10 | 18 | 14 | 6810.6533
2028 | 2008 | 10 | 18 | 15 | 7501.5381
2028 | 2008 | 10 | 18 | 16 | 7642.6826
2028 | 2008 | 10 | 18 | 17 | 7475.9927
2028 | 2008 | 10 | 18 | 18 | 7400.8326
2028 | 2008 | 10 | 18 | 19 | 7914.2225
2028 | 2008 | 10 | 18 | 20 | 9687.7024
2028 | 2008 | 10 | 18 | 21 | 11407.7128
2028 | 2008 | 10 | 18 | 22 | 13290.4126
2028 | 2008 | 10 | 18 | 23 | 14862.0414
2028 | 2008 | 10 | 18 | 24 | 16988.9361
2028 | 2008 | 10 | 19 | 1 | 19189.1522
2028 | 2008 | 10 | 19 | 2 | 20363.8579
2028 | 2008 | 10 | 19 | 3 | 20895.2608
2028 | 2008 | 10 | 19 | 4 | 20771.4955
2028 | 2008 | 10 | 19 | 5 | 20398.4598
2028 | 2008 | 10 | 19 | 6 | 20327.713
2028 | 2008 | 10 | 19 | 7 | 19513.6896
2028 | 2008 | 10 | 19 | 8 | 18993.896
2028 | 2008 | 10 | 19 | 9 | 16891.8242
2028 | 2008 | 10 | 19 | 10 | 10603.4147
2028 | 2008 | 10 | 19 | 11 | 13364.6137
2028 | 2008 | 10 | 19 | 12 | 14657.5248
2028 | 2008 | 10 | 19 | 13 | 13782.1656
2028 | 2008 | 10 | 19 | 14 | 13108.825
2028 | 2008 | 10 | 19 | 15 | 13234.9373
2028 | 2008 | 10 | 19 | 16 | 13302.7883
2028 | 2008 | 10 | 19 | 17 | 13158.6456
2028 | 2008 | 10 | 19 | 18 | 12982.656
2028 | 2008 | 10 | 19 | 19 | 15883.4019
2028 | 2008 | 10 | 19 | 20 | 20578.7706
2028 | 2008 | 10 | 19 | 21 | 25235.5279
2028 | 2008 | 10 | 19 | 22 | 27323.3048
2028 | 2008 | 10 | 19 | 23 | 27365.7136
2028 | 2008 | 10 | 19 | 24 | 27196.8756
2028 | 2008 | 10 | 20 | 1 | 26979.5006
2028 | 2008 | 10 | 20 | 2 | 26364.7421
2028 | 2008 | 10 | 20 | 3 | 25006.738
2028 | 2008 | 10 | 20 | 4 | 23813.7072
2028 | 2008 | 10 | 20 | 5 | 21579.1406
2028 | 2008 | 10 | 20 | 6 | 19873.0259
2028 | 2008 | 10 | 20 | 7 | 18455.1868
2028 | 2008 | 10 | 20 | 8 | 16348.1822
2028 | 2008 | 10 | 20 | 9 | 12769.8174
2028 | 2008 | 10 | 20 | 10 | 7008.6383
2028 | 2008 | 10 | 20 | 11 | 6159.4851
2028 | 2008 | 10 | 20 | 12 | 4933.9208
2028 | 2008 | 10 | 20 | 13 | 3904.4137
2028 | 2008 | 10 | 20 | 14 | 3495.7008
2028 | 2008 | 10 | 20 | 15 | 3551.0557
2028 | 2008 | 10 | 20 | 16 | 3764.0401
2028 | 2008 | 10 | 20 | 17 | 4054.8647
2028 | 2008 | 10 | 20 | 18 | 5415.6701
2028 | 2008 | 10 | 20 | 19 | 8490.6097
2028 | 2008 | 10 | 20 | 20 | 11467.6515
2028 | 2008 | 10 | 20 | 21 | 15181.0564
2028 | 2008 | 10 | 20 | 22 | 16552.3494
2028 | 2008 | 10 | 20 | 23 | 17000.1165
2028 | 2008 | 10 | 20 | 24 | 16153.3408
2028 | 2008 | 10 | 21 | 1 | 15237.1291
2028 | 2008 | 10 | 21 | 2 | 14505.1054
2028 | 2008 | 10 | 21 | 3 | 13918.4698
2028 | 2008 | 10 | 21 | 4 | 12548.7998
2028 | 2008 | 10 | 21 | 5 | 10589.9998
2028 | 2008 | 10 | 21 | 6 | 9244.1797
2028 | 2008 | 10 | 21 | 7 | 5925.6009
2028 | 2008 | 10 | 21 | 8 | 6617.6096
2028 | 2008 | 10 | 21 | 9 | 5629.211
2028 | 2008 | 10 | 21 | 10 | 5088.0931
2028 | 2008 | 10 | 21 | 11 | 6114.0866
2028 | 2008 | 10 | 21 | 12 | 8063.1332
2028 | 2008 | 10 | 21 | 13 | 11134.5218
2028 | 2008 | 10 | 21 | 14 | 13555.156
2028 | 2008 | 10 | 21 | 15 | 15607.9699
2028 | 2008 | 10 | 21 | 16 | 17683.5216
2028 | 2008 | 10 | 21 | 17 | 18527.3211
2028 | 2008 | 10 | 21 | 18 | 18977.0257
2028 | 2008 | 10 | 21 | 19 | 22276.3655
2028 | 2008 | 10 | 21 | 20 | 26692.8896
2028 | 2008 | 10 | 21 | 21 | 29313.3594
2028 | 2008 | 10 | 21 | 22 | 30370.1794
2028 | 2008 | 10 | 21 | 23 | 30489.8692
2028 | 2008 | 10 | 21 | 24 | 31473.2932
2028 | 2008 | 10 | 22 | 1 | 31228.2352
2028 | 2008 | 10 | 22 | 2 | 29909.0254
2028 | 2008 | 10 | 22 | 3 | 30250.3664
2028 | 2008 | 10 | 22 | 4 | 29147.3395
2028 | 2008 | 10 | 22 | 5 | 27433.4641
2028 | 2008 | 10 | 22 | 6 | 25693.4688
2028 | 2008 | 10 | 22 | 7 | 22955.3956
2028 | 2008 | 10 | 22 | 8 | 21806.24
2028 | 2008 | 10 | 22 | 9 | 19238.6026
2028 | 2008 | 10 | 22 | 10 | 21908.3607
2028 | 2008 | 10 | 22 | 11 | 24244.0316
2028 | 2008 | 10 | 22 | 12 | 25193.2974
2028 | 2008 | 10 | 22 | 13 | 26551.5701
2028 | 2008 | 10 | 22 | 14 | 27186.5584
2028 | 2008 | 10 | 22 | 15 | 26526.7195
2028 | 2008 | 10 | 22 | 16 | 26925.5889
2028 | 2008 | 10 | 22 | 17 | 27269.2948
2028 | 2008 | 10 | 22 | 18 | 26772.5701
2028 | 2008 | 10 | 22 | 19 | 24424.5803
2028 | 2008 | 10 | 22 | 20 | 23744.4139
2028 | 2008 | 10 | 22 | 21 | 21996.1129
2028 | 2008 | 10 | 22 | 22 | 19434.518
2028 | 2008 | 10 | 22 | 23 | 16943.2963
2028 | 2008 | 10 | 22 | 24 | 14770.6414
2028 | 2008 | 10 | 23 | 1 | 13270.4174
2028 | 2008 | 10 | 23 | 2 | 14579.0938
2028 | 2008 | 10 | 23 | 3 | 15958.1233
2028 | 2008 | 10 | 23 | 4 | 16753.2592
2028 | 2008 | 10 | 23 | 5 | 17470.7822
2028 | 2008 | 10 | 23 | 6 | 18536.5881
2028 | 2008 | 10 | 23 | 7 | 18868.2573
2028 | 2008 | 10 | 23 | 8 | 18887.2157
2028 | 2008 | 10 | 23 | 9 | 17598.3779
2028 | 2008 | 10 | 23 | 10 | 16634.3448
2028 | 2008 | 10 | 23 | 11 | 15632.406
2028 | 2008 | 10 | 23 | 12 | 16919.2126
2028 | 2008 | 10 | 23 | 13 | 16567.4867
2028 | 2008 | 10 | 23 | 14 | 17487.0285
2028 | 2008 | 10 | 23 | 15 | 18141.6492
2028 | 2008 | 10 | 23 | 16 | 17392.929
2028 | 2008 | 10 | 23 | 17 | 15751.9811
2028 | 2008 | 10 | 23 | 18 | 11841.7161
2028 | 2008 | 10 | 23 | 19 | 8133.8892
2028 | 2008 | 10 | 23 | 20 | 7338.5757
2028 | 2008 | 10 | 23 | 21 | 6369.8723
2028 | 2008 | 10 | 23 | 22 | 8588.583
2028 | 2008 | 10 | 23 | 23 | 9467.0858
2028 | 2008 | 10 | 23 | 24 | 9588.7308
2028 | 2008 | 10 | 24 | 1 | 11519.3158
2028 | 2008 | 10 | 24 | 2 | 11845.4094
2028 | 2008 | 10 | 24 | 3 | 10551.5047
2028 | 2008 | 10 | 24 | 4 | 10026.0511
2028 | 2008 | 10 | 24 | 5 | 9282.4007
2028 | 2008 | 10 | 24 | 6 | 8371.5462
2028 | 2008 | 10 | 24 | 7 | 7742.6382
2028 | 2008 | 10 | 24 | 8 | 6780.7561
2028 | 2008 | 10 | 24 | 9 | 5694.0907
2028 | 2008 | 10 | 24 | 10 | 3426.9337
2028 | 2008 | 10 | 24 | 11 | 2767.5345
2028 | 2008 | 10 | 24 | 12 | 2796.1573
2028 | 2008 | 10 | 24 | 13 | 2478.5862
2028 | 2008 | 10 | 24 | 14 | 2562.3166
2028 | 2008 | 10 | 24 | 15 | 2212.532
2028 | 2008 | 10 | 24 | 16 | 1739.7473
2028 | 2008 | 10 | 24 | 17 | 1235.9358
2028 | 2008 | 10 | 24 | 18 | 1447.5973
2028 | 2008 | 10 | 24 | 19 | 2337.7979
2028 | 2008 | 10 | 24 | 20 | 3496.6916
2028 | 2008 | 10 | 24 | 21 | 5434.5248
2028 | 2008 | 10 | 24 | 22 | 7938.139
2028 | 2008 | 10 | 24 | 23 | 9020.9938
2028 | 2008 | 10 | 24 | 24 | 9550.3404
2028 | 2008 | 10 | 25 | 1 | 9592.2474
2028 | 2008 | 10 | 25 | 2 | 9181.7231
2028 | 2008 | 10 | 25 | 3 | 8084.7477
2028 | 2008 | 10 | 25 | 4 | 7052.7188
2028 | 2008 | 10 | 25 | 5 | 6115.4232
2028 | 2008 | 10 | 25 | 6 | 5204.0969
2028 | 2008 | 10 | 25 | 7 | 4729.595
2028 | 2008 | 10 | 25 | 8 | 4492.0792
2028 | 2008 | 10 | 25 | 9 | 4102.0806
2028 | 2008 | 10 | 25 | 10 | 3699.4737
2028 | 2008 | 10 | 25 | 11 | 3006.5815
2028 | 2008 | 10 | 25 | 12 | 3761.7374
2028 | 2008 | 10 | 25 | 13 | 3974.0498
2028 | 2008 | 10 | 25 | 14 | 4702.9592
2028 | 2008 | 10 | 25 | 15 | 5805.9708
2028 | 2008 | 10 | 25 | 16 | 6715.0161
2028 | 2008 | 10 | 25 | 17 | 6710.2337
2028 | 2008 | 10 | 25 | 18 | 6736.7983
2028 | 2008 | 10 | 25 | 19 | 7982.1577
2028 | 2008 | 10 | 25 | 20 | 11969.8911
2028 | 2008 | 10 | 25 | 21 | 17073.0315
2028 | 2008 | 10 | 25 | 22 | 21831.599
2028 | 2008 | 10 | 25 | 23 | 24880.0249
2028 | 2008 | 10 | 25 | 24 | 27089.8308
2028 | 2008 | 10 | 26 | 1 | 27990.4231
2028 | 2008 | 10 | 26 | 2 | 28048.6532
2028 | 2008 | 10 | 26 | 3 | 27798.7812
2028 | 2008 | 10 | 26 | 4 | 26268.1746
2028 | 2008 | 10 | 26 | 5 | 25968.1501
2028 | 2008 | 10 | 26 | 6 | 25863.446
2028 | 2008 | 10 | 26 | 7 | 24077.264
2028 | 2008 | 10 | 26 | 8 | 21615.3432
2028 | 2008 | 10 | 26 | 9 | 17738.938
2028 | 2008 | 10 | 26 | 10 | 13391.1965
2028 | 2008 | 10 | 26 | 11 | 11522.8905
2028 | 2008 | 10 | 26 | 12 | 9882.9848
2028 | 2008 | 10 | 26 | 13 | 9153.7961
2028 | 2008 | 10 | 26 | 14 | 9910.5053
2028 | 2008 | 10 | 26 | 15 | 13217.9259
2028 | 2008 | 10 | 26 | 16 | 16733.0086
2028 | 2008 | 10 | 26 | 17 | 20158.6486
2028 | 2008 | 10 | 26 | 18 | 24096.6152
2028 | 2008 | 10 | 26 | 19 | 26517.3879
2028 | 2008 | 10 | 26 | 20 | 29197.7003
2028 | 2008 | 10 | 26 | 21 | 31237.3603
2028 | 2008 | 10 | 26 | 22 | 31468.671
2028 | 2008 | 10 | 26 | 23 | 30529.9948
2028 | 2008 | 10 | 26 | 24 | 29367.5058
2028 | 2008 | 10 | 27 | 1 | 27923.6449
2028 | 2008 | 10 | 27 | 2 | 26172.8844
2028 | 2008 | 10 | 27 | 3 | 24803.7156
2028 | 2008 | 10 | 27 | 4 | 23696.3908
2028 | 2008 | 10 | 27 | 5 | 22656.1273
2028 | 2008 | 10 | 27 | 6 | 22727.6179
2028 | 2008 | 10 | 27 | 7 | 22169.1452
2028 | 2008 | 10 | 27 | 8 | 20829.2526
2028 | 2008 | 10 | 27 | 9 | 17613.9298
2028 | 2008 | 10 | 27 | 10 | 15605.1204
2028 | 2008 | 10 | 27 | 11 | 16913.576
2028 | 2008 | 10 | 27 | 12 | 14678.9232
2028 | 2008 | 10 | 27 | 13 | 13976.4451
2028 | 2008 | 10 | 27 | 14 | 12736.9938
2028 | 2008 | 10 | 27 | 15 | 11973.3979
2028 | 2008 | 10 | 27 | 16 | 11097.5761
2028 | 2008 | 10 | 27 | 17 | 9645.3005
2028 | 2008 | 10 | 27 | 18 | 8115.508
2028 | 2008 | 10 | 27 | 19 | 7054.0431
2028 | 2008 | 10 | 27 | 20 | 7512.2204
2028 | 2008 | 10 | 27 | 21 | 8295.5787
2028 | 2008 | 10 | 27 | 22 | 9229.0572
2028 | 2008 | 10 | 27 | 23 | 10213.1256
2028 | 2008 | 10 | 27 | 24 | 11497.9185
2028 | 2008 | 10 | 28 | 1 | 11862.3674
2028 | 2008 | 10 | 28 | 2 | 12447.6738
2028 | 2008 | 10 | 28 | 3 | 13019.8128
2028 | 2008 | 10 | 28 | 4 | 13441.3522
2028 | 2008 | 10 | 28 | 5 | 14450.0689
2028 | 2008 | 10 | 28 | 6 | 15670.9509
2028 | 2008 | 10 | 28 | 7 | 16879.4417
2028 | 2008 | 10 | 28 | 8 | 17175.8572
2028 | 2008 | 10 | 28 | 9 | 15846.4791
2028 | 2008 | 10 | 28 | 10 | 9754.4096
2028 | 2008 | 10 | 28 | 11 | 10354.1945
2028 | 2008 | 10 | 28 | 12 | 11356.4806
2028 | 2008 | 10 | 28 | 13 | 10684.6448
2028 | 2008 | 10 | 28 | 14 | 10164.1992
2028 | 2008 | 10 | 28 | 15 | 10304.9818
2028 | 2008 | 10 | 28 | 16 | 10524.8558
2028 | 2008 | 10 | 28 | 17 | 10795.9475
2028 | 2008 | 10 | 28 | 18 | 11879.805
2028 | 2008 | 10 | 28 | 19 | 15660.9268
2028 | 2008 | 10 | 28 | 20 | 20083.3905
2028 | 2008 | 10 | 28 | 21 | 24178.7524
2028 | 2008 | 10 | 28 | 22 | 25737.1243
2028 | 2008 | 10 | 28 | 23 | 26014.8798
2028 | 2008 | 10 | 28 | 24 | 26243.6559
2028 | 2008 | 10 | 29 | 1 | 26234.2972
2028 | 2008 | 10 | 29 | 2 | 25771.7205
2028 | 2008 | 10 | 29 | 3 | 25140.313
2028 | 2008 | 10 | 29 | 4 | 24125.6922
2028 | 2008 | 10 | 29 | 5 | 23055.5863
2028 | 2008 | 10 | 29 | 6 | 21637.4925
2028 | 2008 | 10 | 29 | 7 | 20281.4339
2028 | 2008 | 10 | 29 | 8 | 18482.1286
2028 | 2008 | 10 | 29 | 9 | 15331.0274
2028 | 2008 | 10 | 29 | 10 | 9745.7852
2028 | 2008 | 10 | 29 | 11 | 9575.2012
2028 | 2008 | 10 | 29 | 12 | 9049.3236
2028 | 2008 | 10 | 29 | 13 | 8258.5943
2028 | 2008 | 10 | 29 | 14 | 7879.0716
2028 | 2008 | 10 | 29 | 15 | 7984.3105
2028 | 2008 | 10 | 29 | 16 | 8385.2772
2028 | 2008 | 10 | 29 | 17 | 8825.0955
2028 | 2008 | 10 | 29 | 18 | 10061.5678
2028 | 2008 | 10 | 29 | 19 | 12962.7963
2028 | 2008 | 10 | 29 | 20 | 17941.9384
2028 | 2008 | 10 | 29 | 21 | 23758.6573
2028 | 2008 | 10 | 29 | 22 | 27123.3478
2028 | 2008 | 10 | 29 | 23 | 28584.6629
2028 | 2008 | 10 | 29 | 24 | 29311.4442
2028 | 2008 | 10 | 30 | 1 | 29608.3351
2028 | 2008 | 10 | 30 | 2 | 29223.1289
2028 | 2008 | 10 | 30 | 3 | 28935.0541
2028 | 2008 | 10 | 30 | 4 | 28545.4783
2028 | 2008 | 10 | 30 | 5 | 28413.8822
2028 | 2008 | 10 | 30 | 6 | 25361.5664
2028 | 2008 | 10 | 30 | 7 | 25064.7464
2028 | 2008 | 10 | 30 | 8 | 24227.7106
2028 | 2008 | 10 | 30 | 9 | 22041.2147
2028 | 2008 | 10 | 30 | 10 | 19923.5861
2028 | 2008 | 10 | 30 | 11 | 18886.2214
2028 | 2008 | 10 | 30 | 12 | 19157.892
2028 | 2008 | 10 | 30 | 13 | 18721.8765
2028 | 2008 | 10 | 30 | 14 | 19388.4308
2028 | 2008 | 10 | 30 | 15 | 19881.3269
2028 | 2008 | 10 | 30 | 16 | 19645.5725
2028 | 2008 | 10 | 30 | 17 | 19159.7903
2028 | 2008 | 10 | 30 | 18 | 19388.2878
2028 | 2008 | 10 | 30 | 19 | 22322.3654
2028 | 2008 | 10 | 30 | 20 | 25243.7932
2028 | 2008 | 10 | 30 | 21 | 26935.8814
2028 | 2008 | 10 | 30 | 22 | 26633.7013
2028 | 2008 | 10 | 30 | 23 | 26616.3951
2028 | 2008 | 10 | 30 | 24 | 29208.5169
2028 | 2008 | 10 | 31 | 1 | 28066.9572
2028 | 2008 | 10 | 31 | 2 | 26913.1144
2028 | 2008 | 10 | 31 | 3 | 25758.7862
2028 | 2008 | 10 | 31 | 4 | 24514.6254
2028 | 2008 | 10 | 31 | 5 | 22193.2998
2028 | 2008 | 10 | 31 | 6 | 20516.6419
2028 | 2008 | 10 | 31 | 7 | 18127.6153
2028 | 2008 | 10 | 31 | 8 | 16421.042
2028 | 2008 | 10 | 31 | 9 | 13400.4037
2028 | 2008 | 10 | 31 | 10 | 13239.1017
2028 | 2008 | 10 | 31 | 11 | 12766.2726
2028 | 2008 | 10 | 31 | 12 | 11358.8213
2028 | 2008 | 10 | 31 | 13 | 10257.7509
2028 | 2008 | 10 | 31 | 14 | 8821.8591
2028 | 2008 | 10 | 31 | 15 | 7444.1347
2028 | 2008 | 10 | 31 | 16 | 5847.2445
2028 | 2008 | 10 | 31 | 17 | 5127.7051
2028 | 2008 | 10 | 31 | 18 | 5342.8239
2028 | 2008 | 10 | 31 | 19 | 8382.4381
2028 | 2008 | 10 | 31 | 20 | 10680.0114
2028 | 2008 | 10 | 31 | 21 | 12739.1922
2028 | 2008 | 10 | 31 | 22 | 14219.5224
2028 | 2008 | 10 | 31 | 23 | 14608.371
2028 | 2008 | 10 | 31 | 24 | 14417.2362
2029 | 2008 | 10 | 1 | 1 | 6636.2232
2029 | 2008 | 10 | 1 | 2 | 6793.4699
2029 | 2008 | 10 | 1 | 3 | 6483.7449
2029 | 2008 | 10 | 1 | 4 | 6866.2229
2029 | 2008 | 10 | 1 | 5 | 6913.4056
2029 | 2008 | 10 | 1 | 6 | 6030.0329
2029 | 2008 | 10 | 1 | 7 | 5354.816
2029 | 2008 | 10 | 1 | 8 | 4531.3852
2029 | 2008 | 10 | 1 | 9 | 3619.7301
2029 | 2008 | 10 | 1 | 10 | 1724.774
2029 | 2008 | 10 | 1 | 11 | 1825.7456
2029 | 2008 | 10 | 1 | 12 | 1646.1095
2029 | 2008 | 10 | 1 | 13 | 1611.5497
2029 | 2008 | 10 | 1 | 14 | 1538.4372
2029 | 2008 | 10 | 1 | 15 | 1330.7201
2029 | 2008 | 10 | 1 | 16 | 1156.9454
2029 | 2008 | 10 | 1 | 17 | 1143.4801
2029 | 2008 | 10 | 1 | 18 | 1696.7147
2029 | 2008 | 10 | 1 | 19 | 3998.0427
2029 | 2008 | 10 | 1 | 20 | 4455.5466
2029 | 2008 | 10 | 1 | 21 | 5943.1331
2029 | 2008 | 10 | 1 | 22 | 8190.8845
2029 | 2008 | 10 | 1 | 23 | 9035.999
2029 | 2008 | 10 | 1 | 24 | 9095.889
2029 | 2008 | 10 | 2 | 1 | 9080.3685
2029 | 2008 | 10 | 2 | 2 | 9585.8682
2029 | 2008 | 10 | 2 | 3 | 9923.3821
2029 | 2008 | 10 | 2 | 4 | 9987.3566
2029 | 2008 | 10 | 2 | 5 | 9629.0262
2029 | 2008 | 10 | 2 | 6 | 8790.8909
2029 | 2008 | 10 | 2 | 7 | 8605.9336
2029 | 2008 | 10 | 2 | 8 | 7262.5895
2029 | 2008 | 10 | 2 | 9 | 6117.0074
2029 | 2008 | 10 | 2 | 10 | 3634.0899
2029 | 2008 | 10 | 2 | 11 | 4498.781
2029 | 2008 | 10 | 2 | 12 | 4092.8002
2029 | 2008 | 10 | 2 | 13 | 3917.1993
2029 | 2008 | 10 | 2 | 14 | 4034.2207
2029 | 2008 | 10 | 2 | 15 | 4414.9342
2029 | 2008 | 10 | 2 | 16 | 4578.8078
2029 | 2008 | 10 | 2 | 17 | 5151.2776
2029 | 2008 | 10 | 2 | 18 | 6439.3635
2029 | 2008 | 10 | 2 | 19 | 8884.4476
2029 | 2008 | 10 | 2 | 20 | 12713.7602
2029 | 2008 | 10 | 2 | 21 | 17558.6533
2029 | 2008 | 10 | 2 | 22 | 21363.5713
2029 | 2008 | 10 | 2 | 23 | 23952.398
2029 | 2008 | 10 | 2 | 24 | 26162.6489
2029 | 2008 | 10 | 3 | 1 | 26985.9552
2029 | 2008 | 10 | 3 | 2 | 27219.6708
2029 | 2008 | 10 | 3 | 3 | 27629.214
2029 | 2008 | 10 | 3 | 4 | 27645.7884
2029 | 2008 | 10 | 3 | 5 | 26789.6976
2029 | 2008 | 10 | 3 | 6 | 26286.1544
2029 | 2008 | 10 | 3 | 7 | 25205.9229
2029 | 2008 | 10 | 3 | 8 | 22831.5824
2029 | 2008 | 10 | 3 | 9 | 19071.7801
2029 | 2008 | 10 | 3 | 10 | 13769.7881
2029 | 2008 | 10 | 3 | 11 | 15050.6593
2029 | 2008 | 10 | 3 | 12 | 16339.2649
2029 | 2008 | 10 | 3 | 13 | 17090.7658
2029 | 2008 | 10 | 3 | 14 | 18273.7877
2029 | 2008 | 10 | 3 | 15 | 19788.9793
2029 | 2008 | 10 | 3 | 16 | 20276.8318
2029 | 2008 | 10 | 3 | 17 | 21749.9702
2029 | 2008 | 10 | 3 | 18 | 22604.3417
2029 | 2008 | 10 | 3 | 19 | 24800.7222
2029 | 2008 | 10 | 3 | 20 | 30017.705
2029 | 2008 | 10 | 3 | 21 | 32769.5982
2029 | 2008 | 10 | 3 | 22 | 33165.3963
2029 | 2008 | 10 | 3 | 23 | 32555.9914
2029 | 2008 | 10 | 3 | 24 | 32749.5815
2029 | 2008 | 10 | 4 | 1 | 32843.657
2029 | 2008 | 10 | 4 | 2 | 33037.0746
2029 | 2008 | 10 | 4 | 3 | 33145.3367
2029 | 2008 | 10 | 4 | 4 | 32608.1021
2029 | 2008 | 10 | 4 | 5 | 32119.1617
2029 | 2008 | 10 | 4 | 6 | 31185.3152
2029 | 2008 | 10 | 4 | 7 | 30873.1136
2029 | 2008 | 10 | 4 | 8 | 28905.0047
2029 | 2008 | 10 | 4 | 9 | 25565.9554
2029 | 2008 | 10 | 4 | 10 | 26552.2365
2029 | 2008 | 10 | 4 | 11 | 29408.2476
2029 | 2008 | 10 | 4 | 12 | 30080.7068
2029 | 2008 | 10 | 4 | 13 | 31026.9196
2029 | 2008 | 10 | 4 | 14 | 31994.4781
2029 | 2008 | 10 | 4 | 15 | 33309.458
2029 | 2008 | 10 | 4 | 16 | 34530.4664
2029 | 2008 | 10 | 4 | 17 | 35005.9899
2029 | 2008 | 10 | 4 | 18 | 35305.9884
2029 | 2008 | 10 | 4 | 19 | 34637.9188
2029 | 2008 | 10 | 4 | 20 | 34953.149
2029 | 2008 | 10 | 4 | 21 | 34938.2398
2029 | 2008 | 10 | 4 | 22 | 34805.1718
2029 | 2008 | 10 | 4 | 23 | 34699.8052
2029 | 2008 | 10 | 4 | 24 | 34368.1426
2029 | 2008 | 10 | 5 | 1 | 34174.5426
2029 | 2008 | 10 | 5 | 2 | 33971.0747
2029 | 2008 | 10 | 5 | 3 | 33452.8352
2029 | 2008 | 10 | 5 | 4 | 33155.96
2029 | 2008 | 10 | 5 | 5 | 32643.9014
2029 | 2008 | 10 | 5 | 6 | 32202.964
2029 | 2008 | 10 | 5 | 7 | 31171.2294
2029 | 2008 | 10 | 5 | 8 | 29058.9486
2029 | 2008 | 10 | 5 | 9 | 25585.6209
2029 | 2008 | 10 | 5 | 10 | 29779.1466
2029 | 2008 | 10 | 5 | 11 | 32788.6498
2029 | 2008 | 10 | 5 | 12 | 33012.0544
2029 | 2008 | 10 | 5 | 13 | 33651.832
2029 | 2008 | 10 | 5 | 14 | 32801.242
2029 | 2008 | 10 | 5 | 15 | 33240.3498
2029 | 2008 | 10 | 5 | 16 | 32782.6488
2029 | 2008 | 10 | 5 | 17 | 32979.9046
2029 | 2008 | 10 | 5 | 18 | 32847.159
2029 | 2008 | 10 | 5 | 19 | 31566.926
2029 | 2008 | 10 | 5 | 20 | 31817.0012
2029 | 2008 | 10 | 5 | 21 | 31620.9795
2029 | 2008 | 10 | 5 | 22 | 29882.8652
2029 | 2008 | 10 | 5 | 23 | 29998.6165
2029 | 2008 | 10 | 5 | 24 | 28672.9732
2029 | 2008 | 10 | 6 | 1 | 28486.3132
2029 | 2008 | 10 | 6 | 2 | 28964.5578
2029 | 2008 | 10 | 6 | 3 | 28331.1296
2029 | 2008 | 10 | 6 | 4 | 28278.2596
2029 | 2008 | 10 | 6 | 5 | 28361.5613
2029 | 2008 | 10 | 6 | 6 | 26868.8036
2029 | 2008 | 10 | 6 | 7 | 25955.748
2029 | 2008 | 10 | 6 | 8 | 24408.5645
2029 | 2008 | 10 | 6 | 9 | 21792.6141
2029 | 2008 | 10 | 6 | 10 | 25125.4537
2029 | 2008 | 10 | 6 | 11 | 26308.0448
2029 | 2008 | 10 | 6 | 12 | 25703.8826
2029 | 2008 | 10 | 6 | 13 | 24552.6439
2029 | 2008 | 10 | 6 | 14 | 23011.2525
2029 | 2008 | 10 | 6 | 15 | 21511.015
2029 | 2008 | 10 | 6 | 16 | 19656.5522
2029 | 2008 | 10 | 6 | 17 | 16349.6608
2029 | 2008 | 10 | 6 | 18 | 13131.0145
2029 | 2008 | 10 | 6 | 19 | 11338.3427
2029 | 2008 | 10 | 6 | 20 | 13618.4599
2029 | 2008 | 10 | 6 | 21 | 16402.8198
2029 | 2008 | 10 | 6 | 22 | 18232.4803
2029 | 2008 | 10 | 6 | 23 | 16596.881
2029 | 2008 | 10 | 6 | 24 | 16476.0671
2029 | 2008 | 10 | 7 | 1 | 16272.5699
2029 | 2008 | 10 | 7 | 2 | 17106.7619
2029 | 2008 | 10 | 7 | 3 | 17591.0457
2029 | 2008 | 10 | 7 | 4 | 18510.0566
2029 | 2008 | 10 | 7 | 5 | 19176.2403
2029 | 2008 | 10 | 7 | 6 | 19341.3748
2029 | 2008 | 10 | 7 | 7 | 20139.9046
2029 | 2008 | 10 | 7 | 8 | 19560.6969
2029 | 2008 | 10 | 7 | 9 | 17395.0498
2029 | 2008 | 10 | 7 | 10 | 16246.5536
2029 | 2008 | 10 | 7 | 11 | 18834.3255
2029 | 2008 | 10 | 7 | 12 | 17959.6473
2029 | 2008 | 10 | 7 | 13 | 17142.9977
2029 | 2008 | 10 | 7 | 14 | 16812.4634
2029 | 2008 | 10 | 7 | 15 | 17118.5706
2029 | 2008 | 10 | 7 | 16 | 15582.3342
2029 | 2008 | 10 | 7 | 17 | 14142.8114
2029 | 2008 | 10 | 7 | 18 | 11094.3598
2029 | 2008 | 10 | 7 | 19 | 8240.3517
2029 | 2008 | 10 | 7 | 20 | 7062.6741
2029 | 2008 | 10 | 7 | 21 | 6595.226
2029 | 2008 | 10 | 7 | 22 | 6974.9855
2029 | 2008 | 10 | 7 | 23 | 7684.7843
2029 | 2008 | 10 | 7 | 24 | 8551.7026
2029 | 2008 | 10 | 8 | 1 | 10408.2141
2029 | 2008 | 10 | 8 | 2 | 12234.4119
2029 | 2008 | 10 | 8 | 3 | 14693.2931
2029 | 2008 | 10 | 8 | 4 | 16249.2589
2029 | 2008 | 10 | 8 | 5 | 17360.7347
2029 | 2008 | 10 | 8 | 6 | 16361.8875
2029 | 2008 | 10 | 8 | 7 | 16710.698
2029 | 2008 | 10 | 8 | 8 | 15632.5987
2029 | 2008 | 10 | 8 | 9 | 13610.5338
2029 | 2008 | 10 | 8 | 10 | 8598.9305
2029 | 2008 | 10 | 8 | 11 | 8380.8948
2029 | 2008 | 10 | 8 | 12 | 8289.6149
2029 | 2008 | 10 | 8 | 13 | 7503.7602
2029 | 2008 | 10 | 8 | 14 | 6557.1002
2029 | 2008 | 10 | 8 | 15 | 6044.1197
2029 | 2008 | 10 | 8 | 16 | 5658.4177
2029 | 2008 | 10 | 8 | 17 | 5435.6459
2029 | 2008 | 10 | 8 | 18 | 5944.0706
2029 | 2008 | 10 | 8 | 19 | 7840.4477
2029 | 2008 | 10 | 8 | 20 | 11313.7184
2029 | 2008 | 10 | 8 | 21 | 16716.1772
2029 | 2008 | 10 | 8 | 22 | 20613.0756
2029 | 2008 | 10 | 8 | 23 | 22992.8495
2029 | 2008 | 10 | 8 | 24 | 24743.2404
2029 | 2008 | 10 | 9 | 1 | 24343.9233
2029 | 2008 | 10 | 9 | 2 | 23730.5978
2029 | 2008 | 10 | 9 | 3 | 23078.8943
2029 | 2008 | 10 | 9 | 4 | 22214.8436
2029 | 2008 | 10 | 9 | 5 | 21482.4987
2029 | 2008 | 10 | 9 | 6 | 21319.0943
2029 | 2008 | 10 | 9 | 7 | 20785.2345
2029 | 2008 | 10 | 9 | 8 | 19998.4086
2029 | 2008 | 10 | 9 | 9 | 17397.799
2029 | 2008 | 10 | 9 | 10 | 11262.1837
2029 | 2008 | 10 | 9 | 11 | 14342.2201
2029 | 2008 | 10 | 9 | 12 | 18301.2486
2029 | 2008 | 10 | 9 | 13 | 19702.4202
2029 | 2008 | 10 | 9 | 14 | 20695.7468
2029 | 2008 | 10 | 9 | 15 | 21142.3444
2029 | 2008 | 10 | 9 | 16 | 21933.7523
2029 | 2008 | 10 | 9 | 17 | 21772.6966
2029 | 2008 | 10 | 9 | 18 | 22202.2442
2029 | 2008 | 10 | 9 | 19 | 24678.6338
2029 | 2008 | 10 | 9 | 20 | 28589.0874
2029 | 2008 | 10 | 9 | 21 | 31104.19
2029 | 2008 | 10 | 9 | 22 | 31348.1021
2029 | 2008 | 10 | 9 | 23 | 31375.667
2029 | 2008 | 10 | 9 | 24 | 31151.3908
2029 | 2008 | 10 | 10 | 1 | 30646.1571
2029 | 2008 | 10 | 10 | 2 | 30423.2333
2029 | 2008 | 10 | 10 | 3 | 30250.6349
2029 | 2008 | 10 | 10 | 4 | 29697.3939
2029 | 2008 | 10 | 10 | 5 | 29476.5994
2029 | 2008 | 10 | 10 | 6 | 29338.4242
2029 | 2008 | 10 | 10 | 7 | 28767.4306
2029 | 2008 | 10 | 10 | 8 | 26931.36
2029 | 2008 | 10 | 10 | 9 | 23141.4125
2029 | 2008 | 10 | 10 | 10 | 20395.268
2029 | 2008 | 10 | 10 | 11 | 21698.1625
2029 | 2008 | 10 | 10 | 12 | 21161.3427
2029 | 2008 | 10 | 10 | 13 | 21277.5099
2029 | 2008 | 10 | 10 | 14 | 21827.2178
2029 | 2008 | 10 | 10 | 15 | 22518.5884
2029 | 2008 | 10 | 10 | 16 | 23610.5225
2029 | 2008 | 10 | 10 | 17 | 24576.6922
2029 | 2008 | 10 | 10 | 18 | 26096.7526
2029 | 2008 | 10 | 10 | 19 | 28338.1911
2029 | 2008 | 10 | 10 | 20 | 31214.3354
2029 | 2008 | 10 | 10 | 21 | 32920.218
2029 | 2008 | 10 | 10 | 22 | 33029.1016
2029 | 2008 | 10 | 10 | 23 | 32319.6562
2029 | 2008 | 10 | 10 | 24 | 31429.9986
2029 | 2008 | 10 | 11 | 1 | 30858.7131
2029 | 2008 | 10 | 11 | 2 | 29821.0669
2029 | 2008 | 10 | 11 | 3 | 29149.1316
2029 | 2008 | 10 | 11 | 4 | 27848.6466
2029 | 2008 | 10 | 11 | 5 | 26569.2669
2029 | 2008 | 10 | 11 | 6 | 24749.4475
2029 | 2008 | 10 | 11 | 7 | 22745.3062
2029 | 2008 | 10 | 11 | 8 | 20677.784
2029 | 2008 | 10 | 11 | 9 | 17312.5001
2029 | 2008 | 10 | 11 | 10 | 18658.8236
2029 | 2008 | 10 | 11 | 11 | 20106.7748
2029 | 2008 | 10 | 11 | 12 | 20732.533
2029 | 2008 | 10 | 11 | 13 | 22602.1238
2029 | 2008 | 10 | 11 | 14 | 24291.35
2029 | 2008 | 10 | 11 | 15 | 27053.9644
2029 | 2008 | 10 | 11 | 16 | 29439.2259
2029 | 2008 | 10 | 11 | 17 | 30490.0832
2029 | 2008 | 10 | 11 | 18 | 32389.8128
2029 | 2008 | 10 | 11 | 19 | 32321.1524
2029 | 2008 | 10 | 11 | 20 | 33487.644
2029 | 2008 | 10 | 11 | 21 | 34046.0167
2029 | 2008 | 10 | 11 | 22 | 33640.1325
2029 | 2008 | 10 | 11 | 23 | 33605.3364
2029 | 2008 | 10 | 11 | 24 | 32981.6607
2029 | 2008 | 10 | 12 | 1 | 32873.9419
2029 | 2008 | 10 | 12 | 2 | 32888.4865
2029 | 2008 | 10 | 12 | 3 | 32932.0062
2029 | 2008 | 10 | 12 | 4 | 32639.2466
2029 | 2008 | 10 | 12 | 5 | 31496.1083
2029 | 2008 | 10 | 12 | 6 | 31217.3903
2029 | 2008 | 10 | 12 | 7 | 30385.1539
2029 | 2008 | 10 | 12 | 8 | 28792.2181
2029 | 2008 | 10 | 12 | 9 | 25913.9878
2029 | 2008 | 10 | 12 | 10 | 30733.45
2029 | 2008 | 10 | 12 | 11 | 32435.9666
2029 | 2008 | 10 | 12 | 12 | 32720.4442
2029 | 2008 | 10 | 12 | 13 | 33771.9044
2029 | 2008 | 10 | 12 | 14 | 34014.0343
2029 | 2008 | 10 | 12 | 15 | 34233.7234
2029 | 2008 | 10 | 12 | 16 | 34381.5178
2029 | 2008 | 10 | 12 | 17 | 32965.4316
2029 | 2008 | 10 | 12 | 18 | 31686.4273
2029 | 2008 | 10 | 12 | 19 | 30421.284
2029 | 2008 | 10 | 12 | 20 | 31810.0858
2029 | 2008 | 10 | 12 | 21 | 32746.0408
2029 | 2008 | 10 | 12 | 22 | 32937.708
2029 | 2008 | 10 | 12 | 23 | 32317.2616
2029 | 2008 | 10 | 12 | 24 | 31925.7104
2029 | 2008 | 10 | 13 | 1 | 29751.4283
2029 | 2008 | 10 | 13 | 2 | 27873.1903
2029 | 2008 | 10 | 13 | 3 | 25846.3967
2029 | 2008 | 10 | 13 | 4 | 23897.8702
2029 | 2008 | 10 | 13 | 5 | 22144.7231
2029 | 2008 | 10 | 13 | 6 | 21193.7859
2029 | 2008 | 10 | 13 | 7 | 20450.4339
2029 | 2008 | 10 | 13 | 8 | 20003.6423
2029 | 2008 | 10 | 13 | 9 | 18327.9783
2029 | 2008 | 10 | 13 | 10 | 21951.9939
2029 | 2008 | 10 | 13 | 11 | 22765.9084
2029 | 2008 | 10 | 13 | 12 | 21470.7789
2029 | 2008 | 10 | 13 | 13 | 20359.0684
2029 | 2008 | 10 | 13 | 14 | 19555.881
2029 | 2008 | 10 | 13 | 15 | 18781.3671
2029 | 2008 | 10 | 13 | 16 | 18202.0795
2029 | 2008 | 10 | 13 | 17 | 18767.7119
2029 | 2008 | 10 | 13 | 18 | 20179.6468
2029 | 2008 | 10 | 13 | 19 | 21015.2647
2029 | 2008 | 10 | 13 | 20 | 21752.2441
2029 | 2008 | 10 | 13 | 21 | 22379.5368
2029 | 2008 | 10 | 13 | 22 | 21883.6698
2029 | 2008 | 10 | 13 | 23 | 20332.205
2029 | 2008 | 10 | 13 | 24 | 18742.2216
2029 | 2008 | 10 | 14 | 1 | 16169.6667
2029 | 2008 | 10 | 14 | 2 | 14926.1223
2029 | 2008 | 10 | 14 | 3 | 13768.0336
2029 | 2008 | 10 | 14 | 4 | 11991.6652
2029 | 2008 | 10 | 14 | 5 | 10082.364
2029 | 2008 | 10 | 14 | 6 | 8237.4412
2029 | 2008 | 10 | 14 | 7 | 7293.9482
2029 | 2008 | 10 | 14 | 8 | 6391.1276
2029 | 2008 | 10 | 14 | 9 | 5035.346
2029 | 2008 | 10 | 14 | 10 | 6153.4475
2029 | 2008 | 10 | 14 | 11 | 6457.3403
2029 | 2008 | 10 | 14 | 12 | 6815.8122
2029 | 2008 | 10 | 14 | 13 | 7446.0604
2029 | 2008 | 10 | 14 | 14 | 8503.8489
2029 | 2008 | 10 | 14 | 15 | 9553.0819
2029 | 2008 | 10 | 14 | 16 | 9996.94
2029 | 2008 | 10 | 14 | 17 | 9475.8497
2029 | 2008 | 10 | 14 | 18 | 9194.8467
2029 | 2008 | 10 | 14 | 19 | 9254.3158
2029 | 2008 | 10 | 14 | 20 | 9171.3578
2029 | 2008 | 10 | 14 | 21 | 10002.0722
2029 | 2008 | 10 | 14 | 22 | 9395.6839
2029 | 2008 | 10 | 14 | 23 | 8185.1805
2029 | 2008 | 10 | 14 | 24 | 7168.4418
2029 | 2008 | 10 | 15 | 1 | 6968.6606
2029 | 2008 | 10 | 15 | 2 | 7882.2761
2029 | 2008 | 10 | 15 | 3 | 8574.6774
2029 | 2008 | 10 | 15 | 4 | 9687.3319
2029 | 2008 | 10 | 15 | 5 | 10594.6191
2029 | 2008 | 10 | 15 | 6 | 11044.1699
2029 | 2008 | 10 | 15 | 7 | 11814.3701
2029 | 2008 | 10 | 15 | 8 | 11536.6356
2029 | 2008 | 10 | 15 | 9 | 10006.263
2029 | 2008 | 10 | 15 | 10 | 11880.1727
2029 | 2008 | 10 | 15 | 11 | 12204.8834
2029 | 2008 | 10 | 15 | 12 | 10657.8259
2029 | 2008 | 10 | 15 | 13 | 9622.6087
2029 | 2008 | 10 | 15 | 14 | 10297.7629
2029 | 2008 | 10 | 15 | 15 | 11300.565
2029 | 2008 | 10 | 15 | 16 | 12234.2706
2029 | 2008 | 10 | 15 | 17 | 12896.4871
2029 | 2008 | 10 | 15 | 18 | 12522.298
2029 | 2008 | 10 | 15 | 19 | 13022.6742
2029 | 2008 | 10 | 15 | 20 | 14369.6505
2029 | 2008 | 10 | 15 | 21 | 15757.4019
2029 | 2008 | 10 | 15 | 22 | 15169.9999
2029 | 2008 | 10 | 15 | 23 | 13601.5389
2029 | 2008 | 10 | 15 | 24 | 13542.8744
2029 | 2008 | 10 | 16 | 1 | 13331.4755
2029 | 2008 | 10 | 16 | 2 | 14007.3989
2029 | 2008 | 10 | 16 | 3 | 14800.0809
2029 | 2008 | 10 | 16 | 4 | 16017.864
2029 | 2008 | 10 | 16 | 5 | 15789.3524
2029 | 2008 | 10 | 16 | 6 | 16412.6229
2029 | 2008 | 10 | 16 | 7 | 16664.2289
2029 | 2008 | 10 | 16 | 8 | 16738.5449
2029 | 2008 | 10 | 16 | 9 | 15186.5292
2029 | 2008 | 10 | 16 | 10 | 19063.9562
2029 | 2008 | 10 | 16 | 11 | 19271.0208
2029 | 2008 | 10 | 16 | 12 | 17423.0099
2029 | 2008 | 10 | 16 | 13 | 15383.0557
2029 | 2008 | 10 | 16 | 14 | 13535.2548
2029 | 2008 | 10 | 16 | 15 | 12311.3962
2029 | 2008 | 10 | 16 | 16 | 10776.7633
2029 | 2008 | 10 | 16 | 17 | 8770.1939
2029 | 2008 | 10 | 16 | 18 | 7182.3006
2029 | 2008 | 10 | 16 | 19 | 5940.8291
2029 | 2008 | 10 | 16 | 20 | 5629.8273
2029 | 2008 | 10 | 16 | 21 | 5594.0475
2029 | 2008 | 10 | 16 | 22 | 5586.1886
2029 | 2008 | 10 | 16 | 23 | 5346.331
2029 | 2008 | 10 | 16 | 24 | 5255.132
2029 | 2008 | 10 | 17 | 1 | 5304.2221
2029 | 2008 | 10 | 17 | 2 | 5364.6763
2029 | 2008 | 10 | 17 | 3 | 5638.9368
2029 | 2008 | 10 | 17 | 4 | 6318.1394
2029 | 2008 | 10 | 17 | 5 | 6970.7263
2029 | 2008 | 10 | 17 | 6 | 7108.0736
2029 | 2008 | 10 | 17 | 7 | 6934.5469
2029 | 2008 | 10 | 17 | 8 | 5802.4165
2029 | 2008 | 10 | 17 | 9 | 5449.9412
2029 | 2008 | 10 | 17 | 10 | 5593.4309
2029 | 2008 | 10 | 17 | 11 | 5358.7296
2029 | 2008 | 10 | 17 | 12 | 5415.4463
2029 | 2008 | 10 | 17 | 13 | 5117.9643
2029 | 2008 | 10 | 17 | 14 | 4935.5525
2029 | 2008 | 10 | 17 | 15 | 4610.8115
2029 | 2008 | 10 | 17 | 16 | 4065.6349
2029 | 2008 | 10 | 17 | 17 | 3472.2908
2029 | 2008 | 10 | 17 | 18 | 3213.8655
2029 | 2008 | 10 | 17 | 19 | 3143.4217
2029 | 2008 | 10 | 17 | 20 | 2863.9419
2029 | 2008 | 10 | 17 | 21 | 2769.747
2029 | 2008 | 10 | 17 | 22 | 2814.9044
2029 | 2008 | 10 | 17 | 23 | 2988.8934
2029 | 2008 | 10 | 17 | 24 | 3592.0465
2029 | 2008 | 10 | 18 | 1 | 3745.3167
2029 | 2008 | 10 | 18 | 2 | 4233.2594
2029 | 2008 | 10 | 18 | 3 | 4439.5502
2029 | 2008 | 10 | 18 | 4 | 4907.8552
2029 | 2008 | 10 | 18 | 5 | 5274.6092
2029 | 2008 | 10 | 18 | 6 | 5853.3442
2029 | 2008 | 10 | 18 | 7 | 6444.7787
2029 | 2008 | 10 | 18 | 8 | 5447.7732
2029 | 2008 | 10 | 18 | 9 | 4411.466
2029 | 2008 | 10 | 18 | 10 | 4436.9981
2029 | 2008 | 10 | 18 | 11 | 4702.9578
2029 | 2008 | 10 | 18 | 12 | 5485.9235
2029 | 2008 | 10 | 18 | 13 | 6051.8433
2029 | 2008 | 10 | 18 | 14 | 6810.6533
2029 | 2008 | 10 | 18 | 15 | 7501.5381
2029 | 2008 | 10 | 18 | 16 | 7642.6826
2029 | 2008 | 10 | 18 | 17 | 7475.9927
2029 | 2008 | 10 | 18 | 18 | 7400.8326
2029 | 2008 | 10 | 18 | 19 | 7914.2225
2029 | 2008 | 10 | 18 | 20 | 9687.7024
2029 | 2008 | 10 | 18 | 21 | 11407.7128
2029 | 2008 | 10 | 18 | 22 | 13290.4126
2029 | 2008 | 10 | 18 | 23 | 14862.0414
2029 | 2008 | 10 | 18 | 24 | 16988.9361
2029 | 2008 | 10 | 19 | 1 | 19189.1522
2029 | 2008 | 10 | 19 | 2 | 20363.8579
2029 | 2008 | 10 | 19 | 3 | 20895.2608
2029 | 2008 | 10 | 19 | 4 | 20771.4955
2029 | 2008 | 10 | 19 | 5 | 20398.4598
2029 | 2008 | 10 | 19 | 6 | 20327.713
2029 | 2008 | 10 | 19 | 7 | 19513.6896
2029 | 2008 | 10 | 19 | 8 | 18993.896
2029 | 2008 | 10 | 19 | 9 | 16891.8242
2029 | 2008 | 10 | 19 | 10 | 10603.4147
2029 | 2008 | 10 | 19 | 11 | 13364.6137
2029 | 2008 | 10 | 19 | 12 | 14657.5248
2029 | 2008 | 10 | 19 | 13 | 13782.1656
2029 | 2008 | 10 | 19 | 14 | 13108.825
2029 | 2008 | 10 | 19 | 15 | 13234.9373
2029 | 2008 | 10 | 19 | 16 | 13302.7883
2029 | 2008 | 10 | 19 | 17 | 13158.6456
2029 | 2008 | 10 | 19 | 18 | 12982.656
2029 | 2008 | 10 | 19 | 19 | 15883.4019
2029 | 2008 | 10 | 19 | 20 | 20578.7706
2029 | 2008 | 10 | 19 | 21 | 25235.5279
2029 | 2008 | 10 | 19 | 22 | 27323.3048
2029 | 2008 | 10 | 19 | 23 | 27365.7136
2029 | 2008 | 10 | 19 | 24 | 27196.8756
2029 | 2008 | 10 | 20 | 1 | 26979.5006
2029 | 2008 | 10 | 20 | 2 | 26364.7421
2029 | 2008 | 10 | 20 | 3 | 25006.738
2029 | 2008 | 10 | 20 | 4 | 23813.7072
2029 | 2008 | 10 | 20 | 5 | 21579.1406
2029 | 2008 | 10 | 20 | 6 | 19873.0259
2029 | 2008 | 10 | 20 | 7 | 18455.1868
2029 | 2008 | 10 | 20 | 8 | 16348.1822
2029 | 2008 | 10 | 20 | 9 | 12769.8174
2029 | 2008 | 10 | 20 | 10 | 7008.6383
2029 | 2008 | 10 | 20 | 11 | 6159.4851
2029 | 2008 | 10 | 20 | 12 | 4933.9208
2029 | 2008 | 10 | 20 | 13 | 3904.4137
2029 | 2008 | 10 | 20 | 14 | 3495.7008
2029 | 2008 | 10 | 20 | 15 | 3551.0557
2029 | 2008 | 10 | 20 | 16 | 3764.0401
2029 | 2008 | 10 | 20 | 17 | 4054.8647
2029 | 2008 | 10 | 20 | 18 | 5415.6701
2029 | 2008 | 10 | 20 | 19 | 8490.6097
2029 | 2008 | 10 | 20 | 20 | 11467.6515
2029 | 2008 | 10 | 20 | 21 | 15181.0564
2029 | 2008 | 10 | 20 | 22 | 16552.3494
2029 | 2008 | 10 | 20 | 23 | 17000.1165
2029 | 2008 | 10 | 20 | 24 | 16153.3408
2029 | 2008 | 10 | 21 | 1 | 15237.1291
2029 | 2008 | 10 | 21 | 2 | 14505.1054
2029 | 2008 | 10 | 21 | 3 | 13918.4698
2029 | 2008 | 10 | 21 | 4 | 12548.7998
2029 | 2008 | 10 | 21 | 5 | 10589.9998
2029 | 2008 | 10 | 21 | 6 | 9244.1797
2029 | 2008 | 10 | 21 | 7 | 5925.6009
2029 | 2008 | 10 | 21 | 8 | 6617.6096
2029 | 2008 | 10 | 21 | 9 | 5629.211
2029 | 2008 | 10 | 21 | 10 | 5088.0931
2029 | 2008 | 10 | 21 | 11 | 6114.0866
2029 | 2008 | 10 | 21 | 12 | 8063.1332
2029 | 2008 | 10 | 21 | 13 | 11134.5218
2029 | 2008 | 10 | 21 | 14 | 13555.156
2029 | 2008 | 10 | 21 | 15 | 15607.9699
2029 | 2008 | 10 | 21 | 16 | 17683.5216
2029 | 2008 | 10 | 21 | 17 | 18527.3211
2029 | 2008 | 10 | 21 | 18 | 18977.0257
2029 | 2008 | 10 | 21 | 19 | 22276.3655
2029 | 2008 | 10 | 21 | 20 | 26692.8896
2029 | 2008 | 10 | 21 | 21 | 29313.3594
2029 | 2008 | 10 | 21 | 22 | 30370.1794
2029 | 2008 | 10 | 21 | 23 | 30489.8692
2029 | 2008 | 10 | 21 | 24 | 31473.2932
2029 | 2008 | 10 | 22 | 1 | 31228.2352
2029 | 2008 | 10 | 22 | 2 | 29909.0254
2029 | 2008 | 10 | 22 | 3 | 30250.3664
2029 | 2008 | 10 | 22 | 4 | 29147.3395
2029 | 2008 | 10 | 22 | 5 | 27433.4641
2029 | 2008 | 10 | 22 | 6 | 25693.4688
2029 | 2008 | 10 | 22 | 7 | 22955.3956
2029 | 2008 | 10 | 22 | 8 | 21806.24
2029 | 2008 | 10 | 22 | 9 | 19238.6026
2029 | 2008 | 10 | 22 | 10 | 21908.3607
2029 | 2008 | 10 | 22 | 11 | 24244.0316
2029 | 2008 | 10 | 22 | 12 | 25193.2974
2029 | 2008 | 10 | 22 | 13 | 26551.5701
2029 | 2008 | 10 | 22 | 14 | 27186.5584
2029 | 2008 | 10 | 22 | 15 | 26526.7195
2029 | 2008 | 10 | 22 | 16 | 26925.5889
2029 | 2008 | 10 | 22 | 17 | 27269.2948
2029 | 2008 | 10 | 22 | 18 | 26772.5701
2029 | 2008 | 10 | 22 | 19 | 24424.5803
2029 | 2008 | 10 | 22 | 20 | 23744.4139
2029 | 2008 | 10 | 22 | 21 | 21996.1129
2029 | 2008 | 10 | 22 | 22 | 19434.518
2029 | 2008 | 10 | 22 | 23 | 16943.2963
2029 | 2008 | 10 | 22 | 24 | 14770.6414
2029 | 2008 | 10 | 23 | 1 | 13270.4174
2029 | 2008 | 10 | 23 | 2 | 14579.0938
2029 | 2008 | 10 | 23 | 3 | 15958.1233
2029 | 2008 | 10 | 23 | 4 | 16753.2592
2029 | 2008 | 10 | 23 | 5 | 17470.7822
2029 | 2008 | 10 | 23 | 6 | 18536.5881
2029 | 2008 | 10 | 23 | 7 | 18868.2573
2029 | 2008 | 10 | 23 | 8 | 18887.2157
2029 | 2008 | 10 | 23 | 9 | 17598.3779
2029 | 2008 | 10 | 23 | 10 | 16634.3448
2029 | 2008 | 10 | 23 | 11 | 15632.406
2029 | 2008 | 10 | 23 | 12 | 16919.2126
2029 | 2008 | 10 | 23 | 13 | 16567.4867
2029 | 2008 | 10 | 23 | 14 | 17487.0285
2029 | 2008 | 10 | 23 | 15 | 18141.6492
2029 | 2008 | 10 | 23 | 16 | 17392.929
2029 | 2008 | 10 | 23 | 17 | 15751.9811
2029 | 2008 | 10 | 23 | 18 | 11841.7161
2029 | 2008 | 10 | 23 | 19 | 8133.8892
2029 | 2008 | 10 | 23 | 20 | 7338.5757
2029 | 2008 | 10 | 23 | 21 | 6369.8723
2029 | 2008 | 10 | 23 | 22 | 8588.583
2029 | 2008 | 10 | 23 | 23 | 9467.0858
2029 | 2008 | 10 | 23 | 24 | 9588.7308
2029 | 2008 | 10 | 24 | 1 | 11519.3158
2029 | 2008 | 10 | 24 | 2 | 11845.4094
2029 | 2008 | 10 | 24 | 3 | 10551.5047
2029 | 2008 | 10 | 24 | 4 | 10026.0511
2029 | 2008 | 10 | 24 | 5 | 9282.4007
2029 | 2008 | 10 | 24 | 6 | 8371.5462
2029 | 2008 | 10 | 24 | 7 | 7742.6382
2029 | 2008 | 10 | 24 | 8 | 6780.7561
2029 | 2008 | 10 | 24 | 9 | 5694.0907
2029 | 2008 | 10 | 24 | 10 | 3426.9337
2029 | 2008 | 10 | 24 | 11 | 2767.5345
2029 | 2008 | 10 | 24 | 12 | 2796.1573
2029 | 2008 | 10 | 24 | 13 | 2478.5862
2029 | 2008 | 10 | 24 | 14 | 2562.3166
2029 | 2008 | 10 | 24 | 15 | 2212.532
2029 | 2008 | 10 | 24 | 16 | 1739.7473
2029 | 2008 | 10 | 24 | 17 | 1235.9358
2029 | 2008 | 10 | 24 | 18 | 1447.5973
2029 | 2008 | 10 | 24 | 19 | 2337.7979
2029 | 2008 | 10 | 24 | 20 | 3496.6916
2029 | 2008 | 10 | 24 | 21 | 5434.5248
2029 | 2008 | 10 | 24 | 22 | 7938.139
2029 | 2008 | 10 | 24 | 23 | 9020.9938
2029 | 2008 | 10 | 24 | 24 | 9550.3404
2029 | 2008 | 10 | 25 | 1 | 9592.2474
2029 | 2008 | 10 | 25 | 2 | 9181.7231
2029 | 2008 | 10 | 25 | 3 | 8084.7477
2029 | 2008 | 10 | 25 | 4 | 7052.7188
2029 | 2008 | 10 | 25 | 5 | 6115.4232
2029 | 2008 | 10 | 25 | 6 | 5204.0969
2029 | 2008 | 10 | 25 | 7 | 4729.595
2029 | 2008 | 10 | 25 | 8 | 4492.0792
2029 | 2008 | 10 | 25 | 9 | 4102.0806
2029 | 2008 | 10 | 25 | 10 | 3699.4737
2029 | 2008 | 10 | 25 | 11 | 3006.5815
2029 | 2008 | 10 | 25 | 12 | 3761.7374
2029 | 2008 | 10 | 25 | 13 | 3974.0498
2029 | 2008 | 10 | 25 | 14 | 4702.9592
2029 | 2008 | 10 | 25 | 15 | 5805.9708
2029 | 2008 | 10 | 25 | 16 | 6715.0161
2029 | 2008 | 10 | 25 | 17 | 6710.2337
2029 | 2008 | 10 | 25 | 18 | 6736.7983
2029 | 2008 | 10 | 25 | 19 | 7982.1577
2029 | 2008 | 10 | 25 | 20 | 11969.8911
2029 | 2008 | 10 | 25 | 21 | 17073.0315
2029 | 2008 | 10 | 25 | 22 | 21831.599
2029 | 2008 | 10 | 25 | 23 | 24880.0249
2029 | 2008 | 10 | 25 | 24 | 27089.8308
2029 | 2008 | 10 | 26 | 1 | 27990.4231
2029 | 2008 | 10 | 26 | 2 | 28048.6532
2029 | 2008 | 10 | 26 | 3 | 27798.7812
2029 | 2008 | 10 | 26 | 4 | 26268.1746
2029 | 2008 | 10 | 26 | 5 | 25968.1501
2029 | 2008 | 10 | 26 | 6 | 25863.446
2029 | 2008 | 10 | 26 | 7 | 24077.264
2029 | 2008 | 10 | 26 | 8 | 21615.3432
2029 | 2008 | 10 | 26 | 9 | 17738.938
2029 | 2008 | 10 | 26 | 10 | 13391.1965
2029 | 2008 | 10 | 26 | 11 | 11522.8905
2029 | 2008 | 10 | 26 | 12 | 9882.9848
2029 | 2008 | 10 | 26 | 13 | 9153.7961
2029 | 2008 | 10 | 26 | 14 | 9910.5053
2029 | 2008 | 10 | 26 | 15 | 13217.9259
2029 | 2008 | 10 | 26 | 16 | 16733.0086
2029 | 2008 | 10 | 26 | 17 | 20158.6486
2029 | 2008 | 10 | 26 | 18 | 24096.6152
2029 | 2008 | 10 | 26 | 19 | 26517.3879
2029 | 2008 | 10 | 26 | 20 | 29197.7003
2029 | 2008 | 10 | 26 | 21 | 31237.3603
2029 | 2008 | 10 | 26 | 22 | 31468.671
2029 | 2008 | 10 | 26 | 23 | 30529.9948
2029 | 2008 | 10 | 26 | 24 | 29367.5058
2029 | 2008 | 10 | 27 | 1 | 27923.6449
2029 | 2008 | 10 | 27 | 2 | 26172.8844
2029 | 2008 | 10 | 27 | 3 | 24803.7156
2029 | 2008 | 10 | 27 | 4 | 23696.3908
2029 | 2008 | 10 | 27 | 5 | 22656.1273
2029 | 2008 | 10 | 27 | 6 | 22727.6179
2029 | 2008 | 10 | 27 | 7 | 22169.1452
2029 | 2008 | 10 | 27 | 8 | 20829.2526
2029 | 2008 | 10 | 27 | 9 | 17613.9298
2029 | 2008 | 10 | 27 | 10 | 15605.1204
2029 | 2008 | 10 | 27 | 11 | 16913.576
2029 | 2008 | 10 | 27 | 12 | 14678.9232
2029 | 2008 | 10 | 27 | 13 | 13976.4451
2029 | 2008 | 10 | 27 | 14 | 12736.9938
2029 | 2008 | 10 | 27 | 15 | 11973.3979
2029 | 2008 | 10 | 27 | 16 | 11097.5761
2029 | 2008 | 10 | 27 | 17 | 9645.3005
2029 | 2008 | 10 | 27 | 18 | 8115.508
2029 | 2008 | 10 | 27 | 19 | 7054.0431
2029 | 2008 | 10 | 27 | 20 | 7512.2204
2029 | 2008 | 10 | 27 | 21 | 8295.5787
2029 | 2008 | 10 | 27 | 22 | 9229.0572
2029 | 2008 | 10 | 27 | 23 | 10213.1256
2029 | 2008 | 10 | 27 | 24 | 11497.9185
2029 | 2008 | 10 | 28 | 1 | 11862.3674
2029 | 2008 | 10 | 28 | 2 | 12447.6738
2029 | 2008 | 10 | 28 | 3 | 13019.8128
2029 | 2008 | 10 | 28 | 4 | 13441.3522
2029 | 2008 | 10 | 28 | 5 | 14450.0689
2029 | 2008 | 10 | 28 | 6 | 15670.9509
2029 | 2008 | 10 | 28 | 7 | 16879.4417
2029 | 2008 | 10 | 28 | 8 | 17175.8572
2029 | 2008 | 10 | 28 | 9 | 15846.4791
2029 | 2008 | 10 | 28 | 10 | 9754.4096
2029 | 2008 | 10 | 28 | 11 | 10354.1945
2029 | 2008 | 10 | 28 | 12 | 11356.4806
2029 | 2008 | 10 | 28 | 13 | 10684.6448
2029 | 2008 | 10 | 28 | 14 | 10164.1992
2029 | 2008 | 10 | 28 | 15 | 10304.9818
2029 | 2008 | 10 | 28 | 16 | 10524.8558
2029 | 2008 | 10 | 28 | 17 | 10795.9475
2029 | 2008 | 10 | 28 | 18 | 11879.805
2029 | 2008 | 10 | 28 | 19 | 15660.9268
2029 | 2008 | 10 | 28 | 20 | 20083.3905
2029 | 2008 | 10 | 28 | 21 | 24178.7524
2029 | 2008 | 10 | 28 | 22 | 25737.1243
2029 | 2008 | 10 | 28 | 23 | 26014.8798
2029 | 2008 | 10 | 28 | 24 | 26243.6559
2029 | 2008 | 10 | 29 | 1 | 26234.2972
2029 | 2008 | 10 | 29 | 2 | 25771.7205
2029 | 2008 | 10 | 29 | 3 | 25140.313
2029 | 2008 | 10 | 29 | 4 | 24125.6922
2029 | 2008 | 10 | 29 | 5 | 23055.5863
2029 | 2008 | 10 | 29 | 6 | 21637.4925
2029 | 2008 | 10 | 29 | 7 | 20281.4339
2029 | 2008 | 10 | 29 | 8 | 18482.1286
2029 | 2008 | 10 | 29 | 9 | 15331.0274
2029 | 2008 | 10 | 29 | 10 | 9745.7852
2029 | 2008 | 10 | 29 | 11 | 9575.2012
2029 | 2008 | 10 | 29 | 12 | 9049.3236
2029 | 2008 | 10 | 29 | 13 | 8258.5943
2029 | 2008 | 10 | 29 | 14 | 7879.0716
2029 | 2008 | 10 | 29 | 15 | 7984.3105
2029 | 2008 | 10 | 29 | 16 | 8385.2772
2029 | 2008 | 10 | 29 | 17 | 8825.0955
2029 | 2008 | 10 | 29 | 18 | 10061.5678
2029 | 2008 | 10 | 29 | 19 | 12962.7963
2029 | 2008 | 10 | 29 | 20 | 17941.9384
2029 | 2008 | 10 | 29 | 21 | 23758.6573
2029 | 2008 | 10 | 29 | 22 | 27123.3478
2029 | 2008 | 10 | 29 | 23 | 28584.6629
2029 | 2008 | 10 | 29 | 24 | 29311.4442
2029 | 2008 | 10 | 30 | 1 | 29608.3351
2029 | 2008 | 10 | 30 | 2 | 29223.1289
2029 | 2008 | 10 | 30 | 3 | 28935.0541
2029 | 2008 | 10 | 30 | 4 | 28545.4783
2029 | 2008 | 10 | 30 | 5 | 28413.8822
2029 | 2008 | 10 | 30 | 6 | 25361.5664
2029 | 2008 | 10 | 30 | 7 | 25064.7464
2029 | 2008 | 10 | 30 | 8 | 24227.7106
2029 | 2008 | 10 | 30 | 9 | 22041.2147
2029 | 2008 | 10 | 30 | 10 | 19923.5861
2029 | 2008 | 10 | 30 | 11 | 18886.2214
2029 | 2008 | 10 | 30 | 12 | 19157.892
2029 | 2008 | 10 | 30 | 13 | 18721.8765
2029 | 2008 | 10 | 30 | 14 | 19388.4308
2029 | 2008 | 10 | 30 | 15 | 19881.3269
2029 | 2008 | 10 | 30 | 16 | 19645.5725
2029 | 2008 | 10 | 30 | 17 | 19159.7903
2029 | 2008 | 10 | 30 | 18 | 19388.2878
2029 | 2008 | 10 | 30 | 19 | 22322.3654
2029 | 2008 | 10 | 30 | 20 | 25243.7932
2029 | 2008 | 10 | 30 | 21 | 26935.8814
2029 | 2008 | 10 | 30 | 22 | 26633.7013
2029 | 2008 | 10 | 30 | 23 | 26616.3951
2029 | 2008 | 10 | 30 | 24 | 29208.5169
2029 | 2008 | 10 | 31 | 1 | 28066.9572
2029 | 2008 | 10 | 31 | 2 | 26913.1144
2029 | 2008 | 10 | 31 | 3 | 25758.7862
2029 | 2008 | 10 | 31 | 4 | 24514.6254
2029 | 2008 | 10 | 31 | 5 | 22193.2998
2029 | 2008 | 10 | 31 | 6 | 20516.6419
2029 | 2008 | 10 | 31 | 7 | 18127.6153
2029 | 2008 | 10 | 31 | 8 | 16421.042
2029 | 2008 | 10 | 31 | 9 | 13400.4037
2029 | 2008 | 10 | 31 | 10 | 13239.1017
2029 | 2008 | 10 | 31 | 11 | 12766.2726
2029 | 2008 | 10 | 31 | 12 | 11358.8213
2029 | 2008 | 10 | 31 | 13 | 10257.7509
2029 | 2008 | 10 | 31 | 14 | 8821.8591
2029 | 2008 | 10 | 31 | 15 | 7444.1347
2029 | 2008 | 10 | 31 | 16 | 5847.2445
2029 | 2008 | 10 | 31 | 17 | 5127.7051
2029 | 2008 | 10 | 31 | 18 | 5342.8239
2029 | 2008 | 10 | 31 | 19 | 8382.4381
2029 | 2008 | 10 | 31 | 20 | 10680.0114
2029 | 2008 | 10 | 31 | 21 | 12739.1922
2029 | 2008 | 10 | 31 | 22 | 14219.5224
2029 | 2008 | 10 | 31 | 23 | 14608.371
2029 | 2008 | 10 | 31 | 24 | 14417.2362
2030 | 2008 | 10 | 1 | 1 | 6636.2232
2030 | 2008 | 10 | 1 | 2 | 6793.4699
2030 | 2008 | 10 | 1 | 3 | 6483.7449
2030 | 2008 | 10 | 1 | 4 | 6866.2229
2030 | 2008 | 10 | 1 | 5 | 6913.4056
2030 | 2008 | 10 | 1 | 6 | 6030.0329
2030 | 2008 | 10 | 1 | 7 | 5354.816
2030 | 2008 | 10 | 1 | 8 | 4531.3852
2030 | 2008 | 10 | 1 | 9 | 3619.7301
2030 | 2008 | 10 | 1 | 10 | 1724.774
2030 | 2008 | 10 | 1 | 11 | 1825.7456
2030 | 2008 | 10 | 1 | 12 | 1646.1095
2030 | 2008 | 10 | 1 | 13 | 1611.5497
2030 | 2008 | 10 | 1 | 14 | 1538.4372
2030 | 2008 | 10 | 1 | 15 | 1330.7201
2030 | 2008 | 10 | 1 | 16 | 1156.9454
2030 | 2008 | 10 | 1 | 17 | 1143.4801
2030 | 2008 | 10 | 1 | 18 | 1696.7147
2030 | 2008 | 10 | 1 | 19 | 3998.0427
2030 | 2008 | 10 | 1 | 20 | 4455.5466
2030 | 2008 | 10 | 1 | 21 | 5943.1331
2030 | 2008 | 10 | 1 | 22 | 8190.8845
2030 | 2008 | 10 | 1 | 23 | 9035.999
2030 | 2008 | 10 | 1 | 24 | 9095.889
2030 | 2008 | 10 | 2 | 1 | 9080.3685
2030 | 2008 | 10 | 2 | 2 | 9585.8682
2030 | 2008 | 10 | 2 | 3 | 9923.3821
2030 | 2008 | 10 | 2 | 4 | 9987.3566
2030 | 2008 | 10 | 2 | 5 | 9629.0262
2030 | 2008 | 10 | 2 | 6 | 8790.8909
2030 | 2008 | 10 | 2 | 7 | 8605.9336
2030 | 2008 | 10 | 2 | 8 | 7262.5895
2030 | 2008 | 10 | 2 | 9 | 6117.0074
2030 | 2008 | 10 | 2 | 10 | 3634.0899
2030 | 2008 | 10 | 2 | 11 | 4498.781
2030 | 2008 | 10 | 2 | 12 | 4092.8002
2030 | 2008 | 10 | 2 | 13 | 3917.1993
2030 | 2008 | 10 | 2 | 14 | 4034.2207
2030 | 2008 | 10 | 2 | 15 | 4414.9342
2030 | 2008 | 10 | 2 | 16 | 4578.8078
2030 | 2008 | 10 | 2 | 17 | 5151.2776
2030 | 2008 | 10 | 2 | 18 | 6439.3635
2030 | 2008 | 10 | 2 | 19 | 8884.4476
2030 | 2008 | 10 | 2 | 20 | 12713.7602
2030 | 2008 | 10 | 2 | 21 | 17558.6533
2030 | 2008 | 10 | 2 | 22 | 21363.5713
2030 | 2008 | 10 | 2 | 23 | 23952.398
2030 | 2008 | 10 | 2 | 24 | 26162.6489
2030 | 2008 | 10 | 3 | 1 | 26985.9552
2030 | 2008 | 10 | 3 | 2 | 27219.6708
2030 | 2008 | 10 | 3 | 3 | 27629.214
2030 | 2008 | 10 | 3 | 4 | 27645.7884
2030 | 2008 | 10 | 3 | 5 | 26789.6976
2030 | 2008 | 10 | 3 | 6 | 26286.1544
2030 | 2008 | 10 | 3 | 7 | 25205.9229
2030 | 2008 | 10 | 3 | 8 | 22831.5824
2030 | 2008 | 10 | 3 | 9 | 19071.7801
2030 | 2008 | 10 | 3 | 10 | 13769.7881
2030 | 2008 | 10 | 3 | 11 | 15050.6593
2030 | 2008 | 10 | 3 | 12 | 16339.2649
2030 | 2008 | 10 | 3 | 13 | 17090.7658
2030 | 2008 | 10 | 3 | 14 | 18273.7877
2030 | 2008 | 10 | 3 | 15 | 19788.9793
2030 | 2008 | 10 | 3 | 16 | 20276.8318
2030 | 2008 | 10 | 3 | 17 | 21749.9702
2030 | 2008 | 10 | 3 | 18 | 22604.3417
2030 | 2008 | 10 | 3 | 19 | 24800.7222
2030 | 2008 | 10 | 3 | 20 | 30017.705
2030 | 2008 | 10 | 3 | 21 | 32769.5982
2030 | 2008 | 10 | 3 | 22 | 33165.3963
2030 | 2008 | 10 | 3 | 23 | 32555.9914
2030 | 2008 | 10 | 3 | 24 | 32749.5815
2030 | 2008 | 10 | 4 | 1 | 32843.657
2030 | 2008 | 10 | 4 | 2 | 33037.0746
2030 | 2008 | 10 | 4 | 3 | 33145.3367
2030 | 2008 | 10 | 4 | 4 | 32608.1021
2030 | 2008 | 10 | 4 | 5 | 32119.1617
2030 | 2008 | 10 | 4 | 6 | 31185.3152
2030 | 2008 | 10 | 4 | 7 | 30873.1136
2030 | 2008 | 10 | 4 | 8 | 28905.0047
2030 | 2008 | 10 | 4 | 9 | 25565.9554
2030 | 2008 | 10 | 4 | 10 | 26552.2365
2030 | 2008 | 10 | 4 | 11 | 29408.2476
2030 | 2008 | 10 | 4 | 12 | 30080.7068
2030 | 2008 | 10 | 4 | 13 | 31026.9196
2030 | 2008 | 10 | 4 | 14 | 31994.4781
2030 | 2008 | 10 | 4 | 15 | 33309.458
2030 | 2008 | 10 | 4 | 16 | 34530.4664
2030 | 2008 | 10 | 4 | 17 | 35005.9899
2030 | 2008 | 10 | 4 | 18 | 35305.9884
2030 | 2008 | 10 | 4 | 19 | 34637.9188
2030 | 2008 | 10 | 4 | 20 | 34953.149
2030 | 2008 | 10 | 4 | 21 | 34938.2398
2030 | 2008 | 10 | 4 | 22 | 34805.1718
2030 | 2008 | 10 | 4 | 23 | 34699.8052
2030 | 2008 | 10 | 4 | 24 | 34368.1426
2030 | 2008 | 10 | 5 | 1 | 34174.5426
2030 | 2008 | 10 | 5 | 2 | 33971.0747
2030 | 2008 | 10 | 5 | 3 | 33452.8352
2030 | 2008 | 10 | 5 | 4 | 33155.96
2030 | 2008 | 10 | 5 | 5 | 32643.9014
2030 | 2008 | 10 | 5 | 6 | 32202.964
2030 | 2008 | 10 | 5 | 7 | 31171.2294
2030 | 2008 | 10 | 5 | 8 | 29058.9486
2030 | 2008 | 10 | 5 | 9 | 25585.6209
2030 | 2008 | 10 | 5 | 10 | 29779.1466
2030 | 2008 | 10 | 5 | 11 | 32788.6498
2030 | 2008 | 10 | 5 | 12 | 33012.0544
2030 | 2008 | 10 | 5 | 13 | 33651.832
2030 | 2008 | 10 | 5 | 14 | 32801.242
2030 | 2008 | 10 | 5 | 15 | 33240.3498
2030 | 2008 | 10 | 5 | 16 | 32782.6488
2030 | 2008 | 10 | 5 | 17 | 32979.9046
2030 | 2008 | 10 | 5 | 18 | 32847.159
2030 | 2008 | 10 | 5 | 19 | 31566.926
2030 | 2008 | 10 | 5 | 20 | 31817.0012
2030 | 2008 | 10 | 5 | 21 | 31620.9795
2030 | 2008 | 10 | 5 | 22 | 29882.8652
2030 | 2008 | 10 | 5 | 23 | 29998.6165
2030 | 2008 | 10 | 5 | 24 | 28672.9732
2030 | 2008 | 10 | 6 | 1 | 28486.3132
2030 | 2008 | 10 | 6 | 2 | 28964.5578
2030 | 2008 | 10 | 6 | 3 | 28331.1296
2030 | 2008 | 10 | 6 | 4 | 28278.2596
2030 | 2008 | 10 | 6 | 5 | 28361.5613
2030 | 2008 | 10 | 6 | 6 | 26868.8036
2030 | 2008 | 10 | 6 | 7 | 25955.748
2030 | 2008 | 10 | 6 | 8 | 24408.5645
2030 | 2008 | 10 | 6 | 9 | 21792.6141
2030 | 2008 | 10 | 6 | 10 | 25125.4537
2030 | 2008 | 10 | 6 | 11 | 26308.0448
2030 | 2008 | 10 | 6 | 12 | 25703.8826
2030 | 2008 | 10 | 6 | 13 | 24552.6439
2030 | 2008 | 10 | 6 | 14 | 23011.2525
2030 | 2008 | 10 | 6 | 15 | 21511.015
2030 | 2008 | 10 | 6 | 16 | 19656.5522
2030 | 2008 | 10 | 6 | 17 | 16349.6608
2030 | 2008 | 10 | 6 | 18 | 13131.0145
2030 | 2008 | 10 | 6 | 19 | 11338.3427
2030 | 2008 | 10 | 6 | 20 | 13618.4599
2030 | 2008 | 10 | 6 | 21 | 16402.8198
2030 | 2008 | 10 | 6 | 22 | 18232.4803
2030 | 2008 | 10 | 6 | 23 | 16596.881
2030 | 2008 | 10 | 6 | 24 | 16476.0671
2030 | 2008 | 10 | 7 | 1 | 16272.5699
2030 | 2008 | 10 | 7 | 2 | 17106.7619
2030 | 2008 | 10 | 7 | 3 | 17591.0457
2030 | 2008 | 10 | 7 | 4 | 18510.0566
2030 | 2008 | 10 | 7 | 5 | 19176.2403
2030 | 2008 | 10 | 7 | 6 | 19341.3748
2030 | 2008 | 10 | 7 | 7 | 20139.9046
2030 | 2008 | 10 | 7 | 8 | 19560.6969
2030 | 2008 | 10 | 7 | 9 | 17395.0498
2030 | 2008 | 10 | 7 | 10 | 16246.5536
2030 | 2008 | 10 | 7 | 11 | 18834.3255
2030 | 2008 | 10 | 7 | 12 | 17959.6473
2030 | 2008 | 10 | 7 | 13 | 17142.9977
2030 | 2008 | 10 | 7 | 14 | 16812.4634
2030 | 2008 | 10 | 7 | 15 | 17118.5706
2030 | 2008 | 10 | 7 | 16 | 15582.3342
2030 | 2008 | 10 | 7 | 17 | 14142.8114
2030 | 2008 | 10 | 7 | 18 | 11094.3598
2030 | 2008 | 10 | 7 | 19 | 8240.3517
2030 | 2008 | 10 | 7 | 20 | 7062.6741
2030 | 2008 | 10 | 7 | 21 | 6595.226
2030 | 2008 | 10 | 7 | 22 | 6974.9855
2030 | 2008 | 10 | 7 | 23 | 7684.7843
2030 | 2008 | 10 | 7 | 24 | 8551.7026
2030 | 2008 | 10 | 8 | 1 | 10408.2141
2030 | 2008 | 10 | 8 | 2 | 12234.4119
2030 | 2008 | 10 | 8 | 3 | 14693.2931
2030 | 2008 | 10 | 8 | 4 | 16249.2589
2030 | 2008 | 10 | 8 | 5 | 17360.7347
2030 | 2008 | 10 | 8 | 6 | 16361.8875
2030 | 2008 | 10 | 8 | 7 | 16710.698
2030 | 2008 | 10 | 8 | 8 | 15632.5987
2030 | 2008 | 10 | 8 | 9 | 13610.5338
2030 | 2008 | 10 | 8 | 10 | 8598.9305
2030 | 2008 | 10 | 8 | 11 | 8380.8948
2030 | 2008 | 10 | 8 | 12 | 8289.6149
2030 | 2008 | 10 | 8 | 13 | 7503.7602
2030 | 2008 | 10 | 8 | 14 | 6557.1002
2030 | 2008 | 10 | 8 | 15 | 6044.1197
2030 | 2008 | 10 | 8 | 16 | 5658.4177
2030 | 2008 | 10 | 8 | 17 | 5435.6459
2030 | 2008 | 10 | 8 | 18 | 5944.0706
2030 | 2008 | 10 | 8 | 19 | 7840.4477
2030 | 2008 | 10 | 8 | 20 | 11313.7184
2030 | 2008 | 10 | 8 | 21 | 16716.1772
2030 | 2008 | 10 | 8 | 22 | 20613.0756
2030 | 2008 | 10 | 8 | 23 | 22992.8495
2030 | 2008 | 10 | 8 | 24 | 24743.2404
2030 | 2008 | 10 | 9 | 1 | 24343.9233
2030 | 2008 | 10 | 9 | 2 | 23730.5978
2030 | 2008 | 10 | 9 | 3 | 23078.8943
2030 | 2008 | 10 | 9 | 4 | 22214.8436
2030 | 2008 | 10 | 9 | 5 | 21482.4987
2030 | 2008 | 10 | 9 | 6 | 21319.0943
2030 | 2008 | 10 | 9 | 7 | 20785.2345
2030 | 2008 | 10 | 9 | 8 | 19998.4086
2030 | 2008 | 10 | 9 | 9 | 17397.799
2030 | 2008 | 10 | 9 | 10 | 11262.1837
2030 | 2008 | 10 | 9 | 11 | 14342.2201
2030 | 2008 | 10 | 9 | 12 | 18301.2486
2030 | 2008 | 10 | 9 | 13 | 19702.4202
2030 | 2008 | 10 | 9 | 14 | 20695.7468
2030 | 2008 | 10 | 9 | 15 | 21142.3444
2030 | 2008 | 10 | 9 | 16 | 21933.7523
2030 | 2008 | 10 | 9 | 17 | 21772.6966
2030 | 2008 | 10 | 9 | 18 | 22202.2442
2030 | 2008 | 10 | 9 | 19 | 24678.6338
2030 | 2008 | 10 | 9 | 20 | 28589.0874
2030 | 2008 | 10 | 9 | 21 | 31104.19
2030 | 2008 | 10 | 9 | 22 | 31348.1021
2030 | 2008 | 10 | 9 | 23 | 31375.667
2030 | 2008 | 10 | 9 | 24 | 31151.3908
2030 | 2008 | 10 | 10 | 1 | 30646.1571
2030 | 2008 | 10 | 10 | 2 | 30423.2333
2030 | 2008 | 10 | 10 | 3 | 30250.6349
2030 | 2008 | 10 | 10 | 4 | 29697.3939
2030 | 2008 | 10 | 10 | 5 | 29476.5994
2030 | 2008 | 10 | 10 | 6 | 29338.4242
2030 | 2008 | 10 | 10 | 7 | 28767.4306
2030 | 2008 | 10 | 10 | 8 | 26931.36
2030 | 2008 | 10 | 10 | 9 | 23141.4125
2030 | 2008 | 10 | 10 | 10 | 20395.268
2030 | 2008 | 10 | 10 | 11 | 21698.1625
2030 | 2008 | 10 | 10 | 12 | 21161.3427
2030 | 2008 | 10 | 10 | 13 | 21277.5099
2030 | 2008 | 10 | 10 | 14 | 21827.2178
2030 | 2008 | 10 | 10 | 15 | 22518.5884
2030 | 2008 | 10 | 10 | 16 | 23610.5225
2030 | 2008 | 10 | 10 | 17 | 24576.6922
2030 | 2008 | 10 | 10 | 18 | 26096.7526
2030 | 2008 | 10 | 10 | 19 | 28338.1911
2030 | 2008 | 10 | 10 | 20 | 31214.3354
2030 | 2008 | 10 | 10 | 21 | 32920.218
2030 | 2008 | 10 | 10 | 22 | 33029.1016
2030 | 2008 | 10 | 10 | 23 | 32319.6562
2030 | 2008 | 10 | 10 | 24 | 31429.9986
2030 | 2008 | 10 | 11 | 1 | 30858.7131
2030 | 2008 | 10 | 11 | 2 | 29821.0669
2030 | 2008 | 10 | 11 | 3 | 29149.1316
2030 | 2008 | 10 | 11 | 4 | 27848.6466
2030 | 2008 | 10 | 11 | 5 | 26569.2669
2030 | 2008 | 10 | 11 | 6 | 24749.4475
2030 | 2008 | 10 | 11 | 7 | 22745.3062
2030 | 2008 | 10 | 11 | 8 | 20677.784
2030 | 2008 | 10 | 11 | 9 | 17312.5001
2030 | 2008 | 10 | 11 | 10 | 18658.8236
2030 | 2008 | 10 | 11 | 11 | 20106.7748
2030 | 2008 | 10 | 11 | 12 | 20732.533
2030 | 2008 | 10 | 11 | 13 | 22602.1238
2030 | 2008 | 10 | 11 | 14 | 24291.35
2030 | 2008 | 10 | 11 | 15 | 27053.9644
2030 | 2008 | 10 | 11 | 16 | 29439.2259
2030 | 2008 | 10 | 11 | 17 | 30490.0832
2030 | 2008 | 10 | 11 | 18 | 32389.8128
2030 | 2008 | 10 | 11 | 19 | 32321.1524
2030 | 2008 | 10 | 11 | 20 | 33487.644
2030 | 2008 | 10 | 11 | 21 | 34046.0167
2030 | 2008 | 10 | 11 | 22 | 33640.1325
2030 | 2008 | 10 | 11 | 23 | 33605.3364
2030 | 2008 | 10 | 11 | 24 | 32981.6607
2030 | 2008 | 10 | 12 | 1 | 32873.9419
2030 | 2008 | 10 | 12 | 2 | 32888.4865
2030 | 2008 | 10 | 12 | 3 | 32932.0062
2030 | 2008 | 10 | 12 | 4 | 32639.2466
2030 | 2008 | 10 | 12 | 5 | 31496.1083
2030 | 2008 | 10 | 12 | 6 | 31217.3903
2030 | 2008 | 10 | 12 | 7 | 30385.1539
2030 | 2008 | 10 | 12 | 8 | 28792.2181
2030 | 2008 | 10 | 12 | 9 | 25913.9878
2030 | 2008 | 10 | 12 | 10 | 30733.45
2030 | 2008 | 10 | 12 | 11 | 32435.9666
2030 | 2008 | 10 | 12 | 12 | 32720.4442
2030 | 2008 | 10 | 12 | 13 | 33771.9044
2030 | 2008 | 10 | 12 | 14 | 34014.0343
2030 | 2008 | 10 | 12 | 15 | 34233.7234
2030 | 2008 | 10 | 12 | 16 | 34381.5178
2030 | 2008 | 10 | 12 | 17 | 32965.4316
2030 | 2008 | 10 | 12 | 18 | 31686.4273
2030 | 2008 | 10 | 12 | 19 | 30421.284
2030 | 2008 | 10 | 12 | 20 | 31810.0858
2030 | 2008 | 10 | 12 | 21 | 32746.0408
2030 | 2008 | 10 | 12 | 22 | 32937.708
2030 | 2008 | 10 | 12 | 23 | 32317.2616
2030 | 2008 | 10 | 12 | 24 | 31925.7104
2030 | 2008 | 10 | 13 | 1 | 29751.4283
2030 | 2008 | 10 | 13 | 2 | 27873.1903
2030 | 2008 | 10 | 13 | 3 | 25846.3967
2030 | 2008 | 10 | 13 | 4 | 23897.8702
2030 | 2008 | 10 | 13 | 5 | 22144.7231
2030 | 2008 | 10 | 13 | 6 | 21193.7859
2030 | 2008 | 10 | 13 | 7 | 20450.4339
2030 | 2008 | 10 | 13 | 8 | 20003.6423
2030 | 2008 | 10 | 13 | 9 | 18327.9783
2030 | 2008 | 10 | 13 | 10 | 21951.9939
2030 | 2008 | 10 | 13 | 11 | 22765.9084
2030 | 2008 | 10 | 13 | 12 | 21470.7789
2030 | 2008 | 10 | 13 | 13 | 20359.0684
2030 | 2008 | 10 | 13 | 14 | 19555.881
2030 | 2008 | 10 | 13 | 15 | 18781.3671
2030 | 2008 | 10 | 13 | 16 | 18202.0795
2030 | 2008 | 10 | 13 | 17 | 18767.7119
2030 | 2008 | 10 | 13 | 18 | 20179.6468
2030 | 2008 | 10 | 13 | 19 | 21015.2647
2030 | 2008 | 10 | 13 | 20 | 21752.2441
2030 | 2008 | 10 | 13 | 21 | 22379.5368
2030 | 2008 | 10 | 13 | 22 | 21883.6698
2030 | 2008 | 10 | 13 | 23 | 20332.205
2030 | 2008 | 10 | 13 | 24 | 18742.2216
2030 | 2008 | 10 | 14 | 1 | 16169.6667
2030 | 2008 | 10 | 14 | 2 | 14926.1223
2030 | 2008 | 10 | 14 | 3 | 13768.0336
2030 | 2008 | 10 | 14 | 4 | 11991.6652
2030 | 2008 | 10 | 14 | 5 | 10082.364
2030 | 2008 | 10 | 14 | 6 | 8237.4412
2030 | 2008 | 10 | 14 | 7 | 7293.9482
2030 | 2008 | 10 | 14 | 8 | 6391.1276
2030 | 2008 | 10 | 14 | 9 | 5035.346
2030 | 2008 | 10 | 14 | 10 | 6153.4475
2030 | 2008 | 10 | 14 | 11 | 6457.3403
2030 | 2008 | 10 | 14 | 12 | 6815.8122
2030 | 2008 | 10 | 14 | 13 | 7446.0604
2030 | 2008 | 10 | 14 | 14 | 8503.8489
2030 | 2008 | 10 | 14 | 15 | 9553.0819
2030 | 2008 | 10 | 14 | 16 | 9996.94
2030 | 2008 | 10 | 14 | 17 | 9475.8497
2030 | 2008 | 10 | 14 | 18 | 9194.8467
2030 | 2008 | 10 | 14 | 19 | 9254.3158
2030 | 2008 | 10 | 14 | 20 | 9171.3578
2030 | 2008 | 10 | 14 | 21 | 10002.0722
2030 | 2008 | 10 | 14 | 22 | 9395.6839
2030 | 2008 | 10 | 14 | 23 | 8185.1805
2030 | 2008 | 10 | 14 | 24 | 7168.4418
2030 | 2008 | 10 | 15 | 1 | 6968.6606
2030 | 2008 | 10 | 15 | 2 | 7882.2761
2030 | 2008 | 10 | 15 | 3 | 8574.6774
2030 | 2008 | 10 | 15 | 4 | 9687.3319
2030 | 2008 | 10 | 15 | 5 | 10594.6191
2030 | 2008 | 10 | 15 | 6 | 11044.1699
2030 | 2008 | 10 | 15 | 7 | 11814.3701
2030 | 2008 | 10 | 15 | 8 | 11536.6356
2030 | 2008 | 10 | 15 | 9 | 10006.263
2030 | 2008 | 10 | 15 | 10 | 11880.1727
2030 | 2008 | 10 | 15 | 11 | 12204.8834
2030 | 2008 | 10 | 15 | 12 | 10657.8259
2030 | 2008 | 10 | 15 | 13 | 9622.6087
2030 | 2008 | 10 | 15 | 14 | 10297.7629
2030 | 2008 | 10 | 15 | 15 | 11300.565
2030 | 2008 | 10 | 15 | 16 | 12234.2706
2030 | 2008 | 10 | 15 | 17 | 12896.4871
2030 | 2008 | 10 | 15 | 18 | 12522.298
2030 | 2008 | 10 | 15 | 19 | 13022.6742
2030 | 2008 | 10 | 15 | 20 | 14369.6505
2030 | 2008 | 10 | 15 | 21 | 15757.4019
2030 | 2008 | 10 | 15 | 22 | 15169.9999
2030 | 2008 | 10 | 15 | 23 | 13601.5389
2030 | 2008 | 10 | 15 | 24 | 13542.8744
2030 | 2008 | 10 | 16 | 1 | 13331.4755
2030 | 2008 | 10 | 16 | 2 | 14007.3989
2030 | 2008 | 10 | 16 | 3 | 14800.0809
2030 | 2008 | 10 | 16 | 4 | 16017.864
2030 | 2008 | 10 | 16 | 5 | 15789.3524
2030 | 2008 | 10 | 16 | 6 | 16412.6229
2030 | 2008 | 10 | 16 | 7 | 16664.2289
2030 | 2008 | 10 | 16 | 8 | 16738.5449
2030 | 2008 | 10 | 16 | 9 | 15186.5292
2030 | 2008 | 10 | 16 | 10 | 19063.9562
2030 | 2008 | 10 | 16 | 11 | 19271.0208
2030 | 2008 | 10 | 16 | 12 | 17423.0099
2030 | 2008 | 10 | 16 | 13 | 15383.0557
2030 | 2008 | 10 | 16 | 14 | 13535.2548
2030 | 2008 | 10 | 16 | 15 | 12311.3962
2030 | 2008 | 10 | 16 | 16 | 10776.7633
2030 | 2008 | 10 | 16 | 17 | 8770.1939
2030 | 2008 | 10 | 16 | 18 | 7182.3006
2030 | 2008 | 10 | 16 | 19 | 5940.8291
2030 | 2008 | 10 | 16 | 20 | 5629.8273
2030 | 2008 | 10 | 16 | 21 | 5594.0475
2030 | 2008 | 10 | 16 | 22 | 5586.1886
2030 | 2008 | 10 | 16 | 23 | 5346.331
2030 | 2008 | 10 | 16 | 24 | 5255.132
2030 | 2008 | 10 | 17 | 1 | 5304.2221
2030 | 2008 | 10 | 17 | 2 | 5364.6763
2030 | 2008 | 10 | 17 | 3 | 5638.9368
2030 | 2008 | 10 | 17 | 4 | 6318.1394
2030 | 2008 | 10 | 17 | 5 | 6970.7263
2030 | 2008 | 10 | 17 | 6 | 7108.0736
2030 | 2008 | 10 | 17 | 7 | 6934.5469
2030 | 2008 | 10 | 17 | 8 | 5802.4165
2030 | 2008 | 10 | 17 | 9 | 5449.9412
2030 | 2008 | 10 | 17 | 10 | 5593.4309
2030 | 2008 | 10 | 17 | 11 | 5358.7296
2030 | 2008 | 10 | 17 | 12 | 5415.4463
2030 | 2008 | 10 | 17 | 13 | 5117.9643
2030 | 2008 | 10 | 17 | 14 | 4935.5525
2030 | 2008 | 10 | 17 | 15 | 4610.8115
2030 | 2008 | 10 | 17 | 16 | 4065.6349
2030 | 2008 | 10 | 17 | 17 | 3472.2908
2030 | 2008 | 10 | 17 | 18 | 3213.8655
2030 | 2008 | 10 | 17 | 19 | 3143.4217
2030 | 2008 | 10 | 17 | 20 | 2863.9419
2030 | 2008 | 10 | 17 | 21 | 2769.747
2030 | 2008 | 10 | 17 | 22 | 2814.9044
2030 | 2008 | 10 | 17 | 23 | 2988.8934
2030 | 2008 | 10 | 17 | 24 | 3592.0465
2030 | 2008 | 10 | 18 | 1 | 3745.3167
2030 | 2008 | 10 | 18 | 2 | 4233.2594
2030 | 2008 | 10 | 18 | 3 | 4439.5502
2030 | 2008 | 10 | 18 | 4 | 4907.8552
2030 | 2008 | 10 | 18 | 5 | 5274.6092
2030 | 2008 | 10 | 18 | 6 | 5853.3442
2030 | 2008 | 10 | 18 | 7 | 6444.7787
2030 | 2008 | 10 | 18 | 8 | 5447.7732
2030 | 2008 | 10 | 18 | 9 | 4411.466
2030 | 2008 | 10 | 18 | 10 | 4436.9981
2030 | 2008 | 10 | 18 | 11 | 4702.9578
2030 | 2008 | 10 | 18 | 12 | 5485.9235
2030 | 2008 | 10 | 18 | 13 | 6051.8433
2030 | 2008 | 10 | 18 | 14 | 6810.6533
2030 | 2008 | 10 | 18 | 15 | 7501.5381
2030 | 2008 | 10 | 18 | 16 | 7642.6826
2030 | 2008 | 10 | 18 | 17 | 7475.9927
2030 | 2008 | 10 | 18 | 18 | 7400.8326
2030 | 2008 | 10 | 18 | 19 | 7914.2225
2030 | 2008 | 10 | 18 | 20 | 9687.7024
2030 | 2008 | 10 | 18 | 21 | 11407.7128
2030 | 2008 | 10 | 18 | 22 | 13290.4126
2030 | 2008 | 10 | 18 | 23 | 14862.0414
2030 | 2008 | 10 | 18 | 24 | 16988.9361
2030 | 2008 | 10 | 19 | 1 | 19189.1522
2030 | 2008 | 10 | 19 | 2 | 20363.8579
2030 | 2008 | 10 | 19 | 3 | 20895.2608
2030 | 2008 | 10 | 19 | 4 | 20771.4955
2030 | 2008 | 10 | 19 | 5 | 20398.4598
2030 | 2008 | 10 | 19 | 6 | 20327.713
2030 | 2008 | 10 | 19 | 7 | 19513.6896
2030 | 2008 | 10 | 19 | 8 | 18993.896
2030 | 2008 | 10 | 19 | 9 | 16891.8242
2030 | 2008 | 10 | 19 | 10 | 10603.4147
2030 | 2008 | 10 | 19 | 11 | 13364.6137
2030 | 2008 | 10 | 19 | 12 | 14657.5248
2030 | 2008 | 10 | 19 | 13 | 13782.1656
2030 | 2008 | 10 | 19 | 14 | 13108.825
2030 | 2008 | 10 | 19 | 15 | 13234.9373
2030 | 2008 | 10 | 19 | 16 | 13302.7883
2030 | 2008 | 10 | 19 | 17 | 13158.6456
2030 | 2008 | 10 | 19 | 18 | 12982.656
2030 | 2008 | 10 | 19 | 19 | 15883.4019
2030 | 2008 | 10 | 19 | 20 | 20578.7706
2030 | 2008 | 10 | 19 | 21 | 25235.5279
2030 | 2008 | 10 | 19 | 22 | 27323.3048
2030 | 2008 | 10 | 19 | 23 | 27365.7136
2030 | 2008 | 10 | 19 | 24 | 27196.8756
2030 | 2008 | 10 | 20 | 1 | 26979.5006
2030 | 2008 | 10 | 20 | 2 | 26364.7421
2030 | 2008 | 10 | 20 | 3 | 25006.738
2030 | 2008 | 10 | 20 | 4 | 23813.7072
2030 | 2008 | 10 | 20 | 5 | 21579.1406
2030 | 2008 | 10 | 20 | 6 | 19873.0259
2030 | 2008 | 10 | 20 | 7 | 18455.1868
2030 | 2008 | 10 | 20 | 8 | 16348.1822
2030 | 2008 | 10 | 20 | 9 | 12769.8174
2030 | 2008 | 10 | 20 | 10 | 7008.6383
2030 | 2008 | 10 | 20 | 11 | 6159.4851
2030 | 2008 | 10 | 20 | 12 | 4933.9208
2030 | 2008 | 10 | 20 | 13 | 3904.4137
2030 | 2008 | 10 | 20 | 14 | 3495.7008
2030 | 2008 | 10 | 20 | 15 | 3551.0557
2030 | 2008 | 10 | 20 | 16 | 3764.0401
2030 | 2008 | 10 | 20 | 17 | 4054.8647
2030 | 2008 | 10 | 20 | 18 | 5415.6701
2030 | 2008 | 10 | 20 | 19 | 8490.6097
2030 | 2008 | 10 | 20 | 20 | 11467.6515
2030 | 2008 | 10 | 20 | 21 | 15181.0564
2030 | 2008 | 10 | 20 | 22 | 16552.3494
2030 | 2008 | 10 | 20 | 23 | 17000.1165
2030 | 2008 | 10 | 20 | 24 | 16153.3408
2030 | 2008 | 10 | 21 | 1 | 15237.1291
2030 | 2008 | 10 | 21 | 2 | 14505.1054
2030 | 2008 | 10 | 21 | 3 | 13918.4698
2030 | 2008 | 10 | 21 | 4 | 12548.7998
2030 | 2008 | 10 | 21 | 5 | 10589.9998
2030 | 2008 | 10 | 21 | 6 | 9244.1797
2030 | 2008 | 10 | 21 | 7 | 5925.6009
2030 | 2008 | 10 | 21 | 8 | 6617.6096
2030 | 2008 | 10 | 21 | 9 | 5629.211
2030 | 2008 | 10 | 21 | 10 | 5088.0931
2030 | 2008 | 10 | 21 | 11 | 6114.0866
2030 | 2008 | 10 | 21 | 12 | 8063.1332
2030 | 2008 | 10 | 21 | 13 | 11134.5218
2030 | 2008 | 10 | 21 | 14 | 13555.156
2030 | 2008 | 10 | 21 | 15 | 15607.9699
2030 | 2008 | 10 | 21 | 16 | 17683.5216
2030 | 2008 | 10 | 21 | 17 | 18527.3211
2030 | 2008 | 10 | 21 | 18 | 18977.0257
2030 | 2008 | 10 | 21 | 19 | 22276.3655
2030 | 2008 | 10 | 21 | 20 | 26692.8896
2030 | 2008 | 10 | 21 | 21 | 29313.3594
2030 | 2008 | 10 | 21 | 22 | 30370.1794
2030 | 2008 | 10 | 21 | 23 | 30489.8692
2030 | 2008 | 10 | 21 | 24 | 31473.2932
2030 | 2008 | 10 | 22 | 1 | 31228.2352
2030 | 2008 | 10 | 22 | 2 | 29909.0254
2030 | 2008 | 10 | 22 | 3 | 30250.3664
2030 | 2008 | 10 | 22 | 4 | 29147.3395
2030 | 2008 | 10 | 22 | 5 | 27433.4641
2030 | 2008 | 10 | 22 | 6 | 25693.4688
2030 | 2008 | 10 | 22 | 7 | 22955.3956
2030 | 2008 | 10 | 22 | 8 | 21806.24
2030 | 2008 | 10 | 22 | 9 | 19238.6026
2030 | 2008 | 10 | 22 | 10 | 21908.3607
2030 | 2008 | 10 | 22 | 11 | 24244.0316
2030 | 2008 | 10 | 22 | 12 | 25193.2974
2030 | 2008 | 10 | 22 | 13 | 26551.5701
2030 | 2008 | 10 | 22 | 14 | 27186.5584
2030 | 2008 | 10 | 22 | 15 | 26526.7195
2030 | 2008 | 10 | 22 | 16 | 26925.5889
2030 | 2008 | 10 | 22 | 17 | 27269.2948
2030 | 2008 | 10 | 22 | 18 | 26772.5701
2030 | 2008 | 10 | 22 | 19 | 24424.5803
2030 | 2008 | 10 | 22 | 20 | 23744.4139
2030 | 2008 | 10 | 22 | 21 | 21996.1129
2030 | 2008 | 10 | 22 | 22 | 19434.518
2030 | 2008 | 10 | 22 | 23 | 16943.2963
2030 | 2008 | 10 | 22 | 24 | 14770.6414
2030 | 2008 | 10 | 23 | 1 | 13270.4174
2030 | 2008 | 10 | 23 | 2 | 14579.0938
2030 | 2008 | 10 | 23 | 3 | 15958.1233
2030 | 2008 | 10 | 23 | 4 | 16753.2592
2030 | 2008 | 10 | 23 | 5 | 17470.7822
2030 | 2008 | 10 | 23 | 6 | 18536.5881
2030 | 2008 | 10 | 23 | 7 | 18868.2573
2030 | 2008 | 10 | 23 | 8 | 18887.2157
2030 | 2008 | 10 | 23 | 9 | 17598.3779
2030 | 2008 | 10 | 23 | 10 | 16634.3448
2030 | 2008 | 10 | 23 | 11 | 15632.406
2030 | 2008 | 10 | 23 | 12 | 16919.2126
2030 | 2008 | 10 | 23 | 13 | 16567.4867
2030 | 2008 | 10 | 23 | 14 | 17487.0285
2030 | 2008 | 10 | 23 | 15 | 18141.6492
2030 | 2008 | 10 | 23 | 16 | 17392.929
2030 | 2008 | 10 | 23 | 17 | 15751.9811
2030 | 2008 | 10 | 23 | 18 | 11841.7161
2030 | 2008 | 10 | 23 | 19 | 8133.8892
2030 | 2008 | 10 | 23 | 20 | 7338.5757
2030 | 2008 | 10 | 23 | 21 | 6369.8723
2030 | 2008 | 10 | 23 | 22 | 8588.583
2030 | 2008 | 10 | 23 | 23 | 9467.0858
2030 | 2008 | 10 | 23 | 24 | 9588.7308
2030 | 2008 | 10 | 24 | 1 | 11519.3158
2030 | 2008 | 10 | 24 | 2 | 11845.4094
2030 | 2008 | 10 | 24 | 3 | 10551.5047
2030 | 2008 | 10 | 24 | 4 | 10026.0511
2030 | 2008 | 10 | 24 | 5 | 9282.4007
2030 | 2008 | 10 | 24 | 6 | 8371.5462
2030 | 2008 | 10 | 24 | 7 | 7742.6382
2030 | 2008 | 10 | 24 | 8 | 6780.7561
2030 | 2008 | 10 | 24 | 9 | 5694.0907
2030 | 2008 | 10 | 24 | 10 | 3426.9337
2030 | 2008 | 10 | 24 | 11 | 2767.5345
2030 | 2008 | 10 | 24 | 12 | 2796.1573
2030 | 2008 | 10 | 24 | 13 | 2478.5862
2030 | 2008 | 10 | 24 | 14 | 2562.3166
2030 | 2008 | 10 | 24 | 15 | 2212.532
2030 | 2008 | 10 | 24 | 16 | 1739.7473
2030 | 2008 | 10 | 24 | 17 | 1235.9358
2030 | 2008 | 10 | 24 | 18 | 1447.5973
2030 | 2008 | 10 | 24 | 19 | 2337.7979
2030 | 2008 | 10 | 24 | 20 | 3496.6916
2030 | 2008 | 10 | 24 | 21 | 5434.5248
2030 | 2008 | 10 | 24 | 22 | 7938.139
2030 | 2008 | 10 | 24 | 23 | 9020.9938
2030 | 2008 | 10 | 24 | 24 | 9550.3404
2030 | 2008 | 10 | 25 | 1 | 9592.2474
2030 | 2008 | 10 | 25 | 2 | 9181.7231
2030 | 2008 | 10 | 25 | 3 | 8084.7477
2030 | 2008 | 10 | 25 | 4 | 7052.7188
2030 | 2008 | 10 | 25 | 5 | 6115.4232
2030 | 2008 | 10 | 25 | 6 | 5204.0969
2030 | 2008 | 10 | 25 | 7 | 4729.595
2030 | 2008 | 10 | 25 | 8 | 4492.0792
2030 | 2008 | 10 | 25 | 9 | 4102.0806
2030 | 2008 | 10 | 25 | 10 | 3699.4737
2030 | 2008 | 10 | 25 | 11 | 3006.5815
2030 | 2008 | 10 | 25 | 12 | 3761.7374
2030 | 2008 | 10 | 25 | 13 | 3974.0498
2030 | 2008 | 10 | 25 | 14 | 4702.9592
2030 | 2008 | 10 | 25 | 15 | 5805.9708
2030 | 2008 | 10 | 25 | 16 | 6715.0161
2030 | 2008 | 10 | 25 | 17 | 6710.2337
2030 | 2008 | 10 | 25 | 18 | 6736.7983
2030 | 2008 | 10 | 25 | 19 | 7982.1577
2030 | 2008 | 10 | 25 | 20 | 11969.8911
2030 | 2008 | 10 | 25 | 21 | 17073.0315
2030 | 2008 | 10 | 25 | 22 | 21831.599
2030 | 2008 | 10 | 25 | 23 | 24880.0249
2030 | 2008 | 10 | 25 | 24 | 27089.8308
2030 | 2008 | 10 | 26 | 1 | 27990.4231
2030 | 2008 | 10 | 26 | 2 | 28048.6532
2030 | 2008 | 10 | 26 | 3 | 27798.7812
2030 | 2008 | 10 | 26 | 4 | 26268.1746
2030 | 2008 | 10 | 26 | 5 | 25968.1501
2030 | 2008 | 10 | 26 | 6 | 25863.446
2030 | 2008 | 10 | 26 | 7 | 24077.264
2030 | 2008 | 10 | 26 | 8 | 21615.3432
2030 | 2008 | 10 | 26 | 9 | 17738.938
2030 | 2008 | 10 | 26 | 10 | 13391.1965
2030 | 2008 | 10 | 26 | 11 | 11522.8905
2030 | 2008 | 10 | 26 | 12 | 9882.9848
2030 | 2008 | 10 | 26 | 13 | 9153.7961
2030 | 2008 | 10 | 26 | 14 | 9910.5053
2030 | 2008 | 10 | 26 | 15 | 13217.9259
2030 | 2008 | 10 | 26 | 16 | 16733.0086
2030 | 2008 | 10 | 26 | 17 | 20158.6486
2030 | 2008 | 10 | 26 | 18 | 24096.6152
2030 | 2008 | 10 | 26 | 19 | 26517.3879
2030 | 2008 | 10 | 26 | 20 | 29197.7003
2030 | 2008 | 10 | 26 | 21 | 31237.3603
2030 | 2008 | 10 | 26 | 22 | 31468.671
2030 | 2008 | 10 | 26 | 23 | 30529.9948
2030 | 2008 | 10 | 26 | 24 | 29367.5058
2030 | 2008 | 10 | 27 | 1 | 27923.6449
2030 | 2008 | 10 | 27 | 2 | 26172.8844
2030 | 2008 | 10 | 27 | 3 | 24803.7156
2030 | 2008 | 10 | 27 | 4 | 23696.3908
2030 | 2008 | 10 | 27 | 5 | 22656.1273
2030 | 2008 | 10 | 27 | 6 | 22727.6179
2030 | 2008 | 10 | 27 | 7 | 22169.1452
2030 | 2008 | 10 | 27 | 8 | 20829.2526
2030 | 2008 | 10 | 27 | 9 | 17613.9298
2030 | 2008 | 10 | 27 | 10 | 15605.1204
2030 | 2008 | 10 | 27 | 11 | 16913.576
2030 | 2008 | 10 | 27 | 12 | 14678.9232
2030 | 2008 | 10 | 27 | 13 | 13976.4451
2030 | 2008 | 10 | 27 | 14 | 12736.9938
2030 | 2008 | 10 | 27 | 15 | 11973.3979
2030 | 2008 | 10 | 27 | 16 | 11097.5761
2030 | 2008 | 10 | 27 | 17 | 9645.3005
2030 | 2008 | 10 | 27 | 18 | 8115.508
2030 | 2008 | 10 | 27 | 19 | 7054.0431
2030 | 2008 | 10 | 27 | 20 | 7512.2204
2030 | 2008 | 10 | 27 | 21 | 8295.5787
2030 | 2008 | 10 | 27 | 22 | 9229.0572
2030 | 2008 | 10 | 27 | 23 | 10213.1256
2030 | 2008 | 10 | 27 | 24 | 11497.9185
2030 | 2008 | 10 | 28 | 1 | 11862.3674
2030 | 2008 | 10 | 28 | 2 | 12447.6738
2030 | 2008 | 10 | 28 | 3 | 13019.8128
2030 | 2008 | 10 | 28 | 4 | 13441.3522
2030 | 2008 | 10 | 28 | 5 | 14450.0689
2030 | 2008 | 10 | 28 | 6 | 15670.9509
2030 | 2008 | 10 | 28 | 7 | 16879.4417
2030 | 2008 | 10 | 28 | 8 | 17175.8572
2030 | 2008 | 10 | 28 | 9 | 15846.4791
2030 | 2008 | 10 | 28 | 10 | 9754.4096
2030 | 2008 | 10 | 28 | 11 | 10354.1945
2030 | 2008 | 10 | 28 | 12 | 11356.4806
2030 | 2008 | 10 | 28 | 13 | 10684.6448
2030 | 2008 | 10 | 28 | 14 | 10164.1992
2030 | 2008 | 10 | 28 | 15 | 10304.9818
2030 | 2008 | 10 | 28 | 16 | 10524.8558
2030 | 2008 | 10 | 28 | 17 | 10795.9475
2030 | 2008 | 10 | 28 | 18 | 11879.805
2030 | 2008 | 10 | 28 | 19 | 15660.9268
2030 | 2008 | 10 | 28 | 20 | 20083.3905
2030 | 2008 | 10 | 28 | 21 | 24178.7524
2030 | 2008 | 10 | 28 | 22 | 25737.1243
2030 | 2008 | 10 | 28 | 23 | 26014.8798
2030 | 2008 | 10 | 28 | 24 | 26243.6559
2030 | 2008 | 10 | 29 | 1 | 26234.2972
2030 | 2008 | 10 | 29 | 2 | 25771.7205
2030 | 2008 | 10 | 29 | 3 | 25140.313
2030 | 2008 | 10 | 29 | 4 | 24125.6922
2030 | 2008 | 10 | 29 | 5 | 23055.5863
2030 | 2008 | 10 | 29 | 6 | 21637.4925
2030 | 2008 | 10 | 29 | 7 | 20281.4339
2030 | 2008 | 10 | 29 | 8 | 18482.1286
2030 | 2008 | 10 | 29 | 9 | 15331.0274
2030 | 2008 | 10 | 29 | 10 | 9745.7852
2030 | 2008 | 10 | 29 | 11 | 9575.2012
2030 | 2008 | 10 | 29 | 12 | 9049.3236
2030 | 2008 | 10 | 29 | 13 | 8258.5943
2030 | 2008 | 10 | 29 | 14 | 7879.0716
2030 | 2008 | 10 | 29 | 15 | 7984.3105
2030 | 2008 | 10 | 29 | 16 | 8385.2772
2030 | 2008 | 10 | 29 | 17 | 8825.0955
2030 | 2008 | 10 | 29 | 18 | 10061.5678
2030 | 2008 | 10 | 29 | 19 | 12962.7963
2030 | 2008 | 10 | 29 | 20 | 17941.9384
2030 | 2008 | 10 | 29 | 21 | 23758.6573
2030 | 2008 | 10 | 29 | 22 | 27123.3478
2030 | 2008 | 10 | 29 | 23 | 28584.6629
2030 | 2008 | 10 | 29 | 24 | 29311.4442
2030 | 2008 | 10 | 30 | 1 | 29608.3351
2030 | 2008 | 10 | 30 | 2 | 29223.1289
2030 | 2008 | 10 | 30 | 3 | 28935.0541
2030 | 2008 | 10 | 30 | 4 | 28545.4783
2030 | 2008 | 10 | 30 | 5 | 28413.8822
2030 | 2008 | 10 | 30 | 6 | 25361.5664
2030 | 2008 | 10 | 30 | 7 | 25064.7464
2030 | 2008 | 10 | 30 | 8 | 24227.7106
2030 | 2008 | 10 | 30 | 9 | 22041.2147
2030 | 2008 | 10 | 30 | 10 | 19923.5861
2030 | 2008 | 10 | 30 | 11 | 18886.2214
2030 | 2008 | 10 | 30 | 12 | 19157.892
2030 | 2008 | 10 | 30 | 13 | 18721.8765
2030 | 2008 | 10 | 30 | 14 | 19388.4308
2030 | 2008 | 10 | 30 | 15 | 19881.3269
2030 | 2008 | 10 | 30 | 16 | 19645.5725
2030 | 2008 | 10 | 30 | 17 | 19159.7903
2030 | 2008 | 10 | 30 | 18 | 19388.2878
2030 | 2008 | 10 | 30 | 19 | 22322.3654
2030 | 2008 | 10 | 30 | 20 | 25243.7932
2030 | 2008 | 10 | 30 | 21 | 26935.8814
2030 | 2008 | 10 | 30 | 22 | 26633.7013
2030 | 2008 | 10 | 30 | 23 | 26616.3951
2030 | 2008 | 10 | 30 | 24 | 29208.5169
2030 | 2008 | 10 | 31 | 1 | 28066.9572
2030 | 2008 | 10 | 31 | 2 | 26913.1144
2030 | 2008 | 10 | 31 | 3 | 25758.7862
2030 | 2008 | 10 | 31 | 4 | 24514.6254
2030 | 2008 | 10 | 31 | 5 | 22193.2998
2030 | 2008 | 10 | 31 | 6 | 20516.6419
2030 | 2008 | 10 | 31 | 7 | 18127.6153
2030 | 2008 | 10 | 31 | 8 | 16421.042
2030 | 2008 | 10 | 31 | 9 | 13400.4037
2030 | 2008 | 10 | 31 | 10 | 13239.1017
2030 | 2008 | 10 | 31 | 11 | 12766.2726
2030 | 2008 | 10 | 31 | 12 | 11358.8213
2030 | 2008 | 10 | 31 | 13 | 10257.7509
2030 | 2008 | 10 | 31 | 14 | 8821.8591
2030 | 2008 | 10 | 31 | 15 | 7444.1347
2030 | 2008 | 10 | 31 | 16 | 5847.2445
2030 | 2008 | 10 | 31 | 17 | 5127.7051
2030 | 2008 | 10 | 31 | 18 | 5342.8239
2030 | 2008 | 10 | 31 | 19 | 8382.4381
2030 | 2008 | 10 | 31 | 20 | 10680.0114
2030 | 2008 | 10 | 31 | 21 | 12739.1922
2030 | 2008 | 10 | 31 | 22 | 14219.5224
2030 | 2008 | 10 | 31 | 23 | 14608.371
2030 | 2008 | 10 | 31 | 24 | 14417.2362

## SolarProfiles
Input cells (non-formulas)
FORECAST YEAR | Year | Month | Day | HE | Value
2026 | 2008 | 8 | 1 | 1 | 0
2026 | 2008 | 8 | 1 | 2 | 0
2026 | 2008 | 8 | 1 | 3 | 0
2026 | 2008 | 8 | 1 | 4 | 0
2026 | 2008 | 8 | 1 | 5 | 0
2026 | 2008 | 8 | 1 | 6 | 0
2026 | 2008 | 8 | 1 | 7 | 2.4214
2026 | 2008 | 8 | 1 | 8 | 3676.098
2026 | 2008 | 8 | 1 | 9 | 14959.9807
2026 | 2008 | 8 | 1 | 10 | 27132.7011
2026 | 2008 | 8 | 1 | 11 | 33863.0237
2026 | 2008 | 8 | 1 | 12 | 35835.6326
2026 | 2008 | 8 | 1 | 13 | 36253.9994
2026 | 2008 | 8 | 1 | 14 | 35440.099
2026 | 2008 | 8 | 1 | 15 | 33919.1053
2026 | 2008 | 8 | 1 | 16 | 31949.4743
2026 | 2008 | 8 | 1 | 17 | 29030.9844
2026 | 2008 | 8 | 1 | 18 | 26824.8281
2026 | 2008 | 8 | 1 | 19 | 22454.1822
2026 | 2008 | 8 | 1 | 20 | 8216.1327
2026 | 2008 | 8 | 1 | 21 | 419.3115
2026 | 2008 | 8 | 1 | 22 | 0
2026 | 2008 | 8 | 1 | 23 | 0
2026 | 2008 | 8 | 1 | 24 | 0
2026 | 2008 | 8 | 2 | 1 | 0
2026 | 2008 | 8 | 2 | 2 | 0
2026 | 2008 | 8 | 2 | 3 | 0
2026 | 2008 | 8 | 2 | 4 | 0
2026 | 2008 | 8 | 2 | 5 | 0
2026 | 2008 | 8 | 2 | 6 | 0
2026 | 2008 | 8 | 2 | 7 | 2.0632
2026 | 2008 | 8 | 2 | 8 | 3827.3198
2026 | 2008 | 8 | 2 | 9 | 15065.141
2026 | 2008 | 8 | 2 | 10 | 28270.6016
2026 | 2008 | 8 | 2 | 11 | 34980.9308
2026 | 2008 | 8 | 2 | 12 | 36732.0224
2026 | 2008 | 8 | 2 | 13 | 35841.9742
2026 | 2008 | 8 | 2 | 14 | 36830.7923
2026 | 2008 | 8 | 2 | 15 | 36075.1206
2026 | 2008 | 8 | 2 | 16 | 35692.1476
2026 | 2008 | 8 | 2 | 17 | 32903.7579
2026 | 2008 | 8 | 2 | 18 | 30347.9074
2026 | 2008 | 8 | 2 | 19 | 23016.2734
2026 | 2008 | 8 | 2 | 20 | 7465.0156
2026 | 2008 | 8 | 2 | 21 | 244.406
2026 | 2008 | 8 | 2 | 22 | 0
2026 | 2008 | 8 | 2 | 23 | 0
2026 | 2008 | 8 | 2 | 24 | 0
2026 | 2008 | 8 | 3 | 1 | 0
2026 | 2008 | 8 | 3 | 2 | 0
2026 | 2008 | 8 | 3 | 3 | 0
2026 | 2008 | 8 | 3 | 4 | 0
2026 | 2008 | 8 | 3 | 5 | 0
2026 | 2008 | 8 | 3 | 6 | 0
2026 | 2008 | 8 | 3 | 7 | 2.9932
2026 | 2008 | 8 | 3 | 8 | 3703.936
2026 | 2008 | 8 | 3 | 9 | 17223.1867
2026 | 2008 | 8 | 3 | 10 | 29925.6831
2026 | 2008 | 8 | 3 | 11 | 35711.912
2026 | 2008 | 8 | 3 | 12 | 37815.6016
2026 | 2008 | 8 | 3 | 13 | 37411.5032
2026 | 2008 | 8 | 3 | 14 | 37749.3372
2026 | 2008 | 8 | 3 | 15 | 36671.661
2026 | 2008 | 8 | 3 | 16 | 35717.797
2026 | 2008 | 8 | 3 | 17 | 34358.6391
2026 | 2008 | 8 | 3 | 18 | 31209.409
2026 | 2008 | 8 | 3 | 19 | 23762.5061
2026 | 2008 | 8 | 3 | 20 | 8053.4938
2026 | 2008 | 8 | 3 | 21 | 106.8632
2026 | 2008 | 8 | 3 | 22 | 0
2026 | 2008 | 8 | 3 | 23 | 0
2026 | 2008 | 8 | 3 | 24 | 0
2026 | 2008 | 8 | 4 | 1 | 0
2026 | 2008 | 8 | 4 | 2 | 0
2026 | 2008 | 8 | 4 | 3 | 0
2026 | 2008 | 8 | 4 | 4 | 0
2026 | 2008 | 8 | 4 | 5 | 0
2026 | 2008 | 8 | 4 | 6 | 0
2026 | 2008 | 8 | 4 | 7 | 1.9784
2026 | 2008 | 8 | 4 | 8 | 4246.1662
2026 | 2008 | 8 | 4 | 9 | 19744.9574
2026 | 2008 | 8 | 4 | 10 | 30304.2919
2026 | 2008 | 8 | 4 | 11 | 35550.8188
2026 | 2008 | 8 | 4 | 12 | 35587.7389
2026 | 2008 | 8 | 4 | 13 | 36335.0034
2026 | 2008 | 8 | 4 | 14 | 35332.3038
2026 | 2008 | 8 | 4 | 15 | 35366.5289
2026 | 2008 | 8 | 4 | 16 | 34488.3383
2026 | 2008 | 8 | 4 | 17 | 32726.6845
2026 | 2008 | 8 | 4 | 18 | 30193.8166
2026 | 2008 | 8 | 4 | 19 | 23772.7681
2026 | 2008 | 8 | 4 | 20 | 7827.454
2026 | 2008 | 8 | 4 | 21 | 53.346
2026 | 2008 | 8 | 4 | 22 | 0
2026 | 2008 | 8 | 4 | 23 | 0
2026 | 2008 | 8 | 4 | 24 | 0
2026 | 2008 | 8 | 5 | 1 | 0
2026 | 2008 | 8 | 5 | 2 | 0
2026 | 2008 | 8 | 5 | 3 | 0
2026 | 2008 | 8 | 5 | 4 | 0
2026 | 2008 | 8 | 5 | 5 | 0
2026 | 2008 | 8 | 5 | 6 | 0
2026 | 2008 | 8 | 5 | 7 | 0.65143
2026 | 2008 | 8 | 5 | 8 | 4554.8077
2026 | 2008 | 8 | 5 | 9 | 18499.8701
2026 | 2008 | 8 | 5 | 10 | 30358.9921
2026 | 2008 | 8 | 5 | 11 | 32339.2434
2026 | 2008 | 8 | 5 | 12 | 33609.6283
2026 | 2008 | 8 | 5 | 13 | 35113.7443
2026 | 2008 | 8 | 5 | 14 | 33736.9709
2026 | 2008 | 8 | 5 | 15 | 31114.1391
2026 | 2008 | 8 | 5 | 16 | 27758.7008
2026 | 2008 | 8 | 5 | 17 | 24411.5643
2026 | 2008 | 8 | 5 | 18 | 23160.3869
2026 | 2008 | 8 | 5 | 19 | 19447.1725
2026 | 2008 | 8 | 5 | 20 | 7606.2288
2026 | 2008 | 8 | 5 | 21 | 50.2841
2026 | 2008 | 8 | 5 | 22 | 0
2026 | 2008 | 8 | 5 | 23 | 0
2026 | 2008 | 8 | 5 | 24 | 0
2026 | 2008 | 8 | 6 | 1 | 0
2026 | 2008 | 8 | 6 | 2 | 0
2026 | 2008 | 8 | 6 | 3 | 0
2026 | 2008 | 8 | 6 | 4 | 0
2026 | 2008 | 8 | 6 | 5 | 0
2026 | 2008 | 8 | 6 | 6 | 0
2026 | 2008 | 8 | 6 | 7 | 0.044932
2026 | 2008 | 8 | 6 | 8 | 2512.0291
2026 | 2008 | 8 | 6 | 9 | 14470.2667
2026 | 2008 | 8 | 6 | 10 | 25193.4985
2026 | 2008 | 8 | 6 | 11 | 28039.0847
2026 | 2008 | 8 | 6 | 12 | 30307.0377
2026 | 2008 | 8 | 6 | 13 | 30522.3387
2026 | 2008 | 8 | 6 | 14 | 30132.9339
2026 | 2008 | 8 | 6 | 15 | 29557.054
2026 | 2008 | 8 | 6 | 16 | 27594.5777
2026 | 2008 | 8 | 6 | 17 | 25152.5215
2026 | 2008 | 8 | 6 | 18 | 23393.3604
2026 | 2008 | 8 | 6 | 19 | 19685.3269
2026 | 2008 | 8 | 6 | 20 | 7301.3333
2026 | 2008 | 8 | 6 | 21 | 38.8185
2026 | 2008 | 8 | 6 | 22 | 0
2026 | 2008 | 8 | 6 | 23 | 0
2026 | 2008 | 8 | 6 | 24 | 0
2026 | 2008 | 8 | 7 | 1 | 0
2026 | 2008 | 8 | 7 | 2 | 0
2026 | 2008 | 8 | 7 | 3 | 0
2026 | 2008 | 8 | 7 | 4 | 0
2026 | 2008 | 8 | 7 | 5 | 0
2026 | 2008 | 8 | 7 | 6 | 0
2026 | 2008 | 8 | 7 | 7 | 0.20704
2026 | 2008 | 8 | 7 | 8 | 2577.3499
2026 | 2008 | 8 | 7 | 9 | 12297.6969
2026 | 2008 | 8 | 7 | 10 | 22394.0309
2026 | 2008 | 8 | 7 | 11 | 30320.9895
2026 | 2008 | 8 | 7 | 12 | 34283.724
2026 | 2008 | 8 | 7 | 13 | 35466.3888
2026 | 2008 | 8 | 7 | 14 | 34435.2111
2026 | 2008 | 8 | 7 | 15 | 34057.6728
2026 | 2008 | 8 | 7 | 16 | 32948.9286
2026 | 2008 | 8 | 7 | 17 | 31772.9117
2026 | 2008 | 8 | 7 | 18 | 27844.7448
2026 | 2008 | 8 | 7 | 19 | 21844.055
2026 | 2008 | 8 | 7 | 20 | 7168.6278
2026 | 2008 | 8 | 7 | 21 | 33.2623
2026 | 2008 | 8 | 7 | 22 | 0
2026 | 2008 | 8 | 7 | 23 | 0
2026 | 2008 | 8 | 7 | 24 | 0
2026 | 2008 | 8 | 8 | 1 | 0
2026 | 2008 | 8 | 8 | 2 | 0
2026 | 2008 | 8 | 8 | 3 | 0
2026 | 2008 | 8 | 8 | 4 | 0
2026 | 2008 | 8 | 8 | 5 | 0
2026 | 2008 | 8 | 8 | 6 | 0
2026 | 2008 | 8 | 8 | 7 | 0.0076014
2026 | 2008 | 8 | 8 | 8 | 2754.7676
2026 | 2008 | 8 | 8 | 9 | 15650.0402
2026 | 2008 | 8 | 8 | 10 | 27956.3183
2026 | 2008 | 8 | 8 | 11 | 32196.7383
2026 | 2008 | 8 | 8 | 12 | 32857.8938
2026 | 2008 | 8 | 8 | 13 | 34669.7441
2026 | 2008 | 8 | 8 | 14 | 35124.0292
2026 | 2008 | 8 | 8 | 15 | 34124.428
2026 | 2008 | 8 | 8 | 16 | 33389.8461
2026 | 2008 | 8 | 8 | 17 | 30046.5596
2026 | 2008 | 8 | 8 | 18 | 26825.9622
2026 | 2008 | 8 | 8 | 19 | 22082.5758
2026 | 2008 | 8 | 8 | 20 | 7613.5579
2026 | 2008 | 8 | 8 | 21 | 26.1682
2026 | 2008 | 8 | 8 | 22 | 0
2026 | 2008 | 8 | 8 | 23 | 0
2026 | 2008 | 8 | 8 | 24 | 0
2026 | 2008 | 8 | 9 | 1 | 0
2026 | 2008 | 8 | 9 | 2 | 0
2026 | 2008 | 8 | 9 | 3 | 0
2026 | 2008 | 8 | 9 | 4 | 0
2026 | 2008 | 8 | 9 | 5 | 0
2026 | 2008 | 8 | 9 | 6 | 0
2026 | 2008 | 8 | 9 | 7 | 0.045975
2026 | 2008 | 8 | 9 | 8 | 2403.8977
2026 | 2008 | 8 | 9 | 9 | 15093.469
2026 | 2008 | 8 | 9 | 10 | 27115.0221
2026 | 2008 | 8 | 9 | 11 | 31075.9295
2026 | 2008 | 8 | 9 | 12 | 33165.6432
2026 | 2008 | 8 | 9 | 13 | 32584.6715
2026 | 2008 | 8 | 9 | 14 | 31648.8233
2026 | 2008 | 8 | 9 | 15 | 30086.1851
2026 | 2008 | 8 | 9 | 16 | 27256.9006
2026 | 2008 | 8 | 9 | 17 | 25862.6801
2026 | 2008 | 8 | 9 | 18 | 25524.2129
2026 | 2008 | 8 | 9 | 19 | 21640.8089
2026 | 2008 | 8 | 9 | 20 | 7377.8256
2026 | 2008 | 8 | 9 | 21 | 0
2026 | 2008 | 8 | 9 | 22 | 0
2026 | 2008 | 8 | 9 | 23 | 0
2026 | 2008 | 8 | 9 | 24 | 0
2026 | 2008 | 8 | 10 | 1 | 0
2026 | 2008 | 8 | 10 | 2 | 0
2026 | 2008 | 8 | 10 | 3 | 0
2026 | 2008 | 8 | 10 | 4 | 0
2026 | 2008 | 8 | 10 | 5 | 0
2026 | 2008 | 8 | 10 | 6 | 0
2026 | 2008 | 8 | 10 | 7 | 0.3285
2026 | 2008 | 8 | 10 | 8 | 2165.347
2026 | 2008 | 8 | 10 | 9 | 13981.056
2026 | 2008 | 8 | 10 | 10 | 26712.5407
2026 | 2008 | 8 | 10 | 11 | 31596.1726
2026 | 2008 | 8 | 10 | 12 | 34510.9545
2026 | 2008 | 8 | 10 | 13 | 35717.0603
2026 | 2008 | 8 | 10 | 14 | 35026.6282
2026 | 2008 | 8 | 10 | 15 | 34697.8209
2026 | 2008 | 8 | 10 | 16 | 33010.0052
2026 | 2008 | 8 | 10 | 17 | 30169.2059
2026 | 2008 | 8 | 10 | 18 | 25665.7331
2026 | 2008 | 8 | 10 | 19 | 20311.6578
2026 | 2008 | 8 | 10 | 20 | 6539.3332
2026 | 2008 | 8 | 10 | 21 | 0
2026 | 2008 | 8 | 10 | 22 | 0
2026 | 2008 | 8 | 10 | 23 | 0
2026 | 2008 | 8 | 10 | 24 | 0
2026 | 2008 | 8 | 11 | 1 | 0
2026 | 2008 | 8 | 11 | 2 | 0
2026 | 2008 | 8 | 11 | 3 | 0
2026 | 2008 | 8 | 11 | 4 | 0
2026 | 2008 | 8 | 11 | 5 | 0
2026 | 2008 | 8 | 11 | 6 | 0
2026 | 2008 | 8 | 11 | 7 | 0
2026 | 2008 | 8 | 11 | 8 | 1420.6462
2026 | 2008 | 8 | 11 | 9 | 10470.4518
2026 | 2008 | 8 | 11 | 10 | 20784.4696
2026 | 2008 | 8 | 11 | 11 | 27956.7228
2026 | 2008 | 8 | 11 | 12 | 31592.4948
2026 | 2008 | 8 | 11 | 13 | 30810.6137
2026 | 2008 | 8 | 11 | 14 | 30784.6724
2026 | 2008 | 8 | 11 | 15 | 29331.6976
2026 | 2008 | 8 | 11 | 16 | 28260.6418
2026 | 2008 | 8 | 11 | 17 | 24854.2029
2026 | 2008 | 8 | 11 | 18 | 22714.6038
2026 | 2008 | 8 | 11 | 19 | 19013.7678
2026 | 2008 | 8 | 11 | 20 | 6531.7794
2026 | 2008 | 8 | 11 | 21 | 0
2026 | 2008 | 8 | 11 | 22 | 0
2026 | 2008 | 8 | 11 | 23 | 0
2026 | 2008 | 8 | 11 | 24 | 0
2026 | 2008 | 8 | 12 | 1 | 0
2026 | 2008 | 8 | 12 | 2 | 0
2026 | 2008 | 8 | 12 | 3 | 0
2026 | 2008 | 8 | 12 | 4 | 0
2026 | 2008 | 8 | 12 | 5 | 0
2026 | 2008 | 8 | 12 | 6 | 0
2026 | 2008 | 8 | 12 | 7 | 0.0022535
2026 | 2008 | 8 | 12 | 8 | 830.0821
2026 | 2008 | 8 | 12 | 9 | 7378.7126
2026 | 2008 | 8 | 12 | 10 | 18768.6261
2026 | 2008 | 8 | 12 | 11 | 25724.5247
2026 | 2008 | 8 | 12 | 12 | 32619.483
2026 | 2008 | 8 | 12 | 13 | 33087.7229
2026 | 2008 | 8 | 12 | 14 | 33915.7584
2026 | 2008 | 8 | 12 | 15 | 32214.1619
2026 | 2008 | 8 | 12 | 16 | 31434.4252
2026 | 2008 | 8 | 12 | 17 | 28906.8633
2026 | 2008 | 8 | 12 | 18 | 26465.3007
2026 | 2008 | 8 | 12 | 19 | 21321.1607
2026 | 2008 | 8 | 12 | 20 | 7318.8072
2026 | 2008 | 8 | 12 | 21 | 0
2026 | 2008 | 8 | 12 | 22 | 0
2026 | 2008 | 8 | 12 | 23 | 0
2026 | 2008 | 8 | 12 | 24 | 0
2026 | 2008 | 8 | 13 | 1 | 0
2026 | 2008 | 8 | 13 | 2 | 0
2026 | 2008 | 8 | 13 | 3 | 0
2026 | 2008 | 8 | 13 | 4 | 0
2026 | 2008 | 8 | 13 | 5 | 0
2026 | 2008 | 8 | 13 | 6 | 0
2026 | 2008 | 8 | 13 | 7 | 0.064221
2026 | 2008 | 8 | 13 | 8 | 3895.7272
2026 | 2008 | 8 | 13 | 9 | 17843.3874
2026 | 2008 | 8 | 13 | 10 | 30651.4542
2026 | 2008 | 8 | 13 | 11 | 33570.9693
2026 | 2008 | 8 | 13 | 12 | 35713.0123
2026 | 2008 | 8 | 13 | 13 | 34743.6266
2026 | 2008 | 8 | 13 | 14 | 34826.8879
2026 | 2008 | 8 | 13 | 15 | 34384.6291
2026 | 2008 | 8 | 13 | 16 | 33505.1285
2026 | 2008 | 8 | 13 | 17 | 31584.2935
2026 | 2008 | 8 | 13 | 18 | 28575.4657
2026 | 2008 | 8 | 13 | 19 | 21581.655
2026 | 2008 | 8 | 13 | 20 | 7458.4101
2026 | 2008 | 8 | 13 | 21 | 0
2026 | 2008 | 8 | 13 | 22 | 0
2026 | 2008 | 8 | 13 | 23 | 0
2026 | 2008 | 8 | 13 | 24 | 0
2026 | 2008 | 8 | 14 | 1 | 0
2026 | 2008 | 8 | 14 | 2 | 0
2026 | 2008 | 8 | 14 | 3 | 0
2026 | 2008 | 8 | 14 | 4 | 0
2026 | 2008 | 8 | 14 | 5 | 0
2026 | 2008 | 8 | 14 | 6 | 0
2026 | 2008 | 8 | 14 | 7 | 0.0029843
2026 | 2008 | 8 | 14 | 8 | 2470.7458
2026 | 2008 | 8 | 14 | 9 | 16327.3611
2026 | 2008 | 8 | 14 | 10 | 27848.6201
2026 | 2008 | 8 | 14 | 11 | 32708.5948
2026 | 2008 | 8 | 14 | 12 | 34053.3617
2026 | 2008 | 8 | 14 | 13 | 35689.5465
2026 | 2008 | 8 | 14 | 14 | 35007.3579
2026 | 2008 | 8 | 14 | 15 | 34373.9807
2026 | 2008 | 8 | 14 | 16 | 32857.9414
2026 | 2008 | 8 | 14 | 17 | 31775.5386
2026 | 2008 | 8 | 14 | 18 | 29494.162
2026 | 2008 | 8 | 14 | 19 | 22959.4625
2026 | 2008 | 8 | 14 | 20 | 8182.3674
2026 | 2008 | 8 | 14 | 21 | 0
2026 | 2008 | 8 | 14 | 22 | 0
2026 | 2008 | 8 | 14 | 23 | 0
2026 | 2008 | 8 | 14 | 24 | 0
2026 | 2008 | 8 | 15 | 1 | 0
2026 | 2008 | 8 | 15 | 2 | 0
2026 | 2008 | 8 | 15 | 3 | 0
2026 | 2008 | 8 | 15 | 4 | 0
2026 | 2008 | 8 | 15 | 5 | 0
2026 | 2008 | 8 | 15 | 6 | 0
2026 | 2008 | 8 | 15 | 7 | 0.018889
2026 | 2008 | 8 | 15 | 8 | 1428.5534
2026 | 2008 | 8 | 15 | 9 | 13619.2054
2026 | 2008 | 8 | 15 | 10 | 23743.8184
2026 | 2008 | 8 | 15 | 11 | 30572.2445
2026 | 2008 | 8 | 15 | 12 | 34590.8012
2026 | 2008 | 8 | 15 | 13 | 35178.8639
2026 | 2008 | 8 | 15 | 14 | 33375.6266
2026 | 2008 | 8 | 15 | 15 | 33283.6522
2026 | 2008 | 8 | 15 | 16 | 33255.93
2026 | 2008 | 8 | 15 | 17 | 32373.8739
2026 | 2008 | 8 | 15 | 18 | 28426.8901
2026 | 2008 | 8 | 15 | 19 | 22548.4987
2026 | 2008 | 8 | 15 | 20 | 6783.2828
2026 | 2008 | 8 | 15 | 21 | 0
2026 | 2008 | 8 | 15 | 22 | 0
2026 | 2008 | 8 | 15 | 23 | 0
2026 | 2008 | 8 | 15 | 24 | 0
2026 | 2008 | 8 | 16 | 1 | 0
2026 | 2008 | 8 | 16 | 2 | 0
2026 | 2008 | 8 | 16 | 3 | 0
2026 | 2008 | 8 | 16 | 4 | 0
2026 | 2008 | 8 | 16 | 5 | 0
2026 | 2008 | 8 | 16 | 6 | 0
2026 | 2008 | 8 | 16 | 7 | 0
2026 | 2008 | 8 | 16 | 8 | 1371.6106
2026 | 2008 | 8 | 16 | 9 | 10213.0748
2026 | 2008 | 8 | 16 | 10 | 20609.6864
2026 | 2008 | 8 | 16 | 11 | 25272.9475
2026 | 2008 | 8 | 16 | 12 | 26588.3741
2026 | 2008 | 8 | 16 | 13 | 27378.327
2026 | 2008 | 8 | 16 | 14 | 27915.2457
2026 | 2008 | 8 | 16 | 15 | 26733.9208
2026 | 2008 | 8 | 16 | 16 | 25089.5154
2026 | 2008 | 8 | 16 | 17 | 25570.1087
2026 | 2008 | 8 | 16 | 18 | 23676.0538
2026 | 2008 | 8 | 16 | 19 | 20025.4482
2026 | 2008 | 8 | 16 | 20 | 6931.5831
2026 | 2008 | 8 | 16 | 21 | 0
2026 | 2008 | 8 | 16 | 22 | 0
2026 | 2008 | 8 | 16 | 23 | 0
2026 | 2008 | 8 | 16 | 24 | 0
2026 | 2008 | 8 | 17 | 1 | 0
2026 | 2008 | 8 | 17 | 2 | 0
2026 | 2008 | 8 | 17 | 3 | 0
2026 | 2008 | 8 | 17 | 4 | 0
2026 | 2008 | 8 | 17 | 5 | 0
2026 | 2008 | 8 | 17 | 6 | 0
2026 | 2008 | 8 | 17 | 7 | 0
2026 | 2008 | 8 | 17 | 8 | 1062.3051
2026 | 2008 | 8 | 17 | 9 | 10253.845
2026 | 2008 | 8 | 17 | 10 | 22034.7269
2026 | 2008 | 8 | 17 | 11 | 25603.4299
2026 | 2008 | 8 | 17 | 12 | 27624.5723
2026 | 2008 | 8 | 17 | 13 | 27949.3431
2026 | 2008 | 8 | 17 | 14 | 26407.2813
2026 | 2008 | 8 | 17 | 15 | 24909.215
2026 | 2008 | 8 | 17 | 16 | 23000.5717
2026 | 2008 | 8 | 17 | 17 | 21485.7333
2026 | 2008 | 8 | 17 | 18 | 19795.0043
2026 | 2008 | 8 | 17 | 19 | 17696.2165
2026 | 2008 | 8 | 17 | 20 | 6190.6202
2026 | 2008 | 8 | 17 | 21 | 0
2026 | 2008 | 8 | 17 | 22 | 0
2026 | 2008 | 8 | 17 | 23 | 0
2026 | 2008 | 8 | 17 | 24 | 0
2026 | 2008 | 8 | 18 | 1 | 0
2026 | 2008 | 8 | 18 | 2 | 0
2026 | 2008 | 8 | 18 | 3 | 0
2026 | 2008 | 8 | 18 | 4 | 0
2026 | 2008 | 8 | 18 | 5 | 0
2026 | 2008 | 8 | 18 | 6 | 0
2026 | 2008 | 8 | 18 | 7 | 0
2026 | 2008 | 8 | 18 | 8 | 885.5704
2026 | 2008 | 8 | 18 | 9 | 8614.6038
2026 | 2008 | 8 | 18 | 10 | 16434.0542
2026 | 2008 | 8 | 18 | 11 | 22038.1314
2026 | 2008 | 8 | 18 | 12 | 26515.0803
2026 | 2008 | 8 | 18 | 13 | 28148.9602
2026 | 2008 | 8 | 18 | 14 | 26994.4493
2026 | 2008 | 8 | 18 | 15 | 25917.4655
2026 | 2008 | 8 | 18 | 16 | 22737.1777
2026 | 2008 | 8 | 18 | 17 | 20542.5423
2026 | 2008 | 8 | 18 | 18 | 19882.6184
2026 | 2008 | 8 | 18 | 19 | 17137.9772
2026 | 2008 | 8 | 18 | 20 | 6128.7695
2026 | 2008 | 8 | 18 | 21 | 0
2026 | 2008 | 8 | 18 | 22 | 0
2026 | 2008 | 8 | 18 | 23 | 0
2026 | 2008 | 8 | 18 | 24 | 0
2026 | 2008 | 8 | 19 | 1 | 0
2026 | 2008 | 8 | 19 | 2 | 0
2026 | 2008 | 8 | 19 | 3 | 0
2026 | 2008 | 8 | 19 | 4 | 0
2026 | 2008 | 8 | 19 | 5 | 0
2026 | 2008 | 8 | 19 | 6 | 0
2026 | 2008 | 8 | 19 | 7 | 0
2026 | 2008 | 8 | 19 | 8 | 894.4431
2026 | 2008 | 8 | 19 | 9 | 8934.3096
2026 | 2008 | 8 | 19 | 10 | 18899.6164
2026 | 2008 | 8 | 19 | 11 | 23615.9882
2026 | 2008 | 8 | 19 | 12 | 27040.5013
2026 | 2008 | 8 | 19 | 13 | 28348.0678
2026 | 2008 | 8 | 19 | 14 | 28512.7578
2026 | 2008 | 8 | 19 | 15 | 27358.9483
2026 | 2008 | 8 | 19 | 16 | 25677.9086
2026 | 2008 | 8 | 19 | 17 | 23576.4031
2026 | 2008 | 8 | 19 | 18 | 22971.6021
2026 | 2008 | 8 | 19 | 19 | 19372.2915
2026 | 2008 | 8 | 19 | 20 | 6711.918
2026 | 2008 | 8 | 19 | 21 | 0
2026 | 2008 | 8 | 19 | 22 | 0
2026 | 2008 | 8 | 19 | 23 | 0
2026 | 2008 | 8 | 19 | 24 | 0
2026 | 2008 | 8 | 20 | 1 | 0
2026 | 2008 | 8 | 20 | 2 | 0
2026 | 2008 | 8 | 20 | 3 | 0
2026 | 2008 | 8 | 20 | 4 | 0
2026 | 2008 | 8 | 20 | 5 | 0
2026 | 2008 | 8 | 20 | 6 | 0
2026 | 2008 | 8 | 20 | 7 | 0
2026 | 2008 | 8 | 20 | 8 | 713.3535
2026 | 2008 | 8 | 20 | 9 | 9489.5506
2026 | 2008 | 8 | 20 | 10 | 20203.2664
2026 | 2008 | 8 | 20 | 11 | 27335.0197
2026 | 2008 | 8 | 20 | 12 | 31315.8121
2026 | 2008 | 8 | 20 | 13 | 30623.6311
2026 | 2008 | 8 | 20 | 14 | 30864.8702
2026 | 2008 | 8 | 20 | 15 | 29828.1574
2026 | 2008 | 8 | 20 | 16 | 29487.4842
2026 | 2008 | 8 | 20 | 17 | 27547.1848
2026 | 2008 | 8 | 20 | 18 | 26748.5036
2026 | 2008 | 8 | 20 | 19 | 20874.8125
2026 | 2008 | 8 | 20 | 20 | 6849.201
2026 | 2008 | 8 | 20 | 21 | 0
2026 | 2008 | 8 | 20 | 22 | 0
2026 | 2008 | 8 | 20 | 23 | 0
2026 | 2008 | 8 | 20 | 24 | 0
2026 | 2008 | 8 | 21 | 1 | 0
2026 | 2008 | 8 | 21 | 2 | 0
2026 | 2008 | 8 | 21 | 3 | 0
2026 | 2008 | 8 | 21 | 4 | 0
2026 | 2008 | 8 | 21 | 5 | 0
2026 | 2008 | 8 | 21 | 6 | 0
2026 | 2008 | 8 | 21 | 7 | 0
2026 | 2008 | 8 | 21 | 8 | 686.1691
2026 | 2008 | 8 | 21 | 9 | 10366.2701
2026 | 2008 | 8 | 21 | 10 | 23124.2764
2026 | 2008 | 8 | 21 | 11 | 27125.9209
2026 | 2008 | 8 | 21 | 12 | 31148.7247
2026 | 2008 | 8 | 21 | 13 | 32654.6436
2026 | 2008 | 8 | 21 | 14 | 32496.8251
2026 | 2008 | 8 | 21 | 15 | 30684.3383
2026 | 2008 | 8 | 21 | 16 | 30868.908
2026 | 2008 | 8 | 21 | 17 | 29748.3173
2026 | 2008 | 8 | 21 | 18 | 24476.2911
2026 | 2008 | 8 | 21 | 19 | 20989.7827
2026 | 2008 | 8 | 21 | 20 | 6537.2232
2026 | 2008 | 8 | 21 | 21 | 0
2026 | 2008 | 8 | 21 | 22 | 0
2026 | 2008 | 8 | 21 | 23 | 0
2026 | 2008 | 8 | 21 | 24 | 0
2026 | 2008 | 8 | 22 | 1 | 0
2026 | 2008 | 8 | 22 | 2 | 0
2026 | 2008 | 8 | 22 | 3 | 0
2026 | 2008 | 8 | 22 | 4 | 0
2026 | 2008 | 8 | 22 | 5 | 0
2026 | 2008 | 8 | 22 | 6 | 0
2026 | 2008 | 8 | 22 | 7 | 0
2026 | 2008 | 8 | 22 | 8 | 1113.3268
2026 | 2008 | 8 | 22 | 9 | 11602.4837
2026 | 2008 | 8 | 22 | 10 | 20686.8371
2026 | 2008 | 8 | 22 | 11 | 27438.8828
2026 | 2008 | 8 | 22 | 12 | 31301.2386
2026 | 2008 | 8 | 22 | 13 | 33781.1038
2026 | 2008 | 8 | 22 | 14 | 33557.3718
2026 | 2008 | 8 | 22 | 15 | 31255.2597
2026 | 2008 | 8 | 22 | 16 | 30061.4993
2026 | 2008 | 8 | 22 | 17 | 27312.5667
2026 | 2008 | 8 | 22 | 18 | 24674.2924
2026 | 2008 | 8 | 22 | 19 | 19161.0531
2026 | 2008 | 8 | 22 | 20 | 6103.4775
2026 | 2008 | 8 | 22 | 21 | 0
2026 | 2008 | 8 | 22 | 22 | 0
2026 | 2008 | 8 | 22 | 23 | 0
2026 | 2008 | 8 | 22 | 24 | 0
2026 | 2008 | 8 | 23 | 1 | 0
2026 | 2008 | 8 | 23 | 2 | 0
2026 | 2008 | 8 | 23 | 3 | 0
2026 | 2008 | 8 | 23 | 4 | 0
2026 | 2008 | 8 | 23 | 5 | 0
2026 | 2008 | 8 | 23 | 6 | 0
2026 | 2008 | 8 | 23 | 7 | 0
2026 | 2008 | 8 | 23 | 8 | 2072.7453
2026 | 2008 | 8 | 23 | 9 | 15466.6039
2026 | 2008 | 8 | 23 | 10 | 27095.6209
2026 | 2008 | 8 | 23 | 11 | 30014.7027
2026 | 2008 | 8 | 23 | 12 | 31645.6245
2026 | 2008 | 8 | 23 | 13 | 31406.5658
2026 | 2008 | 8 | 23 | 14 | 31265.4362
2026 | 2008 | 8 | 23 | 15 | 28685.0173
2026 | 2008 | 8 | 23 | 16 | 27819.6079
2026 | 2008 | 8 | 23 | 17 | 25211.8148
2026 | 2008 | 8 | 23 | 18 | 22866.7547
2026 | 2008 | 8 | 23 | 19 | 19113.8792
2026 | 2008 | 8 | 23 | 20 | 5551.1779
2026 | 2008 | 8 | 23 | 21 | 0
2026 | 2008 | 8 | 23 | 22 | 0
2026 | 2008 | 8 | 23 | 23 | 0
2026 | 2008 | 8 | 23 | 24 | 0
2026 | 2008 | 8 | 24 | 1 | 0
2026 | 2008 | 8 | 24 | 2 | 0
2026 | 2008 | 8 | 24 | 3 | 0
2026 | 2008 | 8 | 24 | 4 | 0
2026 | 2008 | 8 | 24 | 5 | 0
2026 | 2008 | 8 | 24 | 6 | 0
2026 | 2008 | 8 | 24 | 7 | 0
2026 | 2008 | 8 | 24 | 8 | 1958.8991
2026 | 2008 | 8 | 24 | 9 | 14618.2897
2026 | 2008 | 8 | 24 | 10 | 25936.1299
2026 | 2008 | 8 | 24 | 11 | 29652.3296
2026 | 2008 | 8 | 24 | 12 | 31800.8062
2026 | 2008 | 8 | 24 | 13 | 32933.1912
2026 | 2008 | 8 | 24 | 14 | 31548.1326
2026 | 2008 | 8 | 24 | 15 | 32182.9839
2026 | 2008 | 8 | 24 | 16 | 29021.5456
2026 | 2008 | 8 | 24 | 17 | 28424.494
2026 | 2008 | 8 | 24 | 18 | 25832.0986
2026 | 2008 | 8 | 24 | 19 | 20281.3565
2026 | 2008 | 8 | 24 | 20 | 5823.717
2026 | 2008 | 8 | 24 | 21 | 0
2026 | 2008 | 8 | 24 | 22 | 0
2026 | 2008 | 8 | 24 | 23 | 0
2026 | 2008 | 8 | 24 | 24 | 0
2026 | 2008 | 8 | 25 | 1 | 0
2026 | 2008 | 8 | 25 | 2 | 0
2026 | 2008 | 8 | 25 | 3 | 0
2026 | 2008 | 8 | 25 | 4 | 0
2026 | 2008 | 8 | 25 | 5 | 0
2026 | 2008 | 8 | 25 | 6 | 0
2026 | 2008 | 8 | 25 | 7 | 0
2026 | 2008 | 8 | 25 | 8 | 1952.1095
2026 | 2008 | 8 | 25 | 9 | 16656.4719
2026 | 2008 | 8 | 25 | 10 | 29144.9879
2026 | 2008 | 8 | 25 | 11 | 33288.7552
2026 | 2008 | 8 | 25 | 12 | 34825.4812
2026 | 2008 | 8 | 25 | 13 | 34815.1473
2026 | 2008 | 8 | 25 | 14 | 34157.1205
2026 | 2008 | 8 | 25 | 15 | 32512.9334
2026 | 2008 | 8 | 25 | 16 | 32105.1517
2026 | 2008 | 8 | 25 | 17 | 30890.7146
2026 | 2008 | 8 | 25 | 18 | 28301.946
2026 | 2008 | 8 | 25 | 19 | 21932.6507
2026 | 2008 | 8 | 25 | 20 | 5999.9521
2026 | 2008 | 8 | 25 | 21 | 0
2026 | 2008 | 8 | 25 | 22 | 0
2026 | 2008 | 8 | 25 | 23 | 0
2026 | 2008 | 8 | 25 | 24 | 0
2026 | 2008 | 8 | 26 | 1 | 0
2026 | 2008 | 8 | 26 | 2 | 0
2026 | 2008 | 8 | 26 | 3 | 0
2026 | 2008 | 8 | 26 | 4 | 0
2026 | 2008 | 8 | 26 | 5 | 0
2026 | 2008 | 8 | 26 | 6 | 0
2026 | 2008 | 8 | 26 | 7 | 0
2026 | 2008 | 8 | 26 | 8 | 2923.2997
2026 | 2008 | 8 | 26 | 9 | 17947.4308
2026 | 2008 | 8 | 26 | 10 | 29772.3068
2026 | 2008 | 8 | 26 | 11 | 33474.2128
2026 | 2008 | 8 | 26 | 12 | 34981.2964
2026 | 2008 | 8 | 26 | 13 | 34792.4753
2026 | 2008 | 8 | 26 | 14 | 33261.6977
2026 | 2008 | 8 | 26 | 15 | 32092.9687
2026 | 2008 | 8 | 26 | 16 | 31608.8881
2026 | 2008 | 8 | 26 | 17 | 30519.3946
2026 | 2008 | 8 | 26 | 18 | 27726.9965
2026 | 2008 | 8 | 26 | 19 | 21416.4686
2026 | 2008 | 8 | 26 | 20 | 5431.6187
2026 | 2008 | 8 | 26 | 21 | 0
2026 | 2008 | 8 | 26 | 22 | 0
2026 | 2008 | 8 | 26 | 23 | 0
2026 | 2008 | 8 | 26 | 24 | 0
2026 | 2008 | 8 | 27 | 1 | 0
2026 | 2008 | 8 | 27 | 2 | 0
2026 | 2008 | 8 | 27 | 3 | 0
2026 | 2008 | 8 | 27 | 4 | 0
2026 | 2008 | 8 | 27 | 5 | 0
2026 | 2008 | 8 | 27 | 6 | 0
2026 | 2008 | 8 | 27 | 7 | 0
2026 | 2008 | 8 | 27 | 8 | 2426.73
2026 | 2008 | 8 | 27 | 9 | 18409.024
2026 | 2008 | 8 | 27 | 10 | 29276.1419
2026 | 2008 | 8 | 27 | 11 | 33001.9626
2026 | 2008 | 8 | 27 | 12 | 34931.6653
2026 | 2008 | 8 | 27 | 13 | 33012.2421
2026 | 2008 | 8 | 27 | 14 | 33706.6595
2026 | 2008 | 8 | 27 | 15 | 32195.4261
2026 | 2008 | 8 | 27 | 16 | 29486.0418
2026 | 2008 | 8 | 27 | 17 | 28385.1399
2026 | 2008 | 8 | 27 | 18 | 24223.0006
2026 | 2008 | 8 | 27 | 19 | 19168.0527
2026 | 2008 | 8 | 27 | 20 | 4411.362
2026 | 2008 | 8 | 27 | 21 | 0
2026 | 2008 | 8 | 27 | 22 | 0
2026 | 2008 | 8 | 27 | 23 | 0
2026 | 2008 | 8 | 27 | 24 | 0
2026 | 2008 | 8 | 28 | 1 | 0
2026 | 2008 | 8 | 28 | 2 | 0
2026 | 2008 | 8 | 28 | 3 | 0
2026 | 2008 | 8 | 28 | 4 | 0
2026 | 2008 | 8 | 28 | 5 | 0
2026 | 2008 | 8 | 28 | 6 | 0
2026 | 2008 | 8 | 28 | 7 | 0
2026 | 2008 | 8 | 28 | 8 | 1715.4575
2026 | 2008 | 8 | 28 | 9 | 11866.3058
2026 | 2008 | 8 | 28 | 10 | 22408.4962
2026 | 2008 | 8 | 28 | 11 | 30248.2613
2026 | 2008 | 8 | 28 | 12 | 31459.8586
2026 | 2008 | 8 | 28 | 13 | 32160.7868
2026 | 2008 | 8 | 28 | 14 | 31741.2987
2026 | 2008 | 8 | 28 | 15 | 31414.0328
2026 | 2008 | 8 | 28 | 16 | 28976.6121
2026 | 2008 | 8 | 28 | 17 | 26310.7703
2026 | 2008 | 8 | 28 | 18 | 24013.5997
2026 | 2008 | 8 | 28 | 19 | 19695.3212
2026 | 2008 | 8 | 28 | 20 | 4367.0531
2026 | 2008 | 8 | 28 | 21 | 0
2026 | 2008 | 8 | 28 | 22 | 0
2026 | 2008 | 8 | 28 | 23 | 0
2026 | 2008 | 8 | 28 | 24 | 0
2026 | 2008 | 8 | 29 | 1 | 0
2026 | 2008 | 8 | 29 | 2 | 0
2026 | 2008 | 8 | 29 | 3 | 0
2026 | 2008 | 8 | 29 | 4 | 0
2026 | 2008 | 8 | 29 | 5 | 0
2026 | 2008 | 8 | 29 | 6 | 0
2026 | 2008 | 8 | 29 | 7 | 0
2026 | 2008 | 8 | 29 | 8 | 1546.7616
2026 | 2008 | 8 | 29 | 9 | 11833.351
2026 | 2008 | 8 | 29 | 10 | 22669.1412
2026 | 2008 | 8 | 29 | 11 | 26712.6647
2026 | 2008 | 8 | 29 | 12 | 28969.2694
2026 | 2008 | 8 | 29 | 13 | 27928.9372
2026 | 2008 | 8 | 29 | 14 | 26986.2727
2026 | 2008 | 8 | 29 | 15 | 25119.4968
2026 | 2008 | 8 | 29 | 16 | 23024.0996
2026 | 2008 | 8 | 29 | 17 | 20494.7669
2026 | 2008 | 8 | 29 | 18 | 19083.3745
2026 | 2008 | 8 | 29 | 19 | 16264.2249
2026 | 2008 | 8 | 29 | 20 | 3517.3707
2026 | 2008 | 8 | 29 | 21 | 0
2026 | 2008 | 8 | 29 | 22 | 0
2026 | 2008 | 8 | 29 | 23 | 0
2026 | 2008 | 8 | 29 | 24 | 0
2026 | 2008 | 8 | 30 | 1 | 0
2026 | 2008 | 8 | 30 | 2 | 0
2026 | 2008 | 8 | 30 | 3 | 0
2026 | 2008 | 8 | 30 | 4 | 0
2026 | 2008 | 8 | 30 | 5 | 0
2026 | 2008 | 8 | 30 | 6 | 0
2026 | 2008 | 8 | 30 | 7 | 0
2026 | 2008 | 8 | 30 | 8 | 1479.6806
2026 | 2008 | 8 | 30 | 9 | 14387.4058
2026 | 2008 | 8 | 30 | 10 | 25237.8172
2026 | 2008 | 8 | 30 | 11 | 30480.1345
2026 | 2008 | 8 | 30 | 12 | 32020.8339
2026 | 2008 | 8 | 30 | 13 | 31600.7541
2026 | 2008 | 8 | 30 | 14 | 31973.2691
2026 | 2008 | 8 | 30 | 15 | 28809.2183
2026 | 2008 | 8 | 30 | 16 | 28256.7555
2026 | 2008 | 8 | 30 | 17 | 25469.1286
2026 | 2008 | 8 | 30 | 18 | 22813.4281
2026 | 2008 | 8 | 30 | 19 | 18201.8646
2026 | 2008 | 8 | 30 | 20 | 3993.5332
2026 | 2008 | 8 | 30 | 21 | 0
2026 | 2008 | 8 | 30 | 22 | 0
2026 | 2008 | 8 | 30 | 23 | 0
2026 | 2008 | 8 | 30 | 24 | 0
2026 | 2008 | 8 | 31 | 1 | 0
2026 | 2008 | 8 | 31 | 2 | 0
2026 | 2008 | 8 | 31 | 3 | 0
2026 | 2008 | 8 | 31 | 4 | 0
2026 | 2008 | 8 | 31 | 5 | 0
2026 | 2008 | 8 | 31 | 6 | 0
2026 | 2008 | 8 | 31 | 7 | 0
2026 | 2008 | 8 | 31 | 8 | 1278.1535
2026 | 2008 | 8 | 31 | 9 | 14674.4357
2026 | 2008 | 8 | 31 | 10 | 27638.2159
2026 | 2008 | 8 | 31 | 11 | 33011.3372
2026 | 2008 | 8 | 31 | 12 | 34748.8528
2026 | 2008 | 8 | 31 | 13 | 34616.0459
2026 | 2008 | 8 | 31 | 14 | 34858.2872
2026 | 2008 | 8 | 31 | 15 | 33131.932
2026 | 2008 | 8 | 31 | 16 | 32350.3011
2026 | 2008 | 8 | 31 | 17 | 31062.6945
2026 | 2008 | 8 | 31 | 18 | 27788.2936
2026 | 2008 | 8 | 31 | 19 | 18031.25
2026 | 2008 | 8 | 31 | 20 | 3789.0858
2026 | 2008 | 8 | 31 | 21 | 0
2026 | 2008 | 8 | 31 | 22 | 0
2026 | 2008 | 8 | 31 | 23 | 0
2026 | 2008 | 8 | 31 | 24 | 0
2027 | 2008 | 8 | 1 | 1 | 0
2027 | 2008 | 8 | 1 | 2 | 0
2027 | 2008 | 8 | 1 | 3 | 0
2027 | 2008 | 8 | 1 | 4 | 0
2027 | 2008 | 8 | 1 | 5 | 0
2027 | 2008 | 8 | 1 | 6 | 0
2027 | 2008 | 8 | 1 | 7 | 2.4214
2027 | 2008 | 8 | 1 | 8 | 4258.952
2027 | 2008 | 8 | 1 | 9 | 18544.521
2027 | 2008 | 8 | 1 | 10 | 33997.3489
2027 | 2008 | 8 | 1 | 11 | 41691.2012
2027 | 2008 | 8 | 1 | 12 | 45041.8217
2027 | 2008 | 8 | 1 | 13 | 46373.6959
2027 | 2008 | 8 | 1 | 14 | 45111.794
2027 | 2008 | 8 | 1 | 15 | 43409.4734
2027 | 2008 | 8 | 1 | 16 | 40777.0953
2027 | 2008 | 8 | 1 | 17 | 37718.6916
2027 | 2008 | 8 | 1 | 18 | 34431.7839
2027 | 2008 | 8 | 1 | 19 | 28334.7162
2027 | 2008 | 8 | 1 | 20 | 10190.5593
2027 | 2008 | 8 | 1 | 21 | 442.7226
2027 | 2008 | 8 | 1 | 22 | 0
2027 | 2008 | 8 | 1 | 23 | 0
2027 | 2008 | 8 | 1 | 24 | 0
2027 | 2008 | 8 | 2 | 1 | 0
2027 | 2008 | 8 | 2 | 2 | 0
2027 | 2008 | 8 | 2 | 3 | 0
2027 | 2008 | 8 | 2 | 4 | 0
2027 | 2008 | 8 | 2 | 5 | 0
2027 | 2008 | 8 | 2 | 6 | 0
2027 | 2008 | 8 | 2 | 7 | 2.0632
2027 | 2008 | 8 | 2 | 8 | 4435.3666
2027 | 2008 | 8 | 2 | 9 | 17795.4212
2027 | 2008 | 8 | 2 | 10 | 34724.9291
2027 | 2008 | 8 | 2 | 11 | 44421.1877
2027 | 2008 | 8 | 2 | 12 | 46771.6186
2027 | 2008 | 8 | 2 | 13 | 45907.8889
2027 | 2008 | 8 | 2 | 14 | 46963.8182
2027 | 2008 | 8 | 2 | 15 | 45996.0656
2027 | 2008 | 8 | 2 | 16 | 45615.5768
2027 | 2008 | 8 | 2 | 17 | 42061.7165
2027 | 2008 | 8 | 2 | 18 | 38796.1883
2027 | 2008 | 8 | 2 | 19 | 29205.4497
2027 | 2008 | 8 | 2 | 20 | 9288.9189
2027 | 2008 | 8 | 2 | 21 | 263.9711
2027 | 2008 | 8 | 2 | 22 | 0
2027 | 2008 | 8 | 2 | 23 | 0
2027 | 2008 | 8 | 2 | 24 | 0
2027 | 2008 | 8 | 3 | 1 | 0
2027 | 2008 | 8 | 3 | 2 | 0
2027 | 2008 | 8 | 3 | 3 | 0
2027 | 2008 | 8 | 3 | 4 | 0
2027 | 2008 | 8 | 3 | 5 | 0
2027 | 2008 | 8 | 3 | 6 | 0
2027 | 2008 | 8 | 3 | 7 | 2.9932
2027 | 2008 | 8 | 3 | 8 | 4396.4569
2027 | 2008 | 8 | 3 | 9 | 20948.2503
2027 | 2008 | 8 | 3 | 10 | 37012.3537
2027 | 2008 | 8 | 3 | 11 | 45313.2621
2027 | 2008 | 8 | 3 | 12 | 48152.2919
2027 | 2008 | 8 | 3 | 13 | 47644.619
2027 | 2008 | 8 | 3 | 14 | 48049.7551
2027 | 2008 | 8 | 3 | 15 | 46671.1938
2027 | 2008 | 8 | 3 | 16 | 45324.4842
2027 | 2008 | 8 | 3 | 17 | 43726.7432
2027 | 2008 | 8 | 3 | 18 | 39672.6674
2027 | 2008 | 8 | 3 | 19 | 29979.9725
2027 | 2008 | 8 | 3 | 20 | 9856.0285
2027 | 2008 | 8 | 3 | 21 | 109.6374
2027 | 2008 | 8 | 3 | 22 | 0
2027 | 2008 | 8 | 3 | 23 | 0
2027 | 2008 | 8 | 3 | 24 | 0
2027 | 2008 | 8 | 4 | 1 | 0
2027 | 2008 | 8 | 4 | 2 | 0
2027 | 2008 | 8 | 4 | 3 | 0
2027 | 2008 | 8 | 4 | 4 | 0
2027 | 2008 | 8 | 4 | 5 | 0
2027 | 2008 | 8 | 4 | 6 | 0
2027 | 2008 | 8 | 4 | 7 | 1.9784
2027 | 2008 | 8 | 4 | 8 | 4995.6035
2027 | 2008 | 8 | 4 | 9 | 24302.2349
2027 | 2008 | 8 | 4 | 10 | 37703.8692
2027 | 2008 | 8 | 4 | 11 | 44874.3857
2027 | 2008 | 8 | 4 | 12 | 45588.3206
2027 | 2008 | 8 | 4 | 13 | 45710.8382
2027 | 2008 | 8 | 4 | 14 | 44899.2157
2027 | 2008 | 8 | 4 | 15 | 45234.5067
2027 | 2008 | 8 | 4 | 16 | 43723.7219
2027 | 2008 | 8 | 4 | 17 | 41870.7134
2027 | 2008 | 8 | 4 | 18 | 38433.3813
2027 | 2008 | 8 | 4 | 19 | 29876.1778
2027 | 2008 | 8 | 4 | 20 | 9766.0027
2027 | 2008 | 8 | 4 | 21 | 56.5471
2027 | 2008 | 8 | 4 | 22 | 0
2027 | 2008 | 8 | 4 | 23 | 0
2027 | 2008 | 8 | 4 | 24 | 0
2027 | 2008 | 8 | 5 | 1 | 0
2027 | 2008 | 8 | 5 | 2 | 0
2027 | 2008 | 8 | 5 | 3 | 0
2027 | 2008 | 8 | 5 | 4 | 0
2027 | 2008 | 8 | 5 | 5 | 0
2027 | 2008 | 8 | 5 | 6 | 0
2027 | 2008 | 8 | 5 | 7 | 0.65143
2027 | 2008 | 8 | 5 | 8 | 5529.1548
2027 | 2008 | 8 | 5 | 9 | 23186.9723
2027 | 2008 | 8 | 5 | 10 | 38515.5561
2027 | 2008 | 8 | 5 | 11 | 41531.9464
2027 | 2008 | 8 | 5 | 12 | 43051.4634
2027 | 2008 | 8 | 5 | 13 | 44621.922
2027 | 2008 | 8 | 5 | 14 | 42909.4092
2027 | 2008 | 8 | 5 | 15 | 38677.717
2027 | 2008 | 8 | 5 | 16 | 34206.0158
2027 | 2008 | 8 | 5 | 17 | 30271.8369
2027 | 2008 | 8 | 5 | 18 | 28960.205
2027 | 2008 | 8 | 5 | 19 | 25043.4546
2027 | 2008 | 8 | 5 | 20 | 9488.6266
2027 | 2008 | 8 | 5 | 21 | 53.0187
2027 | 2008 | 8 | 5 | 22 | 0
2027 | 2008 | 8 | 5 | 23 | 0
2027 | 2008 | 8 | 5 | 24 | 0
2027 | 2008 | 8 | 6 | 1 | 0
2027 | 2008 | 8 | 6 | 2 | 0
2027 | 2008 | 8 | 6 | 3 | 0
2027 | 2008 | 8 | 6 | 4 | 0
2027 | 2008 | 8 | 6 | 5 | 0
2027 | 2008 | 8 | 6 | 6 | 0
2027 | 2008 | 8 | 6 | 7 | 0.044932
2027 | 2008 | 8 | 6 | 8 | 2995.7743
2027 | 2008 | 8 | 6 | 9 | 17205.1804
2027 | 2008 | 8 | 6 | 10 | 31785.1307
2027 | 2008 | 8 | 6 | 11 | 35425.5649
2027 | 2008 | 8 | 6 | 12 | 38955.491
2027 | 2008 | 8 | 6 | 13 | 38790.6899
2027 | 2008 | 8 | 6 | 14 | 38557.0534
2027 | 2008 | 8 | 6 | 15 | 37545.8021
2027 | 2008 | 8 | 6 | 16 | 35109.7809
2027 | 2008 | 8 | 6 | 17 | 31609.3009
2027 | 2008 | 8 | 6 | 18 | 30005.2993
2027 | 2008 | 8 | 6 | 19 | 25046.3957
2027 | 2008 | 8 | 6 | 20 | 8927.2587
2027 | 2008 | 8 | 6 | 21 | 38.8185
2027 | 2008 | 8 | 6 | 22 | 0
2027 | 2008 | 8 | 6 | 23 | 0
2027 | 2008 | 8 | 6 | 24 | 0
2027 | 2008 | 8 | 7 | 1 | 0
2027 | 2008 | 8 | 7 | 2 | 0
2027 | 2008 | 8 | 7 | 3 | 0
2027 | 2008 | 8 | 7 | 4 | 0
2027 | 2008 | 8 | 7 | 5 | 0
2027 | 2008 | 8 | 7 | 6 | 0
2027 | 2008 | 8 | 7 | 7 | 0.20704
2027 | 2008 | 8 | 7 | 8 | 2974.4266
2027 | 2008 | 8 | 7 | 9 | 14786.0215
2027 | 2008 | 8 | 7 | 10 | 28317.7573
2027 | 2008 | 8 | 7 | 11 | 38740.874
2027 | 2008 | 8 | 7 | 12 | 43972.2128
2027 | 2008 | 8 | 7 | 13 | 45059.8963
2027 | 2008 | 8 | 7 | 14 | 44158.0477
2027 | 2008 | 8 | 7 | 15 | 43400.6744
2027 | 2008 | 8 | 7 | 16 | 42037.4957
2027 | 2008 | 8 | 7 | 17 | 40818.4457
2027 | 2008 | 8 | 7 | 18 | 35816.3956
2027 | 2008 | 8 | 7 | 19 | 27711.3132
2027 | 2008 | 8 | 7 | 20 | 8806.7579
2027 | 2008 | 8 | 7 | 21 | 33.2623
2027 | 2008 | 8 | 7 | 22 | 0
2027 | 2008 | 8 | 7 | 23 | 0
2027 | 2008 | 8 | 7 | 24 | 0
2027 | 2008 | 8 | 8 | 1 | 0
2027 | 2008 | 8 | 8 | 2 | 0
2027 | 2008 | 8 | 8 | 3 | 0
2027 | 2008 | 8 | 8 | 4 | 0
2027 | 2008 | 8 | 8 | 5 | 0
2027 | 2008 | 8 | 8 | 6 | 0
2027 | 2008 | 8 | 8 | 7 | 0.0076014
2027 | 2008 | 8 | 8 | 8 | 3189.9753
2027 | 2008 | 8 | 8 | 9 | 19969.896
2027 | 2008 | 8 | 8 | 10 | 35545.0117
2027 | 2008 | 8 | 8 | 11 | 41538.5575
2027 | 2008 | 8 | 8 | 12 | 42102.4477
2027 | 2008 | 8 | 8 | 13 | 44435.1151
2027 | 2008 | 8 | 8 | 14 | 45201.0002
2027 | 2008 | 8 | 8 | 15 | 44038.4305
2027 | 2008 | 8 | 8 | 16 | 42240.0262
2027 | 2008 | 8 | 8 | 17 | 38590.1064
2027 | 2008 | 8 | 8 | 18 | 34757.2163
2027 | 2008 | 8 | 8 | 19 | 27996.4872
2027 | 2008 | 8 | 8 | 20 | 9606.7743
2027 | 2008 | 8 | 8 | 21 | 26.1682
2027 | 2008 | 8 | 8 | 22 | 0
2027 | 2008 | 8 | 8 | 23 | 0
2027 | 2008 | 8 | 8 | 24 | 0
2027 | 2008 | 8 | 9 | 1 | 0
2027 | 2008 | 8 | 9 | 2 | 0
2027 | 2008 | 8 | 9 | 3 | 0
2027 | 2008 | 8 | 9 | 4 | 0
2027 | 2008 | 8 | 9 | 5 | 0
2027 | 2008 | 8 | 9 | 6 | 0
2027 | 2008 | 8 | 9 | 7 | 0.045975
2027 | 2008 | 8 | 9 | 8 | 2824.8132
2027 | 2008 | 8 | 9 | 9 | 18885.8522
2027 | 2008 | 8 | 9 | 10 | 33730.2914
2027 | 2008 | 8 | 9 | 11 | 39281.4503
2027 | 2008 | 8 | 9 | 12 | 41821.9228
2027 | 2008 | 8 | 9 | 13 | 42187.7617
2027 | 2008 | 8 | 9 | 14 | 40170.3461
2027 | 2008 | 8 | 9 | 15 | 37296.6541
2027 | 2008 | 8 | 9 | 16 | 34379.238
2027 | 2008 | 8 | 9 | 17 | 33592.1432
2027 | 2008 | 8 | 9 | 18 | 32390.0569
2027 | 2008 | 8 | 9 | 19 | 27138.665
2027 | 2008 | 8 | 9 | 20 | 9080.3621
2027 | 2008 | 8 | 9 | 21 | 0
2027 | 2008 | 8 | 9 | 22 | 0
2027 | 2008 | 8 | 9 | 23 | 0
2027 | 2008 | 8 | 9 | 24 | 0
2027 | 2008 | 8 | 10 | 1 | 0
2027 | 2008 | 8 | 10 | 2 | 0
2027 | 2008 | 8 | 10 | 3 | 0
2027 | 2008 | 8 | 10 | 4 | 0
2027 | 2008 | 8 | 10 | 5 | 0
2027 | 2008 | 8 | 10 | 6 | 0
2027 | 2008 | 8 | 10 | 7 | 0.3285
2027 | 2008 | 8 | 10 | 8 | 2418.6719
2027 | 2008 | 8 | 10 | 9 | 17076.6677
2027 | 2008 | 8 | 10 | 10 | 34360.9869
2027 | 2008 | 8 | 10 | 11 | 40625.8622
2027 | 2008 | 8 | 10 | 12 | 43805.1519
2027 | 2008 | 8 | 10 | 13 | 45687.4383
2027 | 2008 | 8 | 10 | 14 | 45125.9975
2027 | 2008 | 8 | 10 | 15 | 44567.9325
2027 | 2008 | 8 | 10 | 16 | 42687.637
2027 | 2008 | 8 | 10 | 17 | 39023.4486
2027 | 2008 | 8 | 10 | 18 | 33049.5039
2027 | 2008 | 8 | 10 | 19 | 26189.642
2027 | 2008 | 8 | 10 | 20 | 8252.4409
2027 | 2008 | 8 | 10 | 21 | 0
2027 | 2008 | 8 | 10 | 22 | 0
2027 | 2008 | 8 | 10 | 23 | 0
2027 | 2008 | 8 | 10 | 24 | 0
2027 | 2008 | 8 | 11 | 1 | 0
2027 | 2008 | 8 | 11 | 2 | 0
2027 | 2008 | 8 | 11 | 3 | 0
2027 | 2008 | 8 | 11 | 4 | 0
2027 | 2008 | 8 | 11 | 5 | 0
2027 | 2008 | 8 | 11 | 6 | 0
2027 | 2008 | 8 | 11 | 7 | 0
2027 | 2008 | 8 | 11 | 8 | 1775.3725
2027 | 2008 | 8 | 11 | 9 | 13584.1403
2027 | 2008 | 8 | 11 | 10 | 25832.4441
2027 | 2008 | 8 | 11 | 11 | 35651.8575
2027 | 2008 | 8 | 11 | 12 | 40153.4693
2027 | 2008 | 8 | 11 | 13 | 39356.0911
2027 | 2008 | 8 | 11 | 14 | 39277.1776
2027 | 2008 | 8 | 11 | 15 | 37442.5062
2027 | 2008 | 8 | 11 | 16 | 35891.4192
2027 | 2008 | 8 | 11 | 17 | 31596.1844
2027 | 2008 | 8 | 11 | 18 | 29569.2813
2027 | 2008 | 8 | 11 | 19 | 24479.7806
2027 | 2008 | 8 | 11 | 20 | 8159.9175
2027 | 2008 | 8 | 11 | 21 | 0
2027 | 2008 | 8 | 11 | 22 | 0
2027 | 2008 | 8 | 11 | 23 | 0
2027 | 2008 | 8 | 11 | 24 | 0
2027 | 2008 | 8 | 12 | 1 | 0
2027 | 2008 | 8 | 12 | 2 | 0
2027 | 2008 | 8 | 12 | 3 | 0
2027 | 2008 | 8 | 12 | 4 | 0
2027 | 2008 | 8 | 12 | 5 | 0
2027 | 2008 | 8 | 12 | 6 | 0
2027 | 2008 | 8 | 12 | 7 | 0.0022535
2027 | 2008 | 8 | 12 | 8 | 897.5998
2027 | 2008 | 8 | 12 | 9 | 8660.0538
2027 | 2008 | 8 | 12 | 10 | 22587.6786
2027 | 2008 | 8 | 12 | 11 | 32912.6511
2027 | 2008 | 8 | 12 | 12 | 39529.0698
2027 | 2008 | 8 | 12 | 13 | 42200.8167
2027 | 2008 | 8 | 12 | 14 | 43104.0167
2027 | 2008 | 8 | 12 | 15 | 41202.4615
2027 | 2008 | 8 | 12 | 16 | 39853.3848
2027 | 2008 | 8 | 12 | 17 | 36732.7488
2027 | 2008 | 8 | 12 | 18 | 33963.4161
2027 | 2008 | 8 | 12 | 19 | 27189.0869
2027 | 2008 | 8 | 12 | 20 | 8979.6374
2027 | 2008 | 8 | 12 | 21 | 0
2027 | 2008 | 8 | 12 | 22 | 0
2027 | 2008 | 8 | 12 | 23 | 0
2027 | 2008 | 8 | 12 | 24 | 0
2027 | 2008 | 8 | 13 | 1 | 0
2027 | 2008 | 8 | 13 | 2 | 0
2027 | 2008 | 8 | 13 | 3 | 0
2027 | 2008 | 8 | 13 | 4 | 0
2027 | 2008 | 8 | 13 | 5 | 0
2027 | 2008 | 8 | 13 | 6 | 0
2027 | 2008 | 8 | 13 | 7 | 0.064221
2027 | 2008 | 8 | 13 | 8 | 4664.3531
2027 | 2008 | 8 | 13 | 9 | 21606.5896
2027 | 2008 | 8 | 13 | 10 | 38777.3839
2027 | 2008 | 8 | 13 | 11 | 42637.1064
2027 | 2008 | 8 | 13 | 12 | 45618.1628
2027 | 2008 | 8 | 13 | 13 | 43603.8929
2027 | 2008 | 8 | 13 | 14 | 44035.1864
2027 | 2008 | 8 | 13 | 15 | 42470.645
2027 | 2008 | 8 | 13 | 16 | 42349.1636
2027 | 2008 | 8 | 13 | 17 | 40357.8723
2027 | 2008 | 8 | 13 | 18 | 36474.7711
2027 | 2008 | 8 | 13 | 19 | 27494.8666
2027 | 2008 | 8 | 13 | 20 | 9597.5502
2027 | 2008 | 8 | 13 | 21 | 0
2027 | 2008 | 8 | 13 | 22 | 0
2027 | 2008 | 8 | 13 | 23 | 0
2027 | 2008 | 8 | 13 | 24 | 0
2027 | 2008 | 8 | 14 | 1 | 0
2027 | 2008 | 8 | 14 | 2 | 0
2027 | 2008 | 8 | 14 | 3 | 0
2027 | 2008 | 8 | 14 | 4 | 0
2027 | 2008 | 8 | 14 | 5 | 0
2027 | 2008 | 8 | 14 | 6 | 0
2027 | 2008 | 8 | 14 | 7 | 0.0029843
2027 | 2008 | 8 | 14 | 8 | 2911.5167
2027 | 2008 | 8 | 14 | 9 | 19890.4698
2027 | 2008 | 8 | 14 | 10 | 34276.7505
2027 | 2008 | 8 | 14 | 11 | 41748.5144
2027 | 2008 | 8 | 14 | 12 | 42904.1467
2027 | 2008 | 8 | 14 | 13 | 45190.3404
2027 | 2008 | 8 | 14 | 14 | 44398.8924
2027 | 2008 | 8 | 14 | 15 | 43579.6024
2027 | 2008 | 8 | 14 | 16 | 41425.7321
2027 | 2008 | 8 | 14 | 17 | 40400.7524
2027 | 2008 | 8 | 14 | 18 | 37434.3568
2027 | 2008 | 8 | 14 | 19 | 28733.7759
2027 | 2008 | 8 | 14 | 20 | 10353.2172
2027 | 2008 | 8 | 14 | 21 | 0
2027 | 2008 | 8 | 14 | 22 | 0
2027 | 2008 | 8 | 14 | 23 | 0
2027 | 2008 | 8 | 14 | 24 | 0
2027 | 2008 | 8 | 15 | 1 | 0
2027 | 2008 | 8 | 15 | 2 | 0
2027 | 2008 | 8 | 15 | 3 | 0
2027 | 2008 | 8 | 15 | 4 | 0
2027 | 2008 | 8 | 15 | 5 | 0
2027 | 2008 | 8 | 15 | 6 | 0
2027 | 2008 | 8 | 15 | 7 | 0.018889
2027 | 2008 | 8 | 15 | 8 | 1825.4824
2027 | 2008 | 8 | 15 | 9 | 17425.0644
2027 | 2008 | 8 | 15 | 10 | 29324.4745
2027 | 2008 | 8 | 15 | 11 | 38729.837
2027 | 2008 | 8 | 15 | 12 | 43897.6935
2027 | 2008 | 8 | 15 | 13 | 44930.1685
2027 | 2008 | 8 | 15 | 14 | 42628.6374
2027 | 2008 | 8 | 15 | 15 | 42813.4351
2027 | 2008 | 8 | 15 | 16 | 42702.6212
2027 | 2008 | 8 | 15 | 17 | 41007.4453
2027 | 2008 | 8 | 15 | 18 | 36423.822
2027 | 2008 | 8 | 15 | 19 | 28764.472
2027 | 2008 | 8 | 15 | 20 | 8434.3013
2027 | 2008 | 8 | 15 | 21 | 0
2027 | 2008 | 8 | 15 | 22 | 0
2027 | 2008 | 8 | 15 | 23 | 0
2027 | 2008 | 8 | 15 | 24 | 0
2027 | 2008 | 8 | 16 | 1 | 0
2027 | 2008 | 8 | 16 | 2 | 0
2027 | 2008 | 8 | 16 | 3 | 0
2027 | 2008 | 8 | 16 | 4 | 0
2027 | 2008 | 8 | 16 | 5 | 0
2027 | 2008 | 8 | 16 | 6 | 0
2027 | 2008 | 8 | 16 | 7 | 0
2027 | 2008 | 8 | 16 | 8 | 1847.4858
2027 | 2008 | 8 | 16 | 9 | 12828.6945
2027 | 2008 | 8 | 16 | 10 | 26690.4464
2027 | 2008 | 8 | 16 | 11 | 33246.3181
2027 | 2008 | 8 | 16 | 12 | 34174.6329
2027 | 2008 | 8 | 16 | 13 | 35143.4289
2027 | 2008 | 8 | 16 | 14 | 35156.4778
2027 | 2008 | 8 | 16 | 15 | 33679.0473
2027 | 2008 | 8 | 16 | 16 | 31879.5994
2027 | 2008 | 8 | 16 | 17 | 32046.2503
2027 | 2008 | 8 | 16 | 18 | 30509.2468
2027 | 2008 | 8 | 16 | 19 | 25704.7531
2027 | 2008 | 8 | 16 | 20 | 8982.2615
2027 | 2008 | 8 | 16 | 21 | 0
2027 | 2008 | 8 | 16 | 22 | 0
2027 | 2008 | 8 | 16 | 23 | 0
2027 | 2008 | 8 | 16 | 24 | 0
2027 | 2008 | 8 | 17 | 1 | 0
2027 | 2008 | 8 | 17 | 2 | 0
2027 | 2008 | 8 | 17 | 3 | 0
2027 | 2008 | 8 | 17 | 4 | 0
2027 | 2008 | 8 | 17 | 5 | 0
2027 | 2008 | 8 | 17 | 6 | 0
2027 | 2008 | 8 | 17 | 7 | 0
2027 | 2008 | 8 | 17 | 8 | 1339.5142
2027 | 2008 | 8 | 17 | 9 | 13134.4545
2027 | 2008 | 8 | 17 | 10 | 27040.7253
2027 | 2008 | 8 | 17 | 11 | 32182.1273
2027 | 2008 | 8 | 17 | 12 | 34762.6556
2027 | 2008 | 8 | 17 | 13 | 35331.064
2027 | 2008 | 8 | 17 | 14 | 33168.0114
2027 | 2008 | 8 | 17 | 15 | 31332.5132
2027 | 2008 | 8 | 17 | 16 | 28360.4897
2027 | 2008 | 8 | 17 | 17 | 26714.9192
2027 | 2008 | 8 | 17 | 18 | 25217.5015
2027 | 2008 | 8 | 17 | 19 | 22407.3393
2027 | 2008 | 8 | 17 | 20 | 7725.6275
2027 | 2008 | 8 | 17 | 21 | 0
2027 | 2008 | 8 | 17 | 22 | 0
2027 | 2008 | 8 | 17 | 23 | 0
2027 | 2008 | 8 | 17 | 24 | 0
2027 | 2008 | 8 | 18 | 1 | 0
2027 | 2008 | 8 | 18 | 2 | 0
2027 | 2008 | 8 | 18 | 3 | 0
2027 | 2008 | 8 | 18 | 4 | 0
2027 | 2008 | 8 | 18 | 5 | 0
2027 | 2008 | 8 | 18 | 6 | 0
2027 | 2008 | 8 | 18 | 7 | 0
2027 | 2008 | 8 | 18 | 8 | 1009.9109
2027 | 2008 | 8 | 18 | 9 | 10754.8381
2027 | 2008 | 8 | 18 | 10 | 20676.9007
2027 | 2008 | 8 | 18 | 11 | 28045.6631
2027 | 2008 | 8 | 18 | 12 | 33197.3581
2027 | 2008 | 8 | 18 | 13 | 35100.3293
2027 | 2008 | 8 | 18 | 14 | 35116.7144
2027 | 2008 | 8 | 18 | 15 | 32346.6528
2027 | 2008 | 8 | 18 | 16 | 29088.2598
2027 | 2008 | 8 | 18 | 17 | 25646.3302
2027 | 2008 | 8 | 18 | 18 | 25060.1498
2027 | 2008 | 8 | 18 | 19 | 21719.0438
2027 | 2008 | 8 | 18 | 20 | 7616.7926
2027 | 2008 | 8 | 18 | 21 | 0
2027 | 2008 | 8 | 18 | 22 | 0
2027 | 2008 | 8 | 18 | 23 | 0
2027 | 2008 | 8 | 18 | 24 | 0
2027 | 2008 | 8 | 19 | 1 | 0
2027 | 2008 | 8 | 19 | 2 | 0
2027 | 2008 | 8 | 19 | 3 | 0
2027 | 2008 | 8 | 19 | 4 | 0
2027 | 2008 | 8 | 19 | 5 | 0
2027 | 2008 | 8 | 19 | 6 | 0
2027 | 2008 | 8 | 19 | 7 | 0
2027 | 2008 | 8 | 19 | 8 | 1142.4087
2027 | 2008 | 8 | 19 | 9 | 11326.9749
2027 | 2008 | 8 | 19 | 10 | 24039.6621
2027 | 2008 | 8 | 19 | 11 | 31181.437
2027 | 2008 | 8 | 19 | 12 | 35302.73
2027 | 2008 | 8 | 19 | 13 | 36338.6541
2027 | 2008 | 8 | 19 | 14 | 36243.0785
2027 | 2008 | 8 | 19 | 15 | 35064.2936
2027 | 2008 | 8 | 19 | 16 | 33343.2105
2027 | 2008 | 8 | 19 | 17 | 30571.8812
2027 | 2008 | 8 | 19 | 18 | 29311.4918
2027 | 2008 | 8 | 19 | 19 | 24633.2302
2027 | 2008 | 8 | 19 | 20 | 8654.3494
2027 | 2008 | 8 | 19 | 21 | 0
2027 | 2008 | 8 | 19 | 22 | 0
2027 | 2008 | 8 | 19 | 23 | 0
2027 | 2008 | 8 | 19 | 24 | 0
2027 | 2008 | 8 | 20 | 1 | 0
2027 | 2008 | 8 | 20 | 2 | 0
2027 | 2008 | 8 | 20 | 3 | 0
2027 | 2008 | 8 | 20 | 4 | 0
2027 | 2008 | 8 | 20 | 5 | 0
2027 | 2008 | 8 | 20 | 6 | 0
2027 | 2008 | 8 | 20 | 7 | 0
2027 | 2008 | 8 | 20 | 8 | 874.0236
2027 | 2008 | 8 | 20 | 9 | 11980.0236
2027 | 2008 | 8 | 20 | 10 | 26209.5518
2027 | 2008 | 8 | 20 | 11 | 34610.0934
2027 | 2008 | 8 | 20 | 12 | 40057.5834
2027 | 2008 | 8 | 20 | 13 | 39060.8526
2027 | 2008 | 8 | 20 | 14 | 38456.0768
2027 | 2008 | 8 | 20 | 15 | 37976.0782
2027 | 2008 | 8 | 20 | 16 | 37721.3011
2027 | 2008 | 8 | 20 | 17 | 35766.5312
2027 | 2008 | 8 | 20 | 18 | 34184.6562
2027 | 2008 | 8 | 20 | 19 | 26452.1578
2027 | 2008 | 8 | 20 | 20 | 8617.4391
2027 | 2008 | 8 | 20 | 21 | 0
2027 | 2008 | 8 | 20 | 22 | 0
2027 | 2008 | 8 | 20 | 23 | 0
2027 | 2008 | 8 | 20 | 24 | 0
2027 | 2008 | 8 | 21 | 1 | 0
2027 | 2008 | 8 | 21 | 2 | 0
2027 | 2008 | 8 | 21 | 3 | 0
2027 | 2008 | 8 | 21 | 4 | 0
2027 | 2008 | 8 | 21 | 5 | 0
2027 | 2008 | 8 | 21 | 6 | 0
2027 | 2008 | 8 | 21 | 7 | 0
2027 | 2008 | 8 | 21 | 8 | 941.2506
2027 | 2008 | 8 | 21 | 9 | 13577.0649
2027 | 2008 | 8 | 21 | 10 | 29917.065
2027 | 2008 | 8 | 21 | 11 | 33825.9049
2027 | 2008 | 8 | 21 | 12 | 39463.6164
2027 | 2008 | 8 | 21 | 13 | 40971.8816
2027 | 2008 | 8 | 21 | 14 | 40673.2145
2027 | 2008 | 8 | 21 | 15 | 38389.8615
2027 | 2008 | 8 | 21 | 16 | 39250.688
2027 | 2008 | 8 | 21 | 17 | 37789.9377
2027 | 2008 | 8 | 21 | 18 | 31133.0942
2027 | 2008 | 8 | 21 | 19 | 26725.2389
2027 | 2008 | 8 | 21 | 20 | 8262.8061
2027 | 2008 | 8 | 21 | 21 | 0
2027 | 2008 | 8 | 21 | 22 | 0
2027 | 2008 | 8 | 21 | 23 | 0
2027 | 2008 | 8 | 21 | 24 | 0
2027 | 2008 | 8 | 22 | 1 | 0
2027 | 2008 | 8 | 22 | 2 | 0
2027 | 2008 | 8 | 22 | 3 | 0
2027 | 2008 | 8 | 22 | 4 | 0
2027 | 2008 | 8 | 22 | 5 | 0
2027 | 2008 | 8 | 22 | 6 | 0
2027 | 2008 | 8 | 22 | 7 | 0
2027 | 2008 | 8 | 22 | 8 | 1320.4894
2027 | 2008 | 8 | 22 | 9 | 13988.7429
2027 | 2008 | 8 | 22 | 10 | 25857.1596
2027 | 2008 | 8 | 22 | 11 | 34610.4268
2027 | 2008 | 8 | 22 | 12 | 39476.5101
2027 | 2008 | 8 | 22 | 13 | 42557.4339
2027 | 2008 | 8 | 22 | 14 | 41938.667
2027 | 2008 | 8 | 22 | 15 | 38237.7537
2027 | 2008 | 8 | 22 | 16 | 38276.8193
2027 | 2008 | 8 | 22 | 17 | 34167.6378
2027 | 2008 | 8 | 22 | 18 | 31001.2342
2027 | 2008 | 8 | 22 | 19 | 24284.9949
2027 | 2008 | 8 | 22 | 20 | 7659.078
2027 | 2008 | 8 | 22 | 21 | 0
2027 | 2008 | 8 | 22 | 22 | 0
2027 | 2008 | 8 | 22 | 23 | 0
2027 | 2008 | 8 | 22 | 24 | 0
2027 | 2008 | 8 | 23 | 1 | 0
2027 | 2008 | 8 | 23 | 2 | 0
2027 | 2008 | 8 | 23 | 3 | 0
2027 | 2008 | 8 | 23 | 4 | 0
2027 | 2008 | 8 | 23 | 5 | 0
2027 | 2008 | 8 | 23 | 6 | 0
2027 | 2008 | 8 | 23 | 7 | 0
2027 | 2008 | 8 | 23 | 8 | 2523.0186
2027 | 2008 | 8 | 23 | 9 | 19465.3215
2027 | 2008 | 8 | 23 | 10 | 34471.0596
2027 | 2008 | 8 | 23 | 11 | 37888.7989
2027 | 2008 | 8 | 23 | 12 | 40580.2659
2027 | 2008 | 8 | 23 | 13 | 39998.1895
2027 | 2008 | 8 | 23 | 14 | 39806.5579
2027 | 2008 | 8 | 23 | 15 | 37355.7225
2027 | 2008 | 8 | 23 | 16 | 35495.494
2027 | 2008 | 8 | 23 | 17 | 32207.2694
2027 | 2008 | 8 | 23 | 18 | 29251.8104
2027 | 2008 | 8 | 23 | 19 | 24245.3601
2027 | 2008 | 8 | 23 | 20 | 7141.5863
2027 | 2008 | 8 | 23 | 21 | 0
2027 | 2008 | 8 | 23 | 22 | 0
2027 | 2008 | 8 | 23 | 23 | 0
2027 | 2008 | 8 | 23 | 24 | 0
2027 | 2008 | 8 | 24 | 1 | 0
2027 | 2008 | 8 | 24 | 2 | 0
2027 | 2008 | 8 | 24 | 3 | 0
2027 | 2008 | 8 | 24 | 4 | 0
2027 | 2008 | 8 | 24 | 5 | 0
2027 | 2008 | 8 | 24 | 6 | 0
2027 | 2008 | 8 | 24 | 7 | 0
2027 | 2008 | 8 | 24 | 8 | 2349.3271
2027 | 2008 | 8 | 24 | 9 | 18803.2293
2027 | 2008 | 8 | 24 | 10 | 32807.2012
2027 | 2008 | 8 | 24 | 11 | 37383.4765
2027 | 2008 | 8 | 24 | 12 | 40281.8183
2027 | 2008 | 8 | 24 | 13 | 40742.197
2027 | 2008 | 8 | 24 | 14 | 39394.7938
2027 | 2008 | 8 | 24 | 15 | 40226.7413
2027 | 2008 | 8 | 24 | 16 | 36072.3014
2027 | 2008 | 8 | 24 | 17 | 35216.9952
2027 | 2008 | 8 | 24 | 18 | 32527.595
2027 | 2008 | 8 | 24 | 19 | 25521.2951
2027 | 2008 | 8 | 24 | 20 | 7371.0391
2027 | 2008 | 8 | 24 | 21 | 0
2027 | 2008 | 8 | 24 | 22 | 0
2027 | 2008 | 8 | 24 | 23 | 0
2027 | 2008 | 8 | 24 | 24 | 0
2027 | 2008 | 8 | 25 | 1 | 0
2027 | 2008 | 8 | 25 | 2 | 0
2027 | 2008 | 8 | 25 | 3 | 0
2027 | 2008 | 8 | 25 | 4 | 0
2027 | 2008 | 8 | 25 | 5 | 0
2027 | 2008 | 8 | 25 | 6 | 0
2027 | 2008 | 8 | 25 | 7 | 0
2027 | 2008 | 8 | 25 | 8 | 2390.383
2027 | 2008 | 8 | 25 | 9 | 21042.5592
2027 | 2008 | 8 | 25 | 10 | 36884.6285
2027 | 2008 | 8 | 25 | 11 | 42504.4104
2027 | 2008 | 8 | 25 | 12 | 44202.2572
2027 | 2008 | 8 | 25 | 13 | 44468.8078
2027 | 2008 | 8 | 25 | 14 | 43461.7909
2027 | 2008 | 8 | 25 | 15 | 41648.5135
2027 | 2008 | 8 | 25 | 16 | 40020.7111
2027 | 2008 | 8 | 25 | 17 | 39372.4544
2027 | 2008 | 8 | 25 | 18 | 35590.9218
2027 | 2008 | 8 | 25 | 19 | 27899.0552
2027 | 2008 | 8 | 25 | 20 | 7647.6798
2027 | 2008 | 8 | 25 | 21 | 0
2027 | 2008 | 8 | 25 | 22 | 0
2027 | 2008 | 8 | 25 | 23 | 0
2027 | 2008 | 8 | 25 | 24 | 0
2027 | 2008 | 8 | 26 | 1 | 0
2027 | 2008 | 8 | 26 | 2 | 0
2027 | 2008 | 8 | 26 | 3 | 0
2027 | 2008 | 8 | 26 | 4 | 0
2027 | 2008 | 8 | 26 | 5 | 0
2027 | 2008 | 8 | 26 | 6 | 0
2027 | 2008 | 8 | 26 | 7 | 0
2027 | 2008 | 8 | 26 | 8 | 3513.0902
2027 | 2008 | 8 | 26 | 9 | 22675.8812
2027 | 2008 | 8 | 26 | 10 | 37715.5774
2027 | 2008 | 8 | 26 | 11 | 42404.9727
2027 | 2008 | 8 | 26 | 12 | 44066.1532
2027 | 2008 | 8 | 26 | 13 | 44420.8634
2027 | 2008 | 8 | 26 | 14 | 41453.1429
2027 | 2008 | 8 | 26 | 15 | 40943.4623
2027 | 2008 | 8 | 26 | 16 | 40630.6951
2027 | 2008 | 8 | 26 | 17 | 39038.5832
2027 | 2008 | 8 | 26 | 18 | 35383.6833
2027 | 2008 | 8 | 26 | 19 | 27431.3362
2027 | 2008 | 8 | 26 | 20 | 6736.1036
2027 | 2008 | 8 | 26 | 21 | 0
2027 | 2008 | 8 | 26 | 22 | 0
2027 | 2008 | 8 | 26 | 23 | 0
2027 | 2008 | 8 | 26 | 24 | 0
2027 | 2008 | 8 | 27 | 1 | 0
2027 | 2008 | 8 | 27 | 2 | 0
2027 | 2008 | 8 | 27 | 3 | 0
2027 | 2008 | 8 | 27 | 4 | 0
2027 | 2008 | 8 | 27 | 5 | 0
2027 | 2008 | 8 | 27 | 6 | 0
2027 | 2008 | 8 | 27 | 7 | 0
2027 | 2008 | 8 | 27 | 8 | 2882.337
2027 | 2008 | 8 | 27 | 9 | 22876.8053
2027 | 2008 | 8 | 27 | 10 | 36854.1596
2027 | 2008 | 8 | 27 | 11 | 41720.7335
2027 | 2008 | 8 | 27 | 12 | 44355.6095
2027 | 2008 | 8 | 27 | 13 | 41631.076
2027 | 2008 | 8 | 27 | 14 | 41518.1259
2027 | 2008 | 8 | 27 | 15 | 41137.2811
2027 | 2008 | 8 | 27 | 16 | 38164.6433
2027 | 2008 | 8 | 27 | 17 | 36452.1081
2027 | 2008 | 8 | 27 | 18 | 31563.317
2027 | 2008 | 8 | 27 | 19 | 24679.1825
2027 | 2008 | 8 | 27 | 20 | 5466.3275
2027 | 2008 | 8 | 27 | 21 | 0
2027 | 2008 | 8 | 27 | 22 | 0
2027 | 2008 | 8 | 27 | 23 | 0
2027 | 2008 | 8 | 27 | 24 | 0
2027 | 2008 | 8 | 28 | 1 | 0
2027 | 2008 | 8 | 28 | 2 | 0
2027 | 2008 | 8 | 28 | 3 | 0
2027 | 2008 | 8 | 28 | 4 | 0
2027 | 2008 | 8 | 28 | 5 | 0
2027 | 2008 | 8 | 28 | 6 | 0
2027 | 2008 | 8 | 28 | 7 | 0
2027 | 2008 | 8 | 28 | 8 | 2052.4511
2027 | 2008 | 8 | 28 | 9 | 14574.3858
2027 | 2008 | 8 | 28 | 10 | 28110.7585
2027 | 2008 | 8 | 28 | 11 | 38693.5697
2027 | 2008 | 8 | 28 | 12 | 40135.807
2027 | 2008 | 8 | 28 | 13 | 41050.064
2027 | 2008 | 8 | 28 | 14 | 40350.635
2027 | 2008 | 8 | 28 | 15 | 39974.6612
2027 | 2008 | 8 | 28 | 16 | 36277.2045
2027 | 2008 | 8 | 28 | 17 | 33714.0439
2027 | 2008 | 8 | 28 | 18 | 30315.2786
2027 | 2008 | 8 | 28 | 19 | 25068.9628
2027 | 2008 | 8 | 28 | 20 | 5464.295
2027 | 2008 | 8 | 28 | 21 | 0
2027 | 2008 | 8 | 28 | 22 | 0
2027 | 2008 | 8 | 28 | 23 | 0
2027 | 2008 | 8 | 28 | 24 | 0
2027 | 2008 | 8 | 29 | 1 | 0
2027 | 2008 | 8 | 29 | 2 | 0
2027 | 2008 | 8 | 29 | 3 | 0
2027 | 2008 | 8 | 29 | 4 | 0
2027 | 2008 | 8 | 29 | 5 | 0
2027 | 2008 | 8 | 29 | 6 | 0
2027 | 2008 | 8 | 29 | 7 | 0
2027 | 2008 | 8 | 29 | 8 | 1881.7381
2027 | 2008 | 8 | 29 | 9 | 14761.9353
2027 | 2008 | 8 | 29 | 10 | 28640.6527
2027 | 2008 | 8 | 29 | 11 | 34167.0859
2027 | 2008 | 8 | 29 | 12 | 36600.7807
2027 | 2008 | 8 | 29 | 13 | 35194.7806
2027 | 2008 | 8 | 29 | 14 | 34070.2519
2027 | 2008 | 8 | 29 | 15 | 31375.5221
2027 | 2008 | 8 | 29 | 16 | 29497.0235
2027 | 2008 | 8 | 29 | 17 | 26698.4522
2027 | 2008 | 8 | 29 | 18 | 24617.3739
2027 | 2008 | 8 | 29 | 19 | 20855.4216
2027 | 2008 | 8 | 29 | 20 | 4393.5447
2027 | 2008 | 8 | 29 | 21 | 0
2027 | 2008 | 8 | 29 | 22 | 0
2027 | 2008 | 8 | 29 | 23 | 0
2027 | 2008 | 8 | 29 | 24 | 0
2027 | 2008 | 8 | 30 | 1 | 0
2027 | 2008 | 8 | 30 | 2 | 0
2027 | 2008 | 8 | 30 | 3 | 0
2027 | 2008 | 8 | 30 | 4 | 0
2027 | 2008 | 8 | 30 | 5 | 0
2027 | 2008 | 8 | 30 | 6 | 0
2027 | 2008 | 8 | 30 | 7 | 0
2027 | 2008 | 8 | 30 | 8 | 1724.9435
2027 | 2008 | 8 | 30 | 9 | 17867.6472
2027 | 2008 | 8 | 30 | 10 | 32308.8755
2027 | 2008 | 8 | 30 | 11 | 39048.8669
2027 | 2008 | 8 | 30 | 12 | 40994.2258
2027 | 2008 | 8 | 30 | 13 | 39778.3965
2027 | 2008 | 8 | 30 | 14 | 41041.0928
2027 | 2008 | 8 | 30 | 15 | 37419.7192
2027 | 2008 | 8 | 30 | 16 | 36458.4594
2027 | 2008 | 8 | 30 | 17 | 32947.7073
2027 | 2008 | 8 | 30 | 18 | 29495.4184
2027 | 2008 | 8 | 30 | 19 | 22946.8267
2027 | 2008 | 8 | 30 | 20 | 4915.4885
2027 | 2008 | 8 | 30 | 21 | 0
2027 | 2008 | 8 | 30 | 22 | 0
2027 | 2008 | 8 | 30 | 23 | 0
2027 | 2008 | 8 | 30 | 24 | 0
2027 | 2008 | 8 | 31 | 1 | 0
2027 | 2008 | 8 | 31 | 2 | 0
2027 | 2008 | 8 | 31 | 3 | 0
2027 | 2008 | 8 | 31 | 4 | 0
2027 | 2008 | 8 | 31 | 5 | 0
2027 | 2008 | 8 | 31 | 6 | 0
2027 | 2008 | 8 | 31 | 7 | 0
2027 | 2008 | 8 | 31 | 8 | 1602.4361
2027 | 2008 | 8 | 31 | 9 | 18582.4586
2027 | 2008 | 8 | 31 | 10 | 35257.3061
2027 | 2008 | 8 | 31 | 11 | 42389.5825
2027 | 2008 | 8 | 31 | 12 | 44214.6741
2027 | 2008 | 8 | 31 | 13 | 43885.4263
2027 | 2008 | 8 | 31 | 14 | 44345.9127
2027 | 2008 | 8 | 31 | 15 | 42342.7464
2027 | 2008 | 8 | 31 | 16 | 40847.5319
2027 | 2008 | 8 | 31 | 17 | 39132.165
2027 | 2008 | 8 | 31 | 18 | 34843.9047
2027 | 2008 | 8 | 31 | 19 | 22986.3866
2027 | 2008 | 8 | 31 | 20 | 4436.3893
2027 | 2008 | 8 | 31 | 21 | 0
2027 | 2008 | 8 | 31 | 22 | 0
2027 | 2008 | 8 | 31 | 23 | 0
2027 | 2008 | 8 | 31 | 24 | 0
2028 | 2008 | 8 | 1 | 1 | 0
2028 | 2008 | 8 | 1 | 2 | 0
2028 | 2008 | 8 | 1 | 3 | 0
2028 | 2008 | 8 | 1 | 4 | 0
2028 | 2008 | 8 | 1 | 5 | 0
2028 | 2008 | 8 | 1 | 6 | 0
2028 | 2008 | 8 | 1 | 7 | 2.4214
2028 | 2008 | 8 | 1 | 8 | 4593.2929
2028 | 2008 | 8 | 1 | 9 | 20172.8553
2028 | 2008 | 8 | 1 | 10 | 37152.7523
2028 | 2008 | 8 | 1 | 11 | 45734.6394
2028 | 2008 | 8 | 1 | 12 | 49231.9951
2028 | 2008 | 8 | 1 | 13 | 50742.0433
2028 | 2008 | 8 | 1 | 14 | 49478.7093
2028 | 2008 | 8 | 1 | 15 | 47467.7974
2028 | 2008 | 8 | 1 | 16 | 44725.0935
2028 | 2008 | 8 | 1 | 17 | 41320.0872
2028 | 2008 | 8 | 1 | 18 | 37699.0568
2028 | 2008 | 8 | 1 | 19 | 31009.1743
2028 | 2008 | 8 | 1 | 20 | 11089.8383
2028 | 2008 | 8 | 1 | 21 | 442.7226
2028 | 2008 | 8 | 1 | 22 | 0
2028 | 2008 | 8 | 1 | 23 | 0
2028 | 2008 | 8 | 1 | 24 | 0
2028 | 2008 | 8 | 2 | 1 | 0
2028 | 2008 | 8 | 2 | 2 | 0
2028 | 2008 | 8 | 2 | 3 | 0
2028 | 2008 | 8 | 2 | 4 | 0
2028 | 2008 | 8 | 2 | 5 | 0
2028 | 2008 | 8 | 2 | 6 | 0
2028 | 2008 | 8 | 2 | 7 | 2.0632
2028 | 2008 | 8 | 2 | 8 | 4701.0205
2028 | 2008 | 8 | 2 | 9 | 19276.009
2028 | 2008 | 8 | 2 | 10 | 37866.4696
2028 | 2008 | 8 | 2 | 11 | 48369.7898
2028 | 2008 | 8 | 2 | 12 | 51171.5819
2028 | 2008 | 8 | 2 | 13 | 49911.2615
2028 | 2008 | 8 | 2 | 14 | 51386.128
2028 | 2008 | 8 | 2 | 15 | 50477.9327
2028 | 2008 | 8 | 2 | 16 | 49943.2834
2028 | 2008 | 8 | 2 | 17 | 46119.1103
2028 | 2008 | 8 | 2 | 18 | 42540.4199
2028 | 2008 | 8 | 2 | 19 | 31954.318
2028 | 2008 | 8 | 2 | 20 | 10020.8399
2028 | 2008 | 8 | 2 | 21 | 263.9711
2028 | 2008 | 8 | 2 | 22 | 0
2028 | 2008 | 8 | 2 | 23 | 0
2028 | 2008 | 8 | 2 | 24 | 0
2028 | 2008 | 8 | 3 | 1 | 0
2028 | 2008 | 8 | 3 | 2 | 0
2028 | 2008 | 8 | 3 | 3 | 0
2028 | 2008 | 8 | 3 | 4 | 0
2028 | 2008 | 8 | 3 | 5 | 0
2028 | 2008 | 8 | 3 | 6 | 0
2028 | 2008 | 8 | 3 | 7 | 2.9932
2028 | 2008 | 8 | 3 | 8 | 4662.1819
2028 | 2008 | 8 | 3 | 9 | 22430.0778
2028 | 2008 | 8 | 3 | 10 | 39977.6146
2028 | 2008 | 8 | 3 | 11 | 49314.1097
2028 | 2008 | 8 | 3 | 12 | 52811.168
2028 | 2008 | 8 | 3 | 13 | 52195.3143
2028 | 2008 | 8 | 3 | 14 | 52709.7404
2028 | 2008 | 8 | 3 | 15 | 51134.1311
2028 | 2008 | 8 | 3 | 16 | 49712.6982
2028 | 2008 | 8 | 3 | 17 | 47872.6442
2028 | 2008 | 8 | 3 | 18 | 43555.9583
2028 | 2008 | 8 | 3 | 19 | 32811.9513
2028 | 2008 | 8 | 3 | 20 | 10792.8169
2028 | 2008 | 8 | 3 | 21 | 109.6374
2028 | 2008 | 8 | 3 | 22 | 0
2028 | 2008 | 8 | 3 | 23 | 0
2028 | 2008 | 8 | 3 | 24 | 0
2028 | 2008 | 8 | 4 | 1 | 0
2028 | 2008 | 8 | 4 | 2 | 0
2028 | 2008 | 8 | 4 | 3 | 0
2028 | 2008 | 8 | 4 | 4 | 0
2028 | 2008 | 8 | 4 | 5 | 0
2028 | 2008 | 8 | 4 | 6 | 0
2028 | 2008 | 8 | 4 | 7 | 1.9784
2028 | 2008 | 8 | 4 | 8 | 5327.4776
2028 | 2008 | 8 | 4 | 9 | 26346.4682
2028 | 2008 | 8 | 4 | 10 | 40814.9594
2028 | 2008 | 8 | 4 | 11 | 49227.6713
2028 | 2008 | 8 | 4 | 12 | 49307.6108
2028 | 2008 | 8 | 4 | 13 | 50297.1041
2028 | 2008 | 8 | 4 | 14 | 49261.3523
2028 | 2008 | 8 | 4 | 15 | 49525.2138
2028 | 2008 | 8 | 4 | 16 | 47702.1693
2028 | 2008 | 8 | 4 | 17 | 45765.4313
2028 | 2008 | 8 | 4 | 18 | 42024.1012
2028 | 2008 | 8 | 4 | 19 | 32731.7602
2028 | 2008 | 8 | 4 | 20 | 10464.2481
2028 | 2008 | 8 | 4 | 21 | 56.5471
2028 | 2008 | 8 | 4 | 22 | 0
2028 | 2008 | 8 | 4 | 23 | 0
2028 | 2008 | 8 | 4 | 24 | 0
2028 | 2008 | 8 | 5 | 1 | 0
2028 | 2008 | 8 | 5 | 2 | 0
2028 | 2008 | 8 | 5 | 3 | 0
2028 | 2008 | 8 | 5 | 4 | 0
2028 | 2008 | 8 | 5 | 5 | 0
2028 | 2008 | 8 | 5 | 6 | 0
2028 | 2008 | 8 | 5 | 7 | 0.65143
2028 | 2008 | 8 | 5 | 8 | 5963.7504
2028 | 2008 | 8 | 5 | 9 | 25148.9761
2028 | 2008 | 8 | 5 | 10 | 42095.0038
2028 | 2008 | 8 | 5 | 11 | 45097.685
2028 | 2008 | 8 | 5 | 12 | 46658.4516
2028 | 2008 | 8 | 5 | 13 | 49022.7939
2028 | 2008 | 8 | 5 | 14 | 47267.5717
2028 | 2008 | 8 | 5 | 15 | 42885.9554
2028 | 2008 | 8 | 5 | 16 | 38132.8205
2028 | 2008 | 8 | 5 | 17 | 34105.8547
2028 | 2008 | 8 | 5 | 18 | 32399.37
2028 | 2008 | 8 | 5 | 19 | 27726.8859
2028 | 2008 | 8 | 5 | 20 | 10358.9833
2028 | 2008 | 8 | 5 | 21 | 53.0187
2028 | 2008 | 8 | 5 | 22 | 0
2028 | 2008 | 8 | 5 | 23 | 0
2028 | 2008 | 8 | 5 | 24 | 0
2028 | 2008 | 8 | 6 | 1 | 0
2028 | 2008 | 8 | 6 | 2 | 0
2028 | 2008 | 8 | 6 | 3 | 0
2028 | 2008 | 8 | 6 | 4 | 0
2028 | 2008 | 8 | 6 | 5 | 0
2028 | 2008 | 8 | 6 | 6 | 0
2028 | 2008 | 8 | 6 | 7 | 0.044932
2028 | 2008 | 8 | 6 | 8 | 3249.5213
2028 | 2008 | 8 | 6 | 9 | 18616.0886
2028 | 2008 | 8 | 6 | 10 | 34687.0279
2028 | 2008 | 8 | 6 | 11 | 38527.5051
2028 | 2008 | 8 | 6 | 12 | 42648.8757
2028 | 2008 | 8 | 6 | 13 | 42287.154
2028 | 2008 | 8 | 6 | 14 | 41737.9176
2028 | 2008 | 8 | 6 | 15 | 40921.1246
2028 | 2008 | 8 | 6 | 16 | 37689.3304
2028 | 2008 | 8 | 6 | 17 | 34016.0937
2028 | 2008 | 8 | 6 | 18 | 32609.1041
2028 | 2008 | 8 | 6 | 19 | 27192.7362
2028 | 2008 | 8 | 6 | 20 | 9693.2689
2028 | 2008 | 8 | 6 | 21 | 38.8185
2028 | 2008 | 8 | 6 | 22 | 0
2028 | 2008 | 8 | 6 | 23 | 0
2028 | 2008 | 8 | 6 | 24 | 0
2028 | 2008 | 8 | 7 | 1 | 0
2028 | 2008 | 8 | 7 | 2 | 0
2028 | 2008 | 8 | 7 | 3 | 0
2028 | 2008 | 8 | 7 | 4 | 0
2028 | 2008 | 8 | 7 | 5 | 0
2028 | 2008 | 8 | 7 | 6 | 0
2028 | 2008 | 8 | 7 | 7 | 0.20704
2028 | 2008 | 8 | 7 | 8 | 3208.7435
2028 | 2008 | 8 | 7 | 9 | 16646.9645
2028 | 2008 | 8 | 7 | 10 | 31591.0957
2028 | 2008 | 8 | 7 | 11 | 42719.0357
2028 | 2008 | 8 | 7 | 12 | 48197.7727
2028 | 2008 | 8 | 7 | 13 | 49195.6623
2028 | 2008 | 8 | 7 | 14 | 48413.6347
2028 | 2008 | 8 | 7 | 15 | 47482.4846
2028 | 2008 | 8 | 7 | 16 | 46328.8456
2028 | 2008 | 8 | 7 | 17 | 44505.6261
2028 | 2008 | 8 | 7 | 18 | 39046.0336
2028 | 2008 | 8 | 7 | 19 | 30301.8329
2028 | 2008 | 8 | 7 | 20 | 9739.367
2028 | 2008 | 8 | 7 | 21 | 33.2623
2028 | 2008 | 8 | 7 | 22 | 0
2028 | 2008 | 8 | 7 | 23 | 0
2028 | 2008 | 8 | 7 | 24 | 0
2028 | 2008 | 8 | 8 | 1 | 0
2028 | 2008 | 8 | 8 | 2 | 0
2028 | 2008 | 8 | 8 | 3 | 0
2028 | 2008 | 8 | 8 | 4 | 0
2028 | 2008 | 8 | 8 | 5 | 0
2028 | 2008 | 8 | 8 | 6 | 0
2028 | 2008 | 8 | 8 | 7 | 0.0076014
2028 | 2008 | 8 | 8 | 8 | 3462.3007
2028 | 2008 | 8 | 8 | 9 | 21774.2102
2028 | 2008 | 8 | 8 | 10 | 39166.2577
2028 | 2008 | 8 | 8 | 11 | 45600.8228
2028 | 2008 | 8 | 8 | 12 | 45722.5084
2028 | 2008 | 8 | 8 | 13 | 48732.8762
2028 | 2008 | 8 | 8 | 14 | 49125.7511
2028 | 2008 | 8 | 8 | 15 | 47774.3664
2028 | 2008 | 8 | 8 | 16 | 46204.7804
2028 | 2008 | 8 | 8 | 17 | 42049.2506
2028 | 2008 | 8 | 8 | 18 | 38008.7917
2028 | 2008 | 8 | 8 | 19 | 30557.3463
2028 | 2008 | 8 | 8 | 20 | 10453.9138
2028 | 2008 | 8 | 8 | 21 | 26.1682
2028 | 2008 | 8 | 8 | 22 | 0
2028 | 2008 | 8 | 8 | 23 | 0
2028 | 2008 | 8 | 8 | 24 | 0
2028 | 2008 | 8 | 9 | 1 | 0
2028 | 2008 | 8 | 9 | 2 | 0
2028 | 2008 | 8 | 9 | 3 | 0
2028 | 2008 | 8 | 9 | 4 | 0
2028 | 2008 | 8 | 9 | 5 | 0
2028 | 2008 | 8 | 9 | 6 | 0
2028 | 2008 | 8 | 9 | 7 | 0.045975
2028 | 2008 | 8 | 9 | 8 | 3058.539
2028 | 2008 | 8 | 9 | 9 | 20833.5184
2028 | 2008 | 8 | 9 | 10 | 37124.8784
2028 | 2008 | 8 | 9 | 11 | 43369.6032
2028 | 2008 | 8 | 9 | 12 | 45881.0843
2028 | 2008 | 8 | 9 | 13 | 45935.2633
2028 | 2008 | 8 | 9 | 14 | 44020.6288
2028 | 2008 | 8 | 9 | 15 | 40903.347
2028 | 2008 | 8 | 9 | 16 | 37790.6045
2028 | 2008 | 8 | 9 | 17 | 36970.065
2028 | 2008 | 8 | 9 | 18 | 35374.779
2028 | 2008 | 8 | 9 | 19 | 29784.1027
2028 | 2008 | 8 | 9 | 20 | 9945.0122
2028 | 2008 | 8 | 9 | 21 | 0
2028 | 2008 | 8 | 9 | 22 | 0
2028 | 2008 | 8 | 9 | 23 | 0
2028 | 2008 | 8 | 9 | 24 | 0
2028 | 2008 | 8 | 10 | 1 | 0
2028 | 2008 | 8 | 10 | 2 | 0
2028 | 2008 | 8 | 10 | 3 | 0
2028 | 2008 | 8 | 10 | 4 | 0
2028 | 2008 | 8 | 10 | 5 | 0
2028 | 2008 | 8 | 10 | 6 | 0
2028 | 2008 | 8 | 10 | 7 | 0.3285
2028 | 2008 | 8 | 10 | 8 | 2651.4921
2028 | 2008 | 8 | 10 | 9 | 19135.8915
2028 | 2008 | 8 | 10 | 10 | 37921.098
2028 | 2008 | 8 | 10 | 11 | 44724.3629
2028 | 2008 | 8 | 10 | 12 | 48058.3357
2028 | 2008 | 8 | 10 | 13 | 50109.9253
2028 | 2008 | 8 | 10 | 14 | 49256.6824
2028 | 2008 | 8 | 10 | 15 | 48674.5498
2028 | 2008 | 8 | 10 | 16 | 46632.2381
2028 | 2008 | 8 | 10 | 17 | 42740.3274
2028 | 2008 | 8 | 10 | 18 | 36556.3815
2028 | 2008 | 8 | 10 | 19 | 28911.8939
2028 | 2008 | 8 | 10 | 20 | 8915.6162
2028 | 2008 | 8 | 10 | 21 | 0
2028 | 2008 | 8 | 10 | 22 | 0
2028 | 2008 | 8 | 10 | 23 | 0
2028 | 2008 | 8 | 10 | 24 | 0
2028 | 2008 | 8 | 11 | 1 | 0
2028 | 2008 | 8 | 11 | 2 | 0
2028 | 2008 | 8 | 11 | 3 | 0
2028 | 2008 | 8 | 11 | 4 | 0
2028 | 2008 | 8 | 11 | 5 | 0
2028 | 2008 | 8 | 11 | 6 | 0
2028 | 2008 | 8 | 11 | 7 | 0
2028 | 2008 | 8 | 11 | 8 | 1960.4071
2028 | 2008 | 8 | 11 | 9 | 15164.5014
2028 | 2008 | 8 | 11 | 10 | 28264.2825
2028 | 2008 | 8 | 11 | 11 | 38941.5952
2028 | 2008 | 8 | 11 | 12 | 43950.1646
2028 | 2008 | 8 | 11 | 13 | 42845.461
2028 | 2008 | 8 | 11 | 14 | 42169.065
2028 | 2008 | 8 | 11 | 15 | 40475.2059
2028 | 2008 | 8 | 11 | 16 | 38615.0648
2028 | 2008 | 8 | 11 | 17 | 34444.6795
2028 | 2008 | 8 | 11 | 18 | 32250.7534
2028 | 2008 | 8 | 11 | 19 | 27001.2142
2028 | 2008 | 8 | 11 | 20 | 8978.3
2028 | 2008 | 8 | 11 | 21 | 0
2028 | 2008 | 8 | 11 | 22 | 0
2028 | 2008 | 8 | 11 | 23 | 0
2028 | 2008 | 8 | 11 | 24 | 0
2028 | 2008 | 8 | 12 | 1 | 0
2028 | 2008 | 8 | 12 | 2 | 0
2028 | 2008 | 8 | 12 | 3 | 0
2028 | 2008 | 8 | 12 | 4 | 0
2028 | 2008 | 8 | 12 | 5 | 0
2028 | 2008 | 8 | 12 | 6 | 0
2028 | 2008 | 8 | 12 | 7 | 0.0022535
2028 | 2008 | 8 | 12 | 8 | 956.0146
2028 | 2008 | 8 | 12 | 9 | 9250.7309
2028 | 2008 | 8 | 12 | 10 | 24543.4264
2028 | 2008 | 8 | 12 | 11 | 36079.5868
2028 | 2008 | 8 | 12 | 12 | 43768.6152
2028 | 2008 | 8 | 12 | 13 | 46540.736
2028 | 2008 | 8 | 12 | 14 | 47340.5075
2028 | 2008 | 8 | 12 | 15 | 45282.9306
2028 | 2008 | 8 | 12 | 16 | 43708.7177
2028 | 2008 | 8 | 12 | 17 | 40622.6877
2028 | 2008 | 8 | 12 | 18 | 37407.779
2028 | 2008 | 8 | 12 | 19 | 29755.922
2028 | 2008 | 8 | 12 | 20 | 9710.7386
2028 | 2008 | 8 | 12 | 21 | 0
2028 | 2008 | 8 | 12 | 22 | 0
2028 | 2008 | 8 | 12 | 23 | 0
2028 | 2008 | 8 | 12 | 24 | 0
2028 | 2008 | 8 | 13 | 1 | 0
2028 | 2008 | 8 | 13 | 2 | 0
2028 | 2008 | 8 | 13 | 3 | 0
2028 | 2008 | 8 | 13 | 4 | 0
2028 | 2008 | 8 | 13 | 5 | 0
2028 | 2008 | 8 | 13 | 6 | 0
2028 | 2008 | 8 | 13 | 7 | 0.064221
2028 | 2008 | 8 | 13 | 8 | 4889.6422
2028 | 2008 | 8 | 13 | 9 | 23150.3837
2028 | 2008 | 8 | 13 | 10 | 41428.333
2028 | 2008 | 8 | 13 | 11 | 46693.4734
2028 | 2008 | 8 | 13 | 12 | 49711.877
2028 | 2008 | 8 | 13 | 13 | 47143.9335
2028 | 2008 | 8 | 13 | 14 | 48102.0382
2028 | 2008 | 8 | 13 | 15 | 46572.3435
2028 | 2008 | 8 | 13 | 16 | 46368.1891
2028 | 2008 | 8 | 13 | 17 | 44030.6842
2028 | 2008 | 8 | 13 | 18 | 40094.6518
2028 | 2008 | 8 | 13 | 19 | 29956.2192
2028 | 2008 | 8 | 13 | 20 | 10328.7463
2028 | 2008 | 8 | 13 | 21 | 0
2028 | 2008 | 8 | 13 | 22 | 0
2028 | 2008 | 8 | 13 | 23 | 0
2028 | 2008 | 8 | 13 | 24 | 0
2028 | 2008 | 8 | 14 | 1 | 0
2028 | 2008 | 8 | 14 | 2 | 0
2028 | 2008 | 8 | 14 | 3 | 0
2028 | 2008 | 8 | 14 | 4 | 0
2028 | 2008 | 8 | 14 | 5 | 0
2028 | 2008 | 8 | 14 | 6 | 0
2028 | 2008 | 8 | 14 | 7 | 0.0029843
2028 | 2008 | 8 | 14 | 8 | 3092.9283
2028 | 2008 | 8 | 14 | 9 | 21572.6899
2028 | 2008 | 8 | 14 | 10 | 37562.2053
2028 | 2008 | 8 | 14 | 11 | 45155.4852
2028 | 2008 | 8 | 14 | 12 | 46479.4875
2028 | 2008 | 8 | 14 | 13 | 49341.2565
2028 | 2008 | 8 | 14 | 14 | 48591.178
2028 | 2008 | 8 | 14 | 15 | 47420.3354
2028 | 2008 | 8 | 14 | 16 | 44832.0893
2028 | 2008 | 8 | 14 | 17 | 43739.4732
2028 | 2008 | 8 | 14 | 18 | 40913.8099
2028 | 2008 | 8 | 14 | 19 | 31467.6549
2028 | 2008 | 8 | 14 | 20 | 11177.5599
2028 | 2008 | 8 | 14 | 21 | 0
2028 | 2008 | 8 | 14 | 22 | 0
2028 | 2008 | 8 | 14 | 23 | 0
2028 | 2008 | 8 | 14 | 24 | 0
2028 | 2008 | 8 | 15 | 1 | 0
2028 | 2008 | 8 | 15 | 2 | 0
2028 | 2008 | 8 | 15 | 3 | 0
2028 | 2008 | 8 | 15 | 4 | 0
2028 | 2008 | 8 | 15 | 5 | 0
2028 | 2008 | 8 | 15 | 6 | 0
2028 | 2008 | 8 | 15 | 7 | 0.018889
2028 | 2008 | 8 | 15 | 8 | 2038.3417
2028 | 2008 | 8 | 15 | 9 | 19489.7554
2028 | 2008 | 8 | 15 | 10 | 32134.385
2028 | 2008 | 8 | 15 | 11 | 42177.0097
2028 | 2008 | 8 | 15 | 12 | 47697.709
2028 | 2008 | 8 | 15 | 13 | 49214.4313
2028 | 2008 | 8 | 15 | 14 | 46843.9854
2028 | 2008 | 8 | 15 | 15 | 46846.5631
2028 | 2008 | 8 | 15 | 16 | 46586.062
2028 | 2008 | 8 | 15 | 17 | 44826.6048
2028 | 2008 | 8 | 15 | 18 | 39970.7428
2028 | 2008 | 8 | 15 | 19 | 31464.9378
2028 | 2008 | 8 | 15 | 20 | 9187.6722
2028 | 2008 | 8 | 15 | 21 | 0
2028 | 2008 | 8 | 15 | 22 | 0
2028 | 2008 | 8 | 15 | 23 | 0
2028 | 2008 | 8 | 15 | 24 | 0
2028 | 2008 | 8 | 16 | 1 | 0
2028 | 2008 | 8 | 16 | 2 | 0
2028 | 2008 | 8 | 16 | 3 | 0
2028 | 2008 | 8 | 16 | 4 | 0
2028 | 2008 | 8 | 16 | 5 | 0
2028 | 2008 | 8 | 16 | 6 | 0
2028 | 2008 | 8 | 16 | 7 | 0
2028 | 2008 | 8 | 16 | 8 | 1967.0067
2028 | 2008 | 8 | 16 | 9 | 14037.7771
2028 | 2008 | 8 | 16 | 10 | 29496.4308
2028 | 2008 | 8 | 16 | 11 | 36529.4562
2028 | 2008 | 8 | 16 | 12 | 37817.9818
2028 | 2008 | 8 | 16 | 13 | 38917.7304
2028 | 2008 | 8 | 16 | 14 | 38357.1741
2028 | 2008 | 8 | 16 | 15 | 36992.2336
2028 | 2008 | 8 | 16 | 16 | 34652.5037
2028 | 2008 | 8 | 16 | 17 | 34978.1216
2028 | 2008 | 8 | 16 | 18 | 33220.6666
2028 | 2008 | 8 | 16 | 19 | 28059.8442
2028 | 2008 | 8 | 16 | 20 | 9641.1487
2028 | 2008 | 8 | 16 | 21 | 0
2028 | 2008 | 8 | 16 | 22 | 0
2028 | 2008 | 8 | 16 | 23 | 0
2028 | 2008 | 8 | 16 | 24 | 0
2028 | 2008 | 8 | 17 | 1 | 0
2028 | 2008 | 8 | 17 | 2 | 0
2028 | 2008 | 8 | 17 | 3 | 0
2028 | 2008 | 8 | 17 | 4 | 0
2028 | 2008 | 8 | 17 | 5 | 0
2028 | 2008 | 8 | 17 | 6 | 0
2028 | 2008 | 8 | 17 | 7 | 0
2028 | 2008 | 8 | 17 | 8 | 1398.3763
2028 | 2008 | 8 | 17 | 9 | 13713.8053
2028 | 2008 | 8 | 17 | 10 | 28939.0589
2028 | 2008 | 8 | 17 | 11 | 35138.7765
2028 | 2008 | 8 | 17 | 12 | 37750.7274
2028 | 2008 | 8 | 17 | 13 | 38247.8503
2028 | 2008 | 8 | 17 | 14 | 36106.0016
2028 | 2008 | 8 | 17 | 15 | 34269.0068
2028 | 2008 | 8 | 17 | 16 | 31123.0394
2028 | 2008 | 8 | 17 | 17 | 29453.7574
2028 | 2008 | 8 | 17 | 18 | 27285.1397
2028 | 2008 | 8 | 17 | 19 | 24739.6386
2028 | 2008 | 8 | 17 | 20 | 8464.1804
2028 | 2008 | 8 | 17 | 21 | 0
2028 | 2008 | 8 | 17 | 22 | 0
2028 | 2008 | 8 | 17 | 23 | 0
2028 | 2008 | 8 | 17 | 24 | 0
2028 | 2008 | 8 | 18 | 1 | 0
2028 | 2008 | 8 | 18 | 2 | 0
2028 | 2008 | 8 | 18 | 3 | 0
2028 | 2008 | 8 | 18 | 4 | 0
2028 | 2008 | 8 | 18 | 5 | 0
2028 | 2008 | 8 | 18 | 6 | 0
2028 | 2008 | 8 | 18 | 7 | 0
2028 | 2008 | 8 | 18 | 8 | 1058.1542
2028 | 2008 | 8 | 18 | 9 | 11553.3677
2028 | 2008 | 8 | 18 | 10 | 22572.9705
2028 | 2008 | 8 | 18 | 11 | 30704.6963
2028 | 2008 | 8 | 18 | 12 | 36386.0948
2028 | 2008 | 8 | 18 | 13 | 38620.7937
2028 | 2008 | 8 | 18 | 14 | 38335.6437
2028 | 2008 | 8 | 18 | 15 | 35351.851
2028 | 2008 | 8 | 18 | 16 | 31758.8332
2028 | 2008 | 8 | 18 | 17 | 28577.7316
2028 | 2008 | 8 | 18 | 18 | 27902.5462
2028 | 2008 | 8 | 18 | 19 | 23944.8415
2028 | 2008 | 8 | 18 | 20 | 8306.7572
2028 | 2008 | 8 | 18 | 21 | 0
2028 | 2008 | 8 | 18 | 22 | 0
2028 | 2008 | 8 | 18 | 23 | 0
2028 | 2008 | 8 | 18 | 24 | 0
2028 | 2008 | 8 | 19 | 1 | 0
2028 | 2008 | 8 | 19 | 2 | 0
2028 | 2008 | 8 | 19 | 3 | 0
2028 | 2008 | 8 | 19 | 4 | 0
2028 | 2008 | 8 | 19 | 5 | 0
2028 | 2008 | 8 | 19 | 6 | 0
2028 | 2008 | 8 | 19 | 7 | 0
2028 | 2008 | 8 | 19 | 8 | 1200.2126
2028 | 2008 | 8 | 19 | 9 | 12170.1755
2028 | 2008 | 8 | 19 | 10 | 25964.3305
2028 | 2008 | 8 | 19 | 11 | 33785.0622
2028 | 2008 | 8 | 19 | 12 | 38669.6138
2028 | 2008 | 8 | 19 | 13 | 39826.412
2028 | 2008 | 8 | 19 | 14 | 39776.5898
2028 | 2008 | 8 | 19 | 15 | 38331.1618
2028 | 2008 | 8 | 19 | 16 | 36329.6147
2028 | 2008 | 8 | 19 | 17 | 33520.2982
2028 | 2008 | 8 | 19 | 18 | 31695.3479
2028 | 2008 | 8 | 19 | 19 | 27134.4586
2028 | 2008 | 8 | 19 | 20 | 9402.3841
2028 | 2008 | 8 | 19 | 21 | 0
2028 | 2008 | 8 | 19 | 22 | 0
2028 | 2008 | 8 | 19 | 23 | 0
2028 | 2008 | 8 | 19 | 24 | 0
2028 | 2008 | 8 | 20 | 1 | 0
2028 | 2008 | 8 | 20 | 2 | 0
2028 | 2008 | 8 | 20 | 3 | 0
2028 | 2008 | 8 | 20 | 4 | 0
2028 | 2008 | 8 | 20 | 5 | 0
2028 | 2008 | 8 | 20 | 6 | 0
2028 | 2008 | 8 | 20 | 7 | 0
2028 | 2008 | 8 | 20 | 8 | 927.4171
2028 | 2008 | 8 | 20 | 9 | 12855.9281
2028 | 2008 | 8 | 20 | 10 | 28455.9458
2028 | 2008 | 8 | 20 | 11 | 37482.6835
2028 | 2008 | 8 | 20 | 12 | 43361.6159
2028 | 2008 | 8 | 20 | 13 | 42815.0251
2028 | 2008 | 8 | 20 | 14 | 42172.672
2028 | 2008 | 8 | 20 | 15 | 41400.2853
2028 | 2008 | 8 | 20 | 16 | 41470.5497
2028 | 2008 | 8 | 20 | 17 | 38876.5693
2028 | 2008 | 8 | 20 | 18 | 37421.7126
2028 | 2008 | 8 | 20 | 19 | 28738.7504
2028 | 2008 | 8 | 20 | 20 | 9296.1451
2028 | 2008 | 8 | 20 | 21 | 0
2028 | 2008 | 8 | 20 | 22 | 0
2028 | 2008 | 8 | 20 | 23 | 0
2028 | 2008 | 8 | 20 | 24 | 0
2028 | 2008 | 8 | 21 | 1 | 0
2028 | 2008 | 8 | 21 | 2 | 0
2028 | 2008 | 8 | 21 | 3 | 0
2028 | 2008 | 8 | 21 | 4 | 0
2028 | 2008 | 8 | 21 | 5 | 0
2028 | 2008 | 8 | 21 | 6 | 0
2028 | 2008 | 8 | 21 | 7 | 0
2028 | 2008 | 8 | 21 | 8 | 1001.2353
2028 | 2008 | 8 | 21 | 9 | 15085.7855
2028 | 2008 | 8 | 21 | 10 | 33076.7509
2028 | 2008 | 8 | 21 | 11 | 37376.813
2028 | 2008 | 8 | 21 | 12 | 43414.3926
2028 | 2008 | 8 | 21 | 13 | 45077.4019
2028 | 2008 | 8 | 21 | 14 | 44479.4006
2028 | 2008 | 8 | 21 | 15 | 42194.4741
2028 | 2008 | 8 | 21 | 16 | 43253.3439
2028 | 2008 | 8 | 21 | 17 | 41653.2184
2028 | 2008 | 8 | 21 | 18 | 34548.5164
2028 | 2008 | 8 | 21 | 19 | 29262.2134
2028 | 2008 | 8 | 21 | 20 | 9066.6987
2028 | 2008 | 8 | 21 | 21 | 0
2028 | 2008 | 8 | 21 | 22 | 0
2028 | 2008 | 8 | 21 | 23 | 0
2028 | 2008 | 8 | 21 | 24 | 0
2028 | 2008 | 8 | 22 | 1 | 0
2028 | 2008 | 8 | 22 | 2 | 0
2028 | 2008 | 8 | 22 | 3 | 0
2028 | 2008 | 8 | 22 | 4 | 0
2028 | 2008 | 8 | 22 | 5 | 0
2028 | 2008 | 8 | 22 | 6 | 0
2028 | 2008 | 8 | 22 | 7 | 0
2028 | 2008 | 8 | 22 | 8 | 1458.2658
2028 | 2008 | 8 | 22 | 9 | 15618.0262
2028 | 2008 | 8 | 22 | 10 | 28678.8086
2028 | 2008 | 8 | 22 | 11 | 38299.4686
2028 | 2008 | 8 | 22 | 12 | 43479.4042
2028 | 2008 | 8 | 22 | 13 | 46683.8451
2028 | 2008 | 8 | 22 | 14 | 45783.3968
2028 | 2008 | 8 | 22 | 15 | 41573.1217
2028 | 2008 | 8 | 22 | 16 | 41596.0498
2028 | 2008 | 8 | 22 | 17 | 37393.9926
2028 | 2008 | 8 | 22 | 18 | 33912.1599
2028 | 2008 | 8 | 22 | 19 | 26445.8731
2028 | 2008 | 8 | 22 | 20 | 8244.8841
2028 | 2008 | 8 | 22 | 21 | 0
2028 | 2008 | 8 | 22 | 22 | 0
2028 | 2008 | 8 | 22 | 23 | 0
2028 | 2008 | 8 | 22 | 24 | 0
2028 | 2008 | 8 | 23 | 1 | 0
2028 | 2008 | 8 | 23 | 2 | 0
2028 | 2008 | 8 | 23 | 3 | 0
2028 | 2008 | 8 | 23 | 4 | 0
2028 | 2008 | 8 | 23 | 5 | 0
2028 | 2008 | 8 | 23 | 6 | 0
2028 | 2008 | 8 | 23 | 7 | 0
2028 | 2008 | 8 | 23 | 8 | 2620.2674
2028 | 2008 | 8 | 23 | 9 | 21017.6876
2028 | 2008 | 8 | 23 | 10 | 37689.8793
2028 | 2008 | 8 | 23 | 11 | 41271.8276
2028 | 2008 | 8 | 23 | 12 | 44462.7407
2028 | 2008 | 8 | 23 | 13 | 43747.9507
2028 | 2008 | 8 | 23 | 14 | 43443.8493
2028 | 2008 | 8 | 23 | 15 | 40629.2561
2028 | 2008 | 8 | 23 | 16 | 38668.95
2028 | 2008 | 8 | 23 | 17 | 35430.5873
2028 | 2008 | 8 | 23 | 18 | 32351.4586
2028 | 2008 | 8 | 23 | 19 | 26555.2099
2028 | 2008 | 8 | 23 | 20 | 7762.3483
2028 | 2008 | 8 | 23 | 21 | 0
2028 | 2008 | 8 | 23 | 22 | 0
2028 | 2008 | 8 | 23 | 23 | 0
2028 | 2008 | 8 | 23 | 24 | 0
2028 | 2008 | 8 | 24 | 1 | 0
2028 | 2008 | 8 | 24 | 2 | 0
2028 | 2008 | 8 | 24 | 3 | 0
2028 | 2008 | 8 | 24 | 4 | 0
2028 | 2008 | 8 | 24 | 5 | 0
2028 | 2008 | 8 | 24 | 6 | 0
2028 | 2008 | 8 | 24 | 7 | 0
2028 | 2008 | 8 | 24 | 8 | 2489.8461
2028 | 2008 | 8 | 24 | 9 | 20377.8053
2028 | 2008 | 8 | 24 | 10 | 35475.6474
2028 | 2008 | 8 | 24 | 11 | 40408.827
2028 | 2008 | 8 | 24 | 12 | 43636.9322
2028 | 2008 | 8 | 24 | 13 | 43926.8317
2028 | 2008 | 8 | 24 | 14 | 42640.1655
2028 | 2008 | 8 | 24 | 15 | 43617.3866
2028 | 2008 | 8 | 24 | 16 | 39539.1381
2028 | 2008 | 8 | 24 | 17 | 38464.3817
2028 | 2008 | 8 | 24 | 18 | 35339.9166
2028 | 2008 | 8 | 24 | 19 | 27693.0745
2028 | 2008 | 8 | 24 | 20 | 7980.5465
2028 | 2008 | 8 | 24 | 21 | 0
2028 | 2008 | 8 | 24 | 22 | 0
2028 | 2008 | 8 | 24 | 23 | 0
2028 | 2008 | 8 | 24 | 24 | 0
2028 | 2008 | 8 | 25 | 1 | 0
2028 | 2008 | 8 | 25 | 2 | 0
2028 | 2008 | 8 | 25 | 3 | 0
2028 | 2008 | 8 | 25 | 4 | 0
2028 | 2008 | 8 | 25 | 5 | 0
2028 | 2008 | 8 | 25 | 6 | 0
2028 | 2008 | 8 | 25 | 7 | 0
2028 | 2008 | 8 | 25 | 8 | 2546.4314
2028 | 2008 | 8 | 25 | 9 | 23070.9202
2028 | 2008 | 8 | 25 | 10 | 40382.0673
2028 | 2008 | 8 | 25 | 11 | 46437.6165
2028 | 2008 | 8 | 25 | 12 | 48197.2288
2028 | 2008 | 8 | 25 | 13 | 48566.9389
2028 | 2008 | 8 | 25 | 14 | 47477.3409
2028 | 2008 | 8 | 25 | 15 | 45317.8497
2028 | 2008 | 8 | 25 | 16 | 43914.2726
2028 | 2008 | 8 | 25 | 17 | 43101.5297
2028 | 2008 | 8 | 25 | 18 | 38999.3805
2028 | 2008 | 8 | 25 | 19 | 30584.5412
2028 | 2008 | 8 | 25 | 20 | 8309.0871
2028 | 2008 | 8 | 25 | 21 | 0
2028 | 2008 | 8 | 25 | 22 | 0
2028 | 2008 | 8 | 25 | 23 | 0
2028 | 2008 | 8 | 25 | 24 | 0
2028 | 2008 | 8 | 26 | 1 | 0
2028 | 2008 | 8 | 26 | 2 | 0
2028 | 2008 | 8 | 26 | 3 | 0
2028 | 2008 | 8 | 26 | 4 | 0
2028 | 2008 | 8 | 26 | 5 | 0
2028 | 2008 | 8 | 26 | 6 | 0
2028 | 2008 | 8 | 26 | 7 | 0
2028 | 2008 | 8 | 26 | 8 | 3737.4849
2028 | 2008 | 8 | 26 | 9 | 24659.7546
2028 | 2008 | 8 | 26 | 10 | 41227.6179
2028 | 2008 | 8 | 26 | 11 | 46500.7446
2028 | 2008 | 8 | 26 | 12 | 48235.7008
2028 | 2008 | 8 | 26 | 13 | 48657.3197
2028 | 2008 | 8 | 26 | 14 | 45547.2959
2028 | 2008 | 8 | 26 | 15 | 45096.4167
2028 | 2008 | 8 | 26 | 16 | 44600.8316
2028 | 2008 | 8 | 26 | 17 | 42276.8772
2028 | 2008 | 8 | 26 | 18 | 38173.0541
2028 | 2008 | 8 | 26 | 19 | 29872.6535
2028 | 2008 | 8 | 26 | 20 | 7228.4188
2028 | 2008 | 8 | 26 | 21 | 0
2028 | 2008 | 8 | 26 | 22 | 0
2028 | 2008 | 8 | 26 | 23 | 0
2028 | 2008 | 8 | 26 | 24 | 0
2028 | 2008 | 8 | 27 | 1 | 0
2028 | 2008 | 8 | 27 | 2 | 0
2028 | 2008 | 8 | 27 | 3 | 0
2028 | 2008 | 8 | 27 | 4 | 0
2028 | 2008 | 8 | 27 | 5 | 0
2028 | 2008 | 8 | 27 | 6 | 0
2028 | 2008 | 8 | 27 | 7 | 0
2028 | 2008 | 8 | 27 | 8 | 3044.2127
2028 | 2008 | 8 | 27 | 9 | 24894.4417
2028 | 2008 | 8 | 27 | 10 | 40240.1326
2028 | 2008 | 8 | 27 | 11 | 45656.3395
2028 | 2008 | 8 | 27 | 12 | 48573.2531
2028 | 2008 | 8 | 27 | 13 | 45760.5218
2028 | 2008 | 8 | 27 | 14 | 45696.2101
2028 | 2008 | 8 | 27 | 15 | 45095.4181
2028 | 2008 | 8 | 27 | 16 | 41677.9884
2028 | 2008 | 8 | 27 | 17 | 40355.437
2028 | 2008 | 8 | 27 | 18 | 34999.7221
2028 | 2008 | 8 | 27 | 19 | 27139.6183
2028 | 2008 | 8 | 27 | 20 | 6026.477
2028 | 2008 | 8 | 27 | 21 | 0
2028 | 2008 | 8 | 27 | 22 | 0
2028 | 2008 | 8 | 27 | 23 | 0
2028 | 2008 | 8 | 27 | 24 | 0
2028 | 2008 | 8 | 28 | 1 | 0
2028 | 2008 | 8 | 28 | 2 | 0
2028 | 2008 | 8 | 28 | 3 | 0
2028 | 2008 | 8 | 28 | 4 | 0
2028 | 2008 | 8 | 28 | 5 | 0
2028 | 2008 | 8 | 28 | 6 | 0
2028 | 2008 | 8 | 28 | 7 | 0
2028 | 2008 | 8 | 28 | 8 | 2204.7305
2028 | 2008 | 8 | 28 | 9 | 16132.4152
2028 | 2008 | 8 | 28 | 10 | 30590.4715
2028 | 2008 | 8 | 28 | 11 | 42426.1513
2028 | 2008 | 8 | 28 | 12 | 43596.4383
2028 | 2008 | 8 | 28 | 13 | 45037.3998
2028 | 2008 | 8 | 28 | 14 | 44152.7948
2028 | 2008 | 8 | 28 | 15 | 43447.0934
2028 | 2008 | 8 | 28 | 16 | 39722.1122
2028 | 2008 | 8 | 28 | 17 | 36497.5093
2028 | 2008 | 8 | 28 | 18 | 33139.2362
2028 | 2008 | 8 | 28 | 19 | 27420.6023
2028 | 2008 | 8 | 28 | 20 | 6038.8996
2028 | 2008 | 8 | 28 | 21 | 0
2028 | 2008 | 8 | 28 | 22 | 0
2028 | 2008 | 8 | 28 | 23 | 0
2028 | 2008 | 8 | 28 | 24 | 0
2028 | 2008 | 8 | 29 | 1 | 0
2028 | 2008 | 8 | 29 | 2 | 0
2028 | 2008 | 8 | 29 | 3 | 0
2028 | 2008 | 8 | 29 | 4 | 0
2028 | 2008 | 8 | 29 | 5 | 0
2028 | 2008 | 8 | 29 | 6 | 0
2028 | 2008 | 8 | 29 | 7 | 0
2028 | 2008 | 8 | 29 | 8 | 1935.8103
2028 | 2008 | 8 | 29 | 9 | 15945.5523
2028 | 2008 | 8 | 29 | 10 | 31195.2763
2028 | 2008 | 8 | 29 | 11 | 37193.859
2028 | 2008 | 8 | 29 | 12 | 39977.4787
2028 | 2008 | 8 | 29 | 13 | 38333.2106
2028 | 2008 | 8 | 29 | 14 | 37454.6548
2028 | 2008 | 8 | 29 | 15 | 34379.9828
2028 | 2008 | 8 | 29 | 16 | 32208.935
2028 | 2008 | 8 | 29 | 17 | 28714.8304
2028 | 2008 | 8 | 29 | 18 | 26406.9117
2028 | 2008 | 8 | 29 | 19 | 22548.2026
2028 | 2008 | 8 | 29 | 20 | 4807.4678
2028 | 2008 | 8 | 29 | 21 | 0
2028 | 2008 | 8 | 29 | 22 | 0
2028 | 2008 | 8 | 29 | 23 | 0
2028 | 2008 | 8 | 29 | 24 | 0
2028 | 2008 | 8 | 30 | 1 | 0
2028 | 2008 | 8 | 30 | 2 | 0
2028 | 2008 | 8 | 30 | 3 | 0
2028 | 2008 | 8 | 30 | 4 | 0
2028 | 2008 | 8 | 30 | 5 | 0
2028 | 2008 | 8 | 30 | 6 | 0
2028 | 2008 | 8 | 30 | 7 | 0
2028 | 2008 | 8 | 30 | 8 | 1794.6466
2028 | 2008 | 8 | 30 | 9 | 19358.4821
2028 | 2008 | 8 | 30 | 10 | 35180.985
2028 | 2008 | 8 | 30 | 11 | 42944.3992
2028 | 2008 | 8 | 30 | 12 | 44903.3898
2028 | 2008 | 8 | 30 | 13 | 43942.6953
2028 | 2008 | 8 | 30 | 14 | 45012.3795
2028 | 2008 | 8 | 30 | 15 | 41061.5602
2028 | 2008 | 8 | 30 | 16 | 39757.4447
2028 | 2008 | 8 | 30 | 17 | 35957.1118
2028 | 2008 | 8 | 30 | 18 | 32211.8474
2028 | 2008 | 8 | 30 | 19 | 25120.3295
2028 | 2008 | 8 | 30 | 20 | 5446.7707
2028 | 2008 | 8 | 30 | 21 | 0
2028 | 2008 | 8 | 30 | 22 | 0
2028 | 2008 | 8 | 30 | 23 | 0
2028 | 2008 | 8 | 30 | 24 | 0
2028 | 2008 | 8 | 31 | 1 | 0
2028 | 2008 | 8 | 31 | 2 | 0
2028 | 2008 | 8 | 31 | 3 | 0
2028 | 2008 | 8 | 31 | 4 | 0
2028 | 2008 | 8 | 31 | 5 | 0
2028 | 2008 | 8 | 31 | 6 | 0
2028 | 2008 | 8 | 31 | 7 | 0
2028 | 2008 | 8 | 31 | 8 | 1723.025
2028 | 2008 | 8 | 31 | 9 | 20411.8362
2028 | 2008 | 8 | 31 | 10 | 38483.6736
2028 | 2008 | 8 | 31 | 11 | 46454.8336
2028 | 2008 | 8 | 31 | 12 | 48404.7997
2028 | 2008 | 8 | 31 | 13 | 48022.0299
2028 | 2008 | 8 | 31 | 14 | 48498.5601
2028 | 2008 | 8 | 31 | 15 | 46337.8892
2028 | 2008 | 8 | 31 | 16 | 44847.1254
2028 | 2008 | 8 | 31 | 17 | 42858.015
2028 | 2008 | 8 | 31 | 18 | 38211.9947
2028 | 2008 | 8 | 31 | 19 | 25253.7553
2028 | 2008 | 8 | 31 | 20 | 4882.2597
2028 | 2008 | 8 | 31 | 21 | 0
2028 | 2008 | 8 | 31 | 22 | 0
2028 | 2008 | 8 | 31 | 23 | 0
2028 | 2008 | 8 | 31 | 24 | 0
2029 | 2008 | 8 | 1 | 1 | 0
2029 | 2008 | 8 | 1 | 2 | 0
2029 | 2008 | 8 | 1 | 3 | 0
2029 | 2008 | 8 | 1 | 4 | 0
2029 | 2008 | 8 | 1 | 5 | 0
2029 | 2008 | 8 | 1 | 6 | 0
2029 | 2008 | 8 | 1 | 7 | 2.4214
2029 | 2008 | 8 | 1 | 8 | 4775.8161
2029 | 2008 | 8 | 1 | 9 | 21204.0745
2029 | 2008 | 8 | 1 | 10 | 38824.1292
2029 | 2008 | 8 | 1 | 11 | 47584.5304
2029 | 2008 | 8 | 1 | 12 | 51269.9672
2029 | 2008 | 8 | 1 | 13 | 52692.6289
2029 | 2008 | 8 | 1 | 14 | 51521.8806
2029 | 2008 | 8 | 1 | 15 | 49419.6182
2029 | 2008 | 8 | 1 | 16 | 46702.1033
2029 | 2008 | 8 | 1 | 17 | 43160.317
2029 | 2008 | 8 | 1 | 18 | 39384.5806
2029 | 2008 | 8 | 1 | 19 | 32336.3624
2029 | 2008 | 8 | 1 | 20 | 11645.9834
2029 | 2008 | 8 | 1 | 21 | 475.7313
2029 | 2008 | 8 | 1 | 22 | 0
2029 | 2008 | 8 | 1 | 23 | 0
2029 | 2008 | 8 | 1 | 24 | 0
2029 | 2008 | 8 | 2 | 1 | 0
2029 | 2008 | 8 | 2 | 2 | 0
2029 | 2008 | 8 | 2 | 3 | 0
2029 | 2008 | 8 | 2 | 4 | 0
2029 | 2008 | 8 | 2 | 5 | 0
2029 | 2008 | 8 | 2 | 6 | 0
2029 | 2008 | 8 | 2 | 7 | 2.0632
2029 | 2008 | 8 | 2 | 8 | 4870.734
2029 | 2008 | 8 | 2 | 9 | 20226.6693
2029 | 2008 | 8 | 2 | 10 | 39529.3496
2029 | 2008 | 8 | 2 | 11 | 50312.2232
2029 | 2008 | 8 | 2 | 12 | 53125.1238
2029 | 2008 | 8 | 2 | 13 | 51938.2022
2029 | 2008 | 8 | 2 | 14 | 53357.9905
2029 | 2008 | 8 | 2 | 15 | 52436.7774
2029 | 2008 | 8 | 2 | 16 | 51880.9041
2029 | 2008 | 8 | 2 | 17 | 47929.0194
2029 | 2008 | 8 | 2 | 18 | 44287.0952
2029 | 2008 | 8 | 2 | 19 | 33320.5697
2029 | 2008 | 8 | 2 | 20 | 10566.0297
2029 | 2008 | 8 | 2 | 21 | 295.6474
2029 | 2008 | 8 | 2 | 22 | 0
2029 | 2008 | 8 | 2 | 23 | 0
2029 | 2008 | 8 | 2 | 24 | 0
2029 | 2008 | 8 | 3 | 1 | 0
2029 | 2008 | 8 | 3 | 2 | 0
2029 | 2008 | 8 | 3 | 3 | 0
2029 | 2008 | 8 | 3 | 4 | 0
2029 | 2008 | 8 | 3 | 5 | 0
2029 | 2008 | 8 | 3 | 6 | 0
2029 | 2008 | 8 | 3 | 7 | 2.9932
2029 | 2008 | 8 | 3 | 8 | 4814.5959
2029 | 2008 | 8 | 3 | 9 | 23445.6261
2029 | 2008 | 8 | 3 | 10 | 41646.9812
2029 | 2008 | 8 | 3 | 11 | 51269.2848
2029 | 2008 | 8 | 3 | 12 | 54806.2913
2029 | 2008 | 8 | 3 | 13 | 54353.7392
2029 | 2008 | 8 | 3 | 14 | 54765.6787
2029 | 2008 | 8 | 3 | 15 | 53082.2506
2029 | 2008 | 8 | 3 | 16 | 51580.7876
2029 | 2008 | 8 | 3 | 17 | 49631.9236
2029 | 2008 | 8 | 3 | 18 | 45163.3978
2029 | 2008 | 8 | 3 | 19 | 34106.8497
2029 | 2008 | 8 | 3 | 20 | 11308.6319
2029 | 2008 | 8 | 3 | 21 | 139.3918
2029 | 2008 | 8 | 3 | 22 | 0
2029 | 2008 | 8 | 3 | 23 | 0
2029 | 2008 | 8 | 3 | 24 | 0
2029 | 2008 | 8 | 4 | 1 | 0
2029 | 2008 | 8 | 4 | 2 | 0
2029 | 2008 | 8 | 4 | 3 | 0
2029 | 2008 | 8 | 4 | 4 | 0
2029 | 2008 | 8 | 4 | 5 | 0
2029 | 2008 | 8 | 4 | 6 | 0
2029 | 2008 | 8 | 4 | 7 | 1.9784
2029 | 2008 | 8 | 4 | 8 | 5470.9368
2029 | 2008 | 8 | 4 | 9 | 27376.8411
2029 | 2008 | 8 | 4 | 10 | 42500.4223
2029 | 2008 | 8 | 4 | 11 | 51130.0111
2029 | 2008 | 8 | 4 | 12 | 51348.1013
2029 | 2008 | 8 | 4 | 13 | 52408.3163
2029 | 2008 | 8 | 4 | 14 | 51270.4831
2029 | 2008 | 8 | 4 | 15 | 51504.5081
2029 | 2008 | 8 | 4 | 16 | 49714.1215
2029 | 2008 | 8 | 4 | 17 | 47635.2431
2029 | 2008 | 8 | 4 | 18 | 43804.1066
2029 | 2008 | 8 | 4 | 19 | 34194.7361
2029 | 2008 | 8 | 4 | 20 | 10996.4747
2029 | 2008 | 8 | 4 | 21 | 84.92
2029 | 2008 | 8 | 4 | 22 | 0
2029 | 2008 | 8 | 4 | 23 | 0
2029 | 2008 | 8 | 4 | 24 | 0
2029 | 2008 | 8 | 5 | 1 | 0
2029 | 2008 | 8 | 5 | 2 | 0
2029 | 2008 | 8 | 5 | 3 | 0
2029 | 2008 | 8 | 5 | 4 | 0
2029 | 2008 | 8 | 5 | 5 | 0
2029 | 2008 | 8 | 5 | 6 | 0
2029 | 2008 | 8 | 5 | 7 | 0.65143
2029 | 2008 | 8 | 5 | 8 | 6123.8198
2029 | 2008 | 8 | 5 | 9 | 26110.4467
2029 | 2008 | 8 | 5 | 10 | 43781.1067
2029 | 2008 | 8 | 5 | 11 | 46991.2627
2029 | 2008 | 8 | 5 | 12 | 48550.0703
2029 | 2008 | 8 | 5 | 13 | 51014.8592
2029 | 2008 | 8 | 5 | 14 | 49170.2477
2029 | 2008 | 8 | 5 | 15 | 44788.3344
2029 | 2008 | 8 | 5 | 16 | 39928.9747
2029 | 2008 | 8 | 5 | 17 | 35812.7605
2029 | 2008 | 8 | 5 | 18 | 34030.4133
2029 | 2008 | 8 | 5 | 19 | 29072.6685
2029 | 2008 | 8 | 5 | 20 | 10924.1416
2029 | 2008 | 8 | 5 | 21 | 77.548
2029 | 2008 | 8 | 5 | 22 | 0
2029 | 2008 | 8 | 5 | 23 | 0
2029 | 2008 | 8 | 5 | 24 | 0
2029 | 2008 | 8 | 6 | 1 | 0
2029 | 2008 | 8 | 6 | 2 | 0
2029 | 2008 | 8 | 6 | 3 | 0
2029 | 2008 | 8 | 6 | 4 | 0
2029 | 2008 | 8 | 6 | 5 | 0
2029 | 2008 | 8 | 6 | 6 | 0
2029 | 2008 | 8 | 6 | 7 | 0.044932
2029 | 2008 | 8 | 6 | 8 | 3368.1613
2029 | 2008 | 8 | 6 | 9 | 19601.1791
2029 | 2008 | 8 | 6 | 10 | 36366.5361
2029 | 2008 | 8 | 6 | 11 | 40195.3611
2029 | 2008 | 8 | 6 | 12 | 44527.5709
2029 | 2008 | 8 | 6 | 13 | 43998.9154
2029 | 2008 | 8 | 6 | 14 | 43532.5748
2029 | 2008 | 8 | 6 | 15 | 42788.2991
2029 | 2008 | 8 | 6 | 16 | 39324.63
2029 | 2008 | 8 | 6 | 17 | 35444.9859
2029 | 2008 | 8 | 6 | 18 | 33934.7887
2029 | 2008 | 8 | 6 | 19 | 28303.3261
2029 | 2008 | 8 | 6 | 20 | 10192.7942
2029 | 2008 | 8 | 6 | 21 | 66.4362
2029 | 2008 | 8 | 6 | 22 | 0
2029 | 2008 | 8 | 6 | 23 | 0
2029 | 2008 | 8 | 6 | 24 | 0
2029 | 2008 | 8 | 7 | 1 | 0
2029 | 2008 | 8 | 7 | 2 | 0
2029 | 2008 | 8 | 7 | 3 | 0
2029 | 2008 | 8 | 7 | 4 | 0
2029 | 2008 | 8 | 7 | 5 | 0
2029 | 2008 | 8 | 7 | 6 | 0
2029 | 2008 | 8 | 7 | 7 | 0.20704
2029 | 2008 | 8 | 7 | 8 | 3315.0422
2029 | 2008 | 8 | 7 | 9 | 17491.434
2029 | 2008 | 8 | 7 | 10 | 32741.0111
2029 | 2008 | 8 | 7 | 11 | 44392.6544
2029 | 2008 | 8 | 7 | 12 | 49873.005
2029 | 2008 | 8 | 7 | 13 | 51050.1107
2029 | 2008 | 8 | 7 | 14 | 50244.383
2029 | 2008 | 8 | 7 | 15 | 49186.2543
2029 | 2008 | 8 | 7 | 16 | 48261.0933
2029 | 2008 | 8 | 7 | 17 | 46334.2347
2029 | 2008 | 8 | 7 | 18 | 40561.5961
2029 | 2008 | 8 | 7 | 19 | 31535.4432
2029 | 2008 | 8 | 7 | 20 | 10242.3993
2029 | 2008 | 8 | 7 | 21 | 33.2623
2029 | 2008 | 8 | 7 | 22 | 0
2029 | 2008 | 8 | 7 | 23 | 0
2029 | 2008 | 8 | 7 | 24 | 0
2029 | 2008 | 8 | 8 | 1 | 0
2029 | 2008 | 8 | 8 | 2 | 0
2029 | 2008 | 8 | 8 | 3 | 0
2029 | 2008 | 8 | 8 | 4 | 0
2029 | 2008 | 8 | 8 | 5 | 0
2029 | 2008 | 8 | 8 | 6 | 0
2029 | 2008 | 8 | 8 | 7 | 0.0076014
2029 | 2008 | 8 | 8 | 8 | 3559.8156
2029 | 2008 | 8 | 8 | 9 | 22591.8448
2029 | 2008 | 8 | 8 | 10 | 40720.0894
2029 | 2008 | 8 | 8 | 11 | 47455.743
2029 | 2008 | 8 | 8 | 12 | 47572.0881
2029 | 2008 | 8 | 8 | 13 | 50713.2682
2029 | 2008 | 8 | 8 | 14 | 50992.9608
2029 | 2008 | 8 | 8 | 15 | 49715.3945
2029 | 2008 | 8 | 8 | 16 | 48028.8828
2029 | 2008 | 8 | 8 | 17 | 43757.8968
2029 | 2008 | 8 | 8 | 18 | 39673.4983
2029 | 2008 | 8 | 8 | 19 | 31750.6996
2029 | 2008 | 8 | 8 | 20 | 10925.7965
2029 | 2008 | 8 | 8 | 21 | 26.1682
2029 | 2008 | 8 | 8 | 22 | 0
2029 | 2008 | 8 | 8 | 23 | 0
2029 | 2008 | 8 | 8 | 24 | 0
2029 | 2008 | 8 | 9 | 1 | 0
2029 | 2008 | 8 | 9 | 2 | 0
2029 | 2008 | 8 | 9 | 3 | 0
2029 | 2008 | 8 | 9 | 4 | 0
2029 | 2008 | 8 | 9 | 5 | 0
2029 | 2008 | 8 | 9 | 6 | 0
2029 | 2008 | 8 | 9 | 7 | 0.045975
2029 | 2008 | 8 | 9 | 8 | 3131.2084
2029 | 2008 | 8 | 9 | 9 | 21618.5811
2029 | 2008 | 8 | 9 | 10 | 38598.2405
2029 | 2008 | 8 | 9 | 11 | 45261.7258
2029 | 2008 | 8 | 9 | 12 | 48026.687
2029 | 2008 | 8 | 9 | 13 | 48044.4774
2029 | 2008 | 8 | 9 | 14 | 46060.3347
2029 | 2008 | 8 | 9 | 15 | 42869.5642
2029 | 2008 | 8 | 9 | 16 | 39736.799
2029 | 2008 | 8 | 9 | 17 | 38773.9099
2029 | 2008 | 8 | 9 | 18 | 36949.2081
2029 | 2008 | 8 | 9 | 19 | 31150.6663
2029 | 2008 | 8 | 9 | 20 | 10423.7097
2029 | 2008 | 8 | 9 | 21 | 0
2029 | 2008 | 8 | 9 | 22 | 0
2029 | 2008 | 8 | 9 | 23 | 0
2029 | 2008 | 8 | 9 | 24 | 0
2029 | 2008 | 8 | 10 | 1 | 0
2029 | 2008 | 8 | 10 | 2 | 0
2029 | 2008 | 8 | 10 | 3 | 0
2029 | 2008 | 8 | 10 | 4 | 0
2029 | 2008 | 8 | 10 | 5 | 0
2029 | 2008 | 8 | 10 | 6 | 0
2029 | 2008 | 8 | 10 | 7 | 0.3285
2029 | 2008 | 8 | 10 | 8 | 2724.6942
2029 | 2008 | 8 | 10 | 9 | 19916.7938
2029 | 2008 | 8 | 10 | 10 | 39475.8276
2029 | 2008 | 8 | 10 | 11 | 46480.8182
2029 | 2008 | 8 | 10 | 12 | 50007.6812
2029 | 2008 | 8 | 10 | 13 | 52000.6979
2029 | 2008 | 8 | 10 | 14 | 51074.8815
2029 | 2008 | 8 | 10 | 15 | 50567.7032
2029 | 2008 | 8 | 10 | 16 | 48453.9102
2029 | 2008 | 8 | 10 | 17 | 44389.2745
2029 | 2008 | 8 | 10 | 18 | 37816.1862
2029 | 2008 | 8 | 10 | 19 | 29992.0959
2029 | 2008 | 8 | 10 | 20 | 9320.3022
2029 | 2008 | 8 | 10 | 21 | 0
2029 | 2008 | 8 | 10 | 22 | 0
2029 | 2008 | 8 | 10 | 23 | 0
2029 | 2008 | 8 | 10 | 24 | 0
2029 | 2008 | 8 | 11 | 1 | 0
2029 | 2008 | 8 | 11 | 2 | 0
2029 | 2008 | 8 | 11 | 3 | 0
2029 | 2008 | 8 | 11 | 4 | 0
2029 | 2008 | 8 | 11 | 5 | 0
2029 | 2008 | 8 | 11 | 6 | 0
2029 | 2008 | 8 | 11 | 7 | 0
2029 | 2008 | 8 | 11 | 8 | 1979.1285
2029 | 2008 | 8 | 11 | 9 | 15909.9093
2029 | 2008 | 8 | 11 | 10 | 29500.5708
2029 | 2008 | 8 | 11 | 11 | 40156.179
2029 | 2008 | 8 | 11 | 12 | 45324.6697
2029 | 2008 | 8 | 11 | 13 | 44460.5781
2029 | 2008 | 8 | 11 | 14 | 43886.6934
2029 | 2008 | 8 | 11 | 15 | 41825.552
2029 | 2008 | 8 | 11 | 16 | 39705.2518
2029 | 2008 | 8 | 11 | 17 | 35645.346
2029 | 2008 | 8 | 11 | 18 | 33547.1931
2029 | 2008 | 8 | 11 | 19 | 28081.1023
2029 | 2008 | 8 | 11 | 20 | 9393.633
2029 | 2008 | 8 | 11 | 21 | 0
2029 | 2008 | 8 | 11 | 22 | 0
2029 | 2008 | 8 | 11 | 23 | 0
2029 | 2008 | 8 | 11 | 24 | 0
2029 | 2008 | 8 | 12 | 1 | 0
2029 | 2008 | 8 | 12 | 2 | 0
2029 | 2008 | 8 | 12 | 3 | 0
2029 | 2008 | 8 | 12 | 4 | 0
2029 | 2008 | 8 | 12 | 5 | 0
2029 | 2008 | 8 | 12 | 6 | 0
2029 | 2008 | 8 | 12 | 7 | 0.0022535
2029 | 2008 | 8 | 12 | 8 | 976.929
2029 | 2008 | 8 | 12 | 9 | 9545.3787
2029 | 2008 | 8 | 12 | 10 | 25335.9654
2029 | 2008 | 8 | 12 | 11 | 37493.6697
2029 | 2008 | 8 | 12 | 12 | 45684.3364
2029 | 2008 | 8 | 12 | 13 | 48601.4701
2029 | 2008 | 8 | 12 | 14 | 49411.015
2029 | 2008 | 8 | 12 | 15 | 47290.8377
2029 | 2008 | 8 | 12 | 16 | 45718.0454
2029 | 2008 | 8 | 12 | 17 | 42394.6819
2029 | 2008 | 8 | 12 | 18 | 39124.3391
2029 | 2008 | 8 | 12 | 19 | 31045.7019
2029 | 2008 | 8 | 12 | 20 | 10226.3664
2029 | 2008 | 8 | 12 | 21 | 0
2029 | 2008 | 8 | 12 | 22 | 0
2029 | 2008 | 8 | 12 | 23 | 0
2029 | 2008 | 8 | 12 | 24 | 0
2029 | 2008 | 8 | 13 | 1 | 0
2029 | 2008 | 8 | 13 | 2 | 0
2029 | 2008 | 8 | 13 | 3 | 0
2029 | 2008 | 8 | 13 | 4 | 0
2029 | 2008 | 8 | 13 | 5 | 0
2029 | 2008 | 8 | 13 | 6 | 0
2029 | 2008 | 8 | 13 | 7 | 0.064221
2029 | 2008 | 8 | 13 | 8 | 5012.0605
2029 | 2008 | 8 | 13 | 9 | 24112.3174
2029 | 2008 | 8 | 13 | 10 | 43186.3495
2029 | 2008 | 8 | 13 | 11 | 48664.7936
2029 | 2008 | 8 | 13 | 12 | 51762.2627
2029 | 2008 | 8 | 13 | 13 | 49128.4117
2029 | 2008 | 8 | 13 | 14 | 50087.8558
2029 | 2008 | 8 | 13 | 15 | 48550.8253
2029 | 2008 | 8 | 13 | 16 | 48356.1639
2029 | 2008 | 8 | 13 | 17 | 45980.0908
2029 | 2008 | 8 | 13 | 18 | 41747.6259
2029 | 2008 | 8 | 13 | 19 | 31326.7783
2029 | 2008 | 8 | 13 | 20 | 10832.616
2029 | 2008 | 8 | 13 | 21 | 0
2029 | 2008 | 8 | 13 | 22 | 0
2029 | 2008 | 8 | 13 | 23 | 0
2029 | 2008 | 8 | 13 | 24 | 0
2029 | 2008 | 8 | 14 | 1 | 0
2029 | 2008 | 8 | 14 | 2 | 0
2029 | 2008 | 8 | 14 | 3 | 0
2029 | 2008 | 8 | 14 | 4 | 0
2029 | 2008 | 8 | 14 | 5 | 0
2029 | 2008 | 8 | 14 | 6 | 0
2029 | 2008 | 8 | 14 | 7 | 0.0029843
2029 | 2008 | 8 | 14 | 8 | 3193.1273
2029 | 2008 | 8 | 14 | 9 | 22464.1089
2029 | 2008 | 8 | 14 | 10 | 39163.8217
2029 | 2008 | 8 | 14 | 11 | 46591.5093
2029 | 2008 | 8 | 14 | 12 | 48293.4398
2029 | 2008 | 8 | 14 | 13 | 51260.3883
2029 | 2008 | 8 | 14 | 14 | 50458.3217
2029 | 2008 | 8 | 14 | 15 | 49438.0391
2029 | 2008 | 8 | 14 | 16 | 46837.1556
2029 | 2008 | 8 | 14 | 17 | 45614.9784
2029 | 2008 | 8 | 14 | 18 | 42533.3302
2029 | 2008 | 8 | 14 | 19 | 32771.0416
2029 | 2008 | 8 | 14 | 20 | 11594.2333
2029 | 2008 | 8 | 14 | 21 | 0
2029 | 2008 | 8 | 14 | 22 | 0
2029 | 2008 | 8 | 14 | 23 | 0
2029 | 2008 | 8 | 14 | 24 | 0
2029 | 2008 | 8 | 15 | 1 | 0
2029 | 2008 | 8 | 15 | 2 | 0
2029 | 2008 | 8 | 15 | 3 | 0
2029 | 2008 | 8 | 15 | 4 | 0
2029 | 2008 | 8 | 15 | 5 | 0
2029 | 2008 | 8 | 15 | 6 | 0
2029 | 2008 | 8 | 15 | 7 | 0.018889
2029 | 2008 | 8 | 15 | 8 | 2090.1577
2029 | 2008 | 8 | 15 | 9 | 20534.4308
2029 | 2008 | 8 | 15 | 10 | 33821.8944
2029 | 2008 | 8 | 15 | 11 | 44017.0741
2029 | 2008 | 8 | 15 | 12 | 49652.0635
2029 | 2008 | 8 | 15 | 13 | 51235.3858
2029 | 2008 | 8 | 15 | 14 | 48723.596
2029 | 2008 | 8 | 15 | 15 | 48728.1569
2029 | 2008 | 8 | 15 | 16 | 48402.1781
2029 | 2008 | 8 | 15 | 17 | 46376.971
2029 | 2008 | 8 | 15 | 18 | 41636.9549
2029 | 2008 | 8 | 15 | 19 | 32719.712
2029 | 2008 | 8 | 15 | 20 | 9653.2546
2029 | 2008 | 8 | 15 | 21 | 0
2029 | 2008 | 8 | 15 | 22 | 0
2029 | 2008 | 8 | 15 | 23 | 0
2029 | 2008 | 8 | 15 | 24 | 0
2029 | 2008 | 8 | 16 | 1 | 0
2029 | 2008 | 8 | 16 | 2 | 0
2029 | 2008 | 8 | 16 | 3 | 0
2029 | 2008 | 8 | 16 | 4 | 0
2029 | 2008 | 8 | 16 | 5 | 0
2029 | 2008 | 8 | 16 | 6 | 0
2029 | 2008 | 8 | 16 | 7 | 0
2029 | 2008 | 8 | 16 | 8 | 1977.0465
2029 | 2008 | 8 | 16 | 9 | 14288.8718
2029 | 2008 | 8 | 16 | 10 | 30238.3716
2029 | 2008 | 8 | 16 | 11 | 37467.102
2029 | 2008 | 8 | 16 | 12 | 38993.6586
2029 | 2008 | 8 | 16 | 13 | 40416.882
2029 | 2008 | 8 | 16 | 14 | 39755.2
2029 | 2008 | 8 | 16 | 15 | 38398.6854
2029 | 2008 | 8 | 16 | 16 | 35668.2136
2029 | 2008 | 8 | 16 | 17 | 35808.4975
2029 | 2008 | 8 | 16 | 18 | 33972.4767
2029 | 2008 | 8 | 16 | 19 | 28967.9151
2029 | 2008 | 8 | 16 | 20 | 9974.7166
2029 | 2008 | 8 | 16 | 21 | 0
2029 | 2008 | 8 | 16 | 22 | 0
2029 | 2008 | 8 | 16 | 23 | 0
2029 | 2008 | 8 | 16 | 24 | 0
2029 | 2008 | 8 | 17 | 1 | 0
2029 | 2008 | 8 | 17 | 2 | 0
2029 | 2008 | 8 | 17 | 3 | 0
2029 | 2008 | 8 | 17 | 4 | 0
2029 | 2008 | 8 | 17 | 5 | 0
2029 | 2008 | 8 | 17 | 6 | 0
2029 | 2008 | 8 | 17 | 7 | 0
2029 | 2008 | 8 | 17 | 8 | 1402.5413
2029 | 2008 | 8 | 17 | 9 | 13822.7314
2029 | 2008 | 8 | 17 | 10 | 29636.3331
2029 | 2008 | 8 | 17 | 11 | 36012.1046
2029 | 2008 | 8 | 17 | 12 | 38655.3485
2029 | 2008 | 8 | 17 | 13 | 39140.2452
2029 | 2008 | 8 | 17 | 14 | 37094.3495
2029 | 2008 | 8 | 17 | 15 | 35204.3654
2029 | 2008 | 8 | 17 | 16 | 32051.1034
2029 | 2008 | 8 | 17 | 17 | 30287.128
2029 | 2008 | 8 | 17 | 18 | 28488.5474
2029 | 2008 | 8 | 17 | 19 | 25741.0533
2029 | 2008 | 8 | 17 | 20 | 8875.7007
2029 | 2008 | 8 | 17 | 21 | 0
2029 | 2008 | 8 | 17 | 22 | 0
2029 | 2008 | 8 | 17 | 23 | 0
2029 | 2008 | 8 | 17 | 24 | 0
2029 | 2008 | 8 | 18 | 1 | 0
2029 | 2008 | 8 | 18 | 2 | 0
2029 | 2008 | 8 | 18 | 3 | 0
2029 | 2008 | 8 | 18 | 4 | 0
2029 | 2008 | 8 | 18 | 5 | 0
2029 | 2008 | 8 | 18 | 6 | 0
2029 | 2008 | 8 | 18 | 7 | 0
2029 | 2008 | 8 | 18 | 8 | 1064.3363
2029 | 2008 | 8 | 18 | 9 | 12007.5144
2029 | 2008 | 8 | 18 | 10 | 23304.4764
2029 | 2008 | 8 | 18 | 11 | 31535.9605
2029 | 2008 | 8 | 18 | 12 | 37829.8512
2029 | 2008 | 8 | 18 | 13 | 39909.8234
2029 | 2008 | 8 | 18 | 14 | 40072.4001
2029 | 2008 | 8 | 18 | 15 | 37081.7101
2029 | 2008 | 8 | 18 | 16 | 33452.9701
2029 | 2008 | 8 | 18 | 17 | 30108.3911
2029 | 2008 | 8 | 18 | 18 | 29159.5632
2029 | 2008 | 8 | 18 | 19 | 25107.5639
2029 | 2008 | 8 | 18 | 20 | 8722.6332
2029 | 2008 | 8 | 18 | 21 | 0
2029 | 2008 | 8 | 18 | 22 | 0
2029 | 2008 | 8 | 18 | 23 | 0
2029 | 2008 | 8 | 18 | 24 | 0
2029 | 2008 | 8 | 19 | 1 | 0
2029 | 2008 | 8 | 19 | 2 | 0
2029 | 2008 | 8 | 19 | 3 | 0
2029 | 2008 | 8 | 19 | 4 | 0
2029 | 2008 | 8 | 19 | 5 | 0
2029 | 2008 | 8 | 19 | 6 | 0
2029 | 2008 | 8 | 19 | 7 | 0
2029 | 2008 | 8 | 19 | 8 | 1218.8171
2029 | 2008 | 8 | 19 | 9 | 12515.2721
2029 | 2008 | 8 | 19 | 10 | 26647.6512
2029 | 2008 | 8 | 19 | 11 | 34603.8252
2029 | 2008 | 8 | 19 | 12 | 39429.0015
2029 | 2008 | 8 | 19 | 13 | 40793.6547
2029 | 2008 | 8 | 19 | 14 | 40803.4019
2029 | 2008 | 8 | 19 | 15 | 39405.8818
2029 | 2008 | 8 | 19 | 16 | 37257.0786
2029 | 2008 | 8 | 19 | 17 | 34413.2956
2029 | 2008 | 8 | 19 | 18 | 32727.5715
2029 | 2008 | 8 | 19 | 19 | 28053.1155
2029 | 2008 | 8 | 19 | 20 | 9759.9616
2029 | 2008 | 8 | 19 | 21 | 0
2029 | 2008 | 8 | 19 | 22 | 0
2029 | 2008 | 8 | 19 | 23 | 0
2029 | 2008 | 8 | 19 | 24 | 0
2029 | 2008 | 8 | 20 | 1 | 0
2029 | 2008 | 8 | 20 | 2 | 0
2029 | 2008 | 8 | 20 | 3 | 0
2029 | 2008 | 8 | 20 | 4 | 0
2029 | 2008 | 8 | 20 | 5 | 0
2029 | 2008 | 8 | 20 | 6 | 0
2029 | 2008 | 8 | 20 | 7 | 0
2029 | 2008 | 8 | 20 | 8 | 941.7203
2029 | 2008 | 8 | 20 | 9 | 13148.7679
2029 | 2008 | 8 | 20 | 10 | 29656.1418
2029 | 2008 | 8 | 20 | 11 | 38913.2458
2029 | 2008 | 8 | 20 | 12 | 45085.0913
2029 | 2008 | 8 | 20 | 13 | 44698.3651
2029 | 2008 | 8 | 20 | 14 | 44072.9065
2029 | 2008 | 8 | 20 | 15 | 43126.168
2029 | 2008 | 8 | 20 | 16 | 43242.1199
2029 | 2008 | 8 | 20 | 17 | 40588.0293
2029 | 2008 | 8 | 20 | 18 | 38888.1844
2029 | 2008 | 8 | 20 | 19 | 29866.1853
2029 | 2008 | 8 | 20 | 20 | 9615.8462
2029 | 2008 | 8 | 20 | 21 | 0
2029 | 2008 | 8 | 20 | 22 | 0
2029 | 2008 | 8 | 20 | 23 | 0
2029 | 2008 | 8 | 20 | 24 | 0
2029 | 2008 | 8 | 21 | 1 | 0
2029 | 2008 | 8 | 21 | 2 | 0
2029 | 2008 | 8 | 21 | 3 | 0
2029 | 2008 | 8 | 21 | 4 | 0
2029 | 2008 | 8 | 21 | 5 | 0
2029 | 2008 | 8 | 21 | 6 | 0
2029 | 2008 | 8 | 21 | 7 | 0
2029 | 2008 | 8 | 21 | 8 | 1044.7548
2029 | 2008 | 8 | 21 | 9 | 16047.2105
2029 | 2008 | 8 | 21 | 10 | 34787.9967
2029 | 2008 | 8 | 21 | 11 | 39313.9249
2029 | 2008 | 8 | 21 | 12 | 45370.8905
2029 | 2008 | 8 | 21 | 13 | 47028.9648
2029 | 2008 | 8 | 21 | 14 | 46311.7803
2029 | 2008 | 8 | 21 | 15 | 44121.0188
2029 | 2008 | 8 | 21 | 16 | 45059.6849
2029 | 2008 | 8 | 21 | 17 | 43404.5134
2029 | 2008 | 8 | 21 | 18 | 36185.4899
2029 | 2008 | 8 | 21 | 19 | 30462.4031
2029 | 2008 | 8 | 21 | 20 | 9336.1091
2029 | 2008 | 8 | 21 | 21 | 0
2029 | 2008 | 8 | 21 | 22 | 0
2029 | 2008 | 8 | 21 | 23 | 0
2029 | 2008 | 8 | 21 | 24 | 0
2029 | 2008 | 8 | 22 | 1 | 0
2029 | 2008 | 8 | 22 | 2 | 0
2029 | 2008 | 8 | 22 | 3 | 0
2029 | 2008 | 8 | 22 | 4 | 0
2029 | 2008 | 8 | 22 | 5 | 0
2029 | 2008 | 8 | 22 | 6 | 0
2029 | 2008 | 8 | 22 | 7 | 0
2029 | 2008 | 8 | 22 | 8 | 1505.9616
2029 | 2008 | 8 | 22 | 9 | 16588.4778
2029 | 2008 | 8 | 22 | 10 | 30244.6723
2029 | 2008 | 8 | 22 | 11 | 40085.6444
2029 | 2008 | 8 | 22 | 12 | 45405.3738
2029 | 2008 | 8 | 22 | 13 | 48725.6658
2029 | 2008 | 8 | 22 | 14 | 47629.0425
2029 | 2008 | 8 | 22 | 15 | 43380.3354
2029 | 2008 | 8 | 22 | 16 | 43514.4269
2029 | 2008 | 8 | 22 | 17 | 39163.487
2029 | 2008 | 8 | 22 | 18 | 35606.048
2029 | 2008 | 8 | 22 | 19 | 27680.8286
2029 | 2008 | 8 | 22 | 20 | 8578.7153
2029 | 2008 | 8 | 22 | 21 | 0
2029 | 2008 | 8 | 22 | 22 | 0
2029 | 2008 | 8 | 22 | 23 | 0
2029 | 2008 | 8 | 22 | 24 | 0
2029 | 2008 | 8 | 23 | 1 | 0
2029 | 2008 | 8 | 23 | 2 | 0
2029 | 2008 | 8 | 23 | 3 | 0
2029 | 2008 | 8 | 23 | 4 | 0
2029 | 2008 | 8 | 23 | 5 | 0
2029 | 2008 | 8 | 23 | 6 | 0
2029 | 2008 | 8 | 23 | 7 | 0
2029 | 2008 | 8 | 23 | 8 | 2669.3106
2029 | 2008 | 8 | 23 | 9 | 21903.7304
2029 | 2008 | 8 | 23 | 10 | 39052.5706
2029 | 2008 | 8 | 23 | 11 | 42796.0233
2029 | 2008 | 8 | 23 | 12 | 46086.7135
2029 | 2008 | 8 | 23 | 13 | 45528.8807
2029 | 2008 | 8 | 23 | 14 | 45086.3937
2029 | 2008 | 8 | 23 | 15 | 42196.2771
2029 | 2008 | 8 | 23 | 16 | 39868.258
2029 | 2008 | 8 | 23 | 17 | 36954.4595
2029 | 2008 | 8 | 23 | 18 | 33853.4105
2029 | 2008 | 8 | 23 | 19 | 27629.4253
2029 | 2008 | 8 | 23 | 20 | 8000.4065
2029 | 2008 | 8 | 23 | 21 | 0
2029 | 2008 | 8 | 23 | 22 | 0
2029 | 2008 | 8 | 23 | 23 | 0
2029 | 2008 | 8 | 23 | 24 | 0
2029 | 2008 | 8 | 24 | 1 | 0
2029 | 2008 | 8 | 24 | 2 | 0
2029 | 2008 | 8 | 24 | 3 | 0
2029 | 2008 | 8 | 24 | 4 | 0
2029 | 2008 | 8 | 24 | 5 | 0
2029 | 2008 | 8 | 24 | 6 | 0
2029 | 2008 | 8 | 24 | 7 | 0
2029 | 2008 | 8 | 24 | 8 | 2519.2191
2029 | 2008 | 8 | 24 | 9 | 21121.2375
2029 | 2008 | 8 | 24 | 10 | 36906.7808
2029 | 2008 | 8 | 24 | 11 | 42004.0516
2029 | 2008 | 8 | 24 | 12 | 45415.7857
2029 | 2008 | 8 | 24 | 13 | 45711.6082
2029 | 2008 | 8 | 24 | 14 | 44295.0174
2029 | 2008 | 8 | 24 | 15 | 44979.2163
2029 | 2008 | 8 | 24 | 16 | 40950.0516
2029 | 2008 | 8 | 24 | 17 | 39896.009
2029 | 2008 | 8 | 24 | 18 | 36834.595
2029 | 2008 | 8 | 24 | 19 | 28846.0475
2029 | 2008 | 8 | 24 | 20 | 8343.1564
2029 | 2008 | 8 | 24 | 21 | 0
2029 | 2008 | 8 | 24 | 22 | 0
2029 | 2008 | 8 | 24 | 23 | 0
2029 | 2008 | 8 | 24 | 24 | 0
2029 | 2008 | 8 | 25 | 1 | 0
2029 | 2008 | 8 | 25 | 2 | 0
2029 | 2008 | 8 | 25 | 3 | 0
2029 | 2008 | 8 | 25 | 4 | 0
2029 | 2008 | 8 | 25 | 5 | 0
2029 | 2008 | 8 | 25 | 6 | 0
2029 | 2008 | 8 | 25 | 7 | 0
2029 | 2008 | 8 | 25 | 8 | 2582.858
2029 | 2008 | 8 | 25 | 9 | 23929.0786
2029 | 2008 | 8 | 25 | 10 | 42046.5876
2029 | 2008 | 8 | 25 | 11 | 48273.7333
2029 | 2008 | 8 | 25 | 12 | 50173.2639
2029 | 2008 | 8 | 25 | 13 | 50501.6315
2029 | 2008 | 8 | 25 | 14 | 49412.9233
2029 | 2008 | 8 | 25 | 15 | 47264.8036
2029 | 2008 | 8 | 25 | 16 | 45836.0567
2029 | 2008 | 8 | 25 | 17 | 44940.0693
2029 | 2008 | 8 | 25 | 18 | 40665.7002
2029 | 2008 | 8 | 25 | 19 | 31811.3013
2029 | 2008 | 8 | 25 | 20 | 8680.5322
2029 | 2008 | 8 | 25 | 21 | 0
2029 | 2008 | 8 | 25 | 22 | 0
2029 | 2008 | 8 | 25 | 23 | 0
2029 | 2008 | 8 | 25 | 24 | 0
2029 | 2008 | 8 | 26 | 1 | 0
2029 | 2008 | 8 | 26 | 2 | 0
2029 | 2008 | 8 | 26 | 3 | 0
2029 | 2008 | 8 | 26 | 4 | 0
2029 | 2008 | 8 | 26 | 5 | 0
2029 | 2008 | 8 | 26 | 6 | 0
2029 | 2008 | 8 | 26 | 7 | 0
2029 | 2008 | 8 | 26 | 8 | 3781.9496
2029 | 2008 | 8 | 26 | 9 | 25610.5359
2029 | 2008 | 8 | 26 | 10 | 42884.9296
2029 | 2008 | 8 | 26 | 11 | 48302.1336
2029 | 2008 | 8 | 26 | 12 | 50198.3366
2029 | 2008 | 8 | 26 | 13 | 50652.3378
2029 | 2008 | 8 | 26 | 14 | 47456.7039
2029 | 2008 | 8 | 26 | 15 | 47019.0712
2029 | 2008 | 8 | 26 | 16 | 46393.0488
2029 | 2008 | 8 | 26 | 17 | 44114.9339
2029 | 2008 | 8 | 26 | 18 | 39758.4064
2029 | 2008 | 8 | 26 | 19 | 31091.7535
2029 | 2008 | 8 | 26 | 20 | 7605.7174
2029 | 2008 | 8 | 26 | 21 | 0
2029 | 2008 | 8 | 26 | 22 | 0
2029 | 2008 | 8 | 26 | 23 | 0
2029 | 2008 | 8 | 26 | 24 | 0
2029 | 2008 | 8 | 27 | 1 | 0
2029 | 2008 | 8 | 27 | 2 | 0
2029 | 2008 | 8 | 27 | 3 | 0
2029 | 2008 | 8 | 27 | 4 | 0
2029 | 2008 | 8 | 27 | 5 | 0
2029 | 2008 | 8 | 27 | 6 | 0
2029 | 2008 | 8 | 27 | 7 | 0
2029 | 2008 | 8 | 27 | 8 | 3083.3035
2029 | 2008 | 8 | 27 | 9 | 25764.2281
2029 | 2008 | 8 | 27 | 10 | 41686.5782
2029 | 2008 | 8 | 27 | 11 | 47382.9809
2029 | 2008 | 8 | 27 | 12 | 50259.716
2029 | 2008 | 8 | 27 | 13 | 47474.3584
2029 | 2008 | 8 | 27 | 14 | 47413.2095
2029 | 2008 | 8 | 27 | 15 | 46806.7992
2029 | 2008 | 8 | 27 | 16 | 43468.8494
2029 | 2008 | 8 | 27 | 17 | 41673.9804
2029 | 2008 | 8 | 27 | 18 | 36070.7181
2029 | 2008 | 8 | 27 | 19 | 28104.0707
2029 | 2008 | 8 | 27 | 20 | 6244.7793
2029 | 2008 | 8 | 27 | 21 | 0
2029 | 2008 | 8 | 27 | 22 | 0
2029 | 2008 | 8 | 27 | 23 | 0
2029 | 2008 | 8 | 27 | 24 | 0
2029 | 2008 | 8 | 28 | 1 | 0
2029 | 2008 | 8 | 28 | 2 | 0
2029 | 2008 | 8 | 28 | 3 | 0
2029 | 2008 | 8 | 28 | 4 | 0
2029 | 2008 | 8 | 28 | 5 | 0
2029 | 2008 | 8 | 28 | 6 | 0
2029 | 2008 | 8 | 28 | 7 | 0
2029 | 2008 | 8 | 28 | 8 | 2227.4827
2029 | 2008 | 8 | 28 | 9 | 16711.6724
2029 | 2008 | 8 | 28 | 10 | 31976.5099
2029 | 2008 | 8 | 28 | 11 | 43853.7636
2029 | 2008 | 8 | 28 | 12 | 45091.1734
2029 | 2008 | 8 | 28 | 13 | 46772.2783
2029 | 2008 | 8 | 28 | 14 | 45797.3743
2029 | 2008 | 8 | 28 | 15 | 45003.9212
2029 | 2008 | 8 | 28 | 16 | 40851.5308
2029 | 2008 | 8 | 28 | 17 | 37551.5322
2029 | 2008 | 8 | 28 | 18 | 34062.3746
2029 | 2008 | 8 | 28 | 19 | 28327.0262
2029 | 2008 | 8 | 28 | 20 | 6359.2868
2029 | 2008 | 8 | 28 | 21 | 0
2029 | 2008 | 8 | 28 | 22 | 0
2029 | 2008 | 8 | 28 | 23 | 0
2029 | 2008 | 8 | 28 | 24 | 0
2029 | 2008 | 8 | 29 | 1 | 0
2029 | 2008 | 8 | 29 | 2 | 0
2029 | 2008 | 8 | 29 | 3 | 0
2029 | 2008 | 8 | 29 | 4 | 0
2029 | 2008 | 8 | 29 | 5 | 0
2029 | 2008 | 8 | 29 | 6 | 0
2029 | 2008 | 8 | 29 | 7 | 0
2029 | 2008 | 8 | 29 | 8 | 1959.6528
2029 | 2008 | 8 | 29 | 9 | 16364.1897
2029 | 2008 | 8 | 29 | 10 | 32156.8152
2029 | 2008 | 8 | 29 | 11 | 38562.9474
2029 | 2008 | 8 | 29 | 12 | 41309.1561
2029 | 2008 | 8 | 29 | 13 | 39518.84
2029 | 2008 | 8 | 29 | 14 | 38660.8124
2029 | 2008 | 8 | 29 | 15 | 35501.5343
2029 | 2008 | 8 | 29 | 16 | 33246.2344
2029 | 2008 | 8 | 29 | 17 | 29507.3413
2029 | 2008 | 8 | 29 | 18 | 27196.1344
2029 | 2008 | 8 | 29 | 19 | 23268.7803
2029 | 2008 | 8 | 29 | 20 | 5059.9462
2029 | 2008 | 8 | 29 | 21 | 0
2029 | 2008 | 8 | 29 | 22 | 0
2029 | 2008 | 8 | 29 | 23 | 0
2029 | 2008 | 8 | 29 | 24 | 0
2029 | 2008 | 8 | 30 | 1 | 0
2029 | 2008 | 8 | 30 | 2 | 0
2029 | 2008 | 8 | 30 | 3 | 0
2029 | 2008 | 8 | 30 | 4 | 0
2029 | 2008 | 8 | 30 | 5 | 0
2029 | 2008 | 8 | 30 | 6 | 0
2029 | 2008 | 8 | 30 | 7 | 0
2029 | 2008 | 8 | 30 | 8 | 1810.7571
2029 | 2008 | 8 | 30 | 9 | 20010.8831
2029 | 2008 | 8 | 30 | 10 | 36502.7446
2029 | 2008 | 8 | 30 | 11 | 44579.11
2029 | 2008 | 8 | 30 | 12 | 46553.4403
2029 | 2008 | 8 | 30 | 13 | 45520.7296
2029 | 2008 | 8 | 30 | 14 | 46668.3029
2029 | 2008 | 8 | 30 | 15 | 42518.3122
2029 | 2008 | 8 | 30 | 16 | 41105.8208
2029 | 2008 | 8 | 30 | 17 | 37228.7463
2029 | 2008 | 8 | 30 | 18 | 33285.9072
2029 | 2008 | 8 | 30 | 19 | 26004.5031
2029 | 2008 | 8 | 30 | 20 | 5739.3593
2029 | 2008 | 8 | 30 | 21 | 0
2029 | 2008 | 8 | 30 | 22 | 0
2029 | 2008 | 8 | 30 | 23 | 0
2029 | 2008 | 8 | 30 | 24 | 0
2029 | 2008 | 8 | 31 | 1 | 0
2029 | 2008 | 8 | 31 | 2 | 0
2029 | 2008 | 8 | 31 | 3 | 0
2029 | 2008 | 8 | 31 | 4 | 0
2029 | 2008 | 8 | 31 | 5 | 0
2029 | 2008 | 8 | 31 | 6 | 0
2029 | 2008 | 8 | 31 | 7 | 0
2029 | 2008 | 8 | 31 | 8 | 1747.8826
2029 | 2008 | 8 | 31 | 9 | 21160.0862
2029 | 2008 | 8 | 31 | 10 | 39879.7853
2029 | 2008 | 8 | 31 | 11 | 48107.0693
2029 | 2008 | 8 | 31 | 12 | 50222.6675
2029 | 2008 | 8 | 31 | 13 | 49961.4161
2029 | 2008 | 8 | 31 | 14 | 50260.4276
2029 | 2008 | 8 | 31 | 15 | 48029.3028
2029 | 2008 | 8 | 31 | 16 | 46318.2735
2029 | 2008 | 8 | 31 | 17 | 44451.7718
2029 | 2008 | 8 | 31 | 18 | 39606.1549
2029 | 2008 | 8 | 31 | 19 | 26261.4801
2029 | 2008 | 8 | 31 | 20 | 5163.3176
2029 | 2008 | 8 | 31 | 21 | 0
2029 | 2008 | 8 | 31 | 22 | 0
2029 | 2008 | 8 | 31 | 23 | 0
2029 | 2008 | 8 | 31 | 24 | 0
2030 | 2008 | 8 | 1 | 1 | 0
2030 | 2008 | 8 | 1 | 2 | 0
2030 | 2008 | 8 | 1 | 3 | 0
2030 | 2008 | 8 | 1 | 4 | 0
2030 | 2008 | 8 | 1 | 5 | 0
2030 | 2008 | 8 | 1 | 6 | 0
2030 | 2008 | 8 | 1 | 7 | 2.4214
2030 | 2008 | 8 | 1 | 8 | 4775.8161
2030 | 2008 | 8 | 1 | 9 | 21204.0745
2030 | 2008 | 8 | 1 | 10 | 38824.1292
2030 | 2008 | 8 | 1 | 11 | 47584.5304
2030 | 2008 | 8 | 1 | 12 | 51269.9672
2030 | 2008 | 8 | 1 | 13 | 52692.6289
2030 | 2008 | 8 | 1 | 14 | 51521.8806
2030 | 2008 | 8 | 1 | 15 | 49419.6182
2030 | 2008 | 8 | 1 | 16 | 46702.1033
2030 | 2008 | 8 | 1 | 17 | 43160.317
2030 | 2008 | 8 | 1 | 18 | 39384.5806
2030 | 2008 | 8 | 1 | 19 | 32336.3624
2030 | 2008 | 8 | 1 | 20 | 11645.9834
2030 | 2008 | 8 | 1 | 21 | 475.7313
2030 | 2008 | 8 | 1 | 22 | 0
2030 | 2008 | 8 | 1 | 23 | 0
2030 | 2008 | 8 | 1 | 24 | 0
2030 | 2008 | 8 | 2 | 1 | 0
2030 | 2008 | 8 | 2 | 2 | 0
2030 | 2008 | 8 | 2 | 3 | 0
2030 | 2008 | 8 | 2 | 4 | 0
2030 | 2008 | 8 | 2 | 5 | 0
2030 | 2008 | 8 | 2 | 6 | 0
2030 | 2008 | 8 | 2 | 7 | 2.0632
2030 | 2008 | 8 | 2 | 8 | 4870.734
2030 | 2008 | 8 | 2 | 9 | 20226.6693
2030 | 2008 | 8 | 2 | 10 | 39529.3496
2030 | 2008 | 8 | 2 | 11 | 50312.2232
2030 | 2008 | 8 | 2 | 12 | 53125.1238
2030 | 2008 | 8 | 2 | 13 | 51938.2022
2030 | 2008 | 8 | 2 | 14 | 53357.9905
2030 | 2008 | 8 | 2 | 15 | 52436.7774
2030 | 2008 | 8 | 2 | 16 | 51880.9041
2030 | 2008 | 8 | 2 | 17 | 47929.0194
2030 | 2008 | 8 | 2 | 18 | 44287.0952
2030 | 2008 | 8 | 2 | 19 | 33320.5697
2030 | 2008 | 8 | 2 | 20 | 10566.0297
2030 | 2008 | 8 | 2 | 21 | 295.6474
2030 | 2008 | 8 | 2 | 22 | 0
2030 | 2008 | 8 | 2 | 23 | 0
2030 | 2008 | 8 | 2 | 24 | 0
2030 | 2008 | 8 | 3 | 1 | 0
2030 | 2008 | 8 | 3 | 2 | 0
2030 | 2008 | 8 | 3 | 3 | 0
2030 | 2008 | 8 | 3 | 4 | 0
2030 | 2008 | 8 | 3 | 5 | 0
2030 | 2008 | 8 | 3 | 6 | 0
2030 | 2008 | 8 | 3 | 7 | 2.9932
2030 | 2008 | 8 | 3 | 8 | 4814.5959
2030 | 2008 | 8 | 3 | 9 | 23445.6261
2030 | 2008 | 8 | 3 | 10 | 41646.9812
2030 | 2008 | 8 | 3 | 11 | 51269.2848
2030 | 2008 | 8 | 3 | 12 | 54806.2913
2030 | 2008 | 8 | 3 | 13 | 54353.7392
2030 | 2008 | 8 | 3 | 14 | 54765.6787
2030 | 2008 | 8 | 3 | 15 | 53082.2506
2030 | 2008 | 8 | 3 | 16 | 51580.7876
2030 | 2008 | 8 | 3 | 17 | 49631.9236
2030 | 2008 | 8 | 3 | 18 | 45163.3978
2030 | 2008 | 8 | 3 | 19 | 34106.8497
2030 | 2008 | 8 | 3 | 20 | 11308.6319
2030 | 2008 | 8 | 3 | 21 | 139.3918
2030 | 2008 | 8 | 3 | 22 | 0
2030 | 2008 | 8 | 3 | 23 | 0
2030 | 2008 | 8 | 3 | 24 | 0
2030 | 2008 | 8 | 4 | 1 | 0
2030 | 2008 | 8 | 4 | 2 | 0
2030 | 2008 | 8 | 4 | 3 | 0
2030 | 2008 | 8 | 4 | 4 | 0
2030 | 2008 | 8 | 4 | 5 | 0
2030 | 2008 | 8 | 4 | 6 | 0
2030 | 2008 | 8 | 4 | 7 | 1.9784
2030 | 2008 | 8 | 4 | 8 | 5470.9368
2030 | 2008 | 8 | 4 | 9 | 27376.8411
2030 | 2008 | 8 | 4 | 10 | 42500.4223
2030 | 2008 | 8 | 4 | 11 | 51130.0111
2030 | 2008 | 8 | 4 | 12 | 51348.1013
2030 | 2008 | 8 | 4 | 13 | 52408.3163
2030 | 2008 | 8 | 4 | 14 | 51270.4831
2030 | 2008 | 8 | 4 | 15 | 51504.5081
2030 | 2008 | 8 | 4 | 16 | 49714.1215
2030 | 2008 | 8 | 4 | 17 | 47635.2431
2030 | 2008 | 8 | 4 | 18 | 43804.1066
2030 | 2008 | 8 | 4 | 19 | 34194.7361
2030 | 2008 | 8 | 4 | 20 | 10996.4747
2030 | 2008 | 8 | 4 | 21 | 84.92
2030 | 2008 | 8 | 4 | 22 | 0
2030 | 2008 | 8 | 4 | 23 | 0
2030 | 2008 | 8 | 4 | 24 | 0
2030 | 2008 | 8 | 5 | 1 | 0
2030 | 2008 | 8 | 5 | 2 | 0
2030 | 2008 | 8 | 5 | 3 | 0
2030 | 2008 | 8 | 5 | 4 | 0
2030 | 2008 | 8 | 5 | 5 | 0
2030 | 2008 | 8 | 5 | 6 | 0
2030 | 2008 | 8 | 5 | 7 | 0.65143
2030 | 2008 | 8 | 5 | 8 | 6123.8198
2030 | 2008 | 8 | 5 | 9 | 26110.4467
2030 | 2008 | 8 | 5 | 10 | 43781.1067
2030 | 2008 | 8 | 5 | 11 | 46991.2627
2030 | 2008 | 8 | 5 | 12 | 48550.0703
2030 | 2008 | 8 | 5 | 13 | 51014.8592
2030 | 2008 | 8 | 5 | 14 | 49170.2477
2030 | 2008 | 8 | 5 | 15 | 44788.3344
2030 | 2008 | 8 | 5 | 16 | 39928.9747
2030 | 2008 | 8 | 5 | 17 | 35812.7605
2030 | 2008 | 8 | 5 | 18 | 34030.4133
2030 | 2008 | 8 | 5 | 19 | 29072.6685
2030 | 2008 | 8 | 5 | 20 | 10924.1416
2030 | 2008 | 8 | 5 | 21 | 77.548
2030 | 2008 | 8 | 5 | 22 | 0
2030 | 2008 | 8 | 5 | 23 | 0
2030 | 2008 | 8 | 5 | 24 | 0
2030 | 2008 | 8 | 6 | 1 | 0
2030 | 2008 | 8 | 6 | 2 | 0
2030 | 2008 | 8 | 6 | 3 | 0
2030 | 2008 | 8 | 6 | 4 | 0
2030 | 2008 | 8 | 6 | 5 | 0
2030 | 2008 | 8 | 6 | 6 | 0
2030 | 2008 | 8 | 6 | 7 | 0.044932
2030 | 2008 | 8 | 6 | 8 | 3368.1613
2030 | 2008 | 8 | 6 | 9 | 19601.1791
2030 | 2008 | 8 | 6 | 10 | 36366.5361
2030 | 2008 | 8 | 6 | 11 | 40195.3611
2030 | 2008 | 8 | 6 | 12 | 44527.5709
2030 | 2008 | 8 | 6 | 13 | 43998.9154
2030 | 2008 | 8 | 6 | 14 | 43532.5748
2030 | 2008 | 8 | 6 | 15 | 42788.2991
2030 | 2008 | 8 | 6 | 16 | 39324.63
2030 | 2008 | 8 | 6 | 17 | 35444.9859
2030 | 2008 | 8 | 6 | 18 | 33934.7887
2030 | 2008 | 8 | 6 | 19 | 28303.3261
2030 | 2008 | 8 | 6 | 20 | 10192.7942
2030 | 2008 | 8 | 6 | 21 | 66.4362
2030 | 2008 | 8 | 6 | 22 | 0
2030 | 2008 | 8 | 6 | 23 | 0
2030 | 2008 | 8 | 6 | 24 | 0
2030 | 2008 | 8 | 7 | 1 | 0
2030 | 2008 | 8 | 7 | 2 | 0
2030 | 2008 | 8 | 7 | 3 | 0
2030 | 2008 | 8 | 7 | 4 | 0
2030 | 2008 | 8 | 7 | 5 | 0
2030 | 2008 | 8 | 7 | 6 | 0
2030 | 2008 | 8 | 7 | 7 | 0.20704
2030 | 2008 | 8 | 7 | 8 | 3315.0422
2030 | 2008 | 8 | 7 | 9 | 17491.434
2030 | 2008 | 8 | 7 | 10 | 32741.0111
2030 | 2008 | 8 | 7 | 11 | 44392.6544
2030 | 2008 | 8 | 7 | 12 | 49873.005
2030 | 2008 | 8 | 7 | 13 | 51050.1107
2030 | 2008 | 8 | 7 | 14 | 50244.383
2030 | 2008 | 8 | 7 | 15 | 49186.2543
2030 | 2008 | 8 | 7 | 16 | 48261.0933
2030 | 2008 | 8 | 7 | 17 | 46334.2347
2030 | 2008 | 8 | 7 | 18 | 40561.5961
2030 | 2008 | 8 | 7 | 19 | 31535.4432
2030 | 2008 | 8 | 7 | 20 | 10242.3993
2030 | 2008 | 8 | 7 | 21 | 33.2623
2030 | 2008 | 8 | 7 | 22 | 0
2030 | 2008 | 8 | 7 | 23 | 0
2030 | 2008 | 8 | 7 | 24 | 0
2030 | 2008 | 8 | 8 | 1 | 0
2030 | 2008 | 8 | 8 | 2 | 0
2030 | 2008 | 8 | 8 | 3 | 0
2030 | 2008 | 8 | 8 | 4 | 0
2030 | 2008 | 8 | 8 | 5 | 0
2030 | 2008 | 8 | 8 | 6 | 0
2030 | 2008 | 8 | 8 | 7 | 0.0076014
2030 | 2008 | 8 | 8 | 8 | 3559.8156
2030 | 2008 | 8 | 8 | 9 | 22591.8448
2030 | 2008 | 8 | 8 | 10 | 40720.0894
2030 | 2008 | 8 | 8 | 11 | 47455.743
2030 | 2008 | 8 | 8 | 12 | 47572.0881
2030 | 2008 | 8 | 8 | 13 | 50713.2682
2030 | 2008 | 8 | 8 | 14 | 50992.9608
2030 | 2008 | 8 | 8 | 15 | 49715.3945
2030 | 2008 | 8 | 8 | 16 | 48028.8828
2030 | 2008 | 8 | 8 | 17 | 43757.8968
2030 | 2008 | 8 | 8 | 18 | 39673.4983
2030 | 2008 | 8 | 8 | 19 | 31750.6996
2030 | 2008 | 8 | 8 | 20 | 10925.7965
2030 | 2008 | 8 | 8 | 21 | 26.1682
2030 | 2008 | 8 | 8 | 22 | 0
2030 | 2008 | 8 | 8 | 23 | 0
2030 | 2008 | 8 | 8 | 24 | 0
2030 | 2008 | 8 | 9 | 1 | 0
2030 | 2008 | 8 | 9 | 2 | 0
2030 | 2008 | 8 | 9 | 3 | 0
2030 | 2008 | 8 | 9 | 4 | 0
2030 | 2008 | 8 | 9 | 5 | 0
2030 | 2008 | 8 | 9 | 6 | 0
2030 | 2008 | 8 | 9 | 7 | 0.045975
2030 | 2008 | 8 | 9 | 8 | 3131.2084
2030 | 2008 | 8 | 9 | 9 | 21618.5811
2030 | 2008 | 8 | 9 | 10 | 38598.2405
2030 | 2008 | 8 | 9 | 11 | 45261.7258
2030 | 2008 | 8 | 9 | 12 | 48026.687
2030 | 2008 | 8 | 9 | 13 | 48044.4774
2030 | 2008 | 8 | 9 | 14 | 46060.3347
2030 | 2008 | 8 | 9 | 15 | 42869.5642
2030 | 2008 | 8 | 9 | 16 | 39736.799
2030 | 2008 | 8 | 9 | 17 | 38773.9099
2030 | 2008 | 8 | 9 | 18 | 36949.2081
2030 | 2008 | 8 | 9 | 19 | 31150.6663
2030 | 2008 | 8 | 9 | 20 | 10423.7097
2030 | 2008 | 8 | 9 | 21 | 0
2030 | 2008 | 8 | 9 | 22 | 0
2030 | 2008 | 8 | 9 | 23 | 0
2030 | 2008 | 8 | 9 | 24 | 0
2030 | 2008 | 8 | 10 | 1 | 0
2030 | 2008 | 8 | 10 | 2 | 0
2030 | 2008 | 8 | 10 | 3 | 0
2030 | 2008 | 8 | 10 | 4 | 0
2030 | 2008 | 8 | 10 | 5 | 0
2030 | 2008 | 8 | 10 | 6 | 0
2030 | 2008 | 8 | 10 | 7 | 0.3285
2030 | 2008 | 8 | 10 | 8 | 2724.6942
2030 | 2008 | 8 | 10 | 9 | 19916.7938
2030 | 2008 | 8 | 10 | 10 | 39475.8276
2030 | 2008 | 8 | 10 | 11 | 46480.8182
2030 | 2008 | 8 | 10 | 12 | 50007.6812
2030 | 2008 | 8 | 10 | 13 | 52000.6979
2030 | 2008 | 8 | 10 | 14 | 51074.8815
2030 | 2008 | 8 | 10 | 15 | 50567.7032
2030 | 2008 | 8 | 10 | 16 | 48453.9102
2030 | 2008 | 8 | 10 | 17 | 44389.2745
2030 | 2008 | 8 | 10 | 18 | 37816.1862
2030 | 2008 | 8 | 10 | 19 | 29992.0959
2030 | 2008 | 8 | 10 | 20 | 9320.3022
2030 | 2008 | 8 | 10 | 21 | 0
2030 | 2008 | 8 | 10 | 22 | 0
2030 | 2008 | 8 | 10 | 23 | 0
2030 | 2008 | 8 | 10 | 24 | 0
2030 | 2008 | 8 | 11 | 1 | 0
2030 | 2008 | 8 | 11 | 2 | 0
2030 | 2008 | 8 | 11 | 3 | 0
2030 | 2008 | 8 | 11 | 4 | 0
2030 | 2008 | 8 | 11 | 5 | 0
2030 | 2008 | 8 | 11 | 6 | 0
2030 | 2008 | 8 | 11 | 7 | 0
2030 | 2008 | 8 | 11 | 8 | 1979.1285
2030 | 2008 | 8 | 11 | 9 | 15909.9093
2030 | 2008 | 8 | 11 | 10 | 29500.5708
2030 | 2008 | 8 | 11 | 11 | 40156.179
2030 | 2008 | 8 | 11 | 12 | 45324.6697
2030 | 2008 | 8 | 11 | 13 | 44460.5781
2030 | 2008 | 8 | 11 | 14 | 43886.6934
2030 | 2008 | 8 | 11 | 15 | 41825.552
2030 | 2008 | 8 | 11 | 16 | 39705.2518
2030 | 2008 | 8 | 11 | 17 | 35645.346
2030 | 2008 | 8 | 11 | 18 | 33547.1931
2030 | 2008 | 8 | 11 | 19 | 28081.1023
2030 | 2008 | 8 | 11 | 20 | 9393.633
2030 | 2008 | 8 | 11 | 21 | 0
2030 | 2008 | 8 | 11 | 22 | 0
2030 | 2008 | 8 | 11 | 23 | 0
2030 | 2008 | 8 | 11 | 24 | 0
2030 | 2008 | 8 | 12 | 1 | 0
2030 | 2008 | 8 | 12 | 2 | 0
2030 | 2008 | 8 | 12 | 3 | 0
2030 | 2008 | 8 | 12 | 4 | 0
2030 | 2008 | 8 | 12 | 5 | 0
2030 | 2008 | 8 | 12 | 6 | 0
2030 | 2008 | 8 | 12 | 7 | 0.0022535
2030 | 2008 | 8 | 12 | 8 | 976.929
2030 | 2008 | 8 | 12 | 9 | 9545.3787
2030 | 2008 | 8 | 12 | 10 | 25335.9654
2030 | 2008 | 8 | 12 | 11 | 37493.6697
2030 | 2008 | 8 | 12 | 12 | 45684.3364
2030 | 2008 | 8 | 12 | 13 | 48601.4701
2030 | 2008 | 8 | 12 | 14 | 49411.015
2030 | 2008 | 8 | 12 | 15 | 47290.8377
2030 | 2008 | 8 | 12 | 16 | 45718.0454
2030 | 2008 | 8 | 12 | 17 | 42394.6819
2030 | 2008 | 8 | 12 | 18 | 39124.3391
2030 | 2008 | 8 | 12 | 19 | 31045.7019
2030 | 2008 | 8 | 12 | 20 | 10226.3664
2030 | 2008 | 8 | 12 | 21 | 0
2030 | 2008 | 8 | 12 | 22 | 0
2030 | 2008 | 8 | 12 | 23 | 0
2030 | 2008 | 8 | 12 | 24 | 0
2030 | 2008 | 8 | 13 | 1 | 0
2030 | 2008 | 8 | 13 | 2 | 0
2030 | 2008 | 8 | 13 | 3 | 0
2030 | 2008 | 8 | 13 | 4 | 0
2030 | 2008 | 8 | 13 | 5 | 0
2030 | 2008 | 8 | 13 | 6 | 0
2030 | 2008 | 8 | 13 | 7 | 0.064221
2030 | 2008 | 8 | 13 | 8 | 5012.0605
2030 | 2008 | 8 | 13 | 9 | 24112.3174
2030 | 2008 | 8 | 13 | 10 | 43186.3495
2030 | 2008 | 8 | 13 | 11 | 48664.7936
2030 | 2008 | 8 | 13 | 12 | 51762.2627
2030 | 2008 | 8 | 13 | 13 | 49128.4117
2030 | 2008 | 8 | 13 | 14 | 50087.8558
2030 | 2008 | 8 | 13 | 15 | 48550.8253
2030 | 2008 | 8 | 13 | 16 | 48356.1639
2030 | 2008 | 8 | 13 | 17 | 45980.0908
2030 | 2008 | 8 | 13 | 18 | 41747.6259
2030 | 2008 | 8 | 13 | 19 | 31326.7783
2030 | 2008 | 8 | 13 | 20 | 10832.616
2030 | 2008 | 8 | 13 | 21 | 0
2030 | 2008 | 8 | 13 | 22 | 0
2030 | 2008 | 8 | 13 | 23 | 0
2030 | 2008 | 8 | 13 | 24 | 0
2030 | 2008 | 8 | 14 | 1 | 0
2030 | 2008 | 8 | 14 | 2 | 0
2030 | 2008 | 8 | 14 | 3 | 0
2030 | 2008 | 8 | 14 | 4 | 0
2030 | 2008 | 8 | 14 | 5 | 0
2030 | 2008 | 8 | 14 | 6 | 0
2030 | 2008 | 8 | 14 | 7 | 0.0029843
2030 | 2008 | 8 | 14 | 8 | 3193.1273
2030 | 2008 | 8 | 14 | 9 | 22464.1089
2030 | 2008 | 8 | 14 | 10 | 39163.8217
2030 | 2008 | 8 | 14 | 11 | 46591.5093
2030 | 2008 | 8 | 14 | 12 | 48293.4398
2030 | 2008 | 8 | 14 | 13 | 51260.3883
2030 | 2008 | 8 | 14 | 14 | 50458.3217
2030 | 2008 | 8 | 14 | 15 | 49438.0391
2030 | 2008 | 8 | 14 | 16 | 46837.1556
2030 | 2008 | 8 | 14 | 17 | 45614.9784
2030 | 2008 | 8 | 14 | 18 | 42533.3302
2030 | 2008 | 8 | 14 | 19 | 32771.0416
2030 | 2008 | 8 | 14 | 20 | 11594.2333
2030 | 2008 | 8 | 14 | 21 | 0
2030 | 2008 | 8 | 14 | 22 | 0
2030 | 2008 | 8 | 14 | 23 | 0
2030 | 2008 | 8 | 14 | 24 | 0
2030 | 2008 | 8 | 15 | 1 | 0
2030 | 2008 | 8 | 15 | 2 | 0
2030 | 2008 | 8 | 15 | 3 | 0
2030 | 2008 | 8 | 15 | 4 | 0
2030 | 2008 | 8 | 15 | 5 | 0
2030 | 2008 | 8 | 15 | 6 | 0
2030 | 2008 | 8 | 15 | 7 | 0.018889
2030 | 2008 | 8 | 15 | 8 | 2090.1577
2030 | 2008 | 8 | 15 | 9 | 20534.4308
2030 | 2008 | 8 | 15 | 10 | 33821.8944
2030 | 2008 | 8 | 15 | 11 | 44017.0741
2030 | 2008 | 8 | 15 | 12 | 49652.0635
2030 | 2008 | 8 | 15 | 13 | 51235.3858
2030 | 2008 | 8 | 15 | 14 | 48723.596
2030 | 2008 | 8 | 15 | 15 | 48728.1569
2030 | 2008 | 8 | 15 | 16 | 48402.1781
2030 | 2008 | 8 | 15 | 17 | 46376.971
2030 | 2008 | 8 | 15 | 18 | 41636.9549
2030 | 2008 | 8 | 15 | 19 | 32719.712
2030 | 2008 | 8 | 15 | 20 | 9653.2546
2030 | 2008 | 8 | 15 | 21 | 0
2030 | 2008 | 8 | 15 | 22 | 0
2030 | 2008 | 8 | 15 | 23 | 0
2030 | 2008 | 8 | 15 | 24 | 0
2030 | 2008 | 8 | 16 | 1 | 0
2030 | 2008 | 8 | 16 | 2 | 0
2030 | 2008 | 8 | 16 | 3 | 0
2030 | 2008 | 8 | 16 | 4 | 0
2030 | 2008 | 8 | 16 | 5 | 0
2030 | 2008 | 8 | 16 | 6 | 0
2030 | 2008 | 8 | 16 | 7 | 0
2030 | 2008 | 8 | 16 | 8 | 1977.0465
2030 | 2008 | 8 | 16 | 9 | 14288.8718
2030 | 2008 | 8 | 16 | 10 | 30238.3716
2030 | 2008 | 8 | 16 | 11 | 37467.102
2030 | 2008 | 8 | 16 | 12 | 38993.6586
2030 | 2008 | 8 | 16 | 13 | 40416.882
2030 | 2008 | 8 | 16 | 14 | 39755.2
2030 | 2008 | 8 | 16 | 15 | 38398.6854
2030 | 2008 | 8 | 16 | 16 | 35668.2136
2030 | 2008 | 8 | 16 | 17 | 35808.4975
2030 | 2008 | 8 | 16 | 18 | 33972.4767
2030 | 2008 | 8 | 16 | 19 | 28967.9151
2030 | 2008 | 8 | 16 | 20 | 9974.7166
2030 | 2008 | 8 | 16 | 21 | 0
2030 | 2008 | 8 | 16 | 22 | 0
2030 | 2008 | 8 | 16 | 23 | 0
2030 | 2008 | 8 | 16 | 24 | 0
2030 | 2008 | 8 | 17 | 1 | 0
2030 | 2008 | 8 | 17 | 2 | 0
2030 | 2008 | 8 | 17 | 3 | 0
2030 | 2008 | 8 | 17 | 4 | 0
2030 | 2008 | 8 | 17 | 5 | 0
2030 | 2008 | 8 | 17 | 6 | 0
2030 | 2008 | 8 | 17 | 7 | 0
2030 | 2008 | 8 | 17 | 8 | 1402.5413
2030 | 2008 | 8 | 17 | 9 | 13822.7314
2030 | 2008 | 8 | 17 | 10 | 29636.3331
2030 | 2008 | 8 | 17 | 11 | 36012.1046
2030 | 2008 | 8 | 17 | 12 | 38655.3485
2030 | 2008 | 8 | 17 | 13 | 39140.2452
2030 | 2008 | 8 | 17 | 14 | 37094.3495
2030 | 2008 | 8 | 17 | 15 | 35204.3654
2030 | 2008 | 8 | 17 | 16 | 32051.1034
2030 | 2008 | 8 | 17 | 17 | 30287.128
2030 | 2008 | 8 | 17 | 18 | 28488.5474
2030 | 2008 | 8 | 17 | 19 | 25741.0533
2030 | 2008 | 8 | 17 | 20 | 8875.7007
2030 | 2008 | 8 | 17 | 21 | 0
2030 | 2008 | 8 | 17 | 22 | 0
2030 | 2008 | 8 | 17 | 23 | 0
2030 | 2008 | 8 | 17 | 24 | 0
2030 | 2008 | 8 | 18 | 1 | 0
2030 | 2008 | 8 | 18 | 2 | 0
2030 | 2008 | 8 | 18 | 3 | 0
2030 | 2008 | 8 | 18 | 4 | 0
2030 | 2008 | 8 | 18 | 5 | 0
2030 | 2008 | 8 | 18 | 6 | 0
2030 | 2008 | 8 | 18 | 7 | 0
2030 | 2008 | 8 | 18 | 8 | 1064.3363
2030 | 2008 | 8 | 18 | 9 | 12007.5144
2030 | 2008 | 8 | 18 | 10 | 23304.4764
2030 | 2008 | 8 | 18 | 11 | 31535.9605
2030 | 2008 | 8 | 18 | 12 | 37829.8512
2030 | 2008 | 8 | 18 | 13 | 39909.8234
2030 | 2008 | 8 | 18 | 14 | 40072.4001
2030 | 2008 | 8 | 18 | 15 | 37081.7101
2030 | 2008 | 8 | 18 | 16 | 33452.9701
2030 | 2008 | 8 | 18 | 17 | 30108.3911
2030 | 2008 | 8 | 18 | 18 | 29159.5632
2030 | 2008 | 8 | 18 | 19 | 25107.5639
2030 | 2008 | 8 | 18 | 20 | 8722.6332
2030 | 2008 | 8 | 18 | 21 | 0
2030 | 2008 | 8 | 18 | 22 | 0
2030 | 2008 | 8 | 18 | 23 | 0
2030 | 2008 | 8 | 18 | 24 | 0
2030 | 2008 | 8 | 19 | 1 | 0
2030 | 2008 | 8 | 19 | 2 | 0
2030 | 2008 | 8 | 19 | 3 | 0
2030 | 2008 | 8 | 19 | 4 | 0
2030 | 2008 | 8 | 19 | 5 | 0
2030 | 2008 | 8 | 19 | 6 | 0
2030 | 2008 | 8 | 19 | 7 | 0
2030 | 2008 | 8 | 19 | 8 | 1218.8171
2030 | 2008 | 8 | 19 | 9 | 12515.2721
2030 | 2008 | 8 | 19 | 10 | 26647.6512
2030 | 2008 | 8 | 19 | 11 | 34603.8252
2030 | 2008 | 8 | 19 | 12 | 39429.0015
2030 | 2008 | 8 | 19 | 13 | 40793.6547
2030 | 2008 | 8 | 19 | 14 | 40803.4019
2030 | 2008 | 8 | 19 | 15 | 39405.8818
2030 | 2008 | 8 | 19 | 16 | 37257.0786
2030 | 2008 | 8 | 19 | 17 | 34413.2956
2030 | 2008 | 8 | 19 | 18 | 32727.5715
2030 | 2008 | 8 | 19 | 19 | 28053.1155
2030 | 2008 | 8 | 19 | 20 | 9759.9616
2030 | 2008 | 8 | 19 | 21 | 0
2030 | 2008 | 8 | 19 | 22 | 0
2030 | 2008 | 8 | 19 | 23 | 0
2030 | 2008 | 8 | 19 | 24 | 0
2030 | 2008 | 8 | 20 | 1 | 0
2030 | 2008 | 8 | 20 | 2 | 0
2030 | 2008 | 8 | 20 | 3 | 0
2030 | 2008 | 8 | 20 | 4 | 0
2030 | 2008 | 8 | 20 | 5 | 0
2030 | 2008 | 8 | 20 | 6 | 0
2030 | 2008 | 8 | 20 | 7 | 0
2030 | 2008 | 8 | 20 | 8 | 941.7203
2030 | 2008 | 8 | 20 | 9 | 13148.7679
2030 | 2008 | 8 | 20 | 10 | 29656.1418
2030 | 2008 | 8 | 20 | 11 | 38913.2458
2030 | 2008 | 8 | 20 | 12 | 45085.0913
2030 | 2008 | 8 | 20 | 13 | 44698.3651
2030 | 2008 | 8 | 20 | 14 | 44072.9065
2030 | 2008 | 8 | 20 | 15 | 43126.168
2030 | 2008 | 8 | 20 | 16 | 43242.1199
2030 | 2008 | 8 | 20 | 17 | 40588.0293
2030 | 2008 | 8 | 20 | 18 | 38888.1844
2030 | 2008 | 8 | 20 | 19 | 29866.1853
2030 | 2008 | 8 | 20 | 20 | 9615.8462
2030 | 2008 | 8 | 20 | 21 | 0
2030 | 2008 | 8 | 20 | 22 | 0
2030 | 2008 | 8 | 20 | 23 | 0
2030 | 2008 | 8 | 20 | 24 | 0
2030 | 2008 | 8 | 21 | 1 | 0
2030 | 2008 | 8 | 21 | 2 | 0
2030 | 2008 | 8 | 21 | 3 | 0
2030 | 2008 | 8 | 21 | 4 | 0
2030 | 2008 | 8 | 21 | 5 | 0
2030 | 2008 | 8 | 21 | 6 | 0
2030 | 2008 | 8 | 21 | 7 | 0
2030 | 2008 | 8 | 21 | 8 | 1044.7548
2030 | 2008 | 8 | 21 | 9 | 16047.2105
2030 | 2008 | 8 | 21 | 10 | 34787.9967
2030 | 2008 | 8 | 21 | 11 | 39313.9249
2030 | 2008 | 8 | 21 | 12 | 45370.8905
2030 | 2008 | 8 | 21 | 13 | 47028.9648
2030 | 2008 | 8 | 21 | 14 | 46311.7803
2030 | 2008 | 8 | 21 | 15 | 44121.0188
2030 | 2008 | 8 | 21 | 16 | 45059.6849
2030 | 2008 | 8 | 21 | 17 | 43404.5134
2030 | 2008 | 8 | 21 | 18 | 36185.4899
2030 | 2008 | 8 | 21 | 19 | 30462.4031
2030 | 2008 | 8 | 21 | 20 | 9336.1091
2030 | 2008 | 8 | 21 | 21 | 0
2030 | 2008 | 8 | 21 | 22 | 0
2030 | 2008 | 8 | 21 | 23 | 0
2030 | 2008 | 8 | 21 | 24 | 0
2030 | 2008 | 8 | 22 | 1 | 0
2030 | 2008 | 8 | 22 | 2 | 0
2030 | 2008 | 8 | 22 | 3 | 0
2030 | 2008 | 8 | 22 | 4 | 0
2030 | 2008 | 8 | 22 | 5 | 0
2030 | 2008 | 8 | 22 | 6 | 0
2030 | 2008 | 8 | 22 | 7 | 0
2030 | 2008 | 8 | 22 | 8 | 1505.9616
2030 | 2008 | 8 | 22 | 9 | 16588.4778
2030 | 2008 | 8 | 22 | 10 | 30244.6723
2030 | 2008 | 8 | 22 | 11 | 40085.6444
2030 | 2008 | 8 | 22 | 12 | 45405.3738
2030 | 2008 | 8 | 22 | 13 | 48725.6658
2030 | 2008 | 8 | 22 | 14 | 47629.0425
2030 | 2008 | 8 | 22 | 15 | 43380.3354
2030 | 2008 | 8 | 22 | 16 | 43514.4269
2030 | 2008 | 8 | 22 | 17 | 39163.487
2030 | 2008 | 8 | 22 | 18 | 35606.048
2030 | 2008 | 8 | 22 | 19 | 27680.8286
2030 | 2008 | 8 | 22 | 20 | 8578.7153
2030 | 2008 | 8 | 22 | 21 | 0
2030 | 2008 | 8 | 22 | 22 | 0
2030 | 2008 | 8 | 22 | 23 | 0
2030 | 2008 | 8 | 22 | 24 | 0
2030 | 2008 | 8 | 23 | 1 | 0
2030 | 2008 | 8 | 23 | 2 | 0
2030 | 2008 | 8 | 23 | 3 | 0
2030 | 2008 | 8 | 23 | 4 | 0
2030 | 2008 | 8 | 23 | 5 | 0
2030 | 2008 | 8 | 23 | 6 | 0
2030 | 2008 | 8 | 23 | 7 | 0
2030 | 2008 | 8 | 23 | 8 | 2669.3106
2030 | 2008 | 8 | 23 | 9 | 21903.7304
2030 | 2008 | 8 | 23 | 10 | 39052.5706
2030 | 2008 | 8 | 23 | 11 | 42796.0233
2030 | 2008 | 8 | 23 | 12 | 46086.7135
2030 | 2008 | 8 | 23 | 13 | 45528.8807
2030 | 2008 | 8 | 23 | 14 | 45086.3937
2030 | 2008 | 8 | 23 | 15 | 42196.2771
2030 | 2008 | 8 | 23 | 16 | 39868.258
2030 | 2008 | 8 | 23 | 17 | 36954.4595
2030 | 2008 | 8 | 23 | 18 | 33853.4105
2030 | 2008 | 8 | 23 | 19 | 27629.4253
2030 | 2008 | 8 | 23 | 20 | 8000.4065
2030 | 2008 | 8 | 23 | 21 | 0
2030 | 2008 | 8 | 23 | 22 | 0
2030 | 2008 | 8 | 23 | 23 | 0
2030 | 2008 | 8 | 23 | 24 | 0
2030 | 2008 | 8 | 24 | 1 | 0
2030 | 2008 | 8 | 24 | 2 | 0
2030 | 2008 | 8 | 24 | 3 | 0
2030 | 2008 | 8 | 24 | 4 | 0
2030 | 2008 | 8 | 24 | 5 | 0
2030 | 2008 | 8 | 24 | 6 | 0
2030 | 2008 | 8 | 24 | 7 | 0
2030 | 2008 | 8 | 24 | 8 | 2519.2191
2030 | 2008 | 8 | 24 | 9 | 21121.2375
2030 | 2008 | 8 | 24 | 10 | 36906.7808
2030 | 2008 | 8 | 24 | 11 | 42004.0516
2030 | 2008 | 8 | 24 | 12 | 45415.7857
2030 | 2008 | 8 | 24 | 13 | 45711.6082
2030 | 2008 | 8 | 24 | 14 | 44295.0174
2030 | 2008 | 8 | 24 | 15 | 44979.2163
2030 | 2008 | 8 | 24 | 16 | 40950.0516
2030 | 2008 | 8 | 24 | 17 | 39896.009
2030 | 2008 | 8 | 24 | 18 | 36834.595
2030 | 2008 | 8 | 24 | 19 | 28846.0475
2030 | 2008 | 8 | 24 | 20 | 8343.1564
2030 | 2008 | 8 | 24 | 21 | 0
2030 | 2008 | 8 | 24 | 22 | 0
2030 | 2008 | 8 | 24 | 23 | 0
2030 | 2008 | 8 | 24 | 24 | 0
2030 | 2008 | 8 | 25 | 1 | 0
2030 | 2008 | 8 | 25 | 2 | 0
2030 | 2008 | 8 | 25 | 3 | 0
2030 | 2008 | 8 | 25 | 4 | 0
2030 | 2008 | 8 | 25 | 5 | 0
2030 | 2008 | 8 | 25 | 6 | 0
2030 | 2008 | 8 | 25 | 7 | 0
2030 | 2008 | 8 | 25 | 8 | 2582.858
2030 | 2008 | 8 | 25 | 9 | 23929.0786
2030 | 2008 | 8 | 25 | 10 | 42046.5876
2030 | 2008 | 8 | 25 | 11 | 48273.7333
2030 | 2008 | 8 | 25 | 12 | 50173.2639
2030 | 2008 | 8 | 25 | 13 | 50501.6315
2030 | 2008 | 8 | 25 | 14 | 49412.9233
2030 | 2008 | 8 | 25 | 15 | 47264.8036
2030 | 2008 | 8 | 25 | 16 | 45836.0567
2030 | 2008 | 8 | 25 | 17 | 44940.0693
2030 | 2008 | 8 | 25 | 18 | 40665.7002
2030 | 2008 | 8 | 25 | 19 | 31811.3013
2030 | 2008 | 8 | 25 | 20 | 8680.5322
2030 | 2008 | 8 | 25 | 21 | 0
2030 | 2008 | 8 | 25 | 22 | 0
2030 | 2008 | 8 | 25 | 23 | 0
2030 | 2008 | 8 | 25 | 24 | 0
2030 | 2008 | 8 | 26 | 1 | 0
2030 | 2008 | 8 | 26 | 2 | 0
2030 | 2008 | 8 | 26 | 3 | 0
2030 | 2008 | 8 | 26 | 4 | 0
2030 | 2008 | 8 | 26 | 5 | 0
2030 | 2008 | 8 | 26 | 6 | 0
2030 | 2008 | 8 | 26 | 7 | 0
2030 | 2008 | 8 | 26 | 8 | 3781.9496
2030 | 2008 | 8 | 26 | 9 | 25610.5359
2030 | 2008 | 8 | 26 | 10 | 42884.9296
2030 | 2008 | 8 | 26 | 11 | 48302.1336
2030 | 2008 | 8 | 26 | 12 | 50198.3366
2030 | 2008 | 8 | 26 | 13 | 50652.3378
2030 | 2008 | 8 | 26 | 14 | 47456.7039
2030 | 2008 | 8 | 26 | 15 | 47019.0712
2030 | 2008 | 8 | 26 | 16 | 46393.0488
2030 | 2008 | 8 | 26 | 17 | 44114.9339
2030 | 2008 | 8 | 26 | 18 | 39758.4064
2030 | 2008 | 8 | 26 | 19 | 31091.7535
2030 | 2008 | 8 | 26 | 20 | 7605.7174
2030 | 2008 | 8 | 26 | 21 | 0
2030 | 2008 | 8 | 26 | 22 | 0
2030 | 2008 | 8 | 26 | 23 | 0
2030 | 2008 | 8 | 26 | 24 | 0
2030 | 2008 | 8 | 27 | 1 | 0
2030 | 2008 | 8 | 27 | 2 | 0
2030 | 2008 | 8 | 27 | 3 | 0
2030 | 2008 | 8 | 27 | 4 | 0
2030 | 2008 | 8 | 27 | 5 | 0
2030 | 2008 | 8 | 27 | 6 | 0
2030 | 2008 | 8 | 27 | 7 | 0
2030 | 2008 | 8 | 27 | 8 | 3083.3035
2030 | 2008 | 8 | 27 | 9 | 25764.2281
2030 | 2008 | 8 | 27 | 10 | 41686.5782
2030 | 2008 | 8 | 27 | 11 | 47382.9809
2030 | 2008 | 8 | 27 | 12 | 50259.716
2030 | 2008 | 8 | 27 | 13 | 47474.3584
2030 | 2008 | 8 | 27 | 14 | 47413.2095
2030 | 2008 | 8 | 27 | 15 | 46806.7992
2030 | 2008 | 8 | 27 | 16 | 43468.8494
2030 | 2008 | 8 | 27 | 17 | 41673.9804
2030 | 2008 | 8 | 27 | 18 | 36070.7181
2030 | 2008 | 8 | 27 | 19 | 28104.0707
2030 | 2008 | 8 | 27 | 20 | 6244.7793
2030 | 2008 | 8 | 27 | 21 | 0
2030 | 2008 | 8 | 27 | 22 | 0
2030 | 2008 | 8 | 27 | 23 | 0
2030 | 2008 | 8 | 27 | 24 | 0
2030 | 2008 | 8 | 28 | 1 | 0
2030 | 2008 | 8 | 28 | 2 | 0
2030 | 2008 | 8 | 28 | 3 | 0
2030 | 2008 | 8 | 28 | 4 | 0
2030 | 2008 | 8 | 28 | 5 | 0
2030 | 2008 | 8 | 28 | 6 | 0
2030 | 2008 | 8 | 28 | 7 | 0
2030 | 2008 | 8 | 28 | 8 | 2227.4827
2030 | 2008 | 8 | 28 | 9 | 16711.6724
2030 | 2008 | 8 | 28 | 10 | 31976.5099
2030 | 2008 | 8 | 28 | 11 | 43853.7636
2030 | 2008 | 8 | 28 | 12 | 45091.1734
2030 | 2008 | 8 | 28 | 13 | 46772.2783
2030 | 2008 | 8 | 28 | 14 | 45797.3743
2030 | 2008 | 8 | 28 | 15 | 45003.9212
2030 | 2008 | 8 | 28 | 16 | 40851.5308
2030 | 2008 | 8 | 28 | 17 | 37551.5322
2030 | 2008 | 8 | 28 | 18 | 34062.3746
2030 | 2008 | 8 | 28 | 19 | 28327.0262
2030 | 2008 | 8 | 28 | 20 | 6359.2868
2030 | 2008 | 8 | 28 | 21 | 0
2030 | 2008 | 8 | 28 | 22 | 0
2030 | 2008 | 8 | 28 | 23 | 0
2030 | 2008 | 8 | 28 | 24 | 0
2030 | 2008 | 8 | 29 | 1 | 0
2030 | 2008 | 8 | 29 | 2 | 0
2030 | 2008 | 8 | 29 | 3 | 0
2030 | 2008 | 8 | 29 | 4 | 0
2030 | 2008 | 8 | 29 | 5 | 0
2030 | 2008 | 8 | 29 | 6 | 0
2030 | 2008 | 8 | 29 | 7 | 0
2030 | 2008 | 8 | 29 | 8 | 1959.6528
2030 | 2008 | 8 | 29 | 9 | 16364.1897
2030 | 2008 | 8 | 29 | 10 | 32156.8152
2030 | 2008 | 8 | 29 | 11 | 38562.9474
2030 | 2008 | 8 | 29 | 12 | 41309.1561
2030 | 2008 | 8 | 29 | 13 | 39518.84
2030 | 2008 | 8 | 29 | 14 | 38660.8124
2030 | 2008 | 8 | 29 | 15 | 35501.5343
2030 | 2008 | 8 | 29 | 16 | 33246.2344
2030 | 2008 | 8 | 29 | 17 | 29507.3413
2030 | 2008 | 8 | 29 | 18 | 27196.1344
2030 | 2008 | 8 | 29 | 19 | 23268.7803
2030 | 2008 | 8 | 29 | 20 | 5059.9462
2030 | 2008 | 8 | 29 | 21 | 0
2030 | 2008 | 8 | 29 | 22 | 0
2030 | 2008 | 8 | 29 | 23 | 0
2030 | 2008 | 8 | 29 | 24 | 0
2030 | 2008 | 8 | 30 | 1 | 0
2030 | 2008 | 8 | 30 | 2 | 0
2030 | 2008 | 8 | 30 | 3 | 0
2030 | 2008 | 8 | 30 | 4 | 0
2030 | 2008 | 8 | 30 | 5 | 0
2030 | 2008 | 8 | 30 | 6 | 0
2030 | 2008 | 8 | 30 | 7 | 0
2030 | 2008 | 8 | 30 | 8 | 1810.7571
2030 | 2008 | 8 | 30 | 9 | 20010.8831
2030 | 2008 | 8 | 30 | 10 | 36502.7446
2030 | 2008 | 8 | 30 | 11 | 44579.11
2030 | 2008 | 8 | 30 | 12 | 46553.4403
2030 | 2008 | 8 | 30 | 13 | 45520.7296
2030 | 2008 | 8 | 30 | 14 | 46668.3029
2030 | 2008 | 8 | 30 | 15 | 42518.3122
2030 | 2008 | 8 | 30 | 16 | 41105.8208
2030 | 2008 | 8 | 30 | 17 | 37228.7463
2030 | 2008 | 8 | 30 | 18 | 33285.9072
2030 | 2008 | 8 | 30 | 19 | 26004.5031
2030 | 2008 | 8 | 30 | 20 | 5739.3593
2030 | 2008 | 8 | 30 | 21 | 0
2030 | 2008 | 8 | 30 | 22 | 0
2030 | 2008 | 8 | 30 | 23 | 0
2030 | 2008 | 8 | 30 | 24 | 0
2030 | 2008 | 8 | 31 | 1 | 0
2030 | 2008 | 8 | 31 | 2 | 0
2030 | 2008 | 8 | 31 | 3 | 0
2030 | 2008 | 8 | 31 | 4 | 0
2030 | 2008 | 8 | 31 | 5 | 0
2030 | 2008 | 8 | 31 | 6 | 0
2030 | 2008 | 8 | 31 | 7 | 0
2030 | 2008 | 8 | 31 | 8 | 1747.8826
2030 | 2008 | 8 | 31 | 9 | 21160.0862
2030 | 2008 | 8 | 31 | 10 | 39879.7853
2030 | 2008 | 8 | 31 | 11 | 48107.0693
2030 | 2008 | 8 | 31 | 12 | 50222.6675
2030 | 2008 | 8 | 31 | 13 | 49961.4161
2030 | 2008 | 8 | 31 | 14 | 50260.4276
2030 | 2008 | 8 | 31 | 15 | 48029.3028
2030 | 2008 | 8 | 31 | 16 | 46318.2735
2030 | 2008 | 8 | 31 | 17 | 44451.7718
2030 | 2008 | 8 | 31 | 18 | 39606.1549
2030 | 2008 | 8 | 31 | 19 | 26261.4801
2030 | 2008 | 8 | 31 | 20 | 5163.3176
2030 | 2008 | 8 | 31 | 21 | 0
2030 | 2008 | 8 | 31 | 22 | 0
2030 | 2008 | 8 | 31 | 23 | 0
2030 | 2008 | 8 | 31 | 24 | 0
2026/2027 | 2008 | 1 | 1 | 1 | 0
2026/2027 | 2008 | 1 | 1 | 2 | 0
2026/2027 | 2008 | 1 | 1 | 3 | 0
2026/2027 | 2008 | 1 | 1 | 4 | 0
2026/2027 | 2008 | 1 | 1 | 5 | 0
2026/2027 | 2008 | 1 | 1 | 6 | 0
2026/2027 | 2008 | 1 | 1 | 7 | 0
2026/2027 | 2008 | 1 | 1 | 8 | 32.3932
2026/2027 | 2008 | 1 | 1 | 9 | 11150.1323
2026/2027 | 2008 | 1 | 1 | 10 | 29853.9623
2026/2027 | 2008 | 1 | 1 | 11 | 33717.1894
2026/2027 | 2008 | 1 | 1 | 12 | 33357.2857
2026/2027 | 2008 | 1 | 1 | 13 | 32605.2264
2026/2027 | 2008 | 1 | 1 | 14 | 32556.248
2026/2027 | 2008 | 1 | 1 | 15 | 32759.7777
2026/2027 | 2008 | 1 | 1 | 16 | 28981.3621
2026/2027 | 2008 | 1 | 1 | 17 | 15332.6559
2026/2027 | 2008 | 1 | 1 | 18 | 756.6113
2026/2027 | 2008 | 1 | 1 | 19 | 0
2026/2027 | 2008 | 1 | 1 | 20 | 0
2026/2027 | 2008 | 1 | 1 | 21 | 0
2026/2027 | 2008 | 1 | 1 | 22 | 0
2026/2027 | 2008 | 1 | 1 | 23 | 0
2026/2027 | 2008 | 1 | 1 | 24 | 0
2026/2027 | 2008 | 1 | 2 | 1 | 0
2026/2027 | 2008 | 1 | 2 | 2 | 0
2026/2027 | 2008 | 1 | 2 | 3 | 0
2026/2027 | 2008 | 1 | 2 | 4 | 0
2026/2027 | 2008 | 1 | 2 | 5 | 0
2026/2027 | 2008 | 1 | 2 | 6 | 0
2026/2027 | 2008 | 1 | 2 | 7 | 0
2026/2027 | 2008 | 1 | 2 | 8 | 30.6219
2026/2027 | 2008 | 1 | 2 | 9 | 10187.3082
2026/2027 | 2008 | 1 | 2 | 10 | 27569.3544
2026/2027 | 2008 | 1 | 2 | 11 | 31685.9895
2026/2027 | 2008 | 1 | 2 | 12 | 30386.4455
2026/2027 | 2008 | 1 | 2 | 13 | 30089.576
2026/2027 | 2008 | 1 | 2 | 14 | 28350.9147
2026/2027 | 2008 | 1 | 2 | 15 | 26488.9493
2026/2027 | 2008 | 1 | 2 | 16 | 20367.6981
2026/2027 | 2008 | 1 | 2 | 17 | 13034.0512
2026/2027 | 2008 | 1 | 2 | 18 | 346.0097
2026/2027 | 2008 | 1 | 2 | 19 | 0
2026/2027 | 2008 | 1 | 2 | 20 | 0
2026/2027 | 2008 | 1 | 2 | 21 | 0
2026/2027 | 2008 | 1 | 2 | 22 | 0
2026/2027 | 2008 | 1 | 2 | 23 | 0
2026/2027 | 2008 | 1 | 2 | 24 | 0
2026/2027 | 2008 | 1 | 3 | 1 | 0
2026/2027 | 2008 | 1 | 3 | 2 | 0
2026/2027 | 2008 | 1 | 3 | 3 | 0
2026/2027 | 2008 | 1 | 3 | 4 | 0
2026/2027 | 2008 | 1 | 3 | 5 | 0
2026/2027 | 2008 | 1 | 3 | 6 | 0
2026/2027 | 2008 | 1 | 3 | 7 | 0
2026/2027 | 2008 | 1 | 3 | 8 | 9.0189
2026/2027 | 2008 | 1 | 3 | 9 | 6226.6795
2026/2027 | 2008 | 1 | 3 | 10 | 20294.9224
2026/2027 | 2008 | 1 | 3 | 11 | 22265.6583
2026/2027 | 2008 | 1 | 3 | 12 | 23772.3956
2026/2027 | 2008 | 1 | 3 | 13 | 24212.1834
2026/2027 | 2008 | 1 | 3 | 14 | 23861.2799
2026/2027 | 2008 | 1 | 3 | 15 | 26448.5689
2026/2027 | 2008 | 1 | 3 | 16 | 24247.6358
2026/2027 | 2008 | 1 | 3 | 17 | 13876.7261
2026/2027 | 2008 | 1 | 3 | 18 | 726.5401
2026/2027 | 2008 | 1 | 3 | 19 | 0
2026/2027 | 2008 | 1 | 3 | 20 | 0
2026/2027 | 2008 | 1 | 3 | 21 | 0
2026/2027 | 2008 | 1 | 3 | 22 | 0
2026/2027 | 2008 | 1 | 3 | 23 | 0
2026/2027 | 2008 | 1 | 3 | 24 | 0
2026/2027 | 2008 | 1 | 4 | 1 | 0
2026/2027 | 2008 | 1 | 4 | 2 | 0
2026/2027 | 2008 | 1 | 4 | 3 | 0
2026/2027 | 2008 | 1 | 4 | 4 | 0
2026/2027 | 2008 | 1 | 4 | 5 | 0
2026/2027 | 2008 | 1 | 4 | 6 | 0
2026/2027 | 2008 | 1 | 4 | 7 | 0
2026/2027 | 2008 | 1 | 4 | 8 | 11.2804
2026/2027 | 2008 | 1 | 4 | 9 | 2093.9801
2026/2027 | 2008 | 1 | 4 | 10 | 8463.7248
2026/2027 | 2008 | 1 | 4 | 11 | 11466.2967
2026/2027 | 2008 | 1 | 4 | 12 | 12679.5322
2026/2027 | 2008 | 1 | 4 | 13 | 13139.0066
2026/2027 | 2008 | 1 | 4 | 14 | 12193.7089
2026/2027 | 2008 | 1 | 4 | 15 | 11122.6098
2026/2027 | 2008 | 1 | 4 | 16 | 8295.7258
2026/2027 | 2008 | 1 | 4 | 17 | 5959.4556
2026/2027 | 2008 | 1 | 4 | 18 | 293.8329
2026/2027 | 2008 | 1 | 4 | 19 | 0
2026/2027 | 2008 | 1 | 4 | 20 | 0
2026/2027 | 2008 | 1 | 4 | 21 | 0
2026/2027 | 2008 | 1 | 4 | 22 | 0
2026/2027 | 2008 | 1 | 4 | 23 | 0
2026/2027 | 2008 | 1 | 4 | 24 | 0
2026/2027 | 2008 | 1 | 5 | 1 | 0
2026/2027 | 2008 | 1 | 5 | 2 | 0
2026/2027 | 2008 | 1 | 5 | 3 | 0
2026/2027 | 2008 | 1 | 5 | 4 | 0
2026/2027 | 2008 | 1 | 5 | 5 | 0
2026/2027 | 2008 | 1 | 5 | 6 | 0
2026/2027 | 2008 | 1 | 5 | 7 | 0
2026/2027 | 2008 | 1 | 5 | 8 | 4.3338
2026/2027 | 2008 | 1 | 5 | 9 | 4486.6134
2026/2027 | 2008 | 1 | 5 | 10 | 14268.7462
2026/2027 | 2008 | 1 | 5 | 11 | 17656.4806
2026/2027 | 2008 | 1 | 5 | 12 | 19657.5806
2026/2027 | 2008 | 1 | 5 | 13 | 22818.8494
2026/2027 | 2008 | 1 | 5 | 14 | 23626.5342
2026/2027 | 2008 | 1 | 5 | 15 | 24802.4137
2026/2027 | 2008 | 1 | 5 | 16 | 24061.4872
2026/2027 | 2008 | 1 | 5 | 17 | 15991.034
2026/2027 | 2008 | 1 | 5 | 18 | 1090.49
2026/2027 | 2008 | 1 | 5 | 19 | 0
2026/2027 | 2008 | 1 | 5 | 20 | 0
2026/2027 | 2008 | 1 | 5 | 21 | 0
2026/2027 | 2008 | 1 | 5 | 22 | 0
2026/2027 | 2008 | 1 | 5 | 23 | 0
2026/2027 | 2008 | 1 | 5 | 24 | 0
2026/2027 | 2008 | 1 | 6 | 1 | 0
2026/2027 | 2008 | 1 | 6 | 2 | 0
2026/2027 | 2008 | 1 | 6 | 3 | 0
2026/2027 | 2008 | 1 | 6 | 4 | 0
2026/2027 | 2008 | 1 | 6 | 5 | 0
2026/2027 | 2008 | 1 | 6 | 6 | 0
2026/2027 | 2008 | 1 | 6 | 7 | 0
2026/2027 | 2008 | 1 | 6 | 8 | 12.5583
2026/2027 | 2008 | 1 | 6 | 9 | 3206.0063
2026/2027 | 2008 | 1 | 6 | 10 | 12467.6454
2026/2027 | 2008 | 1 | 6 | 11 | 16050.633
2026/2027 | 2008 | 1 | 6 | 12 | 18850.3132
2026/2027 | 2008 | 1 | 6 | 13 | 22163.2947
2026/2027 | 2008 | 1 | 6 | 14 | 23411.3448
2026/2027 | 2008 | 1 | 6 | 15 | 22378.2415
2026/2027 | 2008 | 1 | 6 | 16 | 18191.9249
2026/2027 | 2008 | 1 | 6 | 17 | 13911.206
2026/2027 | 2008 | 1 | 6 | 18 | 1340.0521
2026/2027 | 2008 | 1 | 6 | 19 | 0
2026/2027 | 2008 | 1 | 6 | 20 | 0
2026/2027 | 2008 | 1 | 6 | 21 | 0
2026/2027 | 2008 | 1 | 6 | 22 | 0
2026/2027 | 2008 | 1 | 6 | 23 | 0
2026/2027 | 2008 | 1 | 6 | 24 | 0
2026/2027 | 2008 | 1 | 7 | 1 | 0
2026/2027 | 2008 | 1 | 7 | 2 | 0
2026/2027 | 2008 | 1 | 7 | 3 | 0
2026/2027 | 2008 | 1 | 7 | 4 | 0
2026/2027 | 2008 | 1 | 7 | 5 | 0
2026/2027 | 2008 | 1 | 7 | 6 | 0
2026/2027 | 2008 | 1 | 7 | 7 | 0
2026/2027 | 2008 | 1 | 7 | 8 | 2.1121
2026/2027 | 2008 | 1 | 7 | 9 | 2407.0221
2026/2027 | 2008 | 1 | 7 | 10 | 8455.1395
2026/2027 | 2008 | 1 | 7 | 11 | 12829.9318
2026/2027 | 2008 | 1 | 7 | 12 | 13859.0141
2026/2027 | 2008 | 1 | 7 | 13 | 16572.056
2026/2027 | 2008 | 1 | 7 | 14 | 14514.1374
2026/2027 | 2008 | 1 | 7 | 15 | 14275.6856
2026/2027 | 2008 | 1 | 7 | 16 | 13003.8937
2026/2027 | 2008 | 1 | 7 | 17 | 7916.786
2026/2027 | 2008 | 1 | 7 | 18 | 988.2752
2026/2027 | 2008 | 1 | 7 | 19 | 0
2026/2027 | 2008 | 1 | 7 | 20 | 0
2026/2027 | 2008 | 1 | 7 | 21 | 0
2026/2027 | 2008 | 1 | 7 | 22 | 0
2026/2027 | 2008 | 1 | 7 | 23 | 0
2026/2027 | 2008 | 1 | 7 | 24 | 0
2026/2027 | 2008 | 1 | 8 | 1 | 0
2026/2027 | 2008 | 1 | 8 | 2 | 0
2026/2027 | 2008 | 1 | 8 | 3 | 0
2026/2027 | 2008 | 1 | 8 | 4 | 0
2026/2027 | 2008 | 1 | 8 | 5 | 0
2026/2027 | 2008 | 1 | 8 | 6 | 0
2026/2027 | 2008 | 1 | 8 | 7 | 0
2026/2027 | 2008 | 1 | 8 | 8 | 5.9053
2026/2027 | 2008 | 1 | 8 | 9 | 3184.3794
2026/2027 | 2008 | 1 | 8 | 10 | 10704.484
2026/2027 | 2008 | 1 | 8 | 11 | 14448.972
2026/2027 | 2008 | 1 | 8 | 12 | 17524.2284
2026/2027 | 2008 | 1 | 8 | 13 | 18793.9592
2026/2027 | 2008 | 1 | 8 | 14 | 17609.857
2026/2027 | 2008 | 1 | 8 | 15 | 18005.359
2026/2027 | 2008 | 1 | 8 | 16 | 16142.7777
2026/2027 | 2008 | 1 | 8 | 17 | 10620.1098
2026/2027 | 2008 | 1 | 8 | 18 | 1170.0656
2026/2027 | 2008 | 1 | 8 | 19 | 0
2026/2027 | 2008 | 1 | 8 | 20 | 0
2026/2027 | 2008 | 1 | 8 | 21 | 0
2026/2027 | 2008 | 1 | 8 | 22 | 0
2026/2027 | 2008 | 1 | 8 | 23 | 0
2026/2027 | 2008 | 1 | 8 | 24 | 0
2026/2027 | 2008 | 1 | 9 | 1 | 0
2026/2027 | 2008 | 1 | 9 | 2 | 0
2026/2027 | 2008 | 1 | 9 | 3 | 0
2026/2027 | 2008 | 1 | 9 | 4 | 0
2026/2027 | 2008 | 1 | 9 | 5 | 0
2026/2027 | 2008 | 1 | 9 | 6 | 0
2026/2027 | 2008 | 1 | 9 | 7 | 0
2026/2027 | 2008 | 1 | 9 | 8 | 36.5939
2026/2027 | 2008 | 1 | 9 | 9 | 11362.3557
2026/2027 | 2008 | 1 | 9 | 10 | 27484.9976
2026/2027 | 2008 | 1 | 9 | 11 | 30327.1526
2026/2027 | 2008 | 1 | 9 | 12 | 30143.3302
2026/2027 | 2008 | 1 | 9 | 13 | 29965.8663
2026/2027 | 2008 | 1 | 9 | 14 | 29138.8074
2026/2027 | 2008 | 1 | 9 | 15 | 28604.6132
2026/2027 | 2008 | 1 | 9 | 16 | 26250.9547
2026/2027 | 2008 | 1 | 9 | 17 | 18668.2981
2026/2027 | 2008 | 1 | 9 | 18 | 2023.7166
2026/2027 | 2008 | 1 | 9 | 19 | 0
2026/2027 | 2008 | 1 | 9 | 20 | 0
2026/2027 | 2008 | 1 | 9 | 21 | 0
2026/2027 | 2008 | 1 | 9 | 22 | 0
2026/2027 | 2008 | 1 | 9 | 23 | 0
2026/2027 | 2008 | 1 | 9 | 24 | 0
2026/2027 | 2008 | 1 | 10 | 1 | 0
2026/2027 | 2008 | 1 | 10 | 2 | 0
2026/2027 | 2008 | 1 | 10 | 3 | 0
2026/2027 | 2008 | 1 | 10 | 4 | 0
2026/2027 | 2008 | 1 | 10 | 5 | 0
2026/2027 | 2008 | 1 | 10 | 6 | 0
2026/2027 | 2008 | 1 | 10 | 7 | 0
2026/2027 | 2008 | 1 | 10 | 8 | 21.224
2026/2027 | 2008 | 1 | 10 | 9 | 7469.6266
2026/2027 | 2008 | 1 | 10 | 10 | 20832.3259
2026/2027 | 2008 | 1 | 10 | 11 | 24575.3081
2026/2027 | 2008 | 1 | 10 | 12 | 25927.7561
2026/2027 | 2008 | 1 | 10 | 13 | 25849.7986
2026/2027 | 2008 | 1 | 10 | 14 | 26473.6113
2026/2027 | 2008 | 1 | 10 | 15 | 27808.7273
2026/2027 | 2008 | 1 | 10 | 16 | 28504.5115
2026/2027 | 2008 | 1 | 10 | 17 | 17521.9459
2026/2027 | 2008 | 1 | 10 | 18 | 1658.8754
2026/2027 | 2008 | 1 | 10 | 19 | 0
2026/2027 | 2008 | 1 | 10 | 20 | 0
2026/2027 | 2008 | 1 | 10 | 21 | 0
2026/2027 | 2008 | 1 | 10 | 22 | 0
2026/2027 | 2008 | 1 | 10 | 23 | 0
2026/2027 | 2008 | 1 | 10 | 24 | 0
2026/2027 | 2008 | 1 | 11 | 1 | 0
2026/2027 | 2008 | 1 | 11 | 2 | 0
2026/2027 | 2008 | 1 | 11 | 3 | 0
2026/2027 | 2008 | 1 | 11 | 4 | 0
2026/2027 | 2008 | 1 | 11 | 5 | 0
2026/2027 | 2008 | 1 | 11 | 6 | 0
2026/2027 | 2008 | 1 | 11 | 7 | 0
2026/2027 | 2008 | 1 | 11 | 8 | 34.4664
2026/2027 | 2008 | 1 | 11 | 9 | 11615.0045
2026/2027 | 2008 | 1 | 11 | 10 | 29263.603
2026/2027 | 2008 | 1 | 11 | 11 | 31152.517
2026/2027 | 2008 | 1 | 11 | 12 | 31409.3278
2026/2027 | 2008 | 1 | 11 | 13 | 30898.6432
2026/2027 | 2008 | 1 | 11 | 14 | 29943.2343
2026/2027 | 2008 | 1 | 11 | 15 | 29751.3465
2026/2027 | 2008 | 1 | 11 | 16 | 26408.0456
2026/2027 | 2008 | 1 | 11 | 17 | 15911.0978
2026/2027 | 2008 | 1 | 11 | 18 | 1258.0796
2026/2027 | 2008 | 1 | 11 | 19 | 0
2026/2027 | 2008 | 1 | 11 | 20 | 0
2026/2027 | 2008 | 1 | 11 | 21 | 0
2026/2027 | 2008 | 1 | 11 | 22 | 0
2026/2027 | 2008 | 1 | 11 | 23 | 0
2026/2027 | 2008 | 1 | 11 | 24 | 0
2026/2027 | 2008 | 1 | 12 | 1 | 0
2026/2027 | 2008 | 1 | 12 | 2 | 0
2026/2027 | 2008 | 1 | 12 | 3 | 0
2026/2027 | 2008 | 1 | 12 | 4 | 0
2026/2027 | 2008 | 1 | 12 | 5 | 0
2026/2027 | 2008 | 1 | 12 | 6 | 0
2026/2027 | 2008 | 1 | 12 | 7 | 0
2026/2027 | 2008 | 1 | 12 | 8 | 28.2621
2026/2027 | 2008 | 1 | 12 | 9 | 9283.0362
2026/2027 | 2008 | 1 | 12 | 10 | 22710.3336
2026/2027 | 2008 | 1 | 12 | 11 | 24751.8765
2026/2027 | 2008 | 1 | 12 | 12 | 23905.1742
2026/2027 | 2008 | 1 | 12 | 13 | 25196.9762
2026/2027 | 2008 | 1 | 12 | 14 | 25560.8951
2026/2027 | 2008 | 1 | 12 | 15 | 26284.4783
2026/2027 | 2008 | 1 | 12 | 16 | 26444.8223
2026/2027 | 2008 | 1 | 12 | 17 | 16868.5823
2026/2027 | 2008 | 1 | 12 | 18 | 2275.7185
2026/2027 | 2008 | 1 | 12 | 19 | 0
2026/2027 | 2008 | 1 | 12 | 20 | 0
2026/2027 | 2008 | 1 | 12 | 21 | 0
2026/2027 | 2008 | 1 | 12 | 22 | 0
2026/2027 | 2008 | 1 | 12 | 23 | 0
2026/2027 | 2008 | 1 | 12 | 24 | 0
2026/2027 | 2008 | 1 | 13 | 1 | 0
2026/2027 | 2008 | 1 | 13 | 2 | 0
2026/2027 | 2008 | 1 | 13 | 3 | 0
2026/2027 | 2008 | 1 | 13 | 4 | 0
2026/2027 | 2008 | 1 | 13 | 5 | 0
2026/2027 | 2008 | 1 | 13 | 6 | 0
2026/2027 | 2008 | 1 | 13 | 7 | 0
2026/2027 | 2008 | 1 | 13 | 8 | 30.1083
2026/2027 | 2008 | 1 | 13 | 9 | 10416.5382
2026/2027 | 2008 | 1 | 13 | 10 | 27801.2468
2026/2027 | 2008 | 1 | 13 | 11 | 29790.2347
2026/2027 | 2008 | 1 | 13 | 12 | 29924.931
2026/2027 | 2008 | 1 | 13 | 13 | 28998.7953
2026/2027 | 2008 | 1 | 13 | 14 | 27644.3806
2026/2027 | 2008 | 1 | 13 | 15 | 25483.3143
2026/2027 | 2008 | 1 | 13 | 16 | 21964.1164
2026/2027 | 2008 | 1 | 13 | 17 | 14815.6214
2026/2027 | 2008 | 1 | 13 | 18 | 1768.3943
2026/2027 | 2008 | 1 | 13 | 19 | 0
2026/2027 | 2008 | 1 | 13 | 20 | 0
2026/2027 | 2008 | 1 | 13 | 21 | 0
2026/2027 | 2008 | 1 | 13 | 22 | 0
2026/2027 | 2008 | 1 | 13 | 23 | 0
2026/2027 | 2008 | 1 | 13 | 24 | 0
2026/2027 | 2008 | 1 | 14 | 1 | 0
2026/2027 | 2008 | 1 | 14 | 2 | 0
2026/2027 | 2008 | 1 | 14 | 3 | 0
2026/2027 | 2008 | 1 | 14 | 4 | 0
2026/2027 | 2008 | 1 | 14 | 5 | 0
2026/2027 | 2008 | 1 | 14 | 6 | 0
2026/2027 | 2008 | 1 | 14 | 7 | 0
2026/2027 | 2008 | 1 | 14 | 8 | 31.6354
2026/2027 | 2008 | 1 | 14 | 9 | 10809.6471
2026/2027 | 2008 | 1 | 14 | 10 | 28293.6877
2026/2027 | 2008 | 1 | 14 | 11 | 31162.7153
2026/2027 | 2008 | 1 | 14 | 12 | 29782.5969
2026/2027 | 2008 | 1 | 14 | 13 | 28661.1674
2026/2027 | 2008 | 1 | 14 | 14 | 26870.9117
2026/2027 | 2008 | 1 | 14 | 15 | 25635.3901
2026/2027 | 2008 | 1 | 14 | 16 | 24404.6256
2026/2027 | 2008 | 1 | 14 | 17 | 16356.5605
2026/2027 | 2008 | 1 | 14 | 18 | 2280.7124
2026/2027 | 2008 | 1 | 14 | 19 | 0
2026/2027 | 2008 | 1 | 14 | 20 | 0
2026/2027 | 2008 | 1 | 14 | 21 | 0
2026/2027 | 2008 | 1 | 14 | 22 | 0
2026/2027 | 2008 | 1 | 14 | 23 | 0
2026/2027 | 2008 | 1 | 14 | 24 | 0
2026/2027 | 2008 | 1 | 15 | 1 | 0
2026/2027 | 2008 | 1 | 15 | 2 | 0
2026/2027 | 2008 | 1 | 15 | 3 | 0
2026/2027 | 2008 | 1 | 15 | 4 | 0
2026/2027 | 2008 | 1 | 15 | 5 | 0
2026/2027 | 2008 | 1 | 15 | 6 | 0
2026/2027 | 2008 | 1 | 15 | 7 | 0
2026/2027 | 2008 | 1 | 15 | 8 | 11.877
2026/2027 | 2008 | 1 | 15 | 9 | 6116.796
2026/2027 | 2008 | 1 | 15 | 10 | 18199.1318
2026/2027 | 2008 | 1 | 15 | 11 | 19272.9176
2026/2027 | 2008 | 1 | 15 | 12 | 19231.488
2026/2027 | 2008 | 1 | 15 | 13 | 17665.3632
2026/2027 | 2008 | 1 | 15 | 14 | 16911.6463
2026/2027 | 2008 | 1 | 15 | 15 | 16861.0946
2026/2027 | 2008 | 1 | 15 | 16 | 15549.5241
2026/2027 | 2008 | 1 | 15 | 17 | 11673.4066
2026/2027 | 2008 | 1 | 15 | 18 | 1954.7025
2026/2027 | 2008 | 1 | 15 | 19 | 0
2026/2027 | 2008 | 1 | 15 | 20 | 0
2026/2027 | 2008 | 1 | 15 | 21 | 0
2026/2027 | 2008 | 1 | 15 | 22 | 0
2026/2027 | 2008 | 1 | 15 | 23 | 0
2026/2027 | 2008 | 1 | 15 | 24 | 0
2026/2027 | 2008 | 1 | 16 | 1 | 0
2026/2027 | 2008 | 1 | 16 | 2 | 0
2026/2027 | 2008 | 1 | 16 | 3 | 0
2026/2027 | 2008 | 1 | 16 | 4 | 0
2026/2027 | 2008 | 1 | 16 | 5 | 0
2026/2027 | 2008 | 1 | 16 | 6 | 0
2026/2027 | 2008 | 1 | 16 | 7 | 0
2026/2027 | 2008 | 1 | 16 | 8 | 2.3309
2026/2027 | 2008 | 1 | 16 | 9 | 3103.8071
2026/2027 | 2008 | 1 | 16 | 10 | 10452.6089
2026/2027 | 2008 | 1 | 16 | 11 | 12814.9073
2026/2027 | 2008 | 1 | 16 | 12 | 14672.6597
2026/2027 | 2008 | 1 | 16 | 13 | 16884.7373
2026/2027 | 2008 | 1 | 16 | 14 | 19037.4163
2026/2027 | 2008 | 1 | 16 | 15 | 17614.9512
2026/2027 | 2008 | 1 | 16 | 16 | 18680.3893
2026/2027 | 2008 | 1 | 16 | 17 | 16262.9705
2026/2027 | 2008 | 1 | 16 | 18 | 3351.255
2026/2027 | 2008 | 1 | 16 | 19 | 0
2026/2027 | 2008 | 1 | 16 | 20 | 0
2026/2027 | 2008 | 1 | 16 | 21 | 0
2026/2027 | 2008 | 1 | 16 | 22 | 0
2026/2027 | 2008 | 1 | 16 | 23 | 0
2026/2027 | 2008 | 1 | 16 | 24 | 0
2026/2027 | 2008 | 1 | 17 | 1 | 0
2026/2027 | 2008 | 1 | 17 | 2 | 0
2026/2027 | 2008 | 1 | 17 | 3 | 0
2026/2027 | 2008 | 1 | 17 | 4 | 0
2026/2027 | 2008 | 1 | 17 | 5 | 0
2026/2027 | 2008 | 1 | 17 | 6 | 0
2026/2027 | 2008 | 1 | 17 | 7 | 0
2026/2027 | 2008 | 1 | 17 | 8 | 25.9247
2026/2027 | 2008 | 1 | 17 | 9 | 7178.152
2026/2027 | 2008 | 1 | 17 | 10 | 20963.3146
2026/2027 | 2008 | 1 | 17 | 11 | 26420.0139
2026/2027 | 2008 | 1 | 17 | 12 | 28353.1451
2026/2027 | 2008 | 1 | 17 | 13 | 29604.8504
2026/2027 | 2008 | 1 | 17 | 14 | 28279.0317
2026/2027 | 2008 | 1 | 17 | 15 | 27526.194
2026/2027 | 2008 | 1 | 17 | 16 | 25440.0075
2026/2027 | 2008 | 1 | 17 | 17 | 16619.6638
2026/2027 | 2008 | 1 | 17 | 18 | 2747.9455
2026/2027 | 2008 | 1 | 17 | 19 | 0
2026/2027 | 2008 | 1 | 17 | 20 | 0
2026/2027 | 2008 | 1 | 17 | 21 | 0
2026/2027 | 2008 | 1 | 17 | 22 | 0
2026/2027 | 2008 | 1 | 17 | 23 | 0
2026/2027 | 2008 | 1 | 17 | 24 | 0
2026/2027 | 2008 | 1 | 18 | 1 | 0
2026/2027 | 2008 | 1 | 18 | 2 | 0
2026/2027 | 2008 | 1 | 18 | 3 | 0
2026/2027 | 2008 | 1 | 18 | 4 | 0
2026/2027 | 2008 | 1 | 18 | 5 | 0
2026/2027 | 2008 | 1 | 18 | 6 | 0
2026/2027 | 2008 | 1 | 18 | 7 | 0
2026/2027 | 2008 | 1 | 18 | 8 | 10.3298
2026/2027 | 2008 | 1 | 18 | 9 | 4798.9139
2026/2027 | 2008 | 1 | 18 | 10 | 14031.524
2026/2027 | 2008 | 1 | 18 | 11 | 16018.7706
2026/2027 | 2008 | 1 | 18 | 12 | 17160.4814
2026/2027 | 2008 | 1 | 18 | 13 | 16859.8879
2026/2027 | 2008 | 1 | 18 | 14 | 16335.859
2026/2027 | 2008 | 1 | 18 | 15 | 16553.0574
2026/2027 | 2008 | 1 | 18 | 16 | 15334.4067
2026/2027 | 2008 | 1 | 18 | 17 | 13410.5346
2026/2027 | 2008 | 1 | 18 | 18 | 3066.2719
2026/2027 | 2008 | 1 | 18 | 19 | 0
2026/2027 | 2008 | 1 | 18 | 20 | 0
2026/2027 | 2008 | 1 | 18 | 21 | 0
2026/2027 | 2008 | 1 | 18 | 22 | 0
2026/2027 | 2008 | 1 | 18 | 23 | 0
2026/2027 | 2008 | 1 | 18 | 24 | 0
2026/2027 | 2008 | 1 | 19 | 1 | 0
2026/2027 | 2008 | 1 | 19 | 2 | 0
2026/2027 | 2008 | 1 | 19 | 3 | 0
2026/2027 | 2008 | 1 | 19 | 4 | 0
2026/2027 | 2008 | 1 | 19 | 5 | 0
2026/2027 | 2008 | 1 | 19 | 6 | 0
2026/2027 | 2008 | 1 | 19 | 7 | 0
2026/2027 | 2008 | 1 | 19 | 8 | 26.0957
2026/2027 | 2008 | 1 | 19 | 9 | 10326.4688
2026/2027 | 2008 | 1 | 19 | 10 | 31455.7058
2026/2027 | 2008 | 1 | 19 | 11 | 37082.1086
2026/2027 | 2008 | 1 | 19 | 12 | 36160.6411
2026/2027 | 2008 | 1 | 19 | 13 | 35578.3813
2026/2027 | 2008 | 1 | 19 | 14 | 35931.0342
2026/2027 | 2008 | 1 | 19 | 15 | 36007.3815
2026/2027 | 2008 | 1 | 19 | 16 | 33366.4721
2026/2027 | 2008 | 1 | 19 | 17 | 26221.4363
2026/2027 | 2008 | 1 | 19 | 18 | 5156.6654
2026/2027 | 2008 | 1 | 19 | 19 | 0
2026/2027 | 2008 | 1 | 19 | 20 | 0
2026/2027 | 2008 | 1 | 19 | 21 | 0
2026/2027 | 2008 | 1 | 19 | 22 | 0
2026/2027 | 2008 | 1 | 19 | 23 | 0
2026/2027 | 2008 | 1 | 19 | 24 | 0
2026/2027 | 2008 | 1 | 20 | 1 | 0
2026/2027 | 2008 | 1 | 20 | 2 | 0
2026/2027 | 2008 | 1 | 20 | 3 | 0
2026/2027 | 2008 | 1 | 20 | 4 | 0
2026/2027 | 2008 | 1 | 20 | 5 | 0
2026/2027 | 2008 | 1 | 20 | 6 | 0
2026/2027 | 2008 | 1 | 20 | 7 | 0
2026/2027 | 2008 | 1 | 20 | 8 | 42.6181
2026/2027 | 2008 | 1 | 20 | 9 | 13554.0811
2026/2027 | 2008 | 1 | 20 | 10 | 32987.2206
2026/2027 | 2008 | 1 | 20 | 11 | 37397.9862
2026/2027 | 2008 | 1 | 20 | 12 | 35810.4295
2026/2027 | 2008 | 1 | 20 | 13 | 35385.6786
2026/2027 | 2008 | 1 | 20 | 14 | 35186.8899
2026/2027 | 2008 | 1 | 20 | 15 | 33642.0927
2026/2027 | 2008 | 1 | 20 | 16 | 31054.918
2026/2027 | 2008 | 1 | 20 | 17 | 24303.8614
2026/2027 | 2008 | 1 | 20 | 18 | 4768.9588
2026/2027 | 2008 | 1 | 20 | 19 | 0
2026/2027 | 2008 | 1 | 20 | 20 | 0
2026/2027 | 2008 | 1 | 20 | 21 | 0
2026/2027 | 2008 | 1 | 20 | 22 | 0
2026/2027 | 2008 | 1 | 20 | 23 | 0
2026/2027 | 2008 | 1 | 20 | 24 | 0
2026/2027 | 2008 | 1 | 21 | 1 | 0
2026/2027 | 2008 | 1 | 21 | 2 | 0
2026/2027 | 2008 | 1 | 21 | 3 | 0
2026/2027 | 2008 | 1 | 21 | 4 | 0
2026/2027 | 2008 | 1 | 21 | 5 | 0
2026/2027 | 2008 | 1 | 21 | 6 | 0
2026/2027 | 2008 | 1 | 21 | 7 | 0
2026/2027 | 2008 | 1 | 21 | 8 | 0.04657
2026/2027 | 2008 | 1 | 21 | 9 | 447.0364
2026/2027 | 2008 | 1 | 21 | 10 | 3501.8552
2026/2027 | 2008 | 1 | 21 | 11 | 6744.1784
2026/2027 | 2008 | 1 | 21 | 12 | 8723.7318
2026/2027 | 2008 | 1 | 21 | 13 | 9818.7567
2026/2027 | 2008 | 1 | 21 | 14 | 10753.3509
2026/2027 | 2008 | 1 | 21 | 15 | 10966.2815
2026/2027 | 2008 | 1 | 21 | 16 | 11528.6164
2026/2027 | 2008 | 1 | 21 | 17 | 10012.929
2026/2027 | 2008 | 1 | 21 | 18 | 3044.9954
2026/2027 | 2008 | 1 | 21 | 19 | 0
2026/2027 | 2008 | 1 | 21 | 20 | 0
2026/2027 | 2008 | 1 | 21 | 21 | 0
2026/2027 | 2008 | 1 | 21 | 22 | 0
2026/2027 | 2008 | 1 | 21 | 23 | 0
2026/2027 | 2008 | 1 | 21 | 24 | 0
2026/2027 | 2008 | 1 | 22 | 1 | 0
2026/2027 | 2008 | 1 | 22 | 2 | 0
2026/2027 | 2008 | 1 | 22 | 3 | 0
2026/2027 | 2008 | 1 | 22 | 4 | 0
2026/2027 | 2008 | 1 | 22 | 5 | 0
2026/2027 | 2008 | 1 | 22 | 6 | 0
2026/2027 | 2008 | 1 | 22 | 7 | 0
2026/2027 | 2008 | 1 | 22 | 8 | 8.7129
2026/2027 | 2008 | 1 | 22 | 9 | 1576.17
2026/2027 | 2008 | 1 | 22 | 10 | 6640.3871
2026/2027 | 2008 | 1 | 22 | 11 | 9222.6996
2026/2027 | 2008 | 1 | 22 | 12 | 10426.5591
2026/2027 | 2008 | 1 | 22 | 13 | 9945.5484
2026/2027 | 2008 | 1 | 22 | 14 | 9900.4885
2026/2027 | 2008 | 1 | 22 | 15 | 10775.2764
2026/2027 | 2008 | 1 | 22 | 16 | 9714.907
2026/2027 | 2008 | 1 | 22 | 17 | 8503.4849
2026/2027 | 2008 | 1 | 22 | 18 | 2083.0445
2026/2027 | 2008 | 1 | 22 | 19 | 0
2026/2027 | 2008 | 1 | 22 | 20 | 0
2026/2027 | 2008 | 1 | 22 | 21 | 0
2026/2027 | 2008 | 1 | 22 | 22 | 0
2026/2027 | 2008 | 1 | 22 | 23 | 0
2026/2027 | 2008 | 1 | 22 | 24 | 0
2026/2027 | 2008 | 1 | 23 | 1 | 0
2026/2027 | 2008 | 1 | 23 | 2 | 0
2026/2027 | 2008 | 1 | 23 | 3 | 0
2026/2027 | 2008 | 1 | 23 | 4 | 0
2026/2027 | 2008 | 1 | 23 | 5 | 0
2026/2027 | 2008 | 1 | 23 | 6 | 0
2026/2027 | 2008 | 1 | 23 | 7 | 0
2026/2027 | 2008 | 1 | 23 | 8 | 2.8128
2026/2027 | 2008 | 1 | 23 | 9 | 1846.236
2026/2027 | 2008 | 1 | 23 | 10 | 7168.5159
2026/2027 | 2008 | 1 | 23 | 11 | 9315.1446
2026/2027 | 2008 | 1 | 23 | 12 | 10588.143
2026/2027 | 2008 | 1 | 23 | 13 | 10633.9503
2026/2027 | 2008 | 1 | 23 | 14 | 10257.6049
2026/2027 | 2008 | 1 | 23 | 15 | 9957.8575
2026/2027 | 2008 | 1 | 23 | 16 | 8725.4695
2026/2027 | 2008 | 1 | 23 | 17 | 5765.213
2026/2027 | 2008 | 1 | 23 | 18 | 1217.409
2026/2027 | 2008 | 1 | 23 | 19 | 0
2026/2027 | 2008 | 1 | 23 | 20 | 0
2026/2027 | 2008 | 1 | 23 | 21 | 0
2026/2027 | 2008 | 1 | 23 | 22 | 0
2026/2027 | 2008 | 1 | 23 | 23 | 0
2026/2027 | 2008 | 1 | 23 | 24 | 0
2026/2027 | 2008 | 1 | 24 | 1 | 0
2026/2027 | 2008 | 1 | 24 | 2 | 0
2026/2027 | 2008 | 1 | 24 | 3 | 0
2026/2027 | 2008 | 1 | 24 | 4 | 0
2026/2027 | 2008 | 1 | 24 | 5 | 0
2026/2027 | 2008 | 1 | 24 | 6 | 0
2026/2027 | 2008 | 1 | 24 | 7 | 0
2026/2027 | 2008 | 1 | 24 | 8 | 12.0554
2026/2027 | 2008 | 1 | 24 | 9 | 3530.9898
2026/2027 | 2008 | 1 | 24 | 10 | 11647.0269
2026/2027 | 2008 | 1 | 24 | 11 | 14696.8865
2026/2027 | 2008 | 1 | 24 | 12 | 15460.2547
2026/2027 | 2008 | 1 | 24 | 13 | 15061.6026
2026/2027 | 2008 | 1 | 24 | 14 | 14669.1526
2026/2027 | 2008 | 1 | 24 | 15 | 12057.1177
2026/2027 | 2008 | 1 | 24 | 16 | 10017.9778
2026/2027 | 2008 | 1 | 24 | 17 | 4751.4911
2026/2027 | 2008 | 1 | 24 | 18 | 643.4984
2026/2027 | 2008 | 1 | 24 | 19 | 0
2026/2027 | 2008 | 1 | 24 | 20 | 0
2026/2027 | 2008 | 1 | 24 | 21 | 0
2026/2027 | 2008 | 1 | 24 | 22 | 0
2026/2027 | 2008 | 1 | 24 | 23 | 0
2026/2027 | 2008 | 1 | 24 | 24 | 0
2026/2027 | 2008 | 1 | 25 | 1 | 0
2026/2027 | 2008 | 1 | 25 | 2 | 0
2026/2027 | 2008 | 1 | 25 | 3 | 0
2026/2027 | 2008 | 1 | 25 | 4 | 0
2026/2027 | 2008 | 1 | 25 | 5 | 0
2026/2027 | 2008 | 1 | 25 | 6 | 0
2026/2027 | 2008 | 1 | 25 | 7 | 0
2026/2027 | 2008 | 1 | 25 | 8 | 0.001
2026/2027 | 2008 | 1 | 25 | 9 | 453.3305
2026/2027 | 2008 | 1 | 25 | 10 | 3506.7288
2026/2027 | 2008 | 1 | 25 | 11 | 5511.6042
2026/2027 | 2008 | 1 | 25 | 12 | 7051.1189
2026/2027 | 2008 | 1 | 25 | 13 | 9150.3233
2026/2027 | 2008 | 1 | 25 | 14 | 9678.9496
2026/2027 | 2008 | 1 | 25 | 15 | 10683.8261
2026/2027 | 2008 | 1 | 25 | 16 | 11811.1922
2026/2027 | 2008 | 1 | 25 | 17 | 10503.96
2026/2027 | 2008 | 1 | 25 | 18 | 3225.0276
2026/2027 | 2008 | 1 | 25 | 19 | 0
2026/2027 | 2008 | 1 | 25 | 20 | 0
2026/2027 | 2008 | 1 | 25 | 21 | 0
2026/2027 | 2008 | 1 | 25 | 22 | 0
2026/2027 | 2008 | 1 | 25 | 23 | 0
2026/2027 | 2008 | 1 | 25 | 24 | 0
2026/2027 | 2008 | 1 | 26 | 1 | 0
2026/2027 | 2008 | 1 | 26 | 2 | 0
2026/2027 | 2008 | 1 | 26 | 3 | 0
2026/2027 | 2008 | 1 | 26 | 4 | 0
2026/2027 | 2008 | 1 | 26 | 5 | 0
2026/2027 | 2008 | 1 | 26 | 6 | 0
2026/2027 | 2008 | 1 | 26 | 7 | 0
2026/2027 | 2008 | 1 | 26 | 8 | 11.3574
2026/2027 | 2008 | 1 | 26 | 9 | 5463.8764
2026/2027 | 2008 | 1 | 26 | 10 | 17141.2055
2026/2027 | 2008 | 1 | 26 | 11 | 19910.8674
2026/2027 | 2008 | 1 | 26 | 12 | 22431.1406
2026/2027 | 2008 | 1 | 26 | 13 | 25325.3727
2026/2027 | 2008 | 1 | 26 | 14 | 25273.6683
2026/2027 | 2008 | 1 | 26 | 15 | 24514.9811
2026/2027 | 2008 | 1 | 26 | 16 | 22450.523
2026/2027 | 2008 | 1 | 26 | 17 | 16458.5299
2026/2027 | 2008 | 1 | 26 | 18 | 4558.5443
2026/2027 | 2008 | 1 | 26 | 19 | 0
2026/2027 | 2008 | 1 | 26 | 20 | 0
2026/2027 | 2008 | 1 | 26 | 21 | 0
2026/2027 | 2008 | 1 | 26 | 22 | 0
2026/2027 | 2008 | 1 | 26 | 23 | 0
2026/2027 | 2008 | 1 | 26 | 24 | 0
2026/2027 | 2008 | 1 | 27 | 1 | 0
2026/2027 | 2008 | 1 | 27 | 2 | 0
2026/2027 | 2008 | 1 | 27 | 3 | 0
2026/2027 | 2008 | 1 | 27 | 4 | 0
2026/2027 | 2008 | 1 | 27 | 5 | 0
2026/2027 | 2008 | 1 | 27 | 6 | 0
2026/2027 | 2008 | 1 | 27 | 7 | 0
2026/2027 | 2008 | 1 | 27 | 8 | 17.5698
2026/2027 | 2008 | 1 | 27 | 9 | 5073.112
2026/2027 | 2008 | 1 | 27 | 10 | 16396.4133
2026/2027 | 2008 | 1 | 27 | 11 | 20197.5695
2026/2027 | 2008 | 1 | 27 | 12 | 26366.4906
2026/2027 | 2008 | 1 | 27 | 13 | 29786.0843
2026/2027 | 2008 | 1 | 27 | 14 | 30382.87
2026/2027 | 2008 | 1 | 27 | 15 | 29026.1303
2026/2027 | 2008 | 1 | 27 | 16 | 25622.4237
2026/2027 | 2008 | 1 | 27 | 17 | 18814.0319
2026/2027 | 2008 | 1 | 27 | 18 | 4848.1557
2026/2027 | 2008 | 1 | 27 | 19 | 0
2026/2027 | 2008 | 1 | 27 | 20 | 0
2026/2027 | 2008 | 1 | 27 | 21 | 0
2026/2027 | 2008 | 1 | 27 | 22 | 0
2026/2027 | 2008 | 1 | 27 | 23 | 0
2026/2027 | 2008 | 1 | 27 | 24 | 0
2026/2027 | 2008 | 1 | 28 | 1 | 0
2026/2027 | 2008 | 1 | 28 | 2 | 0
2026/2027 | 2008 | 1 | 28 | 3 | 0
2026/2027 | 2008 | 1 | 28 | 4 | 0
2026/2027 | 2008 | 1 | 28 | 5 | 0
2026/2027 | 2008 | 1 | 28 | 6 | 0
2026/2027 | 2008 | 1 | 28 | 7 | 0
2026/2027 | 2008 | 1 | 28 | 8 | 1.3782
2026/2027 | 2008 | 1 | 28 | 9 | 1323.8957
2026/2027 | 2008 | 1 | 28 | 10 | 7142.8004
2026/2027 | 2008 | 1 | 28 | 11 | 8915.657
2026/2027 | 2008 | 1 | 28 | 12 | 10019.3632
2026/2027 | 2008 | 1 | 28 | 13 | 10920.5582
2026/2027 | 2008 | 1 | 28 | 14 | 11553.4759
2026/2027 | 2008 | 1 | 28 | 15 | 10416.1495
2026/2027 | 2008 | 1 | 28 | 16 | 9414.5493
2026/2027 | 2008 | 1 | 28 | 17 | 7729.6017
2026/2027 | 2008 | 1 | 28 | 18 | 2677.8325
2026/2027 | 2008 | 1 | 28 | 19 | 0
2026/2027 | 2008 | 1 | 28 | 20 | 0
2026/2027 | 2008 | 1 | 28 | 21 | 0
2026/2027 | 2008 | 1 | 28 | 22 | 0
2026/2027 | 2008 | 1 | 28 | 23 | 0
2026/2027 | 2008 | 1 | 28 | 24 | 0
2026/2027 | 2008 | 1 | 29 | 1 | 0
2026/2027 | 2008 | 1 | 29 | 2 | 0
2026/2027 | 2008 | 1 | 29 | 3 | 0
2026/2027 | 2008 | 1 | 29 | 4 | 0
2026/2027 | 2008 | 1 | 29 | 5 | 0
2026/2027 | 2008 | 1 | 29 | 6 | 0
2026/2027 | 2008 | 1 | 29 | 7 | 0
2026/2027 | 2008 | 1 | 29 | 8 | 19.3649
2026/2027 | 2008 | 1 | 29 | 9 | 5672.637
2026/2027 | 2008 | 1 | 29 | 10 | 19244.9925
2026/2027 | 2008 | 1 | 29 | 11 | 24279.5621
2026/2027 | 2008 | 1 | 29 | 12 | 27073.402
2026/2027 | 2008 | 1 | 29 | 13 | 29732.5499
2026/2027 | 2008 | 1 | 29 | 14 | 31697.3962
2026/2027 | 2008 | 1 | 29 | 15 | 35685.9964
2026/2027 | 2008 | 1 | 29 | 16 | 36715.196
2026/2027 | 2008 | 1 | 29 | 17 | 28470.2243
2026/2027 | 2008 | 1 | 29 | 18 | 8077.3277
2026/2027 | 2008 | 1 | 29 | 19 | 0
2026/2027 | 2008 | 1 | 29 | 20 | 0
2026/2027 | 2008 | 1 | 29 | 21 | 0
2026/2027 | 2008 | 1 | 29 | 22 | 0
2026/2027 | 2008 | 1 | 29 | 23 | 0
2026/2027 | 2008 | 1 | 29 | 24 | 0
2026/2027 | 2008 | 1 | 30 | 1 | 0
2026/2027 | 2008 | 1 | 30 | 2 | 0
2026/2027 | 2008 | 1 | 30 | 3 | 0
2026/2027 | 2008 | 1 | 30 | 4 | 0
2026/2027 | 2008 | 1 | 30 | 5 | 0
2026/2027 | 2008 | 1 | 30 | 6 | 0
2026/2027 | 2008 | 1 | 30 | 7 | 0
2026/2027 | 2008 | 1 | 30 | 8 | 85.3265
2026/2027 | 2008 | 1 | 30 | 9 | 14217.1904
2026/2027 | 2008 | 1 | 30 | 10 | 35288.0133
2026/2027 | 2008 | 1 | 30 | 11 | 37354.7701
2026/2027 | 2008 | 1 | 30 | 12 | 35900.4819
2026/2027 | 2008 | 1 | 30 | 13 | 34678.2019
2026/2027 | 2008 | 1 | 30 | 14 | 32989.7759
2026/2027 | 2008 | 1 | 30 | 15 | 29626.1137
2026/2027 | 2008 | 1 | 30 | 16 | 27500.3165
2026/2027 | 2008 | 1 | 30 | 17 | 21003.5231
2026/2027 | 2008 | 1 | 30 | 18 | 6282.4674
2026/2027 | 2008 | 1 | 30 | 19 | 0
2026/2027 | 2008 | 1 | 30 | 20 | 0
2026/2027 | 2008 | 1 | 30 | 21 | 0
2026/2027 | 2008 | 1 | 30 | 22 | 0
2026/2027 | 2008 | 1 | 30 | 23 | 0
2026/2027 | 2008 | 1 | 30 | 24 | 0
2026/2027 | 2008 | 1 | 31 | 1 | 0
2026/2027 | 2008 | 1 | 31 | 2 | 0
2026/2027 | 2008 | 1 | 31 | 3 | 0
2026/2027 | 2008 | 1 | 31 | 4 | 0
2026/2027 | 2008 | 1 | 31 | 5 | 0
2026/2027 | 2008 | 1 | 31 | 6 | 0
2026/2027 | 2008 | 1 | 31 | 7 | 0
2026/2027 | 2008 | 1 | 31 | 8 | 23.5081
2026/2027 | 2008 | 1 | 31 | 9 | 6971.4613
2026/2027 | 2008 | 1 | 31 | 10 | 25164.3549
2026/2027 | 2008 | 1 | 31 | 11 | 31862.2055
2026/2027 | 2008 | 1 | 31 | 12 | 33623.7966
2026/2027 | 2008 | 1 | 31 | 13 | 36769.1975
2026/2027 | 2008 | 1 | 31 | 14 | 38701.9088
2026/2027 | 2008 | 1 | 31 | 15 | 40123.2177
2026/2027 | 2008 | 1 | 31 | 16 | 37688.382
2026/2027 | 2008 | 1 | 31 | 17 | 29071.5141
2026/2027 | 2008 | 1 | 31 | 18 | 7930.0457
2026/2027 | 2008 | 1 | 31 | 19 | 0
2026/2027 | 2008 | 1 | 31 | 20 | 0
2026/2027 | 2008 | 1 | 31 | 21 | 0
2026/2027 | 2008 | 1 | 31 | 22 | 0
2026/2027 | 2008 | 1 | 31 | 23 | 0
2026/2027 | 2008 | 1 | 31 | 24 | 0
2027/2028 | 2008 | 1 | 1 | 1 | 0
2027/2028 | 2008 | 1 | 1 | 2 | 0
2027/2028 | 2008 | 1 | 1 | 3 | 0
2027/2028 | 2008 | 1 | 1 | 4 | 0
2027/2028 | 2008 | 1 | 1 | 5 | 0
2027/2028 | 2008 | 1 | 1 | 6 | 0
2027/2028 | 2008 | 1 | 1 | 7 | 0
2027/2028 | 2008 | 1 | 1 | 8 | 32.3932
2027/2028 | 2008 | 1 | 1 | 9 | 13701.604
2027/2028 | 2008 | 1 | 1 | 10 | 36740.558
2027/2028 | 2008 | 1 | 1 | 11 | 41675.2151
2027/2028 | 2008 | 1 | 1 | 12 | 41178.5034
2027/2028 | 2008 | 1 | 1 | 13 | 40303.7603
2027/2028 | 2008 | 1 | 1 | 14 | 40377.2444
2027/2028 | 2008 | 1 | 1 | 15 | 40847.5386
2027/2028 | 2008 | 1 | 1 | 16 | 35919.8341
2027/2028 | 2008 | 1 | 1 | 17 | 18873.7654
2027/2028 | 2008 | 1 | 1 | 18 | 811.5989
2027/2028 | 2008 | 1 | 1 | 19 | 0
2027/2028 | 2008 | 1 | 1 | 20 | 0
2027/2028 | 2008 | 1 | 1 | 21 | 0
2027/2028 | 2008 | 1 | 1 | 22 | 0
2027/2028 | 2008 | 1 | 1 | 23 | 0
2027/2028 | 2008 | 1 | 1 | 24 | 0
2027/2028 | 2008 | 1 | 2 | 1 | 0
2027/2028 | 2008 | 1 | 2 | 2 | 0
2027/2028 | 2008 | 1 | 2 | 3 | 0
2027/2028 | 2008 | 1 | 2 | 4 | 0
2027/2028 | 2008 | 1 | 2 | 5 | 0
2027/2028 | 2008 | 1 | 2 | 6 | 0
2027/2028 | 2008 | 1 | 2 | 7 | 0
2027/2028 | 2008 | 1 | 2 | 8 | 30.6219
2027/2028 | 2008 | 1 | 2 | 9 | 12836.9546
2027/2028 | 2008 | 1 | 2 | 10 | 34976.9858
2027/2028 | 2008 | 1 | 2 | 11 | 40071.3021
2027/2028 | 2008 | 1 | 2 | 12 | 38420.6702
2027/2028 | 2008 | 1 | 2 | 13 | 38183.0298
2027/2028 | 2008 | 1 | 2 | 14 | 35837.0517
2027/2028 | 2008 | 1 | 2 | 15 | 33171.6416
2027/2028 | 2008 | 1 | 2 | 16 | 26024.1661
2027/2028 | 2008 | 1 | 2 | 17 | 16584.9714
2027/2028 | 2008 | 1 | 2 | 18 | 415.7865
2027/2028 | 2008 | 1 | 2 | 19 | 0
2027/2028 | 2008 | 1 | 2 | 20 | 0
2027/2028 | 2008 | 1 | 2 | 21 | 0
2027/2028 | 2008 | 1 | 2 | 22 | 0
2027/2028 | 2008 | 1 | 2 | 23 | 0
2027/2028 | 2008 | 1 | 2 | 24 | 0
2027/2028 | 2008 | 1 | 3 | 1 | 0
2027/2028 | 2008 | 1 | 3 | 2 | 0
2027/2028 | 2008 | 1 | 3 | 3 | 0
2027/2028 | 2008 | 1 | 3 | 4 | 0
2027/2028 | 2008 | 1 | 3 | 5 | 0
2027/2028 | 2008 | 1 | 3 | 6 | 0
2027/2028 | 2008 | 1 | 3 | 7 | 0
2027/2028 | 2008 | 1 | 3 | 8 | 9.0189
2027/2028 | 2008 | 1 | 3 | 9 | 7673.5999
2027/2028 | 2008 | 1 | 3 | 10 | 25158.8439
2027/2028 | 2008 | 1 | 3 | 11 | 28116.3723
2027/2028 | 2008 | 1 | 3 | 12 | 29728.5002
2027/2028 | 2008 | 1 | 3 | 13 | 30569.5556
2027/2028 | 2008 | 1 | 3 | 14 | 30207.8221
2027/2028 | 2008 | 1 | 3 | 15 | 33539.5481
2027/2028 | 2008 | 1 | 3 | 16 | 30491.0171
2027/2028 | 2008 | 1 | 3 | 17 | 17548.2554
2027/2028 | 2008 | 1 | 3 | 18 | 804.0252
2027/2028 | 2008 | 1 | 3 | 19 | 0
2027/2028 | 2008 | 1 | 3 | 20 | 0
2027/2028 | 2008 | 1 | 3 | 21 | 0
2027/2028 | 2008 | 1 | 3 | 22 | 0
2027/2028 | 2008 | 1 | 3 | 23 | 0
2027/2028 | 2008 | 1 | 3 | 24 | 0
2027/2028 | 2008 | 1 | 4 | 1 | 0
2027/2028 | 2008 | 1 | 4 | 2 | 0
2027/2028 | 2008 | 1 | 4 | 3 | 0
2027/2028 | 2008 | 1 | 4 | 4 | 0
2027/2028 | 2008 | 1 | 4 | 5 | 0
2027/2028 | 2008 | 1 | 4 | 6 | 0
2027/2028 | 2008 | 1 | 4 | 7 | 0
2027/2028 | 2008 | 1 | 4 | 8 | 11.2804
2027/2028 | 2008 | 1 | 4 | 9 | 2624.6947
2027/2028 | 2008 | 1 | 4 | 10 | 10499.9121
2027/2028 | 2008 | 1 | 4 | 11 | 14433.1087
2027/2028 | 2008 | 1 | 4 | 12 | 16478.355
2027/2028 | 2008 | 1 | 4 | 13 | 16800.0993
2027/2028 | 2008 | 1 | 4 | 14 | 15531.4447
2027/2028 | 2008 | 1 | 4 | 15 | 14030.2737
2027/2028 | 2008 | 1 | 4 | 16 | 10928.6658
2027/2028 | 2008 | 1 | 4 | 17 | 7602.33
2027/2028 | 2008 | 1 | 4 | 18 | 341.2638
2027/2028 | 2008 | 1 | 4 | 19 | 0
2027/2028 | 2008 | 1 | 4 | 20 | 0
2027/2028 | 2008 | 1 | 4 | 21 | 0
2027/2028 | 2008 | 1 | 4 | 22 | 0
2027/2028 | 2008 | 1 | 4 | 23 | 0
2027/2028 | 2008 | 1 | 4 | 24 | 0
2027/2028 | 2008 | 1 | 5 | 1 | 0
2027/2028 | 2008 | 1 | 5 | 2 | 0
2027/2028 | 2008 | 1 | 5 | 3 | 0
2027/2028 | 2008 | 1 | 5 | 4 | 0
2027/2028 | 2008 | 1 | 5 | 5 | 0
2027/2028 | 2008 | 1 | 5 | 6 | 0
2027/2028 | 2008 | 1 | 5 | 7 | 0
2027/2028 | 2008 | 1 | 5 | 8 | 4.3338
2027/2028 | 2008 | 1 | 5 | 9 | 5640.6912
2027/2028 | 2008 | 1 | 5 | 10 | 18289.5272
2027/2028 | 2008 | 1 | 5 | 11 | 22488.3341
2027/2028 | 2008 | 1 | 5 | 12 | 24841.2271
2027/2028 | 2008 | 1 | 5 | 13 | 28305.1777
2027/2028 | 2008 | 1 | 5 | 14 | 29552.4126
2027/2028 | 2008 | 1 | 5 | 15 | 30969.4213
2027/2028 | 2008 | 1 | 5 | 16 | 30184.777
2027/2028 | 2008 | 1 | 5 | 17 | 19876.5131
2027/2028 | 2008 | 1 | 5 | 18 | 1198.9272
2027/2028 | 2008 | 1 | 5 | 19 | 0
2027/2028 | 2008 | 1 | 5 | 20 | 0
2027/2028 | 2008 | 1 | 5 | 21 | 0
2027/2028 | 2008 | 1 | 5 | 22 | 0
2027/2028 | 2008 | 1 | 5 | 23 | 0
2027/2028 | 2008 | 1 | 5 | 24 | 0
2027/2028 | 2008 | 1 | 6 | 1 | 0
2027/2028 | 2008 | 1 | 6 | 2 | 0
2027/2028 | 2008 | 1 | 6 | 3 | 0
2027/2028 | 2008 | 1 | 6 | 4 | 0
2027/2028 | 2008 | 1 | 6 | 5 | 0
2027/2028 | 2008 | 1 | 6 | 6 | 0
2027/2028 | 2008 | 1 | 6 | 7 | 0
2027/2028 | 2008 | 1 | 6 | 8 | 12.5583
2027/2028 | 2008 | 1 | 6 | 9 | 4149.1908
2027/2028 | 2008 | 1 | 6 | 10 | 16104.497
2027/2028 | 2008 | 1 | 6 | 11 | 20562.9555
2027/2028 | 2008 | 1 | 6 | 12 | 24222.1441
2027/2028 | 2008 | 1 | 6 | 13 | 27836.3884
2027/2028 | 2008 | 1 | 6 | 14 | 29311.9752
2027/2028 | 2008 | 1 | 6 | 15 | 27763.0685
2027/2028 | 2008 | 1 | 6 | 16 | 22625.1589
2027/2028 | 2008 | 1 | 6 | 17 | 17171.614
2027/2028 | 2008 | 1 | 6 | 18 | 1498.0443
2027/2028 | 2008 | 1 | 6 | 19 | 0
2027/2028 | 2008 | 1 | 6 | 20 | 0
2027/2028 | 2008 | 1 | 6 | 21 | 0
2027/2028 | 2008 | 1 | 6 | 22 | 0
2027/2028 | 2008 | 1 | 6 | 23 | 0
2027/2028 | 2008 | 1 | 6 | 24 | 0
2027/2028 | 2008 | 1 | 7 | 1 | 0
2027/2028 | 2008 | 1 | 7 | 2 | 0
2027/2028 | 2008 | 1 | 7 | 3 | 0
2027/2028 | 2008 | 1 | 7 | 4 | 0
2027/2028 | 2008 | 1 | 7 | 5 | 0
2027/2028 | 2008 | 1 | 7 | 6 | 0
2027/2028 | 2008 | 1 | 7 | 7 | 0
2027/2028 | 2008 | 1 | 7 | 8 | 2.1121
2027/2028 | 2008 | 1 | 7 | 9 | 2718.4718
2027/2028 | 2008 | 1 | 7 | 10 | 9539.4501
2027/2028 | 2008 | 1 | 7 | 11 | 15267.1424
2027/2028 | 2008 | 1 | 7 | 12 | 16875.5102
2027/2028 | 2008 | 1 | 7 | 13 | 19899.067
2027/2028 | 2008 | 1 | 7 | 14 | 17610.286
2027/2028 | 2008 | 1 | 7 | 15 | 17033.6741
2027/2028 | 2008 | 1 | 7 | 16 | 16045.3709
2027/2028 | 2008 | 1 | 7 | 17 | 9640.0768
2027/2028 | 2008 | 1 | 7 | 18 | 1097.6925
2027/2028 | 2008 | 1 | 7 | 19 | 0
2027/2028 | 2008 | 1 | 7 | 20 | 0
2027/2028 | 2008 | 1 | 7 | 21 | 0
2027/2028 | 2008 | 1 | 7 | 22 | 0
2027/2028 | 2008 | 1 | 7 | 23 | 0
2027/2028 | 2008 | 1 | 7 | 24 | 0
2027/2028 | 2008 | 1 | 8 | 1 | 0
2027/2028 | 2008 | 1 | 8 | 2 | 0
2027/2028 | 2008 | 1 | 8 | 3 | 0
2027/2028 | 2008 | 1 | 8 | 4 | 0
2027/2028 | 2008 | 1 | 8 | 5 | 0
2027/2028 | 2008 | 1 | 8 | 6 | 0
2027/2028 | 2008 | 1 | 8 | 7 | 0
2027/2028 | 2008 | 1 | 8 | 8 | 5.9053
2027/2028 | 2008 | 1 | 8 | 9 | 3584.7032
2027/2028 | 2008 | 1 | 8 | 10 | 13044.04
2027/2028 | 2008 | 1 | 8 | 11 | 17040.9985
2027/2028 | 2008 | 1 | 8 | 12 | 21642.985
2027/2028 | 2008 | 1 | 8 | 13 | 23509.2752
2027/2028 | 2008 | 1 | 8 | 14 | 22102.0133
2027/2028 | 2008 | 1 | 8 | 15 | 22305.1605
2027/2028 | 2008 | 1 | 8 | 16 | 19922.8042
2027/2028 | 2008 | 1 | 8 | 17 | 12768.2456
2027/2028 | 2008 | 1 | 8 | 18 | 1309.1584
2027/2028 | 2008 | 1 | 8 | 19 | 0
2027/2028 | 2008 | 1 | 8 | 20 | 0
2027/2028 | 2008 | 1 | 8 | 21 | 0
2027/2028 | 2008 | 1 | 8 | 22 | 0
2027/2028 | 2008 | 1 | 8 | 23 | 0
2027/2028 | 2008 | 1 | 8 | 24 | 0
2027/2028 | 2008 | 1 | 9 | 1 | 0
2027/2028 | 2008 | 1 | 9 | 2 | 0
2027/2028 | 2008 | 1 | 9 | 3 | 0
2027/2028 | 2008 | 1 | 9 | 4 | 0
2027/2028 | 2008 | 1 | 9 | 5 | 0
2027/2028 | 2008 | 1 | 9 | 6 | 0
2027/2028 | 2008 | 1 | 9 | 7 | 0
2027/2028 | 2008 | 1 | 9 | 8 | 36.5939
2027/2028 | 2008 | 1 | 9 | 9 | 14149.9892
2027/2028 | 2008 | 1 | 9 | 10 | 34182.6158
2027/2028 | 2008 | 1 | 9 | 11 | 37595.6038
2027/2028 | 2008 | 1 | 9 | 12 | 37365.817
2027/2028 | 2008 | 1 | 9 | 13 | 37258.412
2027/2028 | 2008 | 1 | 9 | 14 | 36080.9792
2027/2028 | 2008 | 1 | 9 | 15 | 35575.4099
2027/2028 | 2008 | 1 | 9 | 16 | 32266.8769
2027/2028 | 2008 | 1 | 9 | 17 | 23121.6504
2027/2028 | 2008 | 1 | 9 | 18 | 2315.408
2027/2028 | 2008 | 1 | 9 | 19 | 0
2027/2028 | 2008 | 1 | 9 | 20 | 0
2027/2028 | 2008 | 1 | 9 | 21 | 0
2027/2028 | 2008 | 1 | 9 | 22 | 0
2027/2028 | 2008 | 1 | 9 | 23 | 0
2027/2028 | 2008 | 1 | 9 | 24 | 0
2027/2028 | 2008 | 1 | 10 | 1 | 0
2027/2028 | 2008 | 1 | 10 | 2 | 0
2027/2028 | 2008 | 1 | 10 | 3 | 0
2027/2028 | 2008 | 1 | 10 | 4 | 0
2027/2028 | 2008 | 1 | 10 | 5 | 0
2027/2028 | 2008 | 1 | 10 | 6 | 0
2027/2028 | 2008 | 1 | 10 | 7 | 0
2027/2028 | 2008 | 1 | 10 | 8 | 21.224
2027/2028 | 2008 | 1 | 10 | 9 | 8982.1222
2027/2028 | 2008 | 1 | 10 | 10 | 25305.949
2027/2028 | 2008 | 1 | 10 | 11 | 30212.2341
2027/2028 | 2008 | 1 | 10 | 12 | 32002.0525
2027/2028 | 2008 | 1 | 10 | 13 | 31559.6109
2027/2028 | 2008 | 1 | 10 | 14 | 32506.2935
2027/2028 | 2008 | 1 | 10 | 15 | 34043.7783
2027/2028 | 2008 | 1 | 10 | 16 | 35154.9428
2027/2028 | 2008 | 1 | 10 | 17 | 21540.9627
2027/2028 | 2008 | 1 | 10 | 18 | 1905.4989
2027/2028 | 2008 | 1 | 10 | 19 | 0
2027/2028 | 2008 | 1 | 10 | 20 | 0
2027/2028 | 2008 | 1 | 10 | 21 | 0
2027/2028 | 2008 | 1 | 10 | 22 | 0
2027/2028 | 2008 | 1 | 10 | 23 | 0
2027/2028 | 2008 | 1 | 10 | 24 | 0
2027/2028 | 2008 | 1 | 11 | 1 | 0
2027/2028 | 2008 | 1 | 11 | 2 | 0
2027/2028 | 2008 | 1 | 11 | 3 | 0
2027/2028 | 2008 | 1 | 11 | 4 | 0
2027/2028 | 2008 | 1 | 11 | 5 | 0
2027/2028 | 2008 | 1 | 11 | 6 | 0
2027/2028 | 2008 | 1 | 11 | 7 | 0
2027/2028 | 2008 | 1 | 11 | 8 | 34.4664
2027/2028 | 2008 | 1 | 11 | 9 | 14268.2367
2027/2028 | 2008 | 1 | 11 | 10 | 36273.067
2027/2028 | 2008 | 1 | 11 | 11 | 38854.8926
2027/2028 | 2008 | 1 | 11 | 12 | 39122.9961
2027/2028 | 2008 | 1 | 11 | 13 | 38487.9688
2027/2028 | 2008 | 1 | 11 | 14 | 37530.9499
2027/2028 | 2008 | 1 | 11 | 15 | 37133.4487
2027/2028 | 2008 | 1 | 11 | 16 | 33188.875
2027/2028 | 2008 | 1 | 11 | 17 | 20031.1684
2027/2028 | 2008 | 1 | 11 | 18 | 1583.3123
2027/2028 | 2008 | 1 | 11 | 19 | 0
2027/2028 | 2008 | 1 | 11 | 20 | 0
2027/2028 | 2008 | 1 | 11 | 21 | 0
2027/2028 | 2008 | 1 | 11 | 22 | 0
2027/2028 | 2008 | 1 | 11 | 23 | 0
2027/2028 | 2008 | 1 | 11 | 24 | 0
2027/2028 | 2008 | 1 | 12 | 1 | 0
2027/2028 | 2008 | 1 | 12 | 2 | 0
2027/2028 | 2008 | 1 | 12 | 3 | 0
2027/2028 | 2008 | 1 | 12 | 4 | 0
2027/2028 | 2008 | 1 | 12 | 5 | 0
2027/2028 | 2008 | 1 | 12 | 6 | 0
2027/2028 | 2008 | 1 | 12 | 7 | 0
2027/2028 | 2008 | 1 | 12 | 8 | 28.2621
2027/2028 | 2008 | 1 | 12 | 9 | 11680.7833
2027/2028 | 2008 | 1 | 12 | 10 | 28558.4478
2027/2028 | 2008 | 1 | 12 | 11 | 31358.0959
2027/2028 | 2008 | 1 | 12 | 12 | 29347.7707
2027/2028 | 2008 | 1 | 12 | 13 | 32001.3224
2027/2028 | 2008 | 1 | 12 | 14 | 32174.7751
2027/2028 | 2008 | 1 | 12 | 15 | 33254.6571
2027/2028 | 2008 | 1 | 12 | 16 | 33002.4844
2027/2028 | 2008 | 1 | 12 | 17 | 20901.4987
2027/2028 | 2008 | 1 | 12 | 18 | 2642.1477
2027/2028 | 2008 | 1 | 12 | 19 | 0
2027/2028 | 2008 | 1 | 12 | 20 | 0
2027/2028 | 2008 | 1 | 12 | 21 | 0
2027/2028 | 2008 | 1 | 12 | 22 | 0
2027/2028 | 2008 | 1 | 12 | 23 | 0
2027/2028 | 2008 | 1 | 12 | 24 | 0
2027/2028 | 2008 | 1 | 13 | 1 | 0
2027/2028 | 2008 | 1 | 13 | 2 | 0
2027/2028 | 2008 | 1 | 13 | 3 | 0
2027/2028 | 2008 | 1 | 13 | 4 | 0
2027/2028 | 2008 | 1 | 13 | 5 | 0
2027/2028 | 2008 | 1 | 13 | 6 | 0
2027/2028 | 2008 | 1 | 13 | 7 | 0
2027/2028 | 2008 | 1 | 13 | 8 | 30.1083
2027/2028 | 2008 | 1 | 13 | 9 | 13105.2578
2027/2028 | 2008 | 1 | 13 | 10 | 35093.6449
2027/2028 | 2008 | 1 | 13 | 11 | 37759.7585
2027/2028 | 2008 | 1 | 13 | 12 | 37629.226
2027/2028 | 2008 | 1 | 13 | 13 | 36300.003
2027/2028 | 2008 | 1 | 13 | 14 | 34620.5267
2027/2028 | 2008 | 1 | 13 | 15 | 31053.5111
2027/2028 | 2008 | 1 | 13 | 16 | 27184.5239
2027/2028 | 2008 | 1 | 13 | 17 | 18083.2261
2027/2028 | 2008 | 1 | 13 | 18 | 2106.9827
2027/2028 | 2008 | 1 | 13 | 19 | 0
2027/2028 | 2008 | 1 | 13 | 20 | 0
2027/2028 | 2008 | 1 | 13 | 21 | 0
2027/2028 | 2008 | 1 | 13 | 22 | 0
2027/2028 | 2008 | 1 | 13 | 23 | 0
2027/2028 | 2008 | 1 | 13 | 24 | 0
2027/2028 | 2008 | 1 | 14 | 1 | 0
2027/2028 | 2008 | 1 | 14 | 2 | 0
2027/2028 | 2008 | 1 | 14 | 3 | 0
2027/2028 | 2008 | 1 | 14 | 4 | 0
2027/2028 | 2008 | 1 | 14 | 5 | 0
2027/2028 | 2008 | 1 | 14 | 6 | 0
2027/2028 | 2008 | 1 | 14 | 7 | 0
2027/2028 | 2008 | 1 | 14 | 8 | 31.6354
2027/2028 | 2008 | 1 | 14 | 9 | 13219.0249
2027/2028 | 2008 | 1 | 14 | 10 | 34859.9568
2027/2028 | 2008 | 1 | 14 | 11 | 38256.0958
2027/2028 | 2008 | 1 | 14 | 12 | 36518.6853
2027/2028 | 2008 | 1 | 14 | 13 | 35066.3215
2027/2028 | 2008 | 1 | 14 | 14 | 32750.7024
2027/2028 | 2008 | 1 | 14 | 15 | 31302.9639
2027/2028 | 2008 | 1 | 14 | 16 | 29507.4289
2027/2028 | 2008 | 1 | 14 | 17 | 19688.2698
2027/2028 | 2008 | 1 | 14 | 18 | 2585.3862
2027/2028 | 2008 | 1 | 14 | 19 | 0
2027/2028 | 2008 | 1 | 14 | 20 | 0
2027/2028 | 2008 | 1 | 14 | 21 | 0
2027/2028 | 2008 | 1 | 14 | 22 | 0
2027/2028 | 2008 | 1 | 14 | 23 | 0
2027/2028 | 2008 | 1 | 14 | 24 | 0
2027/2028 | 2008 | 1 | 15 | 1 | 0
2027/2028 | 2008 | 1 | 15 | 2 | 0
2027/2028 | 2008 | 1 | 15 | 3 | 0
2027/2028 | 2008 | 1 | 15 | 4 | 0
2027/2028 | 2008 | 1 | 15 | 5 | 0
2027/2028 | 2008 | 1 | 15 | 6 | 0
2027/2028 | 2008 | 1 | 15 | 7 | 0
2027/2028 | 2008 | 1 | 15 | 8 | 11.877
2027/2028 | 2008 | 1 | 15 | 9 | 7382.2519
2027/2028 | 2008 | 1 | 15 | 10 | 22049.2862
2027/2028 | 2008 | 1 | 15 | 11 | 23226.3332
2027/2028 | 2008 | 1 | 15 | 12 | 23276.929
2027/2028 | 2008 | 1 | 15 | 13 | 21355.0916
2027/2028 | 2008 | 1 | 15 | 14 | 20437.0658
2027/2028 | 2008 | 1 | 15 | 15 | 20123.7719
2027/2028 | 2008 | 1 | 15 | 16 | 18558.0699
2027/2028 | 2008 | 1 | 15 | 17 | 13800.0721
2027/2028 | 2008 | 1 | 15 | 18 | 2174.5681
2027/2028 | 2008 | 1 | 15 | 19 | 0
2027/2028 | 2008 | 1 | 15 | 20 | 0
2027/2028 | 2008 | 1 | 15 | 21 | 0
2027/2028 | 2008 | 1 | 15 | 22 | 0
2027/2028 | 2008 | 1 | 15 | 23 | 0
2027/2028 | 2008 | 1 | 15 | 24 | 0
2027/2028 | 2008 | 1 | 16 | 1 | 0
2027/2028 | 2008 | 1 | 16 | 2 | 0
2027/2028 | 2008 | 1 | 16 | 3 | 0
2027/2028 | 2008 | 1 | 16 | 4 | 0
2027/2028 | 2008 | 1 | 16 | 5 | 0
2027/2028 | 2008 | 1 | 16 | 6 | 0
2027/2028 | 2008 | 1 | 16 | 7 | 0
2027/2028 | 2008 | 1 | 16 | 8 | 2.3309
2027/2028 | 2008 | 1 | 16 | 9 | 3701.6112
2027/2028 | 2008 | 1 | 16 | 10 | 13008.1426
2027/2028 | 2008 | 1 | 16 | 11 | 16018.4678
2027/2028 | 2008 | 1 | 16 | 12 | 18480.3428
2027/2028 | 2008 | 1 | 16 | 13 | 21561.2224
2027/2028 | 2008 | 1 | 16 | 14 | 23766.7564
2027/2028 | 2008 | 1 | 16 | 15 | 22416.9365
2027/2028 | 2008 | 1 | 16 | 16 | 22969.8707
2027/2028 | 2008 | 1 | 16 | 17 | 19910.0898
2027/2028 | 2008 | 1 | 16 | 18 | 3943.1459
2027/2028 | 2008 | 1 | 16 | 19 | 0
2027/2028 | 2008 | 1 | 16 | 20 | 0
2027/2028 | 2008 | 1 | 16 | 21 | 0
2027/2028 | 2008 | 1 | 16 | 22 | 0
2027/2028 | 2008 | 1 | 16 | 23 | 0
2027/2028 | 2008 | 1 | 16 | 24 | 0
2027/2028 | 2008 | 1 | 17 | 1 | 0
2027/2028 | 2008 | 1 | 17 | 2 | 0
2027/2028 | 2008 | 1 | 17 | 3 | 0
2027/2028 | 2008 | 1 | 17 | 4 | 0
2027/2028 | 2008 | 1 | 17 | 5 | 0
2027/2028 | 2008 | 1 | 17 | 6 | 0
2027/2028 | 2008 | 1 | 17 | 7 | 0
2027/2028 | 2008 | 1 | 17 | 8 | 25.9247
2027/2028 | 2008 | 1 | 17 | 9 | 8615.1673
2027/2028 | 2008 | 1 | 17 | 10 | 25252.658
2027/2028 | 2008 | 1 | 17 | 11 | 32222.6487
2027/2028 | 2008 | 1 | 17 | 12 | 34798.9725
2027/2028 | 2008 | 1 | 17 | 13 | 36092.6492
2027/2028 | 2008 | 1 | 17 | 14 | 34660.1056
2027/2028 | 2008 | 1 | 17 | 15 | 33451.6445
2027/2028 | 2008 | 1 | 17 | 16 | 30905.5497
2027/2028 | 2008 | 1 | 17 | 17 | 20045.9064
2027/2028 | 2008 | 1 | 17 | 18 | 3070.2478
2027/2028 | 2008 | 1 | 17 | 19 | 0
2027/2028 | 2008 | 1 | 17 | 20 | 0
2027/2028 | 2008 | 1 | 17 | 21 | 0
2027/2028 | 2008 | 1 | 17 | 22 | 0
2027/2028 | 2008 | 1 | 17 | 23 | 0
2027/2028 | 2008 | 1 | 17 | 24 | 0
2027/2028 | 2008 | 1 | 18 | 1 | 0
2027/2028 | 2008 | 1 | 18 | 2 | 0
2027/2028 | 2008 | 1 | 18 | 3 | 0
2027/2028 | 2008 | 1 | 18 | 4 | 0
2027/2028 | 2008 | 1 | 18 | 5 | 0
2027/2028 | 2008 | 1 | 18 | 6 | 0
2027/2028 | 2008 | 1 | 18 | 7 | 0
2027/2028 | 2008 | 1 | 18 | 8 | 10.3298
2027/2028 | 2008 | 1 | 18 | 9 | 5559.3357
2027/2028 | 2008 | 1 | 18 | 10 | 16449.0798
2027/2028 | 2008 | 1 | 18 | 11 | 18982.3587
2027/2028 | 2008 | 1 | 18 | 12 | 20230.9197
2027/2028 | 2008 | 1 | 18 | 13 | 20039.7283
2027/2028 | 2008 | 1 | 18 | 14 | 19207.0898
2027/2028 | 2008 | 1 | 18 | 15 | 19606.6063
2027/2028 | 2008 | 1 | 18 | 16 | 17934.8911
2027/2028 | 2008 | 1 | 18 | 17 | 15831.3913
2027/2028 | 2008 | 1 | 18 | 18 | 3469.3858
2027/2028 | 2008 | 1 | 18 | 19 | 0
2027/2028 | 2008 | 1 | 18 | 20 | 0
2027/2028 | 2008 | 1 | 18 | 21 | 0
2027/2028 | 2008 | 1 | 18 | 22 | 0
2027/2028 | 2008 | 1 | 18 | 23 | 0
2027/2028 | 2008 | 1 | 18 | 24 | 0
2027/2028 | 2008 | 1 | 19 | 1 | 0
2027/2028 | 2008 | 1 | 19 | 2 | 0
2027/2028 | 2008 | 1 | 19 | 3 | 0
2027/2028 | 2008 | 1 | 19 | 4 | 0
2027/2028 | 2008 | 1 | 19 | 5 | 0
2027/2028 | 2008 | 1 | 19 | 6 | 0
2027/2028 | 2008 | 1 | 19 | 7 | 0
2027/2028 | 2008 | 1 | 19 | 8 | 26.0957
2027/2028 | 2008 | 1 | 19 | 9 | 12428.6898
2027/2028 | 2008 | 1 | 19 | 10 | 39136.8752
2027/2028 | 2008 | 1 | 19 | 11 | 46097.8617
2027/2028 | 2008 | 1 | 19 | 12 | 45038.708
2027/2028 | 2008 | 1 | 19 | 13 | 44410.5759
2027/2028 | 2008 | 1 | 19 | 14 | 44666.4496
2027/2028 | 2008 | 1 | 19 | 15 | 44695.4322
2027/2028 | 2008 | 1 | 19 | 16 | 41287.377
2027/2028 | 2008 | 1 | 19 | 17 | 32493.7989
2027/2028 | 2008 | 1 | 19 | 18 | 6209.7388
2027/2028 | 2008 | 1 | 19 | 19 | 0
2027/2028 | 2008 | 1 | 19 | 20 | 0
2027/2028 | 2008 | 1 | 19 | 21 | 0
2027/2028 | 2008 | 1 | 19 | 22 | 0
2027/2028 | 2008 | 1 | 19 | 23 | 0
2027/2028 | 2008 | 1 | 19 | 24 | 0
2027/2028 | 2008 | 1 | 20 | 1 | 0
2027/2028 | 2008 | 1 | 20 | 2 | 0
2027/2028 | 2008 | 1 | 20 | 3 | 0
2027/2028 | 2008 | 1 | 20 | 4 | 0
2027/2028 | 2008 | 1 | 20 | 5 | 0
2027/2028 | 2008 | 1 | 20 | 6 | 0
2027/2028 | 2008 | 1 | 20 | 7 | 0
2027/2028 | 2008 | 1 | 20 | 8 | 42.6181
2027/2028 | 2008 | 1 | 20 | 9 | 16804.8187
2027/2028 | 2008 | 1 | 20 | 10 | 41370.0536
2027/2028 | 2008 | 1 | 20 | 11 | 46292.9486
2027/2028 | 2008 | 1 | 20 | 12 | 44218.8278
2027/2028 | 2008 | 1 | 20 | 13 | 43699.2703
2027/2028 | 2008 | 1 | 20 | 14 | 43822.5571
2027/2028 | 2008 | 1 | 20 | 15 | 41953.0396
2027/2028 | 2008 | 1 | 20 | 16 | 38006.3263
2027/2028 | 2008 | 1 | 20 | 17 | 29678.6117
2027/2028 | 2008 | 1 | 20 | 18 | 5592.9016
2027/2028 | 2008 | 1 | 20 | 19 | 0
2027/2028 | 2008 | 1 | 20 | 20 | 0
2027/2028 | 2008 | 1 | 20 | 21 | 0
2027/2028 | 2008 | 1 | 20 | 22 | 0
2027/2028 | 2008 | 1 | 20 | 23 | 0
2027/2028 | 2008 | 1 | 20 | 24 | 0
2027/2028 | 2008 | 1 | 21 | 1 | 0
2027/2028 | 2008 | 1 | 21 | 2 | 0
2027/2028 | 2008 | 1 | 21 | 3 | 0
2027/2028 | 2008 | 1 | 21 | 4 | 0
2027/2028 | 2008 | 1 | 21 | 5 | 0
2027/2028 | 2008 | 1 | 21 | 6 | 0
2027/2028 | 2008 | 1 | 21 | 7 | 0
2027/2028 | 2008 | 1 | 21 | 8 | 0.04657
2027/2028 | 2008 | 1 | 21 | 9 | 528.2756
2027/2028 | 2008 | 1 | 21 | 10 | 4303.094
2027/2028 | 2008 | 1 | 21 | 11 | 7608.8963
2027/2028 | 2008 | 1 | 21 | 12 | 9853.3669
2027/2028 | 2008 | 1 | 21 | 13 | 11109.2414
2027/2028 | 2008 | 1 | 21 | 14 | 12644.7101
2027/2028 | 2008 | 1 | 21 | 15 | 12537.9096
2027/2028 | 2008 | 1 | 21 | 16 | 13387.642
2027/2028 | 2008 | 1 | 21 | 17 | 11845.6466
2027/2028 | 2008 | 1 | 21 | 18 | 3503.9456
2027/2028 | 2008 | 1 | 21 | 19 | 0
2027/2028 | 2008 | 1 | 21 | 20 | 0
2027/2028 | 2008 | 1 | 21 | 21 | 0
2027/2028 | 2008 | 1 | 21 | 22 | 0
2027/2028 | 2008 | 1 | 21 | 23 | 0
2027/2028 | 2008 | 1 | 21 | 24 | 0
2027/2028 | 2008 | 1 | 22 | 1 | 0
2027/2028 | 2008 | 1 | 22 | 2 | 0
2027/2028 | 2008 | 1 | 22 | 3 | 0
2027/2028 | 2008 | 1 | 22 | 4 | 0
2027/2028 | 2008 | 1 | 22 | 5 | 0
2027/2028 | 2008 | 1 | 22 | 6 | 0
2027/2028 | 2008 | 1 | 22 | 7 | 0
2027/2028 | 2008 | 1 | 22 | 8 | 8.7129
2027/2028 | 2008 | 1 | 22 | 9 | 2072.0839
2027/2028 | 2008 | 1 | 22 | 10 | 8976.9735
2027/2028 | 2008 | 1 | 22 | 11 | 11804.8751
2027/2028 | 2008 | 1 | 22 | 12 | 13286.0881
2027/2028 | 2008 | 1 | 22 | 13 | 12598.1443
2027/2028 | 2008 | 1 | 22 | 14 | 11811.8644
2027/2028 | 2008 | 1 | 22 | 15 | 12881.808
2027/2028 | 2008 | 1 | 22 | 16 | 11158.3835
2027/2028 | 2008 | 1 | 22 | 17 | 9869.9571
2027/2028 | 2008 | 1 | 22 | 18 | 2334.7317
2027/2028 | 2008 | 1 | 22 | 19 | 0
2027/2028 | 2008 | 1 | 22 | 20 | 0
2027/2028 | 2008 | 1 | 22 | 21 | 0
2027/2028 | 2008 | 1 | 22 | 22 | 0
2027/2028 | 2008 | 1 | 22 | 23 | 0
2027/2028 | 2008 | 1 | 22 | 24 | 0
2027/2028 | 2008 | 1 | 23 | 1 | 0
2027/2028 | 2008 | 1 | 23 | 2 | 0
2027/2028 | 2008 | 1 | 23 | 3 | 0
2027/2028 | 2008 | 1 | 23 | 4 | 0
2027/2028 | 2008 | 1 | 23 | 5 | 0
2027/2028 | 2008 | 1 | 23 | 6 | 0
2027/2028 | 2008 | 1 | 23 | 7 | 0
2027/2028 | 2008 | 1 | 23 | 8 | 2.8128
2027/2028 | 2008 | 1 | 23 | 9 | 2022.2238
2027/2028 | 2008 | 1 | 23 | 10 | 8218.0835
2027/2028 | 2008 | 1 | 23 | 11 | 10897.5614
2027/2028 | 2008 | 1 | 23 | 12 | 12519.9152
2027/2028 | 2008 | 1 | 23 | 13 | 12605.3779
2027/2028 | 2008 | 1 | 23 | 14 | 12414.3071
2027/2028 | 2008 | 1 | 23 | 15 | 12210.7153
2027/2028 | 2008 | 1 | 23 | 16 | 10547.7652
2027/2028 | 2008 | 1 | 23 | 17 | 6960.6054
2027/2028 | 2008 | 1 | 23 | 18 | 1478.0863
2027/2028 | 2008 | 1 | 23 | 19 | 0
2027/2028 | 2008 | 1 | 23 | 20 | 0
2027/2028 | 2008 | 1 | 23 | 21 | 0
2027/2028 | 2008 | 1 | 23 | 22 | 0
2027/2028 | 2008 | 1 | 23 | 23 | 0
2027/2028 | 2008 | 1 | 23 | 24 | 0
2027/2028 | 2008 | 1 | 24 | 1 | 0
2027/2028 | 2008 | 1 | 24 | 2 | 0
2027/2028 | 2008 | 1 | 24 | 3 | 0
2027/2028 | 2008 | 1 | 24 | 4 | 0
2027/2028 | 2008 | 1 | 24 | 5 | 0
2027/2028 | 2008 | 1 | 24 | 6 | 0
2027/2028 | 2008 | 1 | 24 | 7 | 0
2027/2028 | 2008 | 1 | 24 | 8 | 12.0554
2027/2028 | 2008 | 1 | 24 | 9 | 4157.4308
2027/2028 | 2008 | 1 | 24 | 10 | 14315.4545
2027/2028 | 2008 | 1 | 24 | 11 | 17987.1545
2027/2028 | 2008 | 1 | 24 | 12 | 19510.0705
2027/2028 | 2008 | 1 | 24 | 13 | 18993.2472
2027/2028 | 2008 | 1 | 24 | 14 | 18141.6387
2027/2028 | 2008 | 1 | 24 | 15 | 14587.6886
2027/2028 | 2008 | 1 | 24 | 16 | 12131.8196
2027/2028 | 2008 | 1 | 24 | 17 | 5574.5411
2027/2028 | 2008 | 1 | 24 | 18 | 771.8711
2027/2028 | 2008 | 1 | 24 | 19 | 0
2027/2028 | 2008 | 1 | 24 | 20 | 0
2027/2028 | 2008 | 1 | 24 | 21 | 0
2027/2028 | 2008 | 1 | 24 | 22 | 0
2027/2028 | 2008 | 1 | 24 | 23 | 0
2027/2028 | 2008 | 1 | 24 | 24 | 0
2027/2028 | 2008 | 1 | 25 | 1 | 0
2027/2028 | 2008 | 1 | 25 | 2 | 0
2027/2028 | 2008 | 1 | 25 | 3 | 0
2027/2028 | 2008 | 1 | 25 | 4 | 0
2027/2028 | 2008 | 1 | 25 | 5 | 0
2027/2028 | 2008 | 1 | 25 | 6 | 0
2027/2028 | 2008 | 1 | 25 | 7 | 0
2027/2028 | 2008 | 1 | 25 | 8 | 0.001
2027/2028 | 2008 | 1 | 25 | 9 | 485.66
2027/2028 | 2008 | 1 | 25 | 10 | 4019.5476
2027/2028 | 2008 | 1 | 25 | 11 | 6616.2807
2027/2028 | 2008 | 1 | 25 | 12 | 8375.0796
2027/2028 | 2008 | 1 | 25 | 13 | 11500.498
2027/2028 | 2008 | 1 | 25 | 14 | 12139.4901
2027/2028 | 2008 | 1 | 25 | 15 | 12984.0674
2027/2028 | 2008 | 1 | 25 | 16 | 14169.6956
2027/2028 | 2008 | 1 | 25 | 17 | 12763.8876
2027/2028 | 2008 | 1 | 25 | 18 | 3909.5787
2027/2028 | 2008 | 1 | 25 | 19 | 0
2027/2028 | 2008 | 1 | 25 | 20 | 0
2027/2028 | 2008 | 1 | 25 | 21 | 0
2027/2028 | 2008 | 1 | 25 | 22 | 0
2027/2028 | 2008 | 1 | 25 | 23 | 0
2027/2028 | 2008 | 1 | 25 | 24 | 0
2027/2028 | 2008 | 1 | 26 | 1 | 0
2027/2028 | 2008 | 1 | 26 | 2 | 0
2027/2028 | 2008 | 1 | 26 | 3 | 0
2027/2028 | 2008 | 1 | 26 | 4 | 0
2027/2028 | 2008 | 1 | 26 | 5 | 0
2027/2028 | 2008 | 1 | 26 | 6 | 0
2027/2028 | 2008 | 1 | 26 | 7 | 0
2027/2028 | 2008 | 1 | 26 | 8 | 11.3574
2027/2028 | 2008 | 1 | 26 | 9 | 7047.9336
2027/2028 | 2008 | 1 | 26 | 10 | 22401.8952
2027/2028 | 2008 | 1 | 26 | 11 | 25825.3954
2027/2028 | 2008 | 1 | 26 | 12 | 28645.0774
2027/2028 | 2008 | 1 | 26 | 13 | 32115.3038
2027/2028 | 2008 | 1 | 26 | 14 | 31988.5438
2027/2028 | 2008 | 1 | 26 | 15 | 31017.0571
2027/2028 | 2008 | 1 | 26 | 16 | 28028.6775
2027/2028 | 2008 | 1 | 26 | 17 | 20751.0209
2027/2028 | 2008 | 1 | 26 | 18 | 5544.013
2027/2028 | 2008 | 1 | 26 | 19 | 0
2027/2028 | 2008 | 1 | 26 | 20 | 0
2027/2028 | 2008 | 1 | 26 | 21 | 0
2027/2028 | 2008 | 1 | 26 | 22 | 0
2027/2028 | 2008 | 1 | 26 | 23 | 0
2027/2028 | 2008 | 1 | 26 | 24 | 0
2027/2028 | 2008 | 1 | 27 | 1 | 0
2027/2028 | 2008 | 1 | 27 | 2 | 0
2027/2028 | 2008 | 1 | 27 | 3 | 0
2027/2028 | 2008 | 1 | 27 | 4 | 0
2027/2028 | 2008 | 1 | 27 | 5 | 0
2027/2028 | 2008 | 1 | 27 | 6 | 0
2027/2028 | 2008 | 1 | 27 | 7 | 0
2027/2028 | 2008 | 1 | 27 | 8 | 17.5698
2027/2028 | 2008 | 1 | 27 | 9 | 6409.6003
2027/2028 | 2008 | 1 | 27 | 10 | 20496.6373
2027/2028 | 2008 | 1 | 27 | 11 | 25326.4932
2027/2028 | 2008 | 1 | 27 | 12 | 33261.0239
2027/2028 | 2008 | 1 | 27 | 13 | 37232.6165
2027/2028 | 2008 | 1 | 27 | 14 | 37832.4921
2027/2028 | 2008 | 1 | 27 | 15 | 36201.0354
2027/2028 | 2008 | 1 | 27 | 16 | 32219.9022
2027/2028 | 2008 | 1 | 27 | 17 | 23060.6674
2027/2028 | 2008 | 1 | 27 | 18 | 5923.4316
2027/2028 | 2008 | 1 | 27 | 19 | 0
2027/2028 | 2008 | 1 | 27 | 20 | 0
2027/2028 | 2008 | 1 | 27 | 21 | 0
2027/2028 | 2008 | 1 | 27 | 22 | 0
2027/2028 | 2008 | 1 | 27 | 23 | 0
2027/2028 | 2008 | 1 | 27 | 24 | 0
2027/2028 | 2008 | 1 | 28 | 1 | 0
2027/2028 | 2008 | 1 | 28 | 2 | 0
2027/2028 | 2008 | 1 | 28 | 3 | 0
2027/2028 | 2008 | 1 | 28 | 4 | 0
2027/2028 | 2008 | 1 | 28 | 5 | 0
2027/2028 | 2008 | 1 | 28 | 6 | 0
2027/2028 | 2008 | 1 | 28 | 7 | 0
2027/2028 | 2008 | 1 | 28 | 8 | 1.3782
2027/2028 | 2008 | 1 | 28 | 9 | 1522.5847
2027/2028 | 2008 | 1 | 28 | 10 | 8444.2512
2027/2028 | 2008 | 1 | 28 | 11 | 10786.7024
2027/2028 | 2008 | 1 | 28 | 12 | 12095.5022
2027/2028 | 2008 | 1 | 28 | 13 | 13425.9488
2027/2028 | 2008 | 1 | 28 | 14 | 14372.8714
2027/2028 | 2008 | 1 | 28 | 15 | 13316.8827
2027/2028 | 2008 | 1 | 28 | 16 | 11896.7168
2027/2028 | 2008 | 1 | 28 | 17 | 9795.8298
2027/2028 | 2008 | 1 | 28 | 18 | 3231.2168
2027/2028 | 2008 | 1 | 28 | 19 | 0
2027/2028 | 2008 | 1 | 28 | 20 | 0
2027/2028 | 2008 | 1 | 28 | 21 | 0
2027/2028 | 2008 | 1 | 28 | 22 | 0
2027/2028 | 2008 | 1 | 28 | 23 | 0
2027/2028 | 2008 | 1 | 28 | 24 | 0
2027/2028 | 2008 | 1 | 29 | 1 | 0
2027/2028 | 2008 | 1 | 29 | 2 | 0
2027/2028 | 2008 | 1 | 29 | 3 | 0
2027/2028 | 2008 | 1 | 29 | 4 | 0
2027/2028 | 2008 | 1 | 29 | 5 | 0
2027/2028 | 2008 | 1 | 29 | 6 | 0
2027/2028 | 2008 | 1 | 29 | 7 | 0
2027/2028 | 2008 | 1 | 29 | 8 | 19.3649
2027/2028 | 2008 | 1 | 29 | 9 | 6855.4078
2027/2028 | 2008 | 1 | 29 | 10 | 23038.497
2027/2028 | 2008 | 1 | 29 | 11 | 29309.1389
2027/2028 | 2008 | 1 | 29 | 12 | 32949.8316
2027/2028 | 2008 | 1 | 29 | 13 | 36426.265
2027/2028 | 2008 | 1 | 29 | 14 | 38601.4027
2027/2028 | 2008 | 1 | 29 | 15 | 43840.6863
2027/2028 | 2008 | 1 | 29 | 16 | 45050.3942
2027/2028 | 2008 | 1 | 29 | 17 | 35160.5989
2027/2028 | 2008 | 1 | 29 | 18 | 10058.2531
2027/2028 | 2008 | 1 | 29 | 19 | 0
2027/2028 | 2008 | 1 | 29 | 20 | 0
2027/2028 | 2008 | 1 | 29 | 21 | 0
2027/2028 | 2008 | 1 | 29 | 22 | 0
2027/2028 | 2008 | 1 | 29 | 23 | 0
2027/2028 | 2008 | 1 | 29 | 24 | 0
2027/2028 | 2008 | 1 | 30 | 1 | 0
2027/2028 | 2008 | 1 | 30 | 2 | 0
2027/2028 | 2008 | 1 | 30 | 3 | 0
2027/2028 | 2008 | 1 | 30 | 4 | 0
2027/2028 | 2008 | 1 | 30 | 5 | 0
2027/2028 | 2008 | 1 | 30 | 6 | 0
2027/2028 | 2008 | 1 | 30 | 7 | 0
2027/2028 | 2008 | 1 | 30 | 8 | 85.3265
2027/2028 | 2008 | 1 | 30 | 9 | 17637.2419
2027/2028 | 2008 | 1 | 30 | 10 | 43656.0143
2027/2028 | 2008 | 1 | 30 | 11 | 46092.1291
2027/2028 | 2008 | 1 | 30 | 12 | 44258.321
2027/2028 | 2008 | 1 | 30 | 13 | 42876.3519
2027/2028 | 2008 | 1 | 30 | 14 | 40435.9744
2027/2028 | 2008 | 1 | 30 | 15 | 35729.5032
2027/2028 | 2008 | 1 | 30 | 16 | 33376.4477
2027/2028 | 2008 | 1 | 30 | 17 | 25978.7392
2027/2028 | 2008 | 1 | 30 | 18 | 7736.3005
2027/2028 | 2008 | 1 | 30 | 19 | 0
2027/2028 | 2008 | 1 | 30 | 20 | 0
2027/2028 | 2008 | 1 | 30 | 21 | 0
2027/2028 | 2008 | 1 | 30 | 22 | 0
2027/2028 | 2008 | 1 | 30 | 23 | 0
2027/2028 | 2008 | 1 | 30 | 24 | 0
2027/2028 | 2008 | 1 | 31 | 1 | 0
2027/2028 | 2008 | 1 | 31 | 2 | 0
2027/2028 | 2008 | 1 | 31 | 3 | 0
2027/2028 | 2008 | 1 | 31 | 4 | 0
2027/2028 | 2008 | 1 | 31 | 5 | 0
2027/2028 | 2008 | 1 | 31 | 6 | 0
2027/2028 | 2008 | 1 | 31 | 7 | 0
2027/2028 | 2008 | 1 | 31 | 8 | 23.5081
2027/2028 | 2008 | 1 | 31 | 9 | 8396.3753
2027/2028 | 2008 | 1 | 31 | 10 | 30944.0204
2027/2028 | 2008 | 1 | 31 | 11 | 39578.4731
2027/2028 | 2008 | 1 | 31 | 12 | 41728.4569
2027/2028 | 2008 | 1 | 31 | 13 | 46209.2966
2027/2028 | 2008 | 1 | 31 | 14 | 48347.7198
2027/2028 | 2008 | 1 | 31 | 15 | 50173.6699
2027/2028 | 2008 | 1 | 31 | 16 | 47137.8867
2027/2028 | 2008 | 1 | 31 | 17 | 36365.5806
2027/2028 | 2008 | 1 | 31 | 18 | 9953.1281
2027/2028 | 2008 | 1 | 31 | 19 | 0
2027/2028 | 2008 | 1 | 31 | 20 | 0
2027/2028 | 2008 | 1 | 31 | 21 | 0
2027/2028 | 2008 | 1 | 31 | 22 | 0
2027/2028 | 2008 | 1 | 31 | 23 | 0
2027/2028 | 2008 | 1 | 31 | 24 | 0
2028/2029 | 2008 | 1 | 1 | 1 | 0
2028/2029 | 2008 | 1 | 1 | 2 | 0
2028/2029 | 2008 | 1 | 1 | 3 | 0
2028/2029 | 2008 | 1 | 1 | 4 | 0
2028/2029 | 2008 | 1 | 1 | 5 | 0
2028/2029 | 2008 | 1 | 1 | 6 | 0
2028/2029 | 2008 | 1 | 1 | 7 | 0
2028/2029 | 2008 | 1 | 1 | 8 | 32.3932
2028/2029 | 2008 | 1 | 1 | 9 | 14182.7176
2028/2029 | 2008 | 1 | 1 | 10 | 38033.8469
2028/2029 | 2008 | 1 | 1 | 11 | 43245.8373
2028/2029 | 2008 | 1 | 1 | 12 | 42702.8543
2028/2029 | 2008 | 1 | 1 | 13 | 41801.2536
2028/2029 | 2008 | 1 | 1 | 14 | 41914.2664
2028/2029 | 2008 | 1 | 1 | 15 | 42480.914
2028/2029 | 2008 | 1 | 1 | 16 | 37413.5139
2028/2029 | 2008 | 1 | 1 | 17 | 19758.3855
2028/2029 | 2008 | 1 | 1 | 18 | 911.4129
2028/2029 | 2008 | 1 | 1 | 19 | 0
2028/2029 | 2008 | 1 | 1 | 20 | 0
2028/2029 | 2008 | 1 | 1 | 21 | 0
2028/2029 | 2008 | 1 | 1 | 22 | 0
2028/2029 | 2008 | 1 | 1 | 23 | 0
2028/2029 | 2008 | 1 | 1 | 24 | 0
2028/2029 | 2008 | 1 | 2 | 1 | 0
2028/2029 | 2008 | 1 | 2 | 2 | 0
2028/2029 | 2008 | 1 | 2 | 3 | 0
2028/2029 | 2008 | 1 | 2 | 4 | 0
2028/2029 | 2008 | 1 | 2 | 5 | 0
2028/2029 | 2008 | 1 | 2 | 6 | 0
2028/2029 | 2008 | 1 | 2 | 7 | 0
2028/2029 | 2008 | 1 | 2 | 8 | 30.6219
2028/2029 | 2008 | 1 | 2 | 9 | 13269.5139
2028/2029 | 2008 | 1 | 2 | 10 | 36301.6259
2028/2029 | 2008 | 1 | 2 | 11 | 41566.2777
2028/2029 | 2008 | 1 | 2 | 12 | 39837.3656
2028/2029 | 2008 | 1 | 2 | 13 | 39577.7577
2028/2029 | 2008 | 1 | 2 | 14 | 37219.4755
2028/2029 | 2008 | 1 | 2 | 15 | 34693.3535
2028/2029 | 2008 | 1 | 2 | 16 | 27119.9112
2028/2029 | 2008 | 1 | 2 | 17 | 17375.6971
2028/2029 | 2008 | 1 | 2 | 18 | 472.0658
2028/2029 | 2008 | 1 | 2 | 19 | 0
2028/2029 | 2008 | 1 | 2 | 20 | 0
2028/2029 | 2008 | 1 | 2 | 21 | 0
2028/2029 | 2008 | 1 | 2 | 22 | 0
2028/2029 | 2008 | 1 | 2 | 23 | 0
2028/2029 | 2008 | 1 | 2 | 24 | 0
2028/2029 | 2008 | 1 | 3 | 1 | 0
2028/2029 | 2008 | 1 | 3 | 2 | 0
2028/2029 | 2008 | 1 | 3 | 3 | 0
2028/2029 | 2008 | 1 | 3 | 4 | 0
2028/2029 | 2008 | 1 | 3 | 5 | 0
2028/2029 | 2008 | 1 | 3 | 6 | 0
2028/2029 | 2008 | 1 | 3 | 7 | 0
2028/2029 | 2008 | 1 | 3 | 8 | 9.0189
2028/2029 | 2008 | 1 | 3 | 9 | 7970.3391
2028/2029 | 2008 | 1 | 3 | 10 | 26298.4375
2028/2029 | 2008 | 1 | 3 | 11 | 29355.783
2028/2029 | 2008 | 1 | 3 | 12 | 31022.6759
2028/2029 | 2008 | 1 | 3 | 13 | 31864.6386
2028/2029 | 2008 | 1 | 3 | 14 | 31514.5319
2028/2029 | 2008 | 1 | 3 | 15 | 34874.7024
2028/2029 | 2008 | 1 | 3 | 16 | 31767.8947
2028/2029 | 2008 | 1 | 3 | 17 | 18273.8032
2028/2029 | 2008 | 1 | 3 | 18 | 848.4661
2028/2029 | 2008 | 1 | 3 | 19 | 0
2028/2029 | 2008 | 1 | 3 | 20 | 0
2028/2029 | 2008 | 1 | 3 | 21 | 0
2028/2029 | 2008 | 1 | 3 | 22 | 0
2028/2029 | 2008 | 1 | 3 | 23 | 0
2028/2029 | 2008 | 1 | 3 | 24 | 0
2028/2029 | 2008 | 1 | 4 | 1 | 0
2028/2029 | 2008 | 1 | 4 | 2 | 0
2028/2029 | 2008 | 1 | 4 | 3 | 0
2028/2029 | 2008 | 1 | 4 | 4 | 0
2028/2029 | 2008 | 1 | 4 | 5 | 0
2028/2029 | 2008 | 1 | 4 | 6 | 0
2028/2029 | 2008 | 1 | 4 | 7 | 0
2028/2029 | 2008 | 1 | 4 | 8 | 11.2804
2028/2029 | 2008 | 1 | 4 | 9 | 2775.6556
2028/2029 | 2008 | 1 | 4 | 10 | 11000.2469
2028/2029 | 2008 | 1 | 4 | 11 | 15311.9201
2028/2029 | 2008 | 1 | 4 | 12 | 17372.603
2028/2029 | 2008 | 1 | 4 | 13 | 17648.992
2028/2029 | 2008 | 1 | 4 | 14 | 16290.5932
2028/2029 | 2008 | 1 | 4 | 15 | 14739.4832
2028/2029 | 2008 | 1 | 4 | 16 | 11509.3639
2028/2029 | 2008 | 1 | 4 | 17 | 7979.734
2028/2029 | 2008 | 1 | 4 | 18 | 378.9351
2028/2029 | 2008 | 1 | 4 | 19 | 0
2028/2029 | 2008 | 1 | 4 | 20 | 0
2028/2029 | 2008 | 1 | 4 | 21 | 0
2028/2029 | 2008 | 1 | 4 | 22 | 0
2028/2029 | 2008 | 1 | 4 | 23 | 0
2028/2029 | 2008 | 1 | 4 | 24 | 0
2028/2029 | 2008 | 1 | 5 | 1 | 0
2028/2029 | 2008 | 1 | 5 | 2 | 0
2028/2029 | 2008 | 1 | 5 | 3 | 0
2028/2029 | 2008 | 1 | 5 | 4 | 0
2028/2029 | 2008 | 1 | 5 | 5 | 0
2028/2029 | 2008 | 1 | 5 | 6 | 0
2028/2029 | 2008 | 1 | 5 | 7 | 0
2028/2029 | 2008 | 1 | 5 | 8 | 4.3338
2028/2029 | 2008 | 1 | 5 | 9 | 5978.2853
2028/2029 | 2008 | 1 | 5 | 10 | 19363.416
2028/2029 | 2008 | 1 | 5 | 11 | 23742.0412
2028/2029 | 2008 | 1 | 5 | 12 | 26055.2764
2028/2029 | 2008 | 1 | 5 | 13 | 29649.4731
2028/2029 | 2008 | 1 | 5 | 14 | 30841.6909
2028/2029 | 2008 | 1 | 5 | 15 | 32265.4661
2028/2029 | 2008 | 1 | 5 | 16 | 31426.9581
2028/2029 | 2008 | 1 | 5 | 17 | 20713.1932
2028/2029 | 2008 | 1 | 5 | 18 | 1269.2601
2028/2029 | 2008 | 1 | 5 | 19 | 0
2028/2029 | 2008 | 1 | 5 | 20 | 0
2028/2029 | 2008 | 1 | 5 | 21 | 0
2028/2029 | 2008 | 1 | 5 | 22 | 0
2028/2029 | 2008 | 1 | 5 | 23 | 0
2028/2029 | 2008 | 1 | 5 | 24 | 0
2028/2029 | 2008 | 1 | 6 | 1 | 0
2028/2029 | 2008 | 1 | 6 | 2 | 0
2028/2029 | 2008 | 1 | 6 | 3 | 0
2028/2029 | 2008 | 1 | 6 | 4 | 0
2028/2029 | 2008 | 1 | 6 | 5 | 0
2028/2029 | 2008 | 1 | 6 | 6 | 0
2028/2029 | 2008 | 1 | 6 | 7 | 0
2028/2029 | 2008 | 1 | 6 | 8 | 12.5583
2028/2029 | 2008 | 1 | 6 | 9 | 4435.3164
2028/2029 | 2008 | 1 | 6 | 10 | 17068.6836
2028/2029 | 2008 | 1 | 6 | 11 | 21717.8639
2028/2029 | 2008 | 1 | 6 | 12 | 25413.9725
2028/2029 | 2008 | 1 | 6 | 13 | 29055.5537
2028/2029 | 2008 | 1 | 6 | 14 | 30625.9121
2028/2029 | 2008 | 1 | 6 | 15 | 28917.5686
2028/2029 | 2008 | 1 | 6 | 16 | 23775.9349
2028/2029 | 2008 | 1 | 6 | 17 | 18043.7823
2028/2029 | 2008 | 1 | 6 | 18 | 1618.9639
2028/2029 | 2008 | 1 | 6 | 19 | 0
2028/2029 | 2008 | 1 | 6 | 20 | 0
2028/2029 | 2008 | 1 | 6 | 21 | 0
2028/2029 | 2008 | 1 | 6 | 22 | 0
2028/2029 | 2008 | 1 | 6 | 23 | 0
2028/2029 | 2008 | 1 | 6 | 24 | 0
2028/2029 | 2008 | 1 | 7 | 1 | 0
2028/2029 | 2008 | 1 | 7 | 2 | 0
2028/2029 | 2008 | 1 | 7 | 3 | 0
2028/2029 | 2008 | 1 | 7 | 4 | 0
2028/2029 | 2008 | 1 | 7 | 5 | 0
2028/2029 | 2008 | 1 | 7 | 6 | 0
2028/2029 | 2008 | 1 | 7 | 7 | 0
2028/2029 | 2008 | 1 | 7 | 8 | 2.1121
2028/2029 | 2008 | 1 | 7 | 9 | 2867.8737
2028/2029 | 2008 | 1 | 7 | 10 | 10039.9105
2028/2029 | 2008 | 1 | 7 | 11 | 16079.5151
2028/2029 | 2008 | 1 | 7 | 12 | 17826.0866
2028/2029 | 2008 | 1 | 7 | 13 | 20850.2082
2028/2029 | 2008 | 1 | 7 | 14 | 18453.825
2028/2029 | 2008 | 1 | 7 | 15 | 17932.4595
2028/2029 | 2008 | 1 | 7 | 16 | 16833.7911
2028/2029 | 2008 | 1 | 7 | 17 | 10156.9137
2028/2029 | 2008 | 1 | 7 | 18 | 1186.2638
2028/2029 | 2008 | 1 | 7 | 19 | 0
2028/2029 | 2008 | 1 | 7 | 20 | 0
2028/2029 | 2008 | 1 | 7 | 21 | 0
2028/2029 | 2008 | 1 | 7 | 22 | 0
2028/2029 | 2008 | 1 | 7 | 23 | 0
2028/2029 | 2008 | 1 | 7 | 24 | 0
2028/2029 | 2008 | 1 | 8 | 1 | 0
2028/2029 | 2008 | 1 | 8 | 2 | 0
2028/2029 | 2008 | 1 | 8 | 3 | 0
2028/2029 | 2008 | 1 | 8 | 4 | 0
2028/2029 | 2008 | 1 | 8 | 5 | 0
2028/2029 | 2008 | 1 | 8 | 6 | 0
2028/2029 | 2008 | 1 | 8 | 7 | 0
2028/2029 | 2008 | 1 | 8 | 8 | 5.9053
2028/2029 | 2008 | 1 | 8 | 9 | 3694.9964
2028/2029 | 2008 | 1 | 8 | 10 | 13532.2456
2028/2029 | 2008 | 1 | 8 | 11 | 17779.4603
2028/2029 | 2008 | 1 | 8 | 12 | 22394.099
2028/2029 | 2008 | 1 | 8 | 13 | 24574.4948
2028/2029 | 2008 | 1 | 8 | 14 | 22954.7486
2028/2029 | 2008 | 1 | 8 | 15 | 23123.666
2028/2029 | 2008 | 1 | 8 | 16 | 20728.6328
2028/2029 | 2008 | 1 | 8 | 17 | 13431.6679
2028/2029 | 2008 | 1 | 8 | 18 | 1430.1078
2028/2029 | 2008 | 1 | 8 | 19 | 0
2028/2029 | 2008 | 1 | 8 | 20 | 0
2028/2029 | 2008 | 1 | 8 | 21 | 0
2028/2029 | 2008 | 1 | 8 | 22 | 0
2028/2029 | 2008 | 1 | 8 | 23 | 0
2028/2029 | 2008 | 1 | 8 | 24 | 0
2028/2029 | 2008 | 1 | 9 | 1 | 0
2028/2029 | 2008 | 1 | 9 | 2 | 0
2028/2029 | 2008 | 1 | 9 | 3 | 0
2028/2029 | 2008 | 1 | 9 | 4 | 0
2028/2029 | 2008 | 1 | 9 | 5 | 0
2028/2029 | 2008 | 1 | 9 | 6 | 0
2028/2029 | 2008 | 1 | 9 | 7 | 0
2028/2029 | 2008 | 1 | 9 | 8 | 36.5939
2028/2029 | 2008 | 1 | 9 | 9 | 14638.7782
2028/2029 | 2008 | 1 | 9 | 10 | 35389.6481
2028/2029 | 2008 | 1 | 9 | 11 | 39094.4723
2028/2029 | 2008 | 1 | 9 | 12 | 38716.2684
2028/2029 | 2008 | 1 | 9 | 13 | 38727.8031
2028/2029 | 2008 | 1 | 9 | 14 | 37513.8027
2028/2029 | 2008 | 1 | 9 | 15 | 37008.5488
2028/2029 | 2008 | 1 | 9 | 16 | 33585.8565
2028/2029 | 2008 | 1 | 9 | 17 | 24107.5722
2028/2029 | 2008 | 1 | 9 | 18 | 2468.9125
2028/2029 | 2008 | 1 | 9 | 19 | 0
2028/2029 | 2008 | 1 | 9 | 20 | 0
2028/2029 | 2008 | 1 | 9 | 21 | 0
2028/2029 | 2008 | 1 | 9 | 22 | 0
2028/2029 | 2008 | 1 | 9 | 23 | 0
2028/2029 | 2008 | 1 | 9 | 24 | 0
2028/2029 | 2008 | 1 | 10 | 1 | 0
2028/2029 | 2008 | 1 | 10 | 2 | 0
2028/2029 | 2008 | 1 | 10 | 3 | 0
2028/2029 | 2008 | 1 | 10 | 4 | 0
2028/2029 | 2008 | 1 | 10 | 5 | 0
2028/2029 | 2008 | 1 | 10 | 6 | 0
2028/2029 | 2008 | 1 | 10 | 7 | 0
2028/2029 | 2008 | 1 | 10 | 8 | 21.224
2028/2029 | 2008 | 1 | 10 | 9 | 9255.5445
2028/2029 | 2008 | 1 | 10 | 10 | 26162.4808
2028/2029 | 2008 | 1 | 10 | 11 | 31299.0134
2028/2029 | 2008 | 1 | 10 | 12 | 33259.7523
2028/2029 | 2008 | 1 | 10 | 13 | 32750.4373
2028/2029 | 2008 | 1 | 10 | 14 | 33825.6868
2028/2029 | 2008 | 1 | 10 | 15 | 35473.6238
2028/2029 | 2008 | 1 | 10 | 16 | 36518.3013
2028/2029 | 2008 | 1 | 10 | 17 | 22476.9652
2028/2029 | 2008 | 1 | 10 | 18 | 2038.804
2028/2029 | 2008 | 1 | 10 | 19 | 0
2028/2029 | 2008 | 1 | 10 | 20 | 0
2028/2029 | 2008 | 1 | 10 | 21 | 0
2028/2029 | 2008 | 1 | 10 | 22 | 0
2028/2029 | 2008 | 1 | 10 | 23 | 0
2028/2029 | 2008 | 1 | 10 | 24 | 0
2028/2029 | 2008 | 1 | 11 | 1 | 0
2028/2029 | 2008 | 1 | 11 | 2 | 0
2028/2029 | 2008 | 1 | 11 | 3 | 0
2028/2029 | 2008 | 1 | 11 | 4 | 0
2028/2029 | 2008 | 1 | 11 | 5 | 0
2028/2029 | 2008 | 1 | 11 | 6 | 0
2028/2029 | 2008 | 1 | 11 | 7 | 0
2028/2029 | 2008 | 1 | 11 | 8 | 34.4664
2028/2029 | 2008 | 1 | 11 | 9 | 14789.9089
2028/2029 | 2008 | 1 | 11 | 10 | 37749.7051
2028/2029 | 2008 | 1 | 11 | 11 | 40436.0103
2028/2029 | 2008 | 1 | 11 | 12 | 40784.9166
2028/2029 | 2008 | 1 | 11 | 13 | 40103.3296
2028/2029 | 2008 | 1 | 11 | 14 | 39112.7739
2028/2029 | 2008 | 1 | 11 | 15 | 38655.5709
2028/2029 | 2008 | 1 | 11 | 16 | 34485.8374
2028/2029 | 2008 | 1 | 11 | 17 | 20831.0709
2028/2029 | 2008 | 1 | 11 | 18 | 1735.2309
2028/2029 | 2008 | 1 | 11 | 19 | 0
2028/2029 | 2008 | 1 | 11 | 20 | 0
2028/2029 | 2008 | 1 | 11 | 21 | 0
2028/2029 | 2008 | 1 | 11 | 22 | 0
2028/2029 | 2008 | 1 | 11 | 23 | 0
2028/2029 | 2008 | 1 | 11 | 24 | 0
2028/2029 | 2008 | 1 | 12 | 1 | 0
2028/2029 | 2008 | 1 | 12 | 2 | 0
2028/2029 | 2008 | 1 | 12 | 3 | 0
2028/2029 | 2008 | 1 | 12 | 4 | 0
2028/2029 | 2008 | 1 | 12 | 5 | 0
2028/2029 | 2008 | 1 | 12 | 6 | 0
2028/2029 | 2008 | 1 | 12 | 7 | 0
2028/2029 | 2008 | 1 | 12 | 8 | 28.2621
2028/2029 | 2008 | 1 | 12 | 9 | 12200.5238
2028/2029 | 2008 | 1 | 12 | 10 | 29880.6666
2028/2029 | 2008 | 1 | 12 | 11 | 32716.68
2028/2029 | 2008 | 1 | 12 | 12 | 30811.6023
2028/2029 | 2008 | 1 | 12 | 13 | 33393.873
2028/2029 | 2008 | 1 | 12 | 14 | 33703.7621
2028/2029 | 2008 | 1 | 12 | 15 | 34725.1071
2028/2029 | 2008 | 1 | 12 | 16 | 34466.5287
2028/2029 | 2008 | 1 | 12 | 17 | 21899.1738
2028/2029 | 2008 | 1 | 12 | 18 | 2790.242
2028/2029 | 2008 | 1 | 12 | 19 | 0
2028/2029 | 2008 | 1 | 12 | 20 | 0
2028/2029 | 2008 | 1 | 12 | 21 | 0
2028/2029 | 2008 | 1 | 12 | 22 | 0
2028/2029 | 2008 | 1 | 12 | 23 | 0
2028/2029 | 2008 | 1 | 12 | 24 | 0
2028/2029 | 2008 | 1 | 13 | 1 | 0
2028/2029 | 2008 | 1 | 13 | 2 | 0
2028/2029 | 2008 | 1 | 13 | 3 | 0
2028/2029 | 2008 | 1 | 13 | 4 | 0
2028/2029 | 2008 | 1 | 13 | 5 | 0
2028/2029 | 2008 | 1 | 13 | 6 | 0
2028/2029 | 2008 | 1 | 13 | 7 | 0
2028/2029 | 2008 | 1 | 13 | 8 | 30.1083
2028/2029 | 2008 | 1 | 13 | 9 | 13593.8928
2028/2029 | 2008 | 1 | 13 | 10 | 36485.158
2028/2029 | 2008 | 1 | 13 | 11 | 39297.4655
2028/2029 | 2008 | 1 | 13 | 12 | 39189.0773
2028/2029 | 2008 | 1 | 13 | 13 | 37742.459
2028/2029 | 2008 | 1 | 13 | 14 | 36041.5951
2028/2029 | 2008 | 1 | 13 | 15 | 32310.7076
2028/2029 | 2008 | 1 | 13 | 16 | 28302.6848
2028/2029 | 2008 | 1 | 13 | 17 | 18828.9912
2028/2029 | 2008 | 1 | 13 | 18 | 2250.5302
2028/2029 | 2008 | 1 | 13 | 19 | 0
2028/2029 | 2008 | 1 | 13 | 20 | 0
2028/2029 | 2008 | 1 | 13 | 21 | 0
2028/2029 | 2008 | 1 | 13 | 22 | 0
2028/2029 | 2008 | 1 | 13 | 23 | 0
2028/2029 | 2008 | 1 | 13 | 24 | 0
2028/2029 | 2008 | 1 | 14 | 1 | 0
2028/2029 | 2008 | 1 | 14 | 2 | 0
2028/2029 | 2008 | 1 | 14 | 3 | 0
2028/2029 | 2008 | 1 | 14 | 4 | 0
2028/2029 | 2008 | 1 | 14 | 5 | 0
2028/2029 | 2008 | 1 | 14 | 6 | 0
2028/2029 | 2008 | 1 | 14 | 7 | 0
2028/2029 | 2008 | 1 | 14 | 8 | 31.6354
2028/2029 | 2008 | 1 | 14 | 9 | 13665.8842
2028/2029 | 2008 | 1 | 14 | 10 | 36158.873
2028/2029 | 2008 | 1 | 14 | 11 | 39670.5742
2028/2029 | 2008 | 1 | 14 | 12 | 37876.8343
2028/2029 | 2008 | 1 | 14 | 13 | 36334.3921
2028/2029 | 2008 | 1 | 14 | 14 | 34027.3559
2028/2029 | 2008 | 1 | 14 | 15 | 32458.7013
2028/2029 | 2008 | 1 | 14 | 16 | 30625.5915
2028/2029 | 2008 | 1 | 14 | 17 | 20507.4185
2028/2029 | 2008 | 1 | 14 | 18 | 2760.7974
2028/2029 | 2008 | 1 | 14 | 19 | 0
2028/2029 | 2008 | 1 | 14 | 20 | 0
2028/2029 | 2008 | 1 | 14 | 21 | 0
2028/2029 | 2008 | 1 | 14 | 22 | 0
2028/2029 | 2008 | 1 | 14 | 23 | 0
2028/2029 | 2008 | 1 | 14 | 24 | 0
2028/2029 | 2008 | 1 | 15 | 1 | 0
2028/2029 | 2008 | 1 | 15 | 2 | 0
2028/2029 | 2008 | 1 | 15 | 3 | 0
2028/2029 | 2008 | 1 | 15 | 4 | 0
2028/2029 | 2008 | 1 | 15 | 5 | 0
2028/2029 | 2008 | 1 | 15 | 6 | 0
2028/2029 | 2008 | 1 | 15 | 7 | 0
2028/2029 | 2008 | 1 | 15 | 8 | 11.877
2028/2029 | 2008 | 1 | 15 | 9 | 7719.0774
2028/2029 | 2008 | 1 | 15 | 10 | 22993.092
2028/2029 | 2008 | 1 | 15 | 11 | 24205.3504
2028/2029 | 2008 | 1 | 15 | 12 | 24257.1836
2028/2029 | 2008 | 1 | 15 | 13 | 22264.5485
2028/2029 | 2008 | 1 | 15 | 14 | 21381.8392
2028/2029 | 2008 | 1 | 15 | 15 | 21044.5199
2028/2029 | 2008 | 1 | 15 | 16 | 19401.206
2028/2029 | 2008 | 1 | 15 | 17 | 14459.3801
2028/2029 | 2008 | 1 | 15 | 18 | 2318.7197
2028/2029 | 2008 | 1 | 15 | 19 | 0
2028/2029 | 2008 | 1 | 15 | 20 | 0
2028/2029 | 2008 | 1 | 15 | 21 | 0
2028/2029 | 2008 | 1 | 15 | 22 | 0
2028/2029 | 2008 | 1 | 15 | 23 | 0
2028/2029 | 2008 | 1 | 15 | 24 | 0
2028/2029 | 2008 | 1 | 16 | 1 | 0
2028/2029 | 2008 | 1 | 16 | 2 | 0
2028/2029 | 2008 | 1 | 16 | 3 | 0
2028/2029 | 2008 | 1 | 16 | 4 | 0
2028/2029 | 2008 | 1 | 16 | 5 | 0
2028/2029 | 2008 | 1 | 16 | 6 | 0
2028/2029 | 2008 | 1 | 16 | 7 | 0
2028/2029 | 2008 | 1 | 16 | 8 | 2.3309
2028/2029 | 2008 | 1 | 16 | 9 | 4075.6333
2028/2029 | 2008 | 1 | 16 | 10 | 14035.6513
2028/2029 | 2008 | 1 | 16 | 11 | 17170.9862
2028/2029 | 2008 | 1 | 16 | 12 | 19590.8165
2028/2029 | 2008 | 1 | 16 | 13 | 22658.233
2028/2029 | 2008 | 1 | 16 | 14 | 25061.4627
2028/2029 | 2008 | 1 | 16 | 15 | 23526.7662
2028/2029 | 2008 | 1 | 16 | 16 | 24066.5142
2028/2029 | 2008 | 1 | 16 | 17 | 20945.618
2028/2029 | 2008 | 1 | 16 | 18 | 4184.9921
2028/2029 | 2008 | 1 | 16 | 19 | 0
2028/2029 | 2008 | 1 | 16 | 20 | 0
2028/2029 | 2008 | 1 | 16 | 21 | 0
2028/2029 | 2008 | 1 | 16 | 22 | 0
2028/2029 | 2008 | 1 | 16 | 23 | 0
2028/2029 | 2008 | 1 | 16 | 24 | 0
2028/2029 | 2008 | 1 | 17 | 1 | 0
2028/2029 | 2008 | 1 | 17 | 2 | 0
2028/2029 | 2008 | 1 | 17 | 3 | 0
2028/2029 | 2008 | 1 | 17 | 4 | 0
2028/2029 | 2008 | 1 | 17 | 5 | 0
2028/2029 | 2008 | 1 | 17 | 6 | 0
2028/2029 | 2008 | 1 | 17 | 7 | 0
2028/2029 | 2008 | 1 | 17 | 8 | 25.9247
2028/2029 | 2008 | 1 | 17 | 9 | 8787.1126
2028/2029 | 2008 | 1 | 17 | 10 | 25934.9326
2028/2029 | 2008 | 1 | 17 | 11 | 33290.6056
2028/2029 | 2008 | 1 | 17 | 12 | 36030.4233
2028/2029 | 2008 | 1 | 17 | 13 | 37485.6005
2028/2029 | 2008 | 1 | 17 | 14 | 36054.4117
2028/2029 | 2008 | 1 | 17 | 15 | 34819.2574
2028/2029 | 2008 | 1 | 17 | 16 | 32160.3894
2028/2029 | 2008 | 1 | 17 | 17 | 20889.3758
2028/2029 | 2008 | 1 | 17 | 18 | 3260.2933
2028/2029 | 2008 | 1 | 17 | 19 | 0
2028/2029 | 2008 | 1 | 17 | 20 | 0
2028/2029 | 2008 | 1 | 17 | 21 | 0
2028/2029 | 2008 | 1 | 17 | 22 | 0
2028/2029 | 2008 | 1 | 17 | 23 | 0
2028/2029 | 2008 | 1 | 17 | 24 | 0
2028/2029 | 2008 | 1 | 18 | 1 | 0
2028/2029 | 2008 | 1 | 18 | 2 | 0
2028/2029 | 2008 | 1 | 18 | 3 | 0
2028/2029 | 2008 | 1 | 18 | 4 | 0
2028/2029 | 2008 | 1 | 18 | 5 | 0
2028/2029 | 2008 | 1 | 18 | 6 | 0
2028/2029 | 2008 | 1 | 18 | 7 | 0
2028/2029 | 2008 | 1 | 18 | 8 | 10.3298
2028/2029 | 2008 | 1 | 18 | 9 | 5833.5198
2028/2029 | 2008 | 1 | 18 | 10 | 17268.3468
2028/2029 | 2008 | 1 | 18 | 11 | 19923.8385
2028/2029 | 2008 | 1 | 18 | 12 | 21352.158
2028/2029 | 2008 | 1 | 18 | 13 | 21123.9615
2028/2029 | 2008 | 1 | 18 | 14 | 20230.4068
2028/2029 | 2008 | 1 | 18 | 15 | 20648.2501
2028/2029 | 2008 | 1 | 18 | 16 | 18883.9681
2028/2029 | 2008 | 1 | 18 | 17 | 16743.4291
2028/2029 | 2008 | 1 | 18 | 18 | 3709.7893
2028/2029 | 2008 | 1 | 18 | 19 | 0
2028/2029 | 2008 | 1 | 18 | 20 | 0
2028/2029 | 2008 | 1 | 18 | 21 | 0
2028/2029 | 2008 | 1 | 18 | 22 | 0
2028/2029 | 2008 | 1 | 18 | 23 | 0
2028/2029 | 2008 | 1 | 18 | 24 | 0
2028/2029 | 2008 | 1 | 19 | 1 | 0
2028/2029 | 2008 | 1 | 19 | 2 | 0
2028/2029 | 2008 | 1 | 19 | 3 | 0
2028/2029 | 2008 | 1 | 19 | 4 | 0
2028/2029 | 2008 | 1 | 19 | 5 | 0
2028/2029 | 2008 | 1 | 19 | 6 | 0
2028/2029 | 2008 | 1 | 19 | 7 | 0
2028/2029 | 2008 | 1 | 19 | 8 | 26.0957
2028/2029 | 2008 | 1 | 19 | 9 | 12796.0435
2028/2029 | 2008 | 1 | 19 | 10 | 40687.536
2028/2029 | 2008 | 1 | 19 | 11 | 47823.1439
2028/2029 | 2008 | 1 | 19 | 12 | 46789.5038
2028/2029 | 2008 | 1 | 19 | 13 | 46221.5445
2028/2029 | 2008 | 1 | 19 | 14 | 46497.3592
2028/2029 | 2008 | 1 | 19 | 15 | 46518.4576
2028/2029 | 2008 | 1 | 19 | 16 | 42961.2226
2028/2029 | 2008 | 1 | 19 | 17 | 33929.628
2028/2029 | 2008 | 1 | 19 | 18 | 6531.0225
2028/2029 | 2008 | 1 | 19 | 19 | 0
2028/2029 | 2008 | 1 | 19 | 20 | 0
2028/2029 | 2008 | 1 | 19 | 21 | 0
2028/2029 | 2008 | 1 | 19 | 22 | 0
2028/2029 | 2008 | 1 | 19 | 23 | 0
2028/2029 | 2008 | 1 | 19 | 24 | 0
2028/2029 | 2008 | 1 | 20 | 1 | 0
2028/2029 | 2008 | 1 | 20 | 2 | 0
2028/2029 | 2008 | 1 | 20 | 3 | 0
2028/2029 | 2008 | 1 | 20 | 4 | 0
2028/2029 | 2008 | 1 | 20 | 5 | 0
2028/2029 | 2008 | 1 | 20 | 6 | 0
2028/2029 | 2008 | 1 | 20 | 7 | 0
2028/2029 | 2008 | 1 | 20 | 8 | 42.6181
2028/2029 | 2008 | 1 | 20 | 9 | 17440.9724
2028/2029 | 2008 | 1 | 20 | 10 | 43057.0761
2028/2029 | 2008 | 1 | 20 | 11 | 48207.3111
2028/2029 | 2008 | 1 | 20 | 12 | 46051.7813
2028/2029 | 2008 | 1 | 20 | 13 | 45510.9547
2028/2029 | 2008 | 1 | 20 | 14 | 45677.5115
2028/2029 | 2008 | 1 | 20 | 15 | 43668.4932
2028/2029 | 2008 | 1 | 20 | 16 | 39637.5811
2028/2029 | 2008 | 1 | 20 | 17 | 31079.3769
2028/2029 | 2008 | 1 | 20 | 18 | 5904.8108
2028/2029 | 2008 | 1 | 20 | 19 | 0
2028/2029 | 2008 | 1 | 20 | 20 | 0
2028/2029 | 2008 | 1 | 20 | 21 | 0
2028/2029 | 2008 | 1 | 20 | 22 | 0
2028/2029 | 2008 | 1 | 20 | 23 | 0
2028/2029 | 2008 | 1 | 20 | 24 | 0
2028/2029 | 2008 | 1 | 21 | 1 | 0
2028/2029 | 2008 | 1 | 21 | 2 | 0
2028/2029 | 2008 | 1 | 21 | 3 | 0
2028/2029 | 2008 | 1 | 21 | 4 | 0
2028/2029 | 2008 | 1 | 21 | 5 | 0
2028/2029 | 2008 | 1 | 21 | 6 | 0
2028/2029 | 2008 | 1 | 21 | 7 | 0
2028/2029 | 2008 | 1 | 21 | 8 | 0.04657
2028/2029 | 2008 | 1 | 21 | 9 | 579.9495
2028/2029 | 2008 | 1 | 21 | 10 | 4671.2593
2028/2029 | 2008 | 1 | 21 | 11 | 8138.7927
2028/2029 | 2008 | 1 | 21 | 12 | 10491.0254
2028/2029 | 2008 | 1 | 21 | 13 | 11905.9895
2028/2029 | 2008 | 1 | 21 | 14 | 13547.1056
2028/2029 | 2008 | 1 | 21 | 15 | 13387.8621
2028/2029 | 2008 | 1 | 21 | 16 | 14309.4041
2028/2029 | 2008 | 1 | 21 | 17 | 12748.5466
2028/2029 | 2008 | 1 | 21 | 18 | 3749.1999
2028/2029 | 2008 | 1 | 21 | 19 | 0
2028/2029 | 2008 | 1 | 21 | 20 | 0
2028/2029 | 2008 | 1 | 21 | 21 | 0
2028/2029 | 2008 | 1 | 21 | 22 | 0
2028/2029 | 2008 | 1 | 21 | 23 | 0
2028/2029 | 2008 | 1 | 21 | 24 | 0
2028/2029 | 2008 | 1 | 22 | 1 | 0
2028/2029 | 2008 | 1 | 22 | 2 | 0
2028/2029 | 2008 | 1 | 22 | 3 | 0
2028/2029 | 2008 | 1 | 22 | 4 | 0
2028/2029 | 2008 | 1 | 22 | 5 | 0
2028/2029 | 2008 | 1 | 22 | 6 | 0
2028/2029 | 2008 | 1 | 22 | 7 | 0
2028/2029 | 2008 | 1 | 22 | 8 | 8.7129
2028/2029 | 2008 | 1 | 22 | 9 | 2270.8171
2028/2029 | 2008 | 1 | 22 | 10 | 9631.6375
2028/2029 | 2008 | 1 | 22 | 11 | 12635.8814
2028/2029 | 2008 | 1 | 22 | 12 | 14128.3935
2028/2029 | 2008 | 1 | 22 | 13 | 13304.6754
2028/2029 | 2008 | 1 | 22 | 14 | 12380.4162
2028/2029 | 2008 | 1 | 22 | 15 | 13663.3205
2028/2029 | 2008 | 1 | 22 | 16 | 11629.7182
2028/2029 | 2008 | 1 | 22 | 17 | 10294.226
2028/2029 | 2008 | 1 | 22 | 18 | 2491.385
2028/2029 | 2008 | 1 | 22 | 19 | 0
2028/2029 | 2008 | 1 | 22 | 20 | 0
2028/2029 | 2008 | 1 | 22 | 21 | 0
2028/2029 | 2008 | 1 | 22 | 22 | 0
2028/2029 | 2008 | 1 | 22 | 23 | 0
2028/2029 | 2008 | 1 | 22 | 24 | 0
2028/2029 | 2008 | 1 | 23 | 1 | 0
2028/2029 | 2008 | 1 | 23 | 2 | 0
2028/2029 | 2008 | 1 | 23 | 3 | 0
2028/2029 | 2008 | 1 | 23 | 4 | 0
2028/2029 | 2008 | 1 | 23 | 5 | 0
2028/2029 | 2008 | 1 | 23 | 6 | 0
2028/2029 | 2008 | 1 | 23 | 7 | 0
2028/2029 | 2008 | 1 | 23 | 8 | 2.8128
2028/2029 | 2008 | 1 | 23 | 9 | 2046.9953
2028/2029 | 2008 | 1 | 23 | 10 | 8551.0076
2028/2029 | 2008 | 1 | 23 | 11 | 11434.5591
2028/2029 | 2008 | 1 | 23 | 12 | 13100.1427
2028/2029 | 2008 | 1 | 23 | 13 | 13212.3305
2028/2029 | 2008 | 1 | 23 | 14 | 13018.7823
2028/2029 | 2008 | 1 | 23 | 15 | 12793.5031
2028/2029 | 2008 | 1 | 23 | 16 | 11099.5989
2028/2029 | 2008 | 1 | 23 | 17 | 7277.2513
2028/2029 | 2008 | 1 | 23 | 18 | 1546.3917
2028/2029 | 2008 | 1 | 23 | 19 | 0
2028/2029 | 2008 | 1 | 23 | 20 | 0
2028/2029 | 2008 | 1 | 23 | 21 | 0
2028/2029 | 2008 | 1 | 23 | 22 | 0
2028/2029 | 2008 | 1 | 23 | 23 | 0
2028/2029 | 2008 | 1 | 23 | 24 | 0
2028/2029 | 2008 | 1 | 24 | 1 | 0
2028/2029 | 2008 | 1 | 24 | 2 | 0
2028/2029 | 2008 | 1 | 24 | 3 | 0
2028/2029 | 2008 | 1 | 24 | 4 | 0
2028/2029 | 2008 | 1 | 24 | 5 | 0
2028/2029 | 2008 | 1 | 24 | 6 | 0
2028/2029 | 2008 | 1 | 24 | 7 | 0
2028/2029 | 2008 | 1 | 24 | 8 | 12.0554
2028/2029 | 2008 | 1 | 24 | 9 | 4247.8367
2028/2029 | 2008 | 1 | 24 | 10 | 14679.5369
2028/2029 | 2008 | 1 | 24 | 11 | 18526.5963
2028/2029 | 2008 | 1 | 24 | 12 | 20404.4957
2028/2029 | 2008 | 1 | 24 | 13 | 19814.7776
2028/2029 | 2008 | 1 | 24 | 14 | 18732.0559
2028/2029 | 2008 | 1 | 24 | 15 | 14954.1186
2028/2029 | 2008 | 1 | 24 | 16 | 12371.9142
2028/2029 | 2008 | 1 | 24 | 17 | 5680.1827
2028/2029 | 2008 | 1 | 24 | 18 | 792.1016
2028/2029 | 2008 | 1 | 24 | 19 | 0
2028/2029 | 2008 | 1 | 24 | 20 | 0
2028/2029 | 2008 | 1 | 24 | 21 | 0
2028/2029 | 2008 | 1 | 24 | 22 | 0
2028/2029 | 2008 | 1 | 24 | 23 | 0
2028/2029 | 2008 | 1 | 24 | 24 | 0
2028/2029 | 2008 | 1 | 25 | 1 | 0
2028/2029 | 2008 | 1 | 25 | 2 | 0
2028/2029 | 2008 | 1 | 25 | 3 | 0
2028/2029 | 2008 | 1 | 25 | 4 | 0
2028/2029 | 2008 | 1 | 25 | 5 | 0
2028/2029 | 2008 | 1 | 25 | 6 | 0
2028/2029 | 2008 | 1 | 25 | 7 | 0
2028/2029 | 2008 | 1 | 25 | 8 | 0.001
2028/2029 | 2008 | 1 | 25 | 9 | 488.4946
2028/2029 | 2008 | 1 | 25 | 10 | 4128.483
2028/2029 | 2008 | 1 | 25 | 11 | 7003.2396
2028/2029 | 2008 | 1 | 25 | 12 | 8735.628
2028/2029 | 2008 | 1 | 25 | 13 | 12217.491
2028/2029 | 2008 | 1 | 25 | 14 | 12934.6387
2028/2029 | 2008 | 1 | 25 | 15 | 13658.155
2028/2029 | 2008 | 1 | 25 | 16 | 15071.0021
2028/2029 | 2008 | 1 | 25 | 17 | 13571.6989
2028/2029 | 2008 | 1 | 25 | 18 | 4165.6396
2028/2029 | 2008 | 1 | 25 | 19 | 0
2028/2029 | 2008 | 1 | 25 | 20 | 0
2028/2029 | 2008 | 1 | 25 | 21 | 0
2028/2029 | 2008 | 1 | 25 | 22 | 0
2028/2029 | 2008 | 1 | 25 | 23 | 0
2028/2029 | 2008 | 1 | 25 | 24 | 0
2028/2029 | 2008 | 1 | 26 | 1 | 0
2028/2029 | 2008 | 1 | 26 | 2 | 0
2028/2029 | 2008 | 1 | 26 | 3 | 0
2028/2029 | 2008 | 1 | 26 | 4 | 0
2028/2029 | 2008 | 1 | 26 | 5 | 0
2028/2029 | 2008 | 1 | 26 | 6 | 0
2028/2029 | 2008 | 1 | 26 | 7 | 0
2028/2029 | 2008 | 1 | 26 | 8 | 11.3574
2028/2029 | 2008 | 1 | 26 | 9 | 7314.042
2028/2029 | 2008 | 1 | 26 | 10 | 23119.0518
2028/2029 | 2008 | 1 | 26 | 11 | 26775.3381
2028/2029 | 2008 | 1 | 26 | 12 | 29735.5371
2028/2029 | 2008 | 1 | 26 | 13 | 33514.2897
2028/2029 | 2008 | 1 | 26 | 14 | 33356.1145
2028/2029 | 2008 | 1 | 26 | 15 | 32254.7943
2028/2029 | 2008 | 1 | 26 | 16 | 29165.188
2028/2029 | 2008 | 1 | 26 | 17 | 21598.4676
2028/2029 | 2008 | 1 | 26 | 18 | 5785.8224
2028/2029 | 2008 | 1 | 26 | 19 | 0
2028/2029 | 2008 | 1 | 26 | 20 | 0
2028/2029 | 2008 | 1 | 26 | 21 | 0
2028/2029 | 2008 | 1 | 26 | 22 | 0
2028/2029 | 2008 | 1 | 26 | 23 | 0
2028/2029 | 2008 | 1 | 26 | 24 | 0
2028/2029 | 2008 | 1 | 27 | 1 | 0
2028/2029 | 2008 | 1 | 27 | 2 | 0
2028/2029 | 2008 | 1 | 27 | 3 | 0
2028/2029 | 2008 | 1 | 27 | 4 | 0
2028/2029 | 2008 | 1 | 27 | 5 | 0
2028/2029 | 2008 | 1 | 27 | 6 | 0
2028/2029 | 2008 | 1 | 27 | 7 | 0
2028/2029 | 2008 | 1 | 27 | 8 | 17.5698
2028/2029 | 2008 | 1 | 27 | 9 | 6662.243
2028/2029 | 2008 | 1 | 27 | 10 | 21391.3036
2028/2029 | 2008 | 1 | 27 | 11 | 26368.3799
2028/2029 | 2008 | 1 | 27 | 12 | 34314.0679
2028/2029 | 2008 | 1 | 27 | 13 | 38473.3375
2028/2029 | 2008 | 1 | 27 | 14 | 39234.4565
2028/2029 | 2008 | 1 | 27 | 15 | 37407.9289
2028/2029 | 2008 | 1 | 27 | 16 | 33517.0116
2028/2029 | 2008 | 1 | 27 | 17 | 24009.0905
2028/2029 | 2008 | 1 | 27 | 18 | 6201.5027
2028/2029 | 2008 | 1 | 27 | 19 | 0
2028/2029 | 2008 | 1 | 27 | 20 | 0
2028/2029 | 2008 | 1 | 27 | 21 | 0
2028/2029 | 2008 | 1 | 27 | 22 | 0
2028/2029 | 2008 | 1 | 27 | 23 | 0
2028/2029 | 2008 | 1 | 27 | 24 | 0
2028/2029 | 2008 | 1 | 28 | 1 | 0
2028/2029 | 2008 | 1 | 28 | 2 | 0
2028/2029 | 2008 | 1 | 28 | 3 | 0
2028/2029 | 2008 | 1 | 28 | 4 | 0
2028/2029 | 2008 | 1 | 28 | 5 | 0
2028/2029 | 2008 | 1 | 28 | 6 | 0
2028/2029 | 2008 | 1 | 28 | 7 | 0
2028/2029 | 2008 | 1 | 28 | 8 | 1.3782
2028/2029 | 2008 | 1 | 28 | 9 | 1561.1389
2028/2029 | 2008 | 1 | 28 | 10 | 8802.3137
2028/2029 | 2008 | 1 | 28 | 11 | 11353.7259
2028/2029 | 2008 | 1 | 28 | 12 | 12820.4417
2028/2029 | 2008 | 1 | 28 | 13 | 14186.5944
2028/2029 | 2008 | 1 | 28 | 14 | 15154.1206
2028/2029 | 2008 | 1 | 28 | 15 | 14149.928
2028/2029 | 2008 | 1 | 28 | 16 | 12751.1329
2028/2029 | 2008 | 1 | 28 | 17 | 10490.7935
2028/2029 | 2008 | 1 | 28 | 18 | 3434.4009
2028/2029 | 2008 | 1 | 28 | 19 | 0
2028/2029 | 2008 | 1 | 28 | 20 | 0
2028/2029 | 2008 | 1 | 28 | 21 | 0
2028/2029 | 2008 | 1 | 28 | 22 | 0
2028/2029 | 2008 | 1 | 28 | 23 | 0
2028/2029 | 2008 | 1 | 28 | 24 | 0
2028/2029 | 2008 | 1 | 29 | 1 | 0
2028/2029 | 2008 | 1 | 29 | 2 | 0
2028/2029 | 2008 | 1 | 29 | 3 | 0
2028/2029 | 2008 | 1 | 29 | 4 | 0
2028/2029 | 2008 | 1 | 29 | 5 | 0
2028/2029 | 2008 | 1 | 29 | 6 | 0
2028/2029 | 2008 | 1 | 29 | 7 | 0
2028/2029 | 2008 | 1 | 29 | 8 | 19.3649
2028/2029 | 2008 | 1 | 29 | 9 | 7165.6595
2028/2029 | 2008 | 1 | 29 | 10 | 24069.499
2028/2029 | 2008 | 1 | 29 | 11 | 30603.5422
2028/2029 | 2008 | 1 | 29 | 12 | 34487.9969
2028/2029 | 2008 | 1 | 29 | 13 | 38024.5707
2028/2029 | 2008 | 1 | 29 | 14 | 40110.3353
2028/2029 | 2008 | 1 | 29 | 15 | 45437.0276
2028/2029 | 2008 | 1 | 29 | 16 | 46813.5088
2028/2029 | 2008 | 1 | 29 | 17 | 36656.3025
2028/2029 | 2008 | 1 | 29 | 18 | 10511.8411
2028/2029 | 2008 | 1 | 29 | 19 | 0
2028/2029 | 2008 | 1 | 29 | 20 | 0
2028/2029 | 2008 | 1 | 29 | 21 | 0
2028/2029 | 2008 | 1 | 29 | 22 | 0
2028/2029 | 2008 | 1 | 29 | 23 | 0
2028/2029 | 2008 | 1 | 29 | 24 | 0
2028/2029 | 2008 | 1 | 30 | 1 | 0
2028/2029 | 2008 | 1 | 30 | 2 | 0
2028/2029 | 2008 | 1 | 30 | 3 | 0
2028/2029 | 2008 | 1 | 30 | 4 | 0
2028/2029 | 2008 | 1 | 30 | 5 | 0
2028/2029 | 2008 | 1 | 30 | 6 | 0
2028/2029 | 2008 | 1 | 30 | 7 | 0
2028/2029 | 2008 | 1 | 30 | 8 | 85.3265
2028/2029 | 2008 | 1 | 30 | 9 | 18285.2861
2028/2029 | 2008 | 1 | 30 | 10 | 45239.6086
2028/2029 | 2008 | 1 | 30 | 11 | 47754.559
2028/2029 | 2008 | 1 | 30 | 12 | 45899.5702
2028/2029 | 2008 | 1 | 30 | 13 | 44469.621
2028/2029 | 2008 | 1 | 30 | 14 | 42013.9076
2028/2029 | 2008 | 1 | 30 | 15 | 37033.4941
2028/2029 | 2008 | 1 | 30 | 16 | 34799.6562
2028/2029 | 2008 | 1 | 30 | 17 | 27154.537
2028/2029 | 2008 | 1 | 30 | 18 | 8107.3994
2028/2029 | 2008 | 1 | 30 | 19 | 0
2028/2029 | 2008 | 1 | 30 | 20 | 0
2028/2029 | 2008 | 1 | 30 | 21 | 0
2028/2029 | 2008 | 1 | 30 | 22 | 0
2028/2029 | 2008 | 1 | 30 | 23 | 0
2028/2029 | 2008 | 1 | 30 | 24 | 0
2028/2029 | 2008 | 1 | 31 | 1 | 0
2028/2029 | 2008 | 1 | 31 | 2 | 0
2028/2029 | 2008 | 1 | 31 | 3 | 0
2028/2029 | 2008 | 1 | 31 | 4 | 0
2028/2029 | 2008 | 1 | 31 | 5 | 0
2028/2029 | 2008 | 1 | 31 | 6 | 0
2028/2029 | 2008 | 1 | 31 | 7 | 0
2028/2029 | 2008 | 1 | 31 | 8 | 23.5081
2028/2029 | 2008 | 1 | 31 | 9 | 8744.1945
2028/2029 | 2008 | 1 | 31 | 10 | 32042.6613
2028/2029 | 2008 | 1 | 31 | 11 | 40961.2192
2028/2029 | 2008 | 1 | 31 | 12 | 43520.7121
2028/2029 | 2008 | 1 | 31 | 13 | 48175.7631
2028/2029 | 2008 | 1 | 31 | 14 | 50344.4127
2028/2029 | 2008 | 1 | 31 | 15 | 52250.9889
2028/2029 | 2008 | 1 | 31 | 16 | 49176.2446
2028/2029 | 2008 | 1 | 31 | 17 | 38010.0495
2028/2029 | 2008 | 1 | 31 | 18 | 10460.2485
2028/2029 | 2008 | 1 | 31 | 19 | 0
2028/2029 | 2008 | 1 | 31 | 20 | 0
2028/2029 | 2008 | 1 | 31 | 21 | 0
2028/2029 | 2008 | 1 | 31 | 22 | 0
2028/2029 | 2008 | 1 | 31 | 23 | 0
2028/2029 | 2008 | 1 | 31 | 24 | 0
2029/2030 | 2008 | 1 | 1 | 1 | 0
2029/2030 | 2008 | 1 | 1 | 2 | 0
2029/2030 | 2008 | 1 | 1 | 3 | 0
2029/2030 | 2008 | 1 | 1 | 4 | 0
2029/2030 | 2008 | 1 | 1 | 5 | 0
2029/2030 | 2008 | 1 | 1 | 6 | 0
2029/2030 | 2008 | 1 | 1 | 7 | 0
2029/2030 | 2008 | 1 | 1 | 8 | 32.3932
2029/2030 | 2008 | 1 | 1 | 9 | 14389.6529
2029/2030 | 2008 | 1 | 1 | 10 | 38616.7711
2029/2030 | 2008 | 1 | 1 | 11 | 43927.0794
2029/2030 | 2008 | 1 | 1 | 12 | 43365.0565
2029/2030 | 2008 | 1 | 1 | 13 | 42461.1566
2029/2030 | 2008 | 1 | 1 | 14 | 42581.8677
2029/2030 | 2008 | 1 | 1 | 15 | 43167.0927
2029/2030 | 2008 | 1 | 1 | 16 | 37990.2783
2029/2030 | 2008 | 1 | 1 | 17 | 20014.5696
2029/2030 | 2008 | 1 | 1 | 18 | 911.4129
2029/2030 | 2008 | 1 | 1 | 19 | 0
2029/2030 | 2008 | 1 | 1 | 20 | 0
2029/2030 | 2008 | 1 | 1 | 21 | 0
2029/2030 | 2008 | 1 | 1 | 22 | 0
2029/2030 | 2008 | 1 | 1 | 23 | 0
2029/2030 | 2008 | 1 | 1 | 24 | 0
2029/2030 | 2008 | 1 | 2 | 1 | 0
2029/2030 | 2008 | 1 | 2 | 2 | 0
2029/2030 | 2008 | 1 | 2 | 3 | 0
2029/2030 | 2008 | 1 | 2 | 4 | 0
2029/2030 | 2008 | 1 | 2 | 5 | 0
2029/2030 | 2008 | 1 | 2 | 6 | 0
2029/2030 | 2008 | 1 | 2 | 7 | 0
2029/2030 | 2008 | 1 | 2 | 8 | 30.6219
2029/2030 | 2008 | 1 | 2 | 9 | 13465.0328
2029/2030 | 2008 | 1 | 2 | 10 | 36895.7654
2029/2030 | 2008 | 1 | 2 | 11 | 42226.695
2029/2030 | 2008 | 1 | 2 | 12 | 40480.4846
2029/2030 | 2008 | 1 | 2 | 13 | 40217.1055
2029/2030 | 2008 | 1 | 2 | 14 | 37867.8995
2029/2030 | 2008 | 1 | 2 | 15 | 35293.3912
2029/2030 | 2008 | 1 | 2 | 16 | 27563.6419
2029/2030 | 2008 | 1 | 2 | 17 | 17617.4296
2029/2030 | 2008 | 1 | 2 | 18 | 472.0658
2029/2030 | 2008 | 1 | 2 | 19 | 0
2029/2030 | 2008 | 1 | 2 | 20 | 0
2029/2030 | 2008 | 1 | 2 | 21 | 0
2029/2030 | 2008 | 1 | 2 | 22 | 0
2029/2030 | 2008 | 1 | 2 | 23 | 0
2029/2030 | 2008 | 1 | 2 | 24 | 0
2029/2030 | 2008 | 1 | 3 | 1 | 0
2029/2030 | 2008 | 1 | 3 | 2 | 0
2029/2030 | 2008 | 1 | 3 | 3 | 0
2029/2030 | 2008 | 1 | 3 | 4 | 0
2029/2030 | 2008 | 1 | 3 | 5 | 0
2029/2030 | 2008 | 1 | 3 | 6 | 0
2029/2030 | 2008 | 1 | 3 | 7 | 0
2029/2030 | 2008 | 1 | 3 | 8 | 9.0189
2029/2030 | 2008 | 1 | 3 | 9 | 8108.7069
2029/2030 | 2008 | 1 | 3 | 10 | 26728.5418
2029/2030 | 2008 | 1 | 3 | 11 | 29978.0886
2029/2030 | 2008 | 1 | 3 | 12 | 31596.5767
2029/2030 | 2008 | 1 | 3 | 13 | 32410.0875
2029/2030 | 2008 | 1 | 3 | 14 | 32060.1943
2029/2030 | 2008 | 1 | 3 | 15 | 35420.2977
2029/2030 | 2008 | 1 | 3 | 16 | 32268.7747
2029/2030 | 2008 | 1 | 3 | 17 | 18540.8953
2029/2030 | 2008 | 1 | 3 | 18 | 848.4661
2029/2030 | 2008 | 1 | 3 | 19 | 0
2029/2030 | 2008 | 1 | 3 | 20 | 0
2029/2030 | 2008 | 1 | 3 | 21 | 0
2029/2030 | 2008 | 1 | 3 | 22 | 0
2029/2030 | 2008 | 1 | 3 | 23 | 0
2029/2030 | 2008 | 1 | 3 | 24 | 0
2029/2030 | 2008 | 1 | 4 | 1 | 0
2029/2030 | 2008 | 1 | 4 | 2 | 0
2029/2030 | 2008 | 1 | 4 | 3 | 0
2029/2030 | 2008 | 1 | 4 | 4 | 0
2029/2030 | 2008 | 1 | 4 | 5 | 0
2029/2030 | 2008 | 1 | 4 | 6 | 0
2029/2030 | 2008 | 1 | 4 | 7 | 0
2029/2030 | 2008 | 1 | 4 | 8 | 11.2804
2029/2030 | 2008 | 1 | 4 | 9 | 2797.5848
2029/2030 | 2008 | 1 | 4 | 10 | 11070.7121
2029/2030 | 2008 | 1 | 4 | 11 | 15437.8429
2029/2030 | 2008 | 1 | 4 | 12 | 17555.4606
2029/2030 | 2008 | 1 | 4 | 13 | 17900.981
2029/2030 | 2008 | 1 | 4 | 14 | 16642.2123
2029/2030 | 2008 | 1 | 4 | 15 | 14880.0218
2029/2030 | 2008 | 1 | 4 | 16 | 11658.5096
2029/2030 | 2008 | 1 | 4 | 17 | 8062.921
2029/2030 | 2008 | 1 | 4 | 18 | 378.9351
2029/2030 | 2008 | 1 | 4 | 19 | 0
2029/2030 | 2008 | 1 | 4 | 20 | 0
2029/2030 | 2008 | 1 | 4 | 21 | 0
2029/2030 | 2008 | 1 | 4 | 22 | 0
2029/2030 | 2008 | 1 | 4 | 23 | 0
2029/2030 | 2008 | 1 | 4 | 24 | 0
2029/2030 | 2008 | 1 | 5 | 1 | 0
2029/2030 | 2008 | 1 | 5 | 2 | 0
2029/2030 | 2008 | 1 | 5 | 3 | 0
2029/2030 | 2008 | 1 | 5 | 4 | 0
2029/2030 | 2008 | 1 | 5 | 5 | 0
2029/2030 | 2008 | 1 | 5 | 6 | 0
2029/2030 | 2008 | 1 | 5 | 7 | 0
2029/2030 | 2008 | 1 | 5 | 8 | 4.3338
2029/2030 | 2008 | 1 | 5 | 9 | 6158.7637
2029/2030 | 2008 | 1 | 5 | 10 | 19913.9873
2029/2030 | 2008 | 1 | 5 | 11 | 24300.0154
2029/2030 | 2008 | 1 | 5 | 12 | 26605.6953
2029/2030 | 2008 | 1 | 5 | 13 | 30205.9672
2029/2030 | 2008 | 1 | 5 | 14 | 31344.3661
2029/2030 | 2008 | 1 | 5 | 15 | 32729.5873
2029/2030 | 2008 | 1 | 5 | 16 | 31811.3926
2029/2030 | 2008 | 1 | 5 | 17 | 20969.6663
2029/2030 | 2008 | 1 | 5 | 18 | 1269.2601
2029/2030 | 2008 | 1 | 5 | 19 | 0
2029/2030 | 2008 | 1 | 5 | 20 | 0
2029/2030 | 2008 | 1 | 5 | 21 | 0
2029/2030 | 2008 | 1 | 5 | 22 | 0
2029/2030 | 2008 | 1 | 5 | 23 | 0
2029/2030 | 2008 | 1 | 5 | 24 | 0
2029/2030 | 2008 | 1 | 6 | 1 | 0
2029/2030 | 2008 | 1 | 6 | 2 | 0
2029/2030 | 2008 | 1 | 6 | 3 | 0
2029/2030 | 2008 | 1 | 6 | 4 | 0
2029/2030 | 2008 | 1 | 6 | 5 | 0
2029/2030 | 2008 | 1 | 6 | 6 | 0
2029/2030 | 2008 | 1 | 6 | 7 | 0
2029/2030 | 2008 | 1 | 6 | 8 | 12.5583
2029/2030 | 2008 | 1 | 6 | 9 | 4582.9993
2029/2030 | 2008 | 1 | 6 | 10 | 17500.2307
2029/2030 | 2008 | 1 | 6 | 11 | 22226.3756
2029/2030 | 2008 | 1 | 6 | 12 | 25963.6461
2029/2030 | 2008 | 1 | 6 | 13 | 29567.8717
2029/2030 | 2008 | 1 | 6 | 14 | 31170.0857
2029/2030 | 2008 | 1 | 6 | 15 | 29435.6424
2029/2030 | 2008 | 1 | 6 | 16 | 24254.8867
2029/2030 | 2008 | 1 | 6 | 17 | 18384.4379
2029/2030 | 2008 | 1 | 6 | 18 | 1618.9639
2029/2030 | 2008 | 1 | 6 | 19 | 0
2029/2030 | 2008 | 1 | 6 | 20 | 0
2029/2030 | 2008 | 1 | 6 | 21 | 0
2029/2030 | 2008 | 1 | 6 | 22 | 0
2029/2030 | 2008 | 1 | 6 | 23 | 0
2029/2030 | 2008 | 1 | 6 | 24 | 0
2029/2030 | 2008 | 1 | 7 | 1 | 0
2029/2030 | 2008 | 1 | 7 | 2 | 0
2029/2030 | 2008 | 1 | 7 | 3 | 0
2029/2030 | 2008 | 1 | 7 | 4 | 0
2029/2030 | 2008 | 1 | 7 | 5 | 0
2029/2030 | 2008 | 1 | 7 | 6 | 0
2029/2030 | 2008 | 1 | 7 | 7 | 0
2029/2030 | 2008 | 1 | 7 | 8 | 2.1121
2029/2030 | 2008 | 1 | 7 | 9 | 2920.9476
2029/2030 | 2008 | 1 | 7 | 10 | 10203.3661
2029/2030 | 2008 | 1 | 7 | 11 | 16274.6803
2029/2030 | 2008 | 1 | 7 | 12 | 18069.9803
2029/2030 | 2008 | 1 | 7 | 13 | 21237.4957
2029/2030 | 2008 | 1 | 7 | 14 | 18841.3466
2029/2030 | 2008 | 1 | 7 | 15 | 18314.7986
2029/2030 | 2008 | 1 | 7 | 16 | 17236.4942
2029/2030 | 2008 | 1 | 7 | 17 | 10381.5741
2029/2030 | 2008 | 1 | 7 | 18 | 1186.2638
2029/2030 | 2008 | 1 | 7 | 19 | 0
2029/2030 | 2008 | 1 | 7 | 20 | 0
2029/2030 | 2008 | 1 | 7 | 21 | 0
2029/2030 | 2008 | 1 | 7 | 22 | 0
2029/2030 | 2008 | 1 | 7 | 23 | 0
2029/2030 | 2008 | 1 | 7 | 24 | 0
2029/2030 | 2008 | 1 | 8 | 1 | 0
2029/2030 | 2008 | 1 | 8 | 2 | 0
2029/2030 | 2008 | 1 | 8 | 3 | 0
2029/2030 | 2008 | 1 | 8 | 4 | 0
2029/2030 | 2008 | 1 | 8 | 5 | 0
2029/2030 | 2008 | 1 | 8 | 6 | 0
2029/2030 | 2008 | 1 | 8 | 7 | 0
2029/2030 | 2008 | 1 | 8 | 8 | 5.9053
2029/2030 | 2008 | 1 | 8 | 9 | 3837.2313
2029/2030 | 2008 | 1 | 8 | 10 | 13961.2059
2029/2030 | 2008 | 1 | 8 | 11 | 18398.3916
2029/2030 | 2008 | 1 | 8 | 12 | 23049.5533
2029/2030 | 2008 | 1 | 8 | 13 | 25196.0165
2029/2030 | 2008 | 1 | 8 | 14 | 23585.566
2029/2030 | 2008 | 1 | 8 | 15 | 23752.219
2029/2030 | 2008 | 1 | 8 | 16 | 21322.3535
2029/2030 | 2008 | 1 | 8 | 17 | 13755.9605
2029/2030 | 2008 | 1 | 8 | 18 | 1442.3203
2029/2030 | 2008 | 1 | 8 | 19 | 0
2029/2030 | 2008 | 1 | 8 | 20 | 0
2029/2030 | 2008 | 1 | 8 | 21 | 0
2029/2030 | 2008 | 1 | 8 | 22 | 0
2029/2030 | 2008 | 1 | 8 | 23 | 0
2029/2030 | 2008 | 1 | 8 | 24 | 0
2029/2030 | 2008 | 1 | 9 | 1 | 0
2029/2030 | 2008 | 1 | 9 | 2 | 0
2029/2030 | 2008 | 1 | 9 | 3 | 0
2029/2030 | 2008 | 1 | 9 | 4 | 0
2029/2030 | 2008 | 1 | 9 | 5 | 0
2029/2030 | 2008 | 1 | 9 | 6 | 0
2029/2030 | 2008 | 1 | 9 | 7 | 0
2029/2030 | 2008 | 1 | 9 | 8 | 36.5939
2029/2030 | 2008 | 1 | 9 | 9 | 14783.201
2029/2030 | 2008 | 1 | 9 | 10 | 35913.9922
2029/2030 | 2008 | 1 | 9 | 11 | 39644.557
2029/2030 | 2008 | 1 | 9 | 12 | 39294.5847
2029/2030 | 2008 | 1 | 9 | 13 | 39239.4172
2029/2030 | 2008 | 1 | 9 | 14 | 38082.1826
2029/2030 | 2008 | 1 | 9 | 15 | 37562.046
2029/2030 | 2008 | 1 | 9 | 16 | 34104.2853
2029/2030 | 2008 | 1 | 9 | 17 | 24476.0302
2029/2030 | 2008 | 1 | 9 | 18 | 2485.0794
2029/2030 | 2008 | 1 | 9 | 19 | 0
2029/2030 | 2008 | 1 | 9 | 20 | 0
2029/2030 | 2008 | 1 | 9 | 21 | 0
2029/2030 | 2008 | 1 | 9 | 22 | 0
2029/2030 | 2008 | 1 | 9 | 23 | 0
2029/2030 | 2008 | 1 | 9 | 24 | 0
2029/2030 | 2008 | 1 | 10 | 1 | 0
2029/2030 | 2008 | 1 | 10 | 2 | 0
2029/2030 | 2008 | 1 | 10 | 3 | 0
2029/2030 | 2008 | 1 | 10 | 4 | 0
2029/2030 | 2008 | 1 | 10 | 5 | 0
2029/2030 | 2008 | 1 | 10 | 6 | 0
2029/2030 | 2008 | 1 | 10 | 7 | 0
2029/2030 | 2008 | 1 | 10 | 8 | 21.224
2029/2030 | 2008 | 1 | 10 | 9 | 9455.5205
2029/2030 | 2008 | 1 | 10 | 10 | 26719.2911
2029/2030 | 2008 | 1 | 10 | 11 | 31903.0619
2029/2030 | 2008 | 1 | 10 | 12 | 33896.83
2029/2030 | 2008 | 1 | 10 | 13 | 33367.2855
2029/2030 | 2008 | 1 | 10 | 14 | 34432.83
2029/2030 | 2008 | 1 | 10 | 15 | 36089.1162
2029/2030 | 2008 | 1 | 10 | 16 | 37076.563
2029/2030 | 2008 | 1 | 10 | 17 | 22793.2396
2029/2030 | 2008 | 1 | 10 | 18 | 2053.5336
2029/2030 | 2008 | 1 | 10 | 19 | 0
2029/2030 | 2008 | 1 | 10 | 20 | 0
2029/2030 | 2008 | 1 | 10 | 21 | 0
2029/2030 | 2008 | 1 | 10 | 22 | 0
2029/2030 | 2008 | 1 | 10 | 23 | 0
2029/2030 | 2008 | 1 | 10 | 24 | 0
2029/2030 | 2008 | 1 | 11 | 1 | 0
2029/2030 | 2008 | 1 | 11 | 2 | 0
2029/2030 | 2008 | 1 | 11 | 3 | 0
2029/2030 | 2008 | 1 | 11 | 4 | 0
2029/2030 | 2008 | 1 | 11 | 5 | 0
2029/2030 | 2008 | 1 | 11 | 6 | 0
2029/2030 | 2008 | 1 | 11 | 7 | 0
2029/2030 | 2008 | 1 | 11 | 8 | 34.4664
2029/2030 | 2008 | 1 | 11 | 9 | 14912.7281
2029/2030 | 2008 | 1 | 11 | 10 | 38155.3521
2029/2030 | 2008 | 1 | 11 | 11 | 41054.168
2029/2030 | 2008 | 1 | 11 | 12 | 41414.0116
2029/2030 | 2008 | 1 | 11 | 13 | 40708.807
2029/2030 | 2008 | 1 | 11 | 14 | 39729.2396
2029/2030 | 2008 | 1 | 11 | 15 | 39281.452
2029/2030 | 2008 | 1 | 11 | 16 | 35067.5407
2029/2030 | 2008 | 1 | 11 | 17 | 21150.0509
2029/2030 | 2008 | 1 | 11 | 18 | 1750.9188
2029/2030 | 2008 | 1 | 11 | 19 | 0
2029/2030 | 2008 | 1 | 11 | 20 | 0
2029/2030 | 2008 | 1 | 11 | 21 | 0
2029/2030 | 2008 | 1 | 11 | 22 | 0
2029/2030 | 2008 | 1 | 11 | 23 | 0
2029/2030 | 2008 | 1 | 11 | 24 | 0
2029/2030 | 2008 | 1 | 12 | 1 | 0
2029/2030 | 2008 | 1 | 12 | 2 | 0
2029/2030 | 2008 | 1 | 12 | 3 | 0
2029/2030 | 2008 | 1 | 12 | 4 | 0
2029/2030 | 2008 | 1 | 12 | 5 | 0
2029/2030 | 2008 | 1 | 12 | 6 | 0
2029/2030 | 2008 | 1 | 12 | 7 | 0
2029/2030 | 2008 | 1 | 12 | 8 | 28.2621
2029/2030 | 2008 | 1 | 12 | 9 | 12321.1277
2029/2030 | 2008 | 1 | 12 | 10 | 30274.3451
2029/2030 | 2008 | 1 | 12 | 11 | 33112.0457
2029/2030 | 2008 | 1 | 12 | 12 | 31393.0978
2029/2030 | 2008 | 1 | 12 | 13 | 34029.2509
2029/2030 | 2008 | 1 | 12 | 14 | 34342.1834
2029/2030 | 2008 | 1 | 12 | 15 | 35380.646
2029/2030 | 2008 | 1 | 12 | 16 | 35061.3249
2029/2030 | 2008 | 1 | 12 | 17 | 22244.4201
2029/2030 | 2008 | 1 | 12 | 18 | 2806.6038
2029/2030 | 2008 | 1 | 12 | 19 | 0
2029/2030 | 2008 | 1 | 12 | 20 | 0
2029/2030 | 2008 | 1 | 12 | 21 | 0
2029/2030 | 2008 | 1 | 12 | 22 | 0
2029/2030 | 2008 | 1 | 12 | 23 | 0
2029/2030 | 2008 | 1 | 12 | 24 | 0
2029/2030 | 2008 | 1 | 13 | 1 | 0
2029/2030 | 2008 | 1 | 13 | 2 | 0
2029/2030 | 2008 | 1 | 13 | 3 | 0
2029/2030 | 2008 | 1 | 13 | 4 | 0
2029/2030 | 2008 | 1 | 13 | 5 | 0
2029/2030 | 2008 | 1 | 13 | 6 | 0
2029/2030 | 2008 | 1 | 13 | 7 | 0
2029/2030 | 2008 | 1 | 13 | 8 | 30.1083
2029/2030 | 2008 | 1 | 13 | 9 | 13781.2889
2029/2030 | 2008 | 1 | 13 | 10 | 37042.5736
2029/2030 | 2008 | 1 | 13 | 11 | 39895.0377
2029/2030 | 2008 | 1 | 13 | 12 | 39783.8334
2029/2030 | 2008 | 1 | 13 | 13 | 38302.2928
2029/2030 | 2008 | 1 | 13 | 14 | 36621.2209
2029/2030 | 2008 | 1 | 13 | 15 | 32926.5777
2029/2030 | 2008 | 1 | 13 | 16 | 28639.4317
2029/2030 | 2008 | 1 | 13 | 17 | 18976.2863
2029/2030 | 2008 | 1 | 13 | 18 | 2255.4752
2029/2030 | 2008 | 1 | 13 | 19 | 0
2029/2030 | 2008 | 1 | 13 | 20 | 0
2029/2030 | 2008 | 1 | 13 | 21 | 0
2029/2030 | 2008 | 1 | 13 | 22 | 0
2029/2030 | 2008 | 1 | 13 | 23 | 0
2029/2030 | 2008 | 1 | 13 | 24 | 0
2029/2030 | 2008 | 1 | 14 | 1 | 0
2029/2030 | 2008 | 1 | 14 | 2 | 0
2029/2030 | 2008 | 1 | 14 | 3 | 0
2029/2030 | 2008 | 1 | 14 | 4 | 0
2029/2030 | 2008 | 1 | 14 | 5 | 0
2029/2030 | 2008 | 1 | 14 | 6 | 0
2029/2030 | 2008 | 1 | 14 | 7 | 0
2029/2030 | 2008 | 1 | 14 | 8 | 31.6354
2029/2030 | 2008 | 1 | 14 | 9 | 13880.4567
2029/2030 | 2008 | 1 | 14 | 10 | 36759.8802
2029/2030 | 2008 | 1 | 14 | 11 | 40307.372
2029/2030 | 2008 | 1 | 14 | 12 | 38501.8627
2029/2030 | 2008 | 1 | 14 | 13 | 36973.4922
2029/2030 | 2008 | 1 | 14 | 14 | 34640.6873
2029/2030 | 2008 | 1 | 14 | 15 | 33054.2973
2029/2030 | 2008 | 1 | 14 | 16 | 31190.3157
2029/2030 | 2008 | 1 | 14 | 17 | 20913.856
2029/2030 | 2008 | 1 | 14 | 18 | 2783.8338
2029/2030 | 2008 | 1 | 14 | 19 | 0
2029/2030 | 2008 | 1 | 14 | 20 | 0
2029/2030 | 2008 | 1 | 14 | 21 | 0
2029/2030 | 2008 | 1 | 14 | 22 | 0
2029/2030 | 2008 | 1 | 14 | 23 | 0
2029/2030 | 2008 | 1 | 14 | 24 | 0
2029/2030 | 2008 | 1 | 15 | 1 | 0
2029/2030 | 2008 | 1 | 15 | 2 | 0
2029/2030 | 2008 | 1 | 15 | 3 | 0
2029/2030 | 2008 | 1 | 15 | 4 | 0
2029/2030 | 2008 | 1 | 15 | 5 | 0
2029/2030 | 2008 | 1 | 15 | 6 | 0
2029/2030 | 2008 | 1 | 15 | 7 | 0
2029/2030 | 2008 | 1 | 15 | 8 | 11.877
2029/2030 | 2008 | 1 | 15 | 9 | 7930.7403
2029/2030 | 2008 | 1 | 15 | 10 | 23561.5641
2029/2030 | 2008 | 1 | 15 | 11 | 24824.7818
2029/2030 | 2008 | 1 | 15 | 12 | 24894.5666
2029/2030 | 2008 | 1 | 15 | 13 | 22921.0705
2029/2030 | 2008 | 1 | 15 | 14 | 22010.7453
2029/2030 | 2008 | 1 | 15 | 15 | 21691.6776
2029/2030 | 2008 | 1 | 15 | 16 | 19988.6568
2029/2030 | 2008 | 1 | 15 | 17 | 14869.924
2029/2030 | 2008 | 1 | 15 | 18 | 2364.9054
2029/2030 | 2008 | 1 | 15 | 19 | 0
2029/2030 | 2008 | 1 | 15 | 20 | 0
2029/2030 | 2008 | 1 | 15 | 21 | 0
2029/2030 | 2008 | 1 | 15 | 22 | 0
2029/2030 | 2008 | 1 | 15 | 23 | 0
2029/2030 | 2008 | 1 | 15 | 24 | 0
2029/2030 | 2008 | 1 | 16 | 1 | 0
2029/2030 | 2008 | 1 | 16 | 2 | 0
2029/2030 | 2008 | 1 | 16 | 3 | 0
2029/2030 | 2008 | 1 | 16 | 4 | 0
2029/2030 | 2008 | 1 | 16 | 5 | 0
2029/2030 | 2008 | 1 | 16 | 6 | 0
2029/2030 | 2008 | 1 | 16 | 7 | 0
2029/2030 | 2008 | 1 | 16 | 8 | 2.3309
2029/2030 | 2008 | 1 | 16 | 9 | 4157.1188
2029/2030 | 2008 | 1 | 16 | 10 | 14337.8024
2029/2030 | 2008 | 1 | 16 | 11 | 17493.9326
2029/2030 | 2008 | 1 | 16 | 12 | 20166.9571
2029/2030 | 2008 | 1 | 16 | 13 | 23254.2737
2029/2030 | 2008 | 1 | 16 | 14 | 25550.232
2029/2030 | 2008 | 1 | 16 | 15 | 24135.2205
2029/2030 | 2008 | 1 | 16 | 16 | 24680.6926
2029/2030 | 2008 | 1 | 16 | 17 | 21207.2843
2029/2030 | 2008 | 1 | 16 | 18 | 4220.2956
2029/2030 | 2008 | 1 | 16 | 19 | 0
2029/2030 | 2008 | 1 | 16 | 20 | 0
2029/2030 | 2008 | 1 | 16 | 21 | 0
2029/2030 | 2008 | 1 | 16 | 22 | 0
2029/2030 | 2008 | 1 | 16 | 23 | 0
2029/2030 | 2008 | 1 | 16 | 24 | 0
2029/2030 | 2008 | 1 | 17 | 1 | 0
2029/2030 | 2008 | 1 | 17 | 2 | 0
2029/2030 | 2008 | 1 | 17 | 3 | 0
2029/2030 | 2008 | 1 | 17 | 4 | 0
2029/2030 | 2008 | 1 | 17 | 5 | 0
2029/2030 | 2008 | 1 | 17 | 6 | 0
2029/2030 | 2008 | 1 | 17 | 7 | 0
2029/2030 | 2008 | 1 | 17 | 8 | 25.9247
2029/2030 | 2008 | 1 | 17 | 9 | 8809.2666
2029/2030 | 2008 | 1 | 17 | 10 | 26115.925
2029/2030 | 2008 | 1 | 17 | 11 | 33664.9049
2029/2030 | 2008 | 1 | 17 | 12 | 36479.0716
2029/2030 | 2008 | 1 | 17 | 13 | 38160.5818
2029/2030 | 2008 | 1 | 17 | 14 | 36737.424
2029/2030 | 2008 | 1 | 17 | 15 | 35497.748
2029/2030 | 2008 | 1 | 17 | 16 | 32834.8755
2029/2030 | 2008 | 1 | 17 | 17 | 21306.5398
2029/2030 | 2008 | 1 | 17 | 18 | 3309.647
2029/2030 | 2008 | 1 | 17 | 19 | 0
2029/2030 | 2008 | 1 | 17 | 20 | 0
2029/2030 | 2008 | 1 | 17 | 21 | 0
2029/2030 | 2008 | 1 | 17 | 22 | 0
2029/2030 | 2008 | 1 | 17 | 23 | 0
2029/2030 | 2008 | 1 | 17 | 24 | 0
2029/2030 | 2008 | 1 | 18 | 1 | 0
2029/2030 | 2008 | 1 | 18 | 2 | 0
2029/2030 | 2008 | 1 | 18 | 3 | 0
2029/2030 | 2008 | 1 | 18 | 4 | 0
2029/2030 | 2008 | 1 | 18 | 5 | 0
2029/2030 | 2008 | 1 | 18 | 6 | 0
2029/2030 | 2008 | 1 | 18 | 7 | 0
2029/2030 | 2008 | 1 | 18 | 8 | 10.3298
2029/2030 | 2008 | 1 | 18 | 9 | 6027.2203
2029/2030 | 2008 | 1 | 18 | 10 | 17945.9958
2029/2030 | 2008 | 1 | 18 | 11 | 20639.589
2029/2030 | 2008 | 1 | 18 | 12 | 22105.8858
2029/2030 | 2008 | 1 | 18 | 13 | 21826.3548
2029/2030 | 2008 | 1 | 18 | 14 | 20930.385
2029/2030 | 2008 | 1 | 18 | 15 | 21315.8763
2029/2030 | 2008 | 1 | 18 | 16 | 19518.7204
2029/2030 | 2008 | 1 | 18 | 17 | 17259.3428
2029/2030 | 2008 | 1 | 18 | 18 | 3779.577
2029/2030 | 2008 | 1 | 18 | 19 | 0
2029/2030 | 2008 | 1 | 18 | 20 | 0
2029/2030 | 2008 | 1 | 18 | 21 | 0
2029/2030 | 2008 | 1 | 18 | 22 | 0
2029/2030 | 2008 | 1 | 18 | 23 | 0
2029/2030 | 2008 | 1 | 18 | 24 | 0
2029/2030 | 2008 | 1 | 19 | 1 | 0
2029/2030 | 2008 | 1 | 19 | 2 | 0
2029/2030 | 2008 | 1 | 19 | 3 | 0
2029/2030 | 2008 | 1 | 19 | 4 | 0
2029/2030 | 2008 | 1 | 19 | 5 | 0
2029/2030 | 2008 | 1 | 19 | 6 | 0
2029/2030 | 2008 | 1 | 19 | 7 | 0
2029/2030 | 2008 | 1 | 19 | 8 | 26.0957
2029/2030 | 2008 | 1 | 19 | 9 | 13044.331
2029/2030 | 2008 | 1 | 19 | 10 | 41356.031
2029/2030 | 2008 | 1 | 19 | 11 | 48636.7081
2029/2030 | 2008 | 1 | 19 | 12 | 47512.8414
2029/2030 | 2008 | 1 | 19 | 13 | 46957.4893
2029/2030 | 2008 | 1 | 19 | 14 | 47255.7683
2029/2030 | 2008 | 1 | 19 | 15 | 47164.7037
2029/2030 | 2008 | 1 | 19 | 16 | 43593.5399
2029/2030 | 2008 | 1 | 19 | 17 | 34453.0667
2029/2030 | 2008 | 1 | 19 | 18 | 6603.6582
2029/2030 | 2008 | 1 | 19 | 19 | 0
2029/2030 | 2008 | 1 | 19 | 20 | 0
2029/2030 | 2008 | 1 | 19 | 21 | 0
2029/2030 | 2008 | 1 | 19 | 22 | 0
2029/2030 | 2008 | 1 | 19 | 23 | 0
2029/2030 | 2008 | 1 | 19 | 24 | 0
2029/2030 | 2008 | 1 | 20 | 1 | 0
2029/2030 | 2008 | 1 | 20 | 2 | 0
2029/2030 | 2008 | 1 | 20 | 3 | 0
2029/2030 | 2008 | 1 | 20 | 4 | 0
2029/2030 | 2008 | 1 | 20 | 5 | 0
2029/2030 | 2008 | 1 | 20 | 6 | 0
2029/2030 | 2008 | 1 | 20 | 7 | 0
2029/2030 | 2008 | 1 | 20 | 8 | 42.6181
2029/2030 | 2008 | 1 | 20 | 9 | 17680.8692
2029/2030 | 2008 | 1 | 20 | 10 | 43729.5999
2029/2030 | 2008 | 1 | 20 | 11 | 48963.4634
2029/2030 | 2008 | 1 | 20 | 12 | 46761.5601
2029/2030 | 2008 | 1 | 20 | 13 | 46201.9574
2029/2030 | 2008 | 1 | 20 | 14 | 46469.1523
2029/2030 | 2008 | 1 | 20 | 15 | 44376.1005
2029/2030 | 2008 | 1 | 20 | 16 | 40288.3164
2029/2030 | 2008 | 1 | 20 | 17 | 31629.021
2029/2030 | 2008 | 1 | 20 | 18 | 5985.5139
2029/2030 | 2008 | 1 | 20 | 19 | 0
2029/2030 | 2008 | 1 | 20 | 20 | 0
2029/2030 | 2008 | 1 | 20 | 21 | 0
2029/2030 | 2008 | 1 | 20 | 22 | 0
2029/2030 | 2008 | 1 | 20 | 23 | 0
2029/2030 | 2008 | 1 | 20 | 24 | 0
2029/2030 | 2008 | 1 | 21 | 1 | 0
2029/2030 | 2008 | 1 | 21 | 2 | 0
2029/2030 | 2008 | 1 | 21 | 3 | 0
2029/2030 | 2008 | 1 | 21 | 4 | 0
2029/2030 | 2008 | 1 | 21 | 5 | 0
2029/2030 | 2008 | 1 | 21 | 6 | 0
2029/2030 | 2008 | 1 | 21 | 7 | 0
2029/2030 | 2008 | 1 | 21 | 8 | 0.04657
2029/2030 | 2008 | 1 | 21 | 9 | 579.9495
2029/2030 | 2008 | 1 | 21 | 10 | 4710.1863
2029/2030 | 2008 | 1 | 21 | 11 | 8229.0324
2029/2030 | 2008 | 1 | 21 | 12 | 10581.272
2029/2030 | 2008 | 1 | 21 | 13 | 12012.8902
2029/2030 | 2008 | 1 | 21 | 14 | 13686.2259
2029/2030 | 2008 | 1 | 21 | 15 | 13655.3182
2029/2030 | 2008 | 1 | 21 | 16 | 14588.4175
2029/2030 | 2008 | 1 | 21 | 17 | 12991.0366
2029/2030 | 2008 | 1 | 21 | 18 | 3792.5148
2029/2030 | 2008 | 1 | 21 | 19 | 0
2029/2030 | 2008 | 1 | 21 | 20 | 0
2029/2030 | 2008 | 1 | 21 | 21 | 0
2029/2030 | 2008 | 1 | 21 | 22 | 0
2029/2030 | 2008 | 1 | 21 | 23 | 0
2029/2030 | 2008 | 1 | 21 | 24 | 0
2029/2030 | 2008 | 1 | 22 | 1 | 0
2029/2030 | 2008 | 1 | 22 | 2 | 0
2029/2030 | 2008 | 1 | 22 | 3 | 0
2029/2030 | 2008 | 1 | 22 | 4 | 0
2029/2030 | 2008 | 1 | 22 | 5 | 0
2029/2030 | 2008 | 1 | 22 | 6 | 0
2029/2030 | 2008 | 1 | 22 | 7 | 0
2029/2030 | 2008 | 1 | 22 | 8 | 8.7129
2029/2030 | 2008 | 1 | 22 | 9 | 2295.5415
2029/2030 | 2008 | 1 | 22 | 10 | 9791.2034
2029/2030 | 2008 | 1 | 22 | 11 | 12962.635
2029/2030 | 2008 | 1 | 22 | 12 | 14453.5512
2029/2030 | 2008 | 1 | 22 | 13 | 13661.5606
2029/2030 | 2008 | 1 | 22 | 14 | 12652.0057
2029/2030 | 2008 | 1 | 22 | 15 | 13894.5827
2029/2030 | 2008 | 1 | 22 | 16 | 11816.8156
2029/2030 | 2008 | 1 | 22 | 17 | 10600.5931
2029/2030 | 2008 | 1 | 22 | 18 | 2588.7324
2029/2030 | 2008 | 1 | 22 | 19 | 0
2029/2030 | 2008 | 1 | 22 | 20 | 0
2029/2030 | 2008 | 1 | 22 | 21 | 0
2029/2030 | 2008 | 1 | 22 | 22 | 0
2029/2030 | 2008 | 1 | 22 | 23 | 0
2029/2030 | 2008 | 1 | 22 | 24 | 0
2029/2030 | 2008 | 1 | 23 | 1 | 0
2029/2030 | 2008 | 1 | 23 | 2 | 0
2029/2030 | 2008 | 1 | 23 | 3 | 0
2029/2030 | 2008 | 1 | 23 | 4 | 0
2029/2030 | 2008 | 1 | 23 | 5 | 0
2029/2030 | 2008 | 1 | 23 | 6 | 0
2029/2030 | 2008 | 1 | 23 | 7 | 0
2029/2030 | 2008 | 1 | 23 | 8 | 2.8128
2029/2030 | 2008 | 1 | 23 | 9 | 2196.2791
2029/2030 | 2008 | 1 | 23 | 10 | 9184.2261
2029/2030 | 2008 | 1 | 23 | 11 | 12126.6889
2029/2030 | 2008 | 1 | 23 | 12 | 13825.5799
2029/2030 | 2008 | 1 | 23 | 13 | 13907.8872
2029/2030 | 2008 | 1 | 23 | 14 | 13683.703
2029/2030 | 2008 | 1 | 23 | 15 | 13490.6724
2029/2030 | 2008 | 1 | 23 | 16 | 11765.3514
2029/2030 | 2008 | 1 | 23 | 17 | 7760.1886
2029/2030 | 2008 | 1 | 23 | 18 | 1667.6657
2029/2030 | 2008 | 1 | 23 | 19 | 0
2029/2030 | 2008 | 1 | 23 | 20 | 0
2029/2030 | 2008 | 1 | 23 | 21 | 0
2029/2030 | 2008 | 1 | 23 | 22 | 0
2029/2030 | 2008 | 1 | 23 | 23 | 0
2029/2030 | 2008 | 1 | 23 | 24 | 0
2029/2030 | 2008 | 1 | 24 | 1 | 0
2029/2030 | 2008 | 1 | 24 | 2 | 0
2029/2030 | 2008 | 1 | 24 | 3 | 0
2029/2030 | 2008 | 1 | 24 | 4 | 0
2029/2030 | 2008 | 1 | 24 | 5 | 0
2029/2030 | 2008 | 1 | 24 | 6 | 0
2029/2030 | 2008 | 1 | 24 | 7 | 0
2029/2030 | 2008 | 1 | 24 | 8 | 12.0554
2029/2030 | 2008 | 1 | 24 | 9 | 4411.2651
2029/2030 | 2008 | 1 | 24 | 10 | 15192.9659
2029/2030 | 2008 | 1 | 24 | 11 | 19001.3678
2029/2030 | 2008 | 1 | 24 | 12 | 21069.2513
2029/2030 | 2008 | 1 | 24 | 13 | 20384.6108
2029/2030 | 2008 | 1 | 24 | 14 | 19316.2635
2029/2030 | 2008 | 1 | 24 | 15 | 15402.6633
2029/2030 | 2008 | 1 | 24 | 16 | 12857.8331
2029/2030 | 2008 | 1 | 24 | 17 | 5851.0672
2029/2030 | 2008 | 1 | 24 | 18 | 819.9731
2029/2030 | 2008 | 1 | 24 | 19 | 0
2029/2030 | 2008 | 1 | 24 | 20 | 0
2029/2030 | 2008 | 1 | 24 | 21 | 0
2029/2030 | 2008 | 1 | 24 | 22 | 0
2029/2030 | 2008 | 1 | 24 | 23 | 0
2029/2030 | 2008 | 1 | 24 | 24 | 0
2029/2030 | 2008 | 1 | 25 | 1 | 0
2029/2030 | 2008 | 1 | 25 | 2 | 0
2029/2030 | 2008 | 1 | 25 | 3 | 0
2029/2030 | 2008 | 1 | 25 | 4 | 0
2029/2030 | 2008 | 1 | 25 | 5 | 0
2029/2030 | 2008 | 1 | 25 | 6 | 0
2029/2030 | 2008 | 1 | 25 | 7 | 0
2029/2030 | 2008 | 1 | 25 | 8 | 0.001
2029/2030 | 2008 | 1 | 25 | 9 | 490.143
2029/2030 | 2008 | 1 | 25 | 10 | 4168.479
2029/2030 | 2008 | 1 | 25 | 11 | 7256.8636
2029/2030 | 2008 | 1 | 25 | 12 | 9098.8895
2029/2030 | 2008 | 1 | 25 | 13 | 12844.1012
2029/2030 | 2008 | 1 | 25 | 14 | 13534.8156
2029/2030 | 2008 | 1 | 25 | 15 | 14306.0689
2029/2030 | 2008 | 1 | 25 | 16 | 15752.4307
2029/2030 | 2008 | 1 | 25 | 17 | 14110.0662
2029/2030 | 2008 | 1 | 25 | 18 | 4302.9652
2029/2030 | 2008 | 1 | 25 | 19 | 0
2029/2030 | 2008 | 1 | 25 | 20 | 0
2029/2030 | 2008 | 1 | 25 | 21 | 0
2029/2030 | 2008 | 1 | 25 | 22 | 0
2029/2030 | 2008 | 1 | 25 | 23 | 0
2029/2030 | 2008 | 1 | 25 | 24 | 0
2029/2030 | 2008 | 1 | 26 | 1 | 0
2029/2030 | 2008 | 1 | 26 | 2 | 0
2029/2030 | 2008 | 1 | 26 | 3 | 0
2029/2030 | 2008 | 1 | 26 | 4 | 0
2029/2030 | 2008 | 1 | 26 | 5 | 0
2029/2030 | 2008 | 1 | 26 | 6 | 0
2029/2030 | 2008 | 1 | 26 | 7 | 0
2029/2030 | 2008 | 1 | 26 | 8 | 11.3574
2029/2030 | 2008 | 1 | 26 | 9 | 7556.8088
2029/2030 | 2008 | 1 | 26 | 10 | 23836.4294
2029/2030 | 2008 | 1 | 26 | 11 | 27491.8528
2029/2030 | 2008 | 1 | 26 | 12 | 30445.2008
2029/2030 | 2008 | 1 | 26 | 13 | 34221.211
2029/2030 | 2008 | 1 | 26 | 14 | 34054.9362
2029/2030 | 2008 | 1 | 26 | 15 | 32938.5148
2029/2030 | 2008 | 1 | 26 | 16 | 29792.1137
2029/2030 | 2008 | 1 | 26 | 17 | 22067.6488
2029/2030 | 2008 | 1 | 26 | 18 | 5892.3857
2029/2030 | 2008 | 1 | 26 | 19 | 0
2029/2030 | 2008 | 1 | 26 | 20 | 0
2029/2030 | 2008 | 1 | 26 | 21 | 0
2029/2030 | 2008 | 1 | 26 | 22 | 0
2029/2030 | 2008 | 1 | 26 | 23 | 0
2029/2030 | 2008 | 1 | 26 | 24 | 0
2029/2030 | 2008 | 1 | 27 | 1 | 0
2029/2030 | 2008 | 1 | 27 | 2 | 0
2029/2030 | 2008 | 1 | 27 | 3 | 0
2029/2030 | 2008 | 1 | 27 | 4 | 0
2029/2030 | 2008 | 1 | 27 | 5 | 0
2029/2030 | 2008 | 1 | 27 | 6 | 0
2029/2030 | 2008 | 1 | 27 | 7 | 0
2029/2030 | 2008 | 1 | 27 | 8 | 17.5698
2029/2030 | 2008 | 1 | 27 | 9 | 6842.2933
2029/2030 | 2008 | 1 | 27 | 10 | 22066.8028
2029/2030 | 2008 | 1 | 27 | 11 | 27066.2153
2029/2030 | 2008 | 1 | 27 | 12 | 34986.2211
2029/2030 | 2008 | 1 | 27 | 13 | 39117.9321
2029/2030 | 2008 | 1 | 27 | 14 | 39836.8469
2029/2030 | 2008 | 1 | 27 | 15 | 37997.01
2029/2030 | 2008 | 1 | 27 | 16 | 34013.2535
2029/2030 | 2008 | 1 | 27 | 17 | 24318.7676
2029/2030 | 2008 | 1 | 27 | 18 | 6261.7058
2029/2030 | 2008 | 1 | 27 | 19 | 0
2029/2030 | 2008 | 1 | 27 | 20 | 0
2029/2030 | 2008 | 1 | 27 | 21 | 0
2029/2030 | 2008 | 1 | 27 | 22 | 0
2029/2030 | 2008 | 1 | 27 | 23 | 0
2029/2030 | 2008 | 1 | 27 | 24 | 0
2029/2030 | 2008 | 1 | 28 | 1 | 0
2029/2030 | 2008 | 1 | 28 | 2 | 0
2029/2030 | 2008 | 1 | 28 | 3 | 0
2029/2030 | 2008 | 1 | 28 | 4 | 0
2029/2030 | 2008 | 1 | 28 | 5 | 0
2029/2030 | 2008 | 1 | 28 | 6 | 0
2029/2030 | 2008 | 1 | 28 | 7 | 0
2029/2030 | 2008 | 1 | 28 | 8 | 1.3782
2029/2030 | 2008 | 1 | 28 | 9 | 1617.6855
2029/2030 | 2008 | 1 | 28 | 10 | 9056.1466
2029/2030 | 2008 | 1 | 28 | 11 | 11641.1123
2029/2030 | 2008 | 1 | 28 | 12 | 13129.4612
2029/2030 | 2008 | 1 | 28 | 13 | 14506.2342
2029/2030 | 2008 | 1 | 28 | 14 | 15490.2165
2029/2030 | 2008 | 1 | 28 | 15 | 14401.2273
2029/2030 | 2008 | 1 | 28 | 16 | 13099.274
2029/2030 | 2008 | 1 | 28 | 17 | 10624.3045
2029/2030 | 2008 | 1 | 28 | 18 | 3465.5352
2029/2030 | 2008 | 1 | 28 | 19 | 0
2029/2030 | 2008 | 1 | 28 | 20 | 0
2029/2030 | 2008 | 1 | 28 | 21 | 0
2029/2030 | 2008 | 1 | 28 | 22 | 0
2029/2030 | 2008 | 1 | 28 | 23 | 0
2029/2030 | 2008 | 1 | 28 | 24 | 0
2029/2030 | 2008 | 1 | 29 | 1 | 0
2029/2030 | 2008 | 1 | 29 | 2 | 0
2029/2030 | 2008 | 1 | 29 | 3 | 0
2029/2030 | 2008 | 1 | 29 | 4 | 0
2029/2030 | 2008 | 1 | 29 | 5 | 0
2029/2030 | 2008 | 1 | 29 | 6 | 0
2029/2030 | 2008 | 1 | 29 | 7 | 0
2029/2030 | 2008 | 1 | 29 | 8 | 19.3649
2029/2030 | 2008 | 1 | 29 | 9 | 7423.1732
2029/2030 | 2008 | 1 | 29 | 10 | 24825.0901
2029/2030 | 2008 | 1 | 29 | 11 | 31368.5556
2029/2030 | 2008 | 1 | 29 | 12 | 35270.0542
2029/2030 | 2008 | 1 | 29 | 13 | 38857.8831
2029/2030 | 2008 | 1 | 29 | 14 | 40893.4086
2029/2030 | 2008 | 1 | 29 | 15 | 46312.2513
2029/2030 | 2008 | 1 | 29 | 16 | 47640.6429
2029/2030 | 2008 | 1 | 29 | 17 | 37314.7921
2029/2030 | 2008 | 1 | 29 | 18 | 10755.3583
2029/2030 | 2008 | 1 | 29 | 19 | 0
2029/2030 | 2008 | 1 | 29 | 20 | 0
2029/2030 | 2008 | 1 | 29 | 21 | 0
2029/2030 | 2008 | 1 | 29 | 22 | 0
2029/2030 | 2008 | 1 | 29 | 23 | 0
2029/2030 | 2008 | 1 | 29 | 24 | 0
2029/2030 | 2008 | 1 | 30 | 1 | 0
2029/2030 | 2008 | 1 | 30 | 2 | 0
2029/2030 | 2008 | 1 | 30 | 3 | 0
2029/2030 | 2008 | 1 | 30 | 4 | 0
2029/2030 | 2008 | 1 | 30 | 5 | 0
2029/2030 | 2008 | 1 | 30 | 6 | 0
2029/2030 | 2008 | 1 | 30 | 7 | 0
2029/2030 | 2008 | 1 | 30 | 8 | 85.3265
2029/2030 | 2008 | 1 | 30 | 9 | 18561.1302
2029/2030 | 2008 | 1 | 30 | 10 | 45949.8101
2029/2030 | 2008 | 1 | 30 | 11 | 48424.9166
2029/2030 | 2008 | 1 | 30 | 12 | 46658.9685
2029/2030 | 2008 | 1 | 30 | 13 | 45230.8939
2029/2030 | 2008 | 1 | 30 | 14 | 42733.9747
2029/2030 | 2008 | 1 | 30 | 15 | 37770.3019
2029/2030 | 2008 | 1 | 30 | 16 | 35575.4849
2029/2030 | 2008 | 1 | 30 | 17 | 27776.4336
2029/2030 | 2008 | 1 | 30 | 18 | 8343.1334
2029/2030 | 2008 | 1 | 30 | 19 | 0
2029/2030 | 2008 | 1 | 30 | 20 | 0
2029/2030 | 2008 | 1 | 30 | 21 | 0
2029/2030 | 2008 | 1 | 30 | 22 | 0
2029/2030 | 2008 | 1 | 30 | 23 | 0
2029/2030 | 2008 | 1 | 30 | 24 | 0
2029/2030 | 2008 | 1 | 31 | 1 | 0
2029/2030 | 2008 | 1 | 31 | 2 | 0
2029/2030 | 2008 | 1 | 31 | 3 | 0
2029/2030 | 2008 | 1 | 31 | 4 | 0
2029/2030 | 2008 | 1 | 31 | 5 | 0
2029/2030 | 2008 | 1 | 31 | 6 | 0
2029/2030 | 2008 | 1 | 31 | 7 | 0
2029/2030 | 2008 | 1 | 31 | 8 | 23.5081
2029/2030 | 2008 | 1 | 31 | 9 | 8822.9621
2029/2030 | 2008 | 1 | 31 | 10 | 32307.4675
2029/2030 | 2008 | 1 | 31 | 11 | 41411.2633
2029/2030 | 2008 | 1 | 31 | 12 | 44002.7089
2029/2030 | 2008 | 1 | 31 | 13 | 48770.4508
2029/2030 | 2008 | 1 | 31 | 14 | 51122.8336
2029/2030 | 2008 | 1 | 31 | 15 | 53029.9649
2029/2030 | 2008 | 1 | 31 | 16 | 49985.8824
2029/2030 | 2008 | 1 | 31 | 17 | 38631.4575
2029/2030 | 2008 | 1 | 31 | 18 | 10670.9231
2029/2030 | 2008 | 1 | 31 | 19 | 0
2029/2030 | 2008 | 1 | 31 | 20 | 0
2029/2030 | 2008 | 1 | 31 | 21 | 0
2029/2030 | 2008 | 1 | 31 | 22 | 0
2029/2030 | 2008 | 1 | 31 | 23 | 0
2029/2030 | 2008 | 1 | 31 | 24 | 0
2030/2031 | 2008 | 1 | 1 | 1 | 0
2030/2031 | 2008 | 1 | 1 | 2 | 0
2030/2031 | 2008 | 1 | 1 | 3 | 0
2030/2031 | 2008 | 1 | 1 | 4 | 0
2030/2031 | 2008 | 1 | 1 | 5 | 0
2030/2031 | 2008 | 1 | 1 | 6 | 0
2030/2031 | 2008 | 1 | 1 | 7 | 0
2030/2031 | 2008 | 1 | 1 | 8 | 32.3932
2030/2031 | 2008 | 1 | 1 | 9 | 14389.6529
2030/2031 | 2008 | 1 | 1 | 10 | 38616.7711
2030/2031 | 2008 | 1 | 1 | 11 | 43927.0794
2030/2031 | 2008 | 1 | 1 | 12 | 43365.0565
2030/2031 | 2008 | 1 | 1 | 13 | 42461.1566
2030/2031 | 2008 | 1 | 1 | 14 | 42581.8677
2030/2031 | 2008 | 1 | 1 | 15 | 43167.0927
2030/2031 | 2008 | 1 | 1 | 16 | 37990.2783
2030/2031 | 2008 | 1 | 1 | 17 | 20014.5696
2030/2031 | 2008 | 1 | 1 | 18 | 911.4129
2030/2031 | 2008 | 1 | 1 | 19 | 0
2030/2031 | 2008 | 1 | 1 | 20 | 0
2030/2031 | 2008 | 1 | 1 | 21 | 0
2030/2031 | 2008 | 1 | 1 | 22 | 0
2030/2031 | 2008 | 1 | 1 | 23 | 0
2030/2031 | 2008 | 1 | 1 | 24 | 0
2030/2031 | 2008 | 1 | 2 | 1 | 0
2030/2031 | 2008 | 1 | 2 | 2 | 0
2030/2031 | 2008 | 1 | 2 | 3 | 0
2030/2031 | 2008 | 1 | 2 | 4 | 0
2030/2031 | 2008 | 1 | 2 | 5 | 0
2030/2031 | 2008 | 1 | 2 | 6 | 0
2030/2031 | 2008 | 1 | 2 | 7 | 0
2030/2031 | 2008 | 1 | 2 | 8 | 30.6219
2030/2031 | 2008 | 1 | 2 | 9 | 13465.0328
2030/2031 | 2008 | 1 | 2 | 10 | 36895.7654
2030/2031 | 2008 | 1 | 2 | 11 | 42226.695
2030/2031 | 2008 | 1 | 2 | 12 | 40480.4846
2030/2031 | 2008 | 1 | 2 | 13 | 40217.1055
2030/2031 | 2008 | 1 | 2 | 14 | 37867.8995
2030/2031 | 2008 | 1 | 2 | 15 | 35293.3912
2030/2031 | 2008 | 1 | 2 | 16 | 27563.6419
2030/2031 | 2008 | 1 | 2 | 17 | 17617.4296
2030/2031 | 2008 | 1 | 2 | 18 | 472.0658
2030/2031 | 2008 | 1 | 2 | 19 | 0
2030/2031 | 2008 | 1 | 2 | 20 | 0
2030/2031 | 2008 | 1 | 2 | 21 | 0
2030/2031 | 2008 | 1 | 2 | 22 | 0
2030/2031 | 2008 | 1 | 2 | 23 | 0
2030/2031 | 2008 | 1 | 2 | 24 | 0
2030/2031 | 2008 | 1 | 3 | 1 | 0
2030/2031 | 2008 | 1 | 3 | 2 | 0
2030/2031 | 2008 | 1 | 3 | 3 | 0
2030/2031 | 2008 | 1 | 3 | 4 | 0
2030/2031 | 2008 | 1 | 3 | 5 | 0
2030/2031 | 2008 | 1 | 3 | 6 | 0
2030/2031 | 2008 | 1 | 3 | 7 | 0
2030/2031 | 2008 | 1 | 3 | 8 | 9.0189
2030/2031 | 2008 | 1 | 3 | 9 | 8108.7069
2030/2031 | 2008 | 1 | 3 | 10 | 26728.5418
2030/2031 | 2008 | 1 | 3 | 11 | 29978.0886
2030/2031 | 2008 | 1 | 3 | 12 | 31596.5767
2030/2031 | 2008 | 1 | 3 | 13 | 32410.0875
2030/2031 | 2008 | 1 | 3 | 14 | 32060.1943
2030/2031 | 2008 | 1 | 3 | 15 | 35420.2977
2030/2031 | 2008 | 1 | 3 | 16 | 32268.7747
2030/2031 | 2008 | 1 | 3 | 17 | 18540.8953
2030/2031 | 2008 | 1 | 3 | 18 | 848.4661
2030/2031 | 2008 | 1 | 3 | 19 | 0
2030/2031 | 2008 | 1 | 3 | 20 | 0
2030/2031 | 2008 | 1 | 3 | 21 | 0
2030/2031 | 2008 | 1 | 3 | 22 | 0
2030/2031 | 2008 | 1 | 3 | 23 | 0
2030/2031 | 2008 | 1 | 3 | 24 | 0
2030/2031 | 2008 | 1 | 4 | 1 | 0
2030/2031 | 2008 | 1 | 4 | 2 | 0
2030/2031 | 2008 | 1 | 4 | 3 | 0
2030/2031 | 2008 | 1 | 4 | 4 | 0
2030/2031 | 2008 | 1 | 4 | 5 | 0
2030/2031 | 2008 | 1 | 4 | 6 | 0
2030/2031 | 2008 | 1 | 4 | 7 | 0
2030/2031 | 2008 | 1 | 4 | 8 | 11.2804
2030/2031 | 2008 | 1 | 4 | 9 | 2797.5848
2030/2031 | 2008 | 1 | 4 | 10 | 11070.7121
2030/2031 | 2008 | 1 | 4 | 11 | 15437.8429
2030/2031 | 2008 | 1 | 4 | 12 | 17555.4606
2030/2031 | 2008 | 1 | 4 | 13 | 17900.981
2030/2031 | 2008 | 1 | 4 | 14 | 16642.2123
2030/2031 | 2008 | 1 | 4 | 15 | 14880.0218
2030/2031 | 2008 | 1 | 4 | 16 | 11658.5096
2030/2031 | 2008 | 1 | 4 | 17 | 8062.921
2030/2031 | 2008 | 1 | 4 | 18 | 378.9351
2030/2031 | 2008 | 1 | 4 | 19 | 0
2030/2031 | 2008 | 1 | 4 | 20 | 0
2030/2031 | 2008 | 1 | 4 | 21 | 0
2030/2031 | 2008 | 1 | 4 | 22 | 0
2030/2031 | 2008 | 1 | 4 | 23 | 0
2030/2031 | 2008 | 1 | 4 | 24 | 0
2030/2031 | 2008 | 1 | 5 | 1 | 0
2030/2031 | 2008 | 1 | 5 | 2 | 0
2030/2031 | 2008 | 1 | 5 | 3 | 0
2030/2031 | 2008 | 1 | 5 | 4 | 0
2030/2031 | 2008 | 1 | 5 | 5 | 0
2030/2031 | 2008 | 1 | 5 | 6 | 0
2030/2031 | 2008 | 1 | 5 | 7 | 0
2030/2031 | 2008 | 1 | 5 | 8 | 4.3338
2030/2031 | 2008 | 1 | 5 | 9 | 6158.7637
2030/2031 | 2008 | 1 | 5 | 10 | 19913.9873
2030/2031 | 2008 | 1 | 5 | 11 | 24300.0154
2030/2031 | 2008 | 1 | 5 | 12 | 26605.6953
2030/2031 | 2008 | 1 | 5 | 13 | 30205.9672
2030/2031 | 2008 | 1 | 5 | 14 | 31344.3661
2030/2031 | 2008 | 1 | 5 | 15 | 32729.5873
2030/2031 | 2008 | 1 | 5 | 16 | 31811.3926
2030/2031 | 2008 | 1 | 5 | 17 | 20969.6663
2030/2031 | 2008 | 1 | 5 | 18 | 1269.2601
2030/2031 | 2008 | 1 | 5 | 19 | 0
2030/2031 | 2008 | 1 | 5 | 20 | 0
2030/2031 | 2008 | 1 | 5 | 21 | 0
2030/2031 | 2008 | 1 | 5 | 22 | 0
2030/2031 | 2008 | 1 | 5 | 23 | 0
2030/2031 | 2008 | 1 | 5 | 24 | 0
2030/2031 | 2008 | 1 | 6 | 1 | 0
2030/2031 | 2008 | 1 | 6 | 2 | 0
2030/2031 | 2008 | 1 | 6 | 3 | 0
2030/2031 | 2008 | 1 | 6 | 4 | 0
2030/2031 | 2008 | 1 | 6 | 5 | 0
2030/2031 | 2008 | 1 | 6 | 6 | 0
2030/2031 | 2008 | 1 | 6 | 7 | 0
2030/2031 | 2008 | 1 | 6 | 8 | 12.5583
2030/2031 | 2008 | 1 | 6 | 9 | 4582.9993
2030/2031 | 2008 | 1 | 6 | 10 | 17500.2307
2030/2031 | 2008 | 1 | 6 | 11 | 22226.3756
2030/2031 | 2008 | 1 | 6 | 12 | 25963.6461
2030/2031 | 2008 | 1 | 6 | 13 | 29567.8717
2030/2031 | 2008 | 1 | 6 | 14 | 31170.0857
2030/2031 | 2008 | 1 | 6 | 15 | 29435.6424
2030/2031 | 2008 | 1 | 6 | 16 | 24254.8867
2030/2031 | 2008 | 1 | 6 | 17 | 18384.4379
2030/2031 | 2008 | 1 | 6 | 18 | 1618.9639
2030/2031 | 2008 | 1 | 6 | 19 | 0
2030/2031 | 2008 | 1 | 6 | 20 | 0
2030/2031 | 2008 | 1 | 6 | 21 | 0
2030/2031 | 2008 | 1 | 6 | 22 | 0
2030/2031 | 2008 | 1 | 6 | 23 | 0
2030/2031 | 2008 | 1 | 6 | 24 | 0
2030/2031 | 2008 | 1 | 7 | 1 | 0
2030/2031 | 2008 | 1 | 7 | 2 | 0
2030/2031 | 2008 | 1 | 7 | 3 | 0
2030/2031 | 2008 | 1 | 7 | 4 | 0
2030/2031 | 2008 | 1 | 7 | 5 | 0
2030/2031 | 2008 | 1 | 7 | 6 | 0
2030/2031 | 2008 | 1 | 7 | 7 | 0
2030/2031 | 2008 | 1 | 7 | 8 | 2.1121
2030/2031 | 2008 | 1 | 7 | 9 | 2920.9476
2030/2031 | 2008 | 1 | 7 | 10 | 10203.3661
2030/2031 | 2008 | 1 | 7 | 11 | 16274.6803
2030/2031 | 2008 | 1 | 7 | 12 | 18069.9803
2030/2031 | 2008 | 1 | 7 | 13 | 21237.4957
2030/2031 | 2008 | 1 | 7 | 14 | 18841.3466
2030/2031 | 2008 | 1 | 7 | 15 | 18314.7986
2030/2031 | 2008 | 1 | 7 | 16 | 17236.4942
2030/2031 | 2008 | 1 | 7 | 17 | 10381.5741
2030/2031 | 2008 | 1 | 7 | 18 | 1186.2638
2030/2031 | 2008 | 1 | 7 | 19 | 0
2030/2031 | 2008 | 1 | 7 | 20 | 0
2030/2031 | 2008 | 1 | 7 | 21 | 0
2030/2031 | 2008 | 1 | 7 | 22 | 0
2030/2031 | 2008 | 1 | 7 | 23 | 0
2030/2031 | 2008 | 1 | 7 | 24 | 0
2030/2031 | 2008 | 1 | 8 | 1 | 0
2030/2031 | 2008 | 1 | 8 | 2 | 0
2030/2031 | 2008 | 1 | 8 | 3 | 0
2030/2031 | 2008 | 1 | 8 | 4 | 0
2030/2031 | 2008 | 1 | 8 | 5 | 0
2030/2031 | 2008 | 1 | 8 | 6 | 0
2030/2031 | 2008 | 1 | 8 | 7 | 0
2030/2031 | 2008 | 1 | 8 | 8 | 5.9053
2030/2031 | 2008 | 1 | 8 | 9 | 3837.2313
2030/2031 | 2008 | 1 | 8 | 10 | 13961.2059
2030/2031 | 2008 | 1 | 8 | 11 | 18398.3916
2030/2031 | 2008 | 1 | 8 | 12 | 23049.5533
2030/2031 | 2008 | 1 | 8 | 13 | 25196.0165
2030/2031 | 2008 | 1 | 8 | 14 | 23585.566
2030/2031 | 2008 | 1 | 8 | 15 | 23752.219
2030/2031 | 2008 | 1 | 8 | 16 | 21322.3535
2030/2031 | 2008 | 1 | 8 | 17 | 13755.9605
2030/2031 | 2008 | 1 | 8 | 18 | 1442.3203
2030/2031 | 2008 | 1 | 8 | 19 | 0
2030/2031 | 2008 | 1 | 8 | 20 | 0
2030/2031 | 2008 | 1 | 8 | 21 | 0
2030/2031 | 2008 | 1 | 8 | 22 | 0
2030/2031 | 2008 | 1 | 8 | 23 | 0
2030/2031 | 2008 | 1 | 8 | 24 | 0
2030/2031 | 2008 | 1 | 9 | 1 | 0
2030/2031 | 2008 | 1 | 9 | 2 | 0
2030/2031 | 2008 | 1 | 9 | 3 | 0
2030/2031 | 2008 | 1 | 9 | 4 | 0
2030/2031 | 2008 | 1 | 9 | 5 | 0
2030/2031 | 2008 | 1 | 9 | 6 | 0
2030/2031 | 2008 | 1 | 9 | 7 | 0
2030/2031 | 2008 | 1 | 9 | 8 | 36.5939
2030/2031 | 2008 | 1 | 9 | 9 | 14783.201
2030/2031 | 2008 | 1 | 9 | 10 | 35913.9922
2030/2031 | 2008 | 1 | 9 | 11 | 39644.557
2030/2031 | 2008 | 1 | 9 | 12 | 39294.5847
2030/2031 | 2008 | 1 | 9 | 13 | 39239.4172
2030/2031 | 2008 | 1 | 9 | 14 | 38082.1826
2030/2031 | 2008 | 1 | 9 | 15 | 37562.046
2030/2031 | 2008 | 1 | 9 | 16 | 34104.2853
2030/2031 | 2008 | 1 | 9 | 17 | 24476.0302
2030/2031 | 2008 | 1 | 9 | 18 | 2485.0794
2030/2031 | 2008 | 1 | 9 | 19 | 0
2030/2031 | 2008 | 1 | 9 | 20 | 0
2030/2031 | 2008 | 1 | 9 | 21 | 0
2030/2031 | 2008 | 1 | 9 | 22 | 0
2030/2031 | 2008 | 1 | 9 | 23 | 0
2030/2031 | 2008 | 1 | 9 | 24 | 0
2030/2031 | 2008 | 1 | 10 | 1 | 0
2030/2031 | 2008 | 1 | 10 | 2 | 0
2030/2031 | 2008 | 1 | 10 | 3 | 0
2030/2031 | 2008 | 1 | 10 | 4 | 0
2030/2031 | 2008 | 1 | 10 | 5 | 0
2030/2031 | 2008 | 1 | 10 | 6 | 0
2030/2031 | 2008 | 1 | 10 | 7 | 0
2030/2031 | 2008 | 1 | 10 | 8 | 21.224
2030/2031 | 2008 | 1 | 10 | 9 | 9455.5205
2030/2031 | 2008 | 1 | 10 | 10 | 26719.2911
2030/2031 | 2008 | 1 | 10 | 11 | 31903.0619
2030/2031 | 2008 | 1 | 10 | 12 | 33896.83
2030/2031 | 2008 | 1 | 10 | 13 | 33367.2855
2030/2031 | 2008 | 1 | 10 | 14 | 34432.83
2030/2031 | 2008 | 1 | 10 | 15 | 36089.1162
2030/2031 | 2008 | 1 | 10 | 16 | 37076.563
2030/2031 | 2008 | 1 | 10 | 17 | 22793.2396
2030/2031 | 2008 | 1 | 10 | 18 | 2053.5336
2030/2031 | 2008 | 1 | 10 | 19 | 0
2030/2031 | 2008 | 1 | 10 | 20 | 0
2030/2031 | 2008 | 1 | 10 | 21 | 0
2030/2031 | 2008 | 1 | 10 | 22 | 0
2030/2031 | 2008 | 1 | 10 | 23 | 0
2030/2031 | 2008 | 1 | 10 | 24 | 0
2030/2031 | 2008 | 1 | 11 | 1 | 0
2030/2031 | 2008 | 1 | 11 | 2 | 0
2030/2031 | 2008 | 1 | 11 | 3 | 0
2030/2031 | 2008 | 1 | 11 | 4 | 0
2030/2031 | 2008 | 1 | 11 | 5 | 0
2030/2031 | 2008 | 1 | 11 | 6 | 0
2030/2031 | 2008 | 1 | 11 | 7 | 0
2030/2031 | 2008 | 1 | 11 | 8 | 34.4664
2030/2031 | 2008 | 1 | 11 | 9 | 14912.7281
2030/2031 | 2008 | 1 | 11 | 10 | 38155.3521
2030/2031 | 2008 | 1 | 11 | 11 | 41054.168
2030/2031 | 2008 | 1 | 11 | 12 | 41414.0116
2030/2031 | 2008 | 1 | 11 | 13 | 40708.807
2030/2031 | 2008 | 1 | 11 | 14 | 39729.2396
2030/2031 | 2008 | 1 | 11 | 15 | 39281.452
2030/2031 | 2008 | 1 | 11 | 16 | 35067.5407
2030/2031 | 2008 | 1 | 11 | 17 | 21150.0509
2030/2031 | 2008 | 1 | 11 | 18 | 1750.9188
2030/2031 | 2008 | 1 | 11 | 19 | 0
2030/2031 | 2008 | 1 | 11 | 20 | 0
2030/2031 | 2008 | 1 | 11 | 21 | 0
2030/2031 | 2008 | 1 | 11 | 22 | 0
2030/2031 | 2008 | 1 | 11 | 23 | 0
2030/2031 | 2008 | 1 | 11 | 24 | 0
2030/2031 | 2008 | 1 | 12 | 1 | 0
2030/2031 | 2008 | 1 | 12 | 2 | 0
2030/2031 | 2008 | 1 | 12 | 3 | 0
2030/2031 | 2008 | 1 | 12 | 4 | 0
2030/2031 | 2008 | 1 | 12 | 5 | 0
2030/2031 | 2008 | 1 | 12 | 6 | 0
2030/2031 | 2008 | 1 | 12 | 7 | 0
2030/2031 | 2008 | 1 | 12 | 8 | 28.2621
2030/2031 | 2008 | 1 | 12 | 9 | 12321.1277
2030/2031 | 2008 | 1 | 12 | 10 | 30274.3451
2030/2031 | 2008 | 1 | 12 | 11 | 33112.0457
2030/2031 | 2008 | 1 | 12 | 12 | 31393.0978
2030/2031 | 2008 | 1 | 12 | 13 | 34029.2509
2030/2031 | 2008 | 1 | 12 | 14 | 34342.1834
2030/2031 | 2008 | 1 | 12 | 15 | 35380.646
2030/2031 | 2008 | 1 | 12 | 16 | 35061.3249
2030/2031 | 2008 | 1 | 12 | 17 | 22244.4201
2030/2031 | 2008 | 1 | 12 | 18 | 2806.6038
2030/2031 | 2008 | 1 | 12 | 19 | 0
2030/2031 | 2008 | 1 | 12 | 20 | 0
2030/2031 | 2008 | 1 | 12 | 21 | 0
2030/2031 | 2008 | 1 | 12 | 22 | 0
2030/2031 | 2008 | 1 | 12 | 23 | 0
2030/2031 | 2008 | 1 | 12 | 24 | 0
2030/2031 | 2008 | 1 | 13 | 1 | 0
2030/2031 | 2008 | 1 | 13 | 2 | 0
2030/2031 | 2008 | 1 | 13 | 3 | 0
2030/2031 | 2008 | 1 | 13 | 4 | 0
2030/2031 | 2008 | 1 | 13 | 5 | 0
2030/2031 | 2008 | 1 | 13 | 6 | 0
2030/2031 | 2008 | 1 | 13 | 7 | 0
2030/2031 | 2008 | 1 | 13 | 8 | 30.1083
2030/2031 | 2008 | 1 | 13 | 9 | 13781.2889
2030/2031 | 2008 | 1 | 13 | 10 | 37042.5736
2030/2031 | 2008 | 1 | 13 | 11 | 39895.0377
2030/2031 | 2008 | 1 | 13 | 12 | 39783.8334
2030/2031 | 2008 | 1 | 13 | 13 | 38302.2928
2030/2031 | 2008 | 1 | 13 | 14 | 36621.2209
2030/2031 | 2008 | 1 | 13 | 15 | 32926.5777
2030/2031 | 2008 | 1 | 13 | 16 | 28639.4317
2030/2031 | 2008 | 1 | 13 | 17 | 18976.2863
2030/2031 | 2008 | 1 | 13 | 18 | 2255.4752
2030/2031 | 2008 | 1 | 13 | 19 | 0
2030/2031 | 2008 | 1 | 13 | 20 | 0
2030/2031 | 2008 | 1 | 13 | 21 | 0
2030/2031 | 2008 | 1 | 13 | 22 | 0
2030/2031 | 2008 | 1 | 13 | 23 | 0
2030/2031 | 2008 | 1 | 13 | 24 | 0
2030/2031 | 2008 | 1 | 14 | 1 | 0
2030/2031 | 2008 | 1 | 14 | 2 | 0
2030/2031 | 2008 | 1 | 14 | 3 | 0
2030/2031 | 2008 | 1 | 14 | 4 | 0
2030/2031 | 2008 | 1 | 14 | 5 | 0
2030/2031 | 2008 | 1 | 14 | 6 | 0
2030/2031 | 2008 | 1 | 14 | 7 | 0
2030/2031 | 2008 | 1 | 14 | 8 | 31.6354
2030/2031 | 2008 | 1 | 14 | 9 | 13880.4567
2030/2031 | 2008 | 1 | 14 | 10 | 36759.8802
2030/2031 | 2008 | 1 | 14 | 11 | 40307.372
2030/2031 | 2008 | 1 | 14 | 12 | 38501.8627
2030/2031 | 2008 | 1 | 14 | 13 | 36973.4922
2030/2031 | 2008 | 1 | 14 | 14 | 34640.6873
2030/2031 | 2008 | 1 | 14 | 15 | 33054.2973
2030/2031 | 2008 | 1 | 14 | 16 | 31190.3157
2030/2031 | 2008 | 1 | 14 | 17 | 20913.856
2030/2031 | 2008 | 1 | 14 | 18 | 2783.8338
2030/2031 | 2008 | 1 | 14 | 19 | 0
2030/2031 | 2008 | 1 | 14 | 20 | 0
2030/2031 | 2008 | 1 | 14 | 21 | 0
2030/2031 | 2008 | 1 | 14 | 22 | 0
2030/2031 | 2008 | 1 | 14 | 23 | 0
2030/2031 | 2008 | 1 | 14 | 24 | 0
2030/2031 | 2008 | 1 | 15 | 1 | 0
2030/2031 | 2008 | 1 | 15 | 2 | 0
2030/2031 | 2008 | 1 | 15 | 3 | 0
2030/2031 | 2008 | 1 | 15 | 4 | 0
2030/2031 | 2008 | 1 | 15 | 5 | 0
2030/2031 | 2008 | 1 | 15 | 6 | 0
2030/2031 | 2008 | 1 | 15 | 7 | 0
2030/2031 | 2008 | 1 | 15 | 8 | 11.877
2030/2031 | 2008 | 1 | 15 | 9 | 7930.7403
2030/2031 | 2008 | 1 | 15 | 10 | 23561.5641
2030/2031 | 2008 | 1 | 15 | 11 | 24824.7818
2030/2031 | 2008 | 1 | 15 | 12 | 24894.5666
2030/2031 | 2008 | 1 | 15 | 13 | 22921.0705
2030/2031 | 2008 | 1 | 15 | 14 | 22010.7453
2030/2031 | 2008 | 1 | 15 | 15 | 21691.6776
2030/2031 | 2008 | 1 | 15 | 16 | 19988.6568
2030/2031 | 2008 | 1 | 15 | 17 | 14869.924
2030/2031 | 2008 | 1 | 15 | 18 | 2364.9054
2030/2031 | 2008 | 1 | 15 | 19 | 0
2030/2031 | 2008 | 1 | 15 | 20 | 0
2030/2031 | 2008 | 1 | 15 | 21 | 0
2030/2031 | 2008 | 1 | 15 | 22 | 0
2030/2031 | 2008 | 1 | 15 | 23 | 0
2030/2031 | 2008 | 1 | 15 | 24 | 0
2030/2031 | 2008 | 1 | 16 | 1 | 0
2030/2031 | 2008 | 1 | 16 | 2 | 0
2030/2031 | 2008 | 1 | 16 | 3 | 0
2030/2031 | 2008 | 1 | 16 | 4 | 0
2030/2031 | 2008 | 1 | 16 | 5 | 0
2030/2031 | 2008 | 1 | 16 | 6 | 0
2030/2031 | 2008 | 1 | 16 | 7 | 0
2030/2031 | 2008 | 1 | 16 | 8 | 2.3309
2030/2031 | 2008 | 1 | 16 | 9 | 4157.1188
2030/2031 | 2008 | 1 | 16 | 10 | 14337.8024
2030/2031 | 2008 | 1 | 16 | 11 | 17493.9326
2030/2031 | 2008 | 1 | 16 | 12 | 20166.9571
2030/2031 | 2008 | 1 | 16 | 13 | 23254.2737
2030/2031 | 2008 | 1 | 16 | 14 | 25550.232
2030/2031 | 2008 | 1 | 16 | 15 | 24135.2205
2030/2031 | 2008 | 1 | 16 | 16 | 24680.6926
2030/2031 | 2008 | 1 | 16 | 17 | 21207.2843
2030/2031 | 2008 | 1 | 16 | 18 | 4220.2956
2030/2031 | 2008 | 1 | 16 | 19 | 0
2030/2031 | 2008 | 1 | 16 | 20 | 0
2030/2031 | 2008 | 1 | 16 | 21 | 0
2030/2031 | 2008 | 1 | 16 | 22 | 0
2030/2031 | 2008 | 1 | 16 | 23 | 0
2030/2031 | 2008 | 1 | 16 | 24 | 0
2030/2031 | 2008 | 1 | 17 | 1 | 0
2030/2031 | 2008 | 1 | 17 | 2 | 0
2030/2031 | 2008 | 1 | 17 | 3 | 0
2030/2031 | 2008 | 1 | 17 | 4 | 0
2030/2031 | 2008 | 1 | 17 | 5 | 0
2030/2031 | 2008 | 1 | 17 | 6 | 0
2030/2031 | 2008 | 1 | 17 | 7 | 0
2030/2031 | 2008 | 1 | 17 | 8 | 25.9247
2030/2031 | 2008 | 1 | 17 | 9 | 8809.2666
2030/2031 | 2008 | 1 | 17 | 10 | 26115.925
2030/2031 | 2008 | 1 | 17 | 11 | 33664.9049
2030/2031 | 2008 | 1 | 17 | 12 | 36479.0716
2030/2031 | 2008 | 1 | 17 | 13 | 38160.5818
2030/2031 | 2008 | 1 | 17 | 14 | 36737.424
2030/2031 | 2008 | 1 | 17 | 15 | 35497.748
2030/2031 | 2008 | 1 | 17 | 16 | 32834.8755
2030/2031 | 2008 | 1 | 17 | 17 | 21306.5398
2030/2031 | 2008 | 1 | 17 | 18 | 3309.647
2030/2031 | 2008 | 1 | 17 | 19 | 0
2030/2031 | 2008 | 1 | 17 | 20 | 0
2030/2031 | 2008 | 1 | 17 | 21 | 0
2030/2031 | 2008 | 1 | 17 | 22 | 0
2030/2031 | 2008 | 1 | 17 | 23 | 0
2030/2031 | 2008 | 1 | 17 | 24 | 0
2030/2031 | 2008 | 1 | 18 | 1 | 0
2030/2031 | 2008 | 1 | 18 | 2 | 0
2030/2031 | 2008 | 1 | 18 | 3 | 0
2030/2031 | 2008 | 1 | 18 | 4 | 0
2030/2031 | 2008 | 1 | 18 | 5 | 0
2030/2031 | 2008 | 1 | 18 | 6 | 0
2030/2031 | 2008 | 1 | 18 | 7 | 0
2030/2031 | 2008 | 1 | 18 | 8 | 10.3298
2030/2031 | 2008 | 1 | 18 | 9 | 6027.2203
2030/2031 | 2008 | 1 | 18 | 10 | 17945.9958
2030/2031 | 2008 | 1 | 18 | 11 | 20639.589
2030/2031 | 2008 | 1 | 18 | 12 | 22105.8858
2030/2031 | 2008 | 1 | 18 | 13 | 21826.3548
2030/2031 | 2008 | 1 | 18 | 14 | 20930.385
2030/2031 | 2008 | 1 | 18 | 15 | 21315.8763
2030/2031 | 2008 | 1 | 18 | 16 | 19518.7204
2030/2031 | 2008 | 1 | 18 | 17 | 17259.3428
2030/2031 | 2008 | 1 | 18 | 18 | 3779.577
2030/2031 | 2008 | 1 | 18 | 19 | 0
2030/2031 | 2008 | 1 | 18 | 20 | 0
2030/2031 | 2008 | 1 | 18 | 21 | 0
2030/2031 | 2008 | 1 | 18 | 22 | 0
2030/2031 | 2008 | 1 | 18 | 23 | 0
2030/2031 | 2008 | 1 | 18 | 24 | 0
2030/2031 | 2008 | 1 | 19 | 1 | 0
2030/2031 | 2008 | 1 | 19 | 2 | 0
2030/2031 | 2008 | 1 | 19 | 3 | 0
2030/2031 | 2008 | 1 | 19 | 4 | 0
2030/2031 | 2008 | 1 | 19 | 5 | 0
2030/2031 | 2008 | 1 | 19 | 6 | 0
2030/2031 | 2008 | 1 | 19 | 7 | 0
2030/2031 | 2008 | 1 | 19 | 8 | 26.0957
2030/2031 | 2008 | 1 | 19 | 9 | 13044.331
2030/2031 | 2008 | 1 | 19 | 10 | 41356.031
2030/2031 | 2008 | 1 | 19 | 11 | 48636.7081
2030/2031 | 2008 | 1 | 19 | 12 | 47512.8414
2030/2031 | 2008 | 1 | 19 | 13 | 46957.4893
2030/2031 | 2008 | 1 | 19 | 14 | 47255.7683
2030/2031 | 2008 | 1 | 19 | 15 | 47164.7037
2030/2031 | 2008 | 1 | 19 | 16 | 43593.5399
2030/2031 | 2008 | 1 | 19 | 17 | 34453.0667
2030/2031 | 2008 | 1 | 19 | 18 | 6603.6582
2030/2031 | 2008 | 1 | 19 | 19 | 0
2030/2031 | 2008 | 1 | 19 | 20 | 0
2030/2031 | 2008 | 1 | 19 | 21 | 0
2030/2031 | 2008 | 1 | 19 | 22 | 0
2030/2031 | 2008 | 1 | 19 | 23 | 0
2030/2031 | 2008 | 1 | 19 | 24 | 0
2030/2031 | 2008 | 1 | 20 | 1 | 0
2030/2031 | 2008 | 1 | 20 | 2 | 0
2030/2031 | 2008 | 1 | 20 | 3 | 0
2030/2031 | 2008 | 1 | 20 | 4 | 0
2030/2031 | 2008 | 1 | 20 | 5 | 0
2030/2031 | 2008 | 1 | 20 | 6 | 0
2030/2031 | 2008 | 1 | 20 | 7 | 0
2030/2031 | 2008 | 1 | 20 | 8 | 42.6181
2030/2031 | 2008 | 1 | 20 | 9 | 17680.8692
2030/2031 | 2008 | 1 | 20 | 10 | 43729.5999
2030/2031 | 2008 | 1 | 20 | 11 | 48963.4634
2030/2031 | 2008 | 1 | 20 | 12 | 46761.5601
2030/2031 | 2008 | 1 | 20 | 13 | 46201.9574
2030/2031 | 2008 | 1 | 20 | 14 | 46469.1523
2030/2031 | 2008 | 1 | 20 | 15 | 44376.1005
2030/2031 | 2008 | 1 | 20 | 16 | 40288.3164
2030/2031 | 2008 | 1 | 20 | 17 | 31629.021
2030/2031 | 2008 | 1 | 20 | 18 | 5985.5139
2030/2031 | 2008 | 1 | 20 | 19 | 0
2030/2031 | 2008 | 1 | 20 | 20 | 0
2030/2031 | 2008 | 1 | 20 | 21 | 0
2030/2031 | 2008 | 1 | 20 | 22 | 0
2030/2031 | 2008 | 1 | 20 | 23 | 0
2030/2031 | 2008 | 1 | 20 | 24 | 0
2030/2031 | 2008 | 1 | 21 | 1 | 0
2030/2031 | 2008 | 1 | 21 | 2 | 0
2030/2031 | 2008 | 1 | 21 | 3 | 0
2030/2031 | 2008 | 1 | 21 | 4 | 0
2030/2031 | 2008 | 1 | 21 | 5 | 0
2030/2031 | 2008 | 1 | 21 | 6 | 0
2030/2031 | 2008 | 1 | 21 | 7 | 0
2030/2031 | 2008 | 1 | 21 | 8 | 0.04657
2030/2031 | 2008 | 1 | 21 | 9 | 579.9495
2030/2031 | 2008 | 1 | 21 | 10 | 4710.1863
2030/2031 | 2008 | 1 | 21 | 11 | 8229.0324
2030/2031 | 2008 | 1 | 21 | 12 | 10581.272
2030/2031 | 2008 | 1 | 21 | 13 | 12012.8902
2030/2031 | 2008 | 1 | 21 | 14 | 13686.2259
2030/2031 | 2008 | 1 | 21 | 15 | 13655.3182
2030/2031 | 2008 | 1 | 21 | 16 | 14588.4175
2030/2031 | 2008 | 1 | 21 | 17 | 12991.0366
2030/2031 | 2008 | 1 | 21 | 18 | 3792.5148
2030/2031 | 2008 | 1 | 21 | 19 | 0
2030/2031 | 2008 | 1 | 21 | 20 | 0
2030/2031 | 2008 | 1 | 21 | 21 | 0
2030/2031 | 2008 | 1 | 21 | 22 | 0
2030/2031 | 2008 | 1 | 21 | 23 | 0
2030/2031 | 2008 | 1 | 21 | 24 | 0
2030/2031 | 2008 | 1 | 22 | 1 | 0
2030/2031 | 2008 | 1 | 22 | 2 | 0
2030/2031 | 2008 | 1 | 22 | 3 | 0
2030/2031 | 2008 | 1 | 22 | 4 | 0
2030/2031 | 2008 | 1 | 22 | 5 | 0
2030/2031 | 2008 | 1 | 22 | 6 | 0
2030/2031 | 2008 | 1 | 22 | 7 | 0
2030/2031 | 2008 | 1 | 22 | 8 | 8.7129
2030/2031 | 2008 | 1 | 22 | 9 | 2295.5415
2030/2031 | 2008 | 1 | 22 | 10 | 9791.2034
2030/2031 | 2008 | 1 | 22 | 11 | 12962.635
2030/2031 | 2008 | 1 | 22 | 12 | 14453.5512
2030/2031 | 2008 | 1 | 22 | 13 | 13661.5606
2030/2031 | 2008 | 1 | 22 | 14 | 12652.0057
2030/2031 | 2008 | 1 | 22 | 15 | 13894.5827
2030/2031 | 2008 | 1 | 22 | 16 | 11816.8156
2030/2031 | 2008 | 1 | 22 | 17 | 10600.5931
2030/2031 | 2008 | 1 | 22 | 18 | 2588.7324
2030/2031 | 2008 | 1 | 22 | 19 | 0
2030/2031 | 2008 | 1 | 22 | 20 | 0
2030/2031 | 2008 | 1 | 22 | 21 | 0
2030/2031 | 2008 | 1 | 22 | 22 | 0
2030/2031 | 2008 | 1 | 22 | 23 | 0
2030/2031 | 2008 | 1 | 22 | 24 | 0
2030/2031 | 2008 | 1 | 23 | 1 | 0
2030/2031 | 2008 | 1 | 23 | 2 | 0
2030/2031 | 2008 | 1 | 23 | 3 | 0
2030/2031 | 2008 | 1 | 23 | 4 | 0
2030/2031 | 2008 | 1 | 23 | 5 | 0
2030/2031 | 2008 | 1 | 23 | 6 | 0
2030/2031 | 2008 | 1 | 23 | 7 | 0
2030/2031 | 2008 | 1 | 23 | 8 | 2.8128
2030/2031 | 2008 | 1 | 23 | 9 | 2196.2791
2030/2031 | 2008 | 1 | 23 | 10 | 9184.2261
2030/2031 | 2008 | 1 | 23 | 11 | 12126.6889
2030/2031 | 2008 | 1 | 23 | 12 | 13825.5799
2030/2031 | 2008 | 1 | 23 | 13 | 13907.8872
2030/2031 | 2008 | 1 | 23 | 14 | 13683.703
2030/2031 | 2008 | 1 | 23 | 15 | 13490.6724
2030/2031 | 2008 | 1 | 23 | 16 | 11765.3514
2030/2031 | 2008 | 1 | 23 | 17 | 7760.1886
2030/2031 | 2008 | 1 | 23 | 18 | 1667.6657
2030/2031 | 2008 | 1 | 23 | 19 | 0
2030/2031 | 2008 | 1 | 23 | 20 | 0
2030/2031 | 2008 | 1 | 23 | 21 | 0
2030/2031 | 2008 | 1 | 23 | 22 | 0
2030/2031 | 2008 | 1 | 23 | 23 | 0
2030/2031 | 2008 | 1 | 23 | 24 | 0
2030/2031 | 2008 | 1 | 24 | 1 | 0
2030/2031 | 2008 | 1 | 24 | 2 | 0
2030/2031 | 2008 | 1 | 24 | 3 | 0
2030/2031 | 2008 | 1 | 24 | 4 | 0
2030/2031 | 2008 | 1 | 24 | 5 | 0
2030/2031 | 2008 | 1 | 24 | 6 | 0
2030/2031 | 2008 | 1 | 24 | 7 | 0
2030/2031 | 2008 | 1 | 24 | 8 | 12.0554
2030/2031 | 2008 | 1 | 24 | 9 | 4411.2651
2030/2031 | 2008 | 1 | 24 | 10 | 15192.9659
2030/2031 | 2008 | 1 | 24 | 11 | 19001.3678
2030/2031 | 2008 | 1 | 24 | 12 | 21069.2513
2030/2031 | 2008 | 1 | 24 | 13 | 20384.6108
2030/2031 | 2008 | 1 | 24 | 14 | 19316.2635
2030/2031 | 2008 | 1 | 24 | 15 | 15402.6633
2030/2031 | 2008 | 1 | 24 | 16 | 12857.8331
2030/2031 | 2008 | 1 | 24 | 17 | 5851.0672
2030/2031 | 2008 | 1 | 24 | 18 | 819.9731
2030/2031 | 2008 | 1 | 24 | 19 | 0
2030/2031 | 2008 | 1 | 24 | 20 | 0
2030/2031 | 2008 | 1 | 24 | 21 | 0
2030/2031 | 2008 | 1 | 24 | 22 | 0
2030/2031 | 2008 | 1 | 24 | 23 | 0
2030/2031 | 2008 | 1 | 24 | 24 | 0
2030/2031 | 2008 | 1 | 25 | 1 | 0
2030/2031 | 2008 | 1 | 25 | 2 | 0
2030/2031 | 2008 | 1 | 25 | 3 | 0
2030/2031 | 2008 | 1 | 25 | 4 | 0
2030/2031 | 2008 | 1 | 25 | 5 | 0
2030/2031 | 2008 | 1 | 25 | 6 | 0
2030/2031 | 2008 | 1 | 25 | 7 | 0
2030/2031 | 2008 | 1 | 25 | 8 | 0.001
2030/2031 | 2008 | 1 | 25 | 9 | 490.143
2030/2031 | 2008 | 1 | 25 | 10 | 4168.479
2030/2031 | 2008 | 1 | 25 | 11 | 7256.8636
2030/2031 | 2008 | 1 | 25 | 12 | 9098.8895
2030/2031 | 2008 | 1 | 25 | 13 | 12844.1012
2030/2031 | 2008 | 1 | 25 | 14 | 13534.8156
2030/2031 | 2008 | 1 | 25 | 15 | 14306.0689
2030/2031 | 2008 | 1 | 25 | 16 | 15752.4307
2030/2031 | 2008 | 1 | 25 | 17 | 14110.0662
2030/2031 | 2008 | 1 | 25 | 18 | 4302.9652
2030/2031 | 2008 | 1 | 25 | 19 | 0
2030/2031 | 2008 | 1 | 25 | 20 | 0
2030/2031 | 2008 | 1 | 25 | 21 | 0
2030/2031 | 2008 | 1 | 25 | 22 | 0
2030/2031 | 2008 | 1 | 25 | 23 | 0
2030/2031 | 2008 | 1 | 25 | 24 | 0
2030/2031 | 2008 | 1 | 26 | 1 | 0
2030/2031 | 2008 | 1 | 26 | 2 | 0
2030/2031 | 2008 | 1 | 26 | 3 | 0
2030/2031 | 2008 | 1 | 26 | 4 | 0
2030/2031 | 2008 | 1 | 26 | 5 | 0
2030/2031 | 2008 | 1 | 26 | 6 | 0
2030/2031 | 2008 | 1 | 26 | 7 | 0
2030/2031 | 2008 | 1 | 26 | 8 | 11.3574
2030/2031 | 2008 | 1 | 26 | 9 | 7556.8088
2030/2031 | 2008 | 1 | 26 | 10 | 23836.4294
2030/2031 | 2008 | 1 | 26 | 11 | 27491.8528
2030/2031 | 2008 | 1 | 26 | 12 | 30445.2008
2030/2031 | 2008 | 1 | 26 | 13 | 34221.211
2030/2031 | 2008 | 1 | 26 | 14 | 34054.9362
2030/2031 | 2008 | 1 | 26 | 15 | 32938.5148
2030/2031 | 2008 | 1 | 26 | 16 | 29792.1137
2030/2031 | 2008 | 1 | 26 | 17 | 22067.6488
2030/2031 | 2008 | 1 | 26 | 18 | 5892.3857
2030/2031 | 2008 | 1 | 26 | 19 | 0
2030/2031 | 2008 | 1 | 26 | 20 | 0
2030/2031 | 2008 | 1 | 26 | 21 | 0
2030/2031 | 2008 | 1 | 26 | 22 | 0
2030/2031 | 2008 | 1 | 26 | 23 | 0
2030/2031 | 2008 | 1 | 26 | 24 | 0
2030/2031 | 2008 | 1 | 27 | 1 | 0
2030/2031 | 2008 | 1 | 27 | 2 | 0
2030/2031 | 2008 | 1 | 27 | 3 | 0
2030/2031 | 2008 | 1 | 27 | 4 | 0
2030/2031 | 2008 | 1 | 27 | 5 | 0
2030/2031 | 2008 | 1 | 27 | 6 | 0
2030/2031 | 2008 | 1 | 27 | 7 | 0
2030/2031 | 2008 | 1 | 27 | 8 | 17.5698
2030/2031 | 2008 | 1 | 27 | 9 | 6842.2933
2030/2031 | 2008 | 1 | 27 | 10 | 22066.8028
2030/2031 | 2008 | 1 | 27 | 11 | 27066.2153
2030/2031 | 2008 | 1 | 27 | 12 | 34986.2211
2030/2031 | 2008 | 1 | 27 | 13 | 39117.9321
2030/2031 | 2008 | 1 | 27 | 14 | 39836.8469
2030/2031 | 2008 | 1 | 27 | 15 | 37997.01
2030/2031 | 2008 | 1 | 27 | 16 | 34013.2535
2030/2031 | 2008 | 1 | 27 | 17 | 24318.7676
2030/2031 | 2008 | 1 | 27 | 18 | 6261.7058
2030/2031 | 2008 | 1 | 27 | 19 | 0
2030/2031 | 2008 | 1 | 27 | 20 | 0
2030/2031 | 2008 | 1 | 27 | 21 | 0
2030/2031 | 2008 | 1 | 27 | 22 | 0
2030/2031 | 2008 | 1 | 27 | 23 | 0
2030/2031 | 2008 | 1 | 27 | 24 | 0
2030/2031 | 2008 | 1 | 28 | 1 | 0
2030/2031 | 2008 | 1 | 28 | 2 | 0
2030/2031 | 2008 | 1 | 28 | 3 | 0
2030/2031 | 2008 | 1 | 28 | 4 | 0
2030/2031 | 2008 | 1 | 28 | 5 | 0
2030/2031 | 2008 | 1 | 28 | 6 | 0
2030/2031 | 2008 | 1 | 28 | 7 | 0
2030/2031 | 2008 | 1 | 28 | 8 | 1.3782
2030/2031 | 2008 | 1 | 28 | 9 | 1617.6855
2030/2031 | 2008 | 1 | 28 | 10 | 9056.1466
2030/2031 | 2008 | 1 | 28 | 11 | 11641.1123
2030/2031 | 2008 | 1 | 28 | 12 | 13129.4612
2030/2031 | 2008 | 1 | 28 | 13 | 14506.2342
2030/2031 | 2008 | 1 | 28 | 14 | 15490.2165
2030/2031 | 2008 | 1 | 28 | 15 | 14401.2273
2030/2031 | 2008 | 1 | 28 | 16 | 13099.274
2030/2031 | 2008 | 1 | 28 | 17 | 10624.3045
2030/2031 | 2008 | 1 | 28 | 18 | 3465.5352
2030/2031 | 2008 | 1 | 28 | 19 | 0
2030/2031 | 2008 | 1 | 28 | 20 | 0
2030/2031 | 2008 | 1 | 28 | 21 | 0
2030/2031 | 2008 | 1 | 28 | 22 | 0
2030/2031 | 2008 | 1 | 28 | 23 | 0
2030/2031 | 2008 | 1 | 28 | 24 | 0
2030/2031 | 2008 | 1 | 29 | 1 | 0
2030/2031 | 2008 | 1 | 29 | 2 | 0
2030/2031 | 2008 | 1 | 29 | 3 | 0
2030/2031 | 2008 | 1 | 29 | 4 | 0
2030/2031 | 2008 | 1 | 29 | 5 | 0
2030/2031 | 2008 | 1 | 29 | 6 | 0
2030/2031 | 2008 | 1 | 29 | 7 | 0
2030/2031 | 2008 | 1 | 29 | 8 | 19.3649
2030/2031 | 2008 | 1 | 29 | 9 | 7423.1732
2030/2031 | 2008 | 1 | 29 | 10 | 24825.0901
2030/2031 | 2008 | 1 | 29 | 11 | 31368.5556
2030/2031 | 2008 | 1 | 29 | 12 | 35270.0542
2030/2031 | 2008 | 1 | 29 | 13 | 38857.8831
2030/2031 | 2008 | 1 | 29 | 14 | 40893.4086
2030/2031 | 2008 | 1 | 29 | 15 | 46312.2513
2030/2031 | 2008 | 1 | 29 | 16 | 47640.6429
2030/2031 | 2008 | 1 | 29 | 17 | 37314.7921
2030/2031 | 2008 | 1 | 29 | 18 | 10755.3583
2030/2031 | 2008 | 1 | 29 | 19 | 0
2030/2031 | 2008 | 1 | 29 | 20 | 0
2030/2031 | 2008 | 1 | 29 | 21 | 0
2030/2031 | 2008 | 1 | 29 | 22 | 0
2030/2031 | 2008 | 1 | 29 | 23 | 0
2030/2031 | 2008 | 1 | 29 | 24 | 0
2030/2031 | 2008 | 1 | 30 | 1 | 0
2030/2031 | 2008 | 1 | 30 | 2 | 0
2030/2031 | 2008 | 1 | 30 | 3 | 0
2030/2031 | 2008 | 1 | 30 | 4 | 0
2030/2031 | 2008 | 1 | 30 | 5 | 0
2030/2031 | 2008 | 1 | 30 | 6 | 0
2030/2031 | 2008 | 1 | 30 | 7 | 0
2030/2031 | 2008 | 1 | 30 | 8 | 85.3265
2030/2031 | 2008 | 1 | 30 | 9 | 18561.1302
2030/2031 | 2008 | 1 | 30 | 10 | 45949.8101
2030/2031 | 2008 | 1 | 30 | 11 | 48424.9166
2030/2031 | 2008 | 1 | 30 | 12 | 46658.9685
2030/2031 | 2008 | 1 | 30 | 13 | 45230.8939
2030/2031 | 2008 | 1 | 30 | 14 | 42733.9747
2030/2031 | 2008 | 1 | 30 | 15 | 37770.3019
2030/2031 | 2008 | 1 | 30 | 16 | 35575.4849
2030/2031 | 2008 | 1 | 30 | 17 | 27776.4336
2030/2031 | 2008 | 1 | 30 | 18 | 8343.1334
2030/2031 | 2008 | 1 | 30 | 19 | 0
2030/2031 | 2008 | 1 | 30 | 20 | 0
2030/2031 | 2008 | 1 | 30 | 21 | 0
2030/2031 | 2008 | 1 | 30 | 22 | 0
2030/2031 | 2008 | 1 | 30 | 23 | 0
2030/2031 | 2008 | 1 | 30 | 24 | 0
2030/2031 | 2008 | 1 | 31 | 1 | 0
2030/2031 | 2008 | 1 | 31 | 2 | 0
2030/2031 | 2008 | 1 | 31 | 3 | 0
2030/2031 | 2008 | 1 | 31 | 4 | 0
2030/2031 | 2008 | 1 | 31 | 5 | 0
2030/2031 | 2008 | 1 | 31 | 6 | 0
2030/2031 | 2008 | 1 | 31 | 7 | 0
2030/2031 | 2008 | 1 | 31 | 8 | 23.5081
2030/2031 | 2008 | 1 | 31 | 9 | 8822.9621
2030/2031 | 2008 | 1 | 31 | 10 | 32307.4675
2030/2031 | 2008 | 1 | 31 | 11 | 41411.2633
2030/2031 | 2008 | 1 | 31 | 12 | 44002.7089
2030/2031 | 2008 | 1 | 31 | 13 | 48770.4508
2030/2031 | 2008 | 1 | 31 | 14 | 51122.8336
2030/2031 | 2008 | 1 | 31 | 15 | 53029.9649
2030/2031 | 2008 | 1 | 31 | 16 | 49985.8824
2030/2031 | 2008 | 1 | 31 | 17 | 38631.4575
2030/2031 | 2008 | 1 | 31 | 18 | 10670.9231
2030/2031 | 2008 | 1 | 31 | 19 | 0
2030/2031 | 2008 | 1 | 31 | 20 | 0
2030/2031 | 2008 | 1 | 31 | 21 | 0
2030/2031 | 2008 | 1 | 31 | 22 | 0
2030/2031 | 2008 | 1 | 31 | 23 | 0
2030/2031 | 2008 | 1 | 31 | 24 | 0
2026 | 2008 | 5 | 1 | 1 | 0
2026 | 2008 | 5 | 1 | 2 | 0
2026 | 2008 | 5 | 1 | 3 | 0
2026 | 2008 | 5 | 1 | 4 | 0
2026 | 2008 | 5 | 1 | 5 | 0
2026 | 2008 | 5 | 1 | 6 | 0
2026 | 2008 | 5 | 1 | 7 | 0.040681
2026 | 2008 | 5 | 1 | 8 | 2015.7693
2026 | 2008 | 5 | 1 | 9 | 13507.0146
2026 | 2008 | 5 | 1 | 10 | 18943.1411
2026 | 2008 | 5 | 1 | 11 | 20041.7769
2026 | 2008 | 5 | 1 | 12 | 22452.3124
2026 | 2008 | 5 | 1 | 13 | 24772.6443
2026 | 2008 | 5 | 1 | 14 | 27368.9599
2026 | 2008 | 5 | 1 | 15 | 28094.7991
2026 | 2008 | 5 | 1 | 16 | 26273.5736
2026 | 2008 | 5 | 1 | 17 | 26995.9845
2026 | 2008 | 5 | 1 | 18 | 25462.7929
2026 | 2008 | 5 | 1 | 19 | 19511.1047
2026 | 2008 | 5 | 1 | 20 | 7942.9067
2026 | 2008 | 5 | 1 | 21 | 0
2026 | 2008 | 5 | 1 | 22 | 0
2026 | 2008 | 5 | 1 | 23 | 0
2026 | 2008 | 5 | 1 | 24 | 0
2026 | 2008 | 5 | 2 | 1 | 0
2026 | 2008 | 5 | 2 | 2 | 0
2026 | 2008 | 5 | 2 | 3 | 0
2026 | 2008 | 5 | 2 | 4 | 0
2026 | 2008 | 5 | 2 | 5 | 0
2026 | 2008 | 5 | 2 | 6 | 0
2026 | 2008 | 5 | 2 | 7 | 0.4491
2026 | 2008 | 5 | 2 | 8 | 4131.7999
2026 | 2008 | 5 | 2 | 9 | 20450.606
2026 | 2008 | 5 | 2 | 10 | 25890.3116
2026 | 2008 | 5 | 2 | 11 | 28664.6955
2026 | 2008 | 5 | 2 | 12 | 30301.5326
2026 | 2008 | 5 | 2 | 13 | 30859.415
2026 | 2008 | 5 | 2 | 14 | 33555.0182
2026 | 2008 | 5 | 2 | 15 | 32123.9867
2026 | 2008 | 5 | 2 | 16 | 31120.4759
2026 | 2008 | 5 | 2 | 17 | 30008.8017
2026 | 2008 | 5 | 2 | 18 | 27608.1223
2026 | 2008 | 5 | 2 | 19 | 20774.0834
2026 | 2008 | 5 | 2 | 20 | 8569.9204
2026 | 2008 | 5 | 2 | 21 | 0
2026 | 2008 | 5 | 2 | 22 | 0
2026 | 2008 | 5 | 2 | 23 | 0
2026 | 2008 | 5 | 2 | 24 | 0
2026 | 2008 | 5 | 3 | 1 | 0
2026 | 2008 | 5 | 3 | 2 | 0
2026 | 2008 | 5 | 3 | 3 | 0
2026 | 2008 | 5 | 3 | 4 | 0
2026 | 2008 | 5 | 3 | 5 | 0
2026 | 2008 | 5 | 3 | 6 | 0
2026 | 2008 | 5 | 3 | 7 | 5.3963
2026 | 2008 | 5 | 3 | 8 | 7524.1016
2026 | 2008 | 5 | 3 | 9 | 25528.7008
2026 | 2008 | 5 | 3 | 10 | 31028.9575
2026 | 2008 | 5 | 3 | 11 | 31174.2914
2026 | 2008 | 5 | 3 | 12 | 33416.8457
2026 | 2008 | 5 | 3 | 13 | 33841.727
2026 | 2008 | 5 | 3 | 14 | 34341.8357
2026 | 2008 | 5 | 3 | 15 | 33720.0207
2026 | 2008 | 5 | 3 | 16 | 32648.113
2026 | 2008 | 5 | 3 | 17 | 30415.6108
2026 | 2008 | 5 | 3 | 18 | 28011.5582
2026 | 2008 | 5 | 3 | 19 | 20782.9005
2026 | 2008 | 5 | 3 | 20 | 8458.9604
2026 | 2008 | 5 | 3 | 21 | 0
2026 | 2008 | 5 | 3 | 22 | 0
2026 | 2008 | 5 | 3 | 23 | 0
2026 | 2008 | 5 | 3 | 24 | 0
2026 | 2008 | 5 | 4 | 1 | 0
2026 | 2008 | 5 | 4 | 2 | 0
2026 | 2008 | 5 | 4 | 3 | 0
2026 | 2008 | 5 | 4 | 4 | 0
2026 | 2008 | 5 | 4 | 5 | 0
2026 | 2008 | 5 | 4 | 6 | 0
2026 | 2008 | 5 | 4 | 7 | 6.1047
2026 | 2008 | 5 | 4 | 8 | 7584.6802
2026 | 2008 | 5 | 4 | 9 | 24630.0924
2026 | 2008 | 5 | 4 | 10 | 31187.2844
2026 | 2008 | 5 | 4 | 11 | 31607.3308
2026 | 2008 | 5 | 4 | 12 | 31036.0122
2026 | 2008 | 5 | 4 | 13 | 30229.506
2026 | 2008 | 5 | 4 | 14 | 30453.8357
2026 | 2008 | 5 | 4 | 15 | 28178.4374
2026 | 2008 | 5 | 4 | 16 | 27143.1754
2026 | 2008 | 5 | 4 | 17 | 23799.8364
2026 | 2008 | 5 | 4 | 18 | 20535.413
2026 | 2008 | 5 | 4 | 19 | 15742.8884
2026 | 2008 | 5 | 4 | 20 | 6604.6503
2026 | 2008 | 5 | 4 | 21 | 0
2026 | 2008 | 5 | 4 | 22 | 0
2026 | 2008 | 5 | 4 | 23 | 0
2026 | 2008 | 5 | 4 | 24 | 0
2026 | 2008 | 5 | 5 | 1 | 0
2026 | 2008 | 5 | 5 | 2 | 0
2026 | 2008 | 5 | 5 | 3 | 0
2026 | 2008 | 5 | 5 | 4 | 0
2026 | 2008 | 5 | 5 | 5 | 0
2026 | 2008 | 5 | 5 | 6 | 0
2026 | 2008 | 5 | 5 | 7 | 4.6217
2026 | 2008 | 5 | 5 | 8 | 1104.7939
2026 | 2008 | 5 | 5 | 9 | 7684.9023
2026 | 2008 | 5 | 5 | 10 | 13233.9778
2026 | 2008 | 5 | 5 | 11 | 15423.4472
2026 | 2008 | 5 | 5 | 12 | 17173.4019
2026 | 2008 | 5 | 5 | 13 | 21001.8502
2026 | 2008 | 5 | 5 | 14 | 21400.8786
2026 | 2008 | 5 | 5 | 15 | 22586.2811
2026 | 2008 | 5 | 5 | 16 | 21995.0599
2026 | 2008 | 5 | 5 | 17 | 20667.1782
2026 | 2008 | 5 | 5 | 18 | 19877.6545
2026 | 2008 | 5 | 5 | 19 | 17412.6449
2026 | 2008 | 5 | 5 | 20 | 6350.7822
2026 | 2008 | 5 | 5 | 21 | 0
2026 | 2008 | 5 | 5 | 22 | 0
2026 | 2008 | 5 | 5 | 23 | 0
2026 | 2008 | 5 | 5 | 24 | 0
2026 | 2008 | 5 | 6 | 1 | 0
2026 | 2008 | 5 | 6 | 2 | 0
2026 | 2008 | 5 | 6 | 3 | 0
2026 | 2008 | 5 | 6 | 4 | 0
2026 | 2008 | 5 | 6 | 5 | 0
2026 | 2008 | 5 | 6 | 6 | 0
2026 | 2008 | 5 | 6 | 7 | 0.76052
2026 | 2008 | 5 | 6 | 8 | 707.3304
2026 | 2008 | 5 | 6 | 9 | 6204.4041
2026 | 2008 | 5 | 6 | 10 | 13181.316
2026 | 2008 | 5 | 6 | 11 | 17845.1202
2026 | 2008 | 5 | 6 | 12 | 22034.6395
2026 | 2008 | 5 | 6 | 13 | 25999.1629
2026 | 2008 | 5 | 6 | 14 | 27597.3871
2026 | 2008 | 5 | 6 | 15 | 27510.3369
2026 | 2008 | 5 | 6 | 16 | 26486.2989
2026 | 2008 | 5 | 6 | 17 | 26069.3539
2026 | 2008 | 5 | 6 | 18 | 25173.7432
2026 | 2008 | 5 | 6 | 19 | 18030.2788
2026 | 2008 | 5 | 6 | 20 | 7207.7533
2026 | 2008 | 5 | 6 | 21 | 0
2026 | 2008 | 5 | 6 | 22 | 0
2026 | 2008 | 5 | 6 | 23 | 0
2026 | 2008 | 5 | 6 | 24 | 0
2026 | 2008 | 5 | 7 | 1 | 0
2026 | 2008 | 5 | 7 | 2 | 0
2026 | 2008 | 5 | 7 | 3 | 0
2026 | 2008 | 5 | 7 | 4 | 0
2026 | 2008 | 5 | 7 | 5 | 0
2026 | 2008 | 5 | 7 | 6 | 0
2026 | 2008 | 5 | 7 | 7 | 0
2026 | 2008 | 5 | 7 | 8 | 1862.1663
2026 | 2008 | 5 | 7 | 9 | 10995.1355
2026 | 2008 | 5 | 7 | 10 | 17693.1728
2026 | 2008 | 5 | 7 | 11 | 21689.5194
2026 | 2008 | 5 | 7 | 12 | 22899.5444
2026 | 2008 | 5 | 7 | 13 | 23978.2729
2026 | 2008 | 5 | 7 | 14 | 28891.5052
2026 | 2008 | 5 | 7 | 15 | 28705.4427
2026 | 2008 | 5 | 7 | 16 | 28204.4274
2026 | 2008 | 5 | 7 | 17 | 28143.6395
2026 | 2008 | 5 | 7 | 18 | 27299.3491
2026 | 2008 | 5 | 7 | 19 | 20584.6325
2026 | 2008 | 5 | 7 | 20 | 7373.1993
2026 | 2008 | 5 | 7 | 21 | 0
2026 | 2008 | 5 | 7 | 22 | 0
2026 | 2008 | 5 | 7 | 23 | 0
2026 | 2008 | 5 | 7 | 24 | 0
2026 | 2008 | 5 | 8 | 1 | 0
2026 | 2008 | 5 | 8 | 2 | 0
2026 | 2008 | 5 | 8 | 3 | 0
2026 | 2008 | 5 | 8 | 4 | 0
2026 | 2008 | 5 | 8 | 5 | 0
2026 | 2008 | 5 | 8 | 6 | 0
2026 | 2008 | 5 | 8 | 7 | 11.6985
2026 | 2008 | 5 | 8 | 8 | 7323.1177
2026 | 2008 | 5 | 8 | 9 | 22896.2783
2026 | 2008 | 5 | 8 | 10 | 28599.8648
2026 | 2008 | 5 | 8 | 11 | 32078.8658
2026 | 2008 | 5 | 8 | 12 | 33764.9115
2026 | 2008 | 5 | 8 | 13 | 33658.5567
2026 | 2008 | 5 | 8 | 14 | 33836.3218
2026 | 2008 | 5 | 8 | 15 | 32971.6273
2026 | 2008 | 5 | 8 | 16 | 30934.7076
2026 | 2008 | 5 | 8 | 17 | 29310.7213
2026 | 2008 | 5 | 8 | 18 | 26429.5994
2026 | 2008 | 5 | 8 | 19 | 19274.5757
2026 | 2008 | 5 | 8 | 20 | 8264.5786
2026 | 2008 | 5 | 8 | 21 | 0
2026 | 2008 | 5 | 8 | 22 | 0
2026 | 2008 | 5 | 8 | 23 | 0
2026 | 2008 | 5 | 8 | 24 | 0
2026 | 2008 | 5 | 9 | 1 | 0
2026 | 2008 | 5 | 9 | 2 | 0
2026 | 2008 | 5 | 9 | 3 | 0
2026 | 2008 | 5 | 9 | 4 | 0
2026 | 2008 | 5 | 9 | 5 | 0
2026 | 2008 | 5 | 9 | 6 | 0
2026 | 2008 | 5 | 9 | 7 | 11.6492
2026 | 2008 | 5 | 9 | 8 | 6358.7501
2026 | 2008 | 5 | 9 | 9 | 20868.9955
2026 | 2008 | 5 | 9 | 10 | 26430.3699
2026 | 2008 | 5 | 9 | 11 | 30424.155
2026 | 2008 | 5 | 9 | 12 | 31476.6819
2026 | 2008 | 5 | 9 | 13 | 33450.1078
2026 | 2008 | 5 | 9 | 14 | 33387.2299
2026 | 2008 | 5 | 9 | 15 | 32445.3449
2026 | 2008 | 5 | 9 | 16 | 31250.7886
2026 | 2008 | 5 | 9 | 17 | 29832.7598
2026 | 2008 | 5 | 9 | 18 | 26266.2975
2026 | 2008 | 5 | 9 | 19 | 18925.3833
2026 | 2008 | 5 | 9 | 20 | 7597.7273
2026 | 2008 | 5 | 9 | 21 | 0
2026 | 2008 | 5 | 9 | 22 | 0
2026 | 2008 | 5 | 9 | 23 | 0
2026 | 2008 | 5 | 9 | 24 | 0
2026 | 2008 | 5 | 10 | 1 | 0
2026 | 2008 | 5 | 10 | 2 | 0
2026 | 2008 | 5 | 10 | 3 | 0
2026 | 2008 | 5 | 10 | 4 | 0
2026 | 2008 | 5 | 10 | 5 | 0
2026 | 2008 | 5 | 10 | 6 | 0
2026 | 2008 | 5 | 10 | 7 | 0.7841
2026 | 2008 | 5 | 10 | 8 | 3505.9829
2026 | 2008 | 5 | 10 | 9 | 15887.4737
2026 | 2008 | 5 | 10 | 10 | 21882.3913
2026 | 2008 | 5 | 10 | 11 | 25511.5564
2026 | 2008 | 5 | 10 | 12 | 30771.1653
2026 | 2008 | 5 | 10 | 13 | 33220.5038
2026 | 2008 | 5 | 10 | 14 | 33299.726
2026 | 2008 | 5 | 10 | 15 | 31680.3071
2026 | 2008 | 5 | 10 | 16 | 30067.6054
2026 | 2008 | 5 | 10 | 17 | 25908.8651
2026 | 2008 | 5 | 10 | 18 | 23791.0254
2026 | 2008 | 5 | 10 | 19 | 18639.1026
2026 | 2008 | 5 | 10 | 20 | 6810.557
2026 | 2008 | 5 | 10 | 21 | 0
2026 | 2008 | 5 | 10 | 22 | 0
2026 | 2008 | 5 | 10 | 23 | 0
2026 | 2008 | 5 | 10 | 24 | 0
2026 | 2008 | 5 | 11 | 1 | 0
2026 | 2008 | 5 | 11 | 2 | 0
2026 | 2008 | 5 | 11 | 3 | 0
2026 | 2008 | 5 | 11 | 4 | 0
2026 | 2008 | 5 | 11 | 5 | 0
2026 | 2008 | 5 | 11 | 6 | 0
2026 | 2008 | 5 | 11 | 7 | 21.0823
2026 | 2008 | 5 | 11 | 8 | 9741.4791
2026 | 2008 | 5 | 11 | 9 | 26885.6215
2026 | 2008 | 5 | 11 | 10 | 32039.2592
2026 | 2008 | 5 | 11 | 11 | 32150.2684
2026 | 2008 | 5 | 11 | 12 | 33149.0731
2026 | 2008 | 5 | 11 | 13 | 33595.6101
2026 | 2008 | 5 | 11 | 14 | 33662.3945
2026 | 2008 | 5 | 11 | 15 | 32411.9598
2026 | 2008 | 5 | 11 | 16 | 30807.096
2026 | 2008 | 5 | 11 | 17 | 28687.711
2026 | 2008 | 5 | 11 | 18 | 25020.4089
2026 | 2008 | 5 | 11 | 19 | 19410.9845
2026 | 2008 | 5 | 11 | 20 | 7591.3119
2026 | 2008 | 5 | 11 | 21 | 0
2026 | 2008 | 5 | 11 | 22 | 0
2026 | 2008 | 5 | 11 | 23 | 0
2026 | 2008 | 5 | 11 | 24 | 0
2026 | 2008 | 5 | 12 | 1 | 0
2026 | 2008 | 5 | 12 | 2 | 0
2026 | 2008 | 5 | 12 | 3 | 0
2026 | 2008 | 5 | 12 | 4 | 0
2026 | 2008 | 5 | 12 | 5 | 0
2026 | 2008 | 5 | 12 | 6 | 0
2026 | 2008 | 5 | 12 | 7 | 22.4307
2026 | 2008 | 5 | 12 | 8 | 8792.5489
2026 | 2008 | 5 | 12 | 9 | 24399.6979
2026 | 2008 | 5 | 12 | 10 | 29824.6586
2026 | 2008 | 5 | 12 | 11 | 30906.2369
2026 | 2008 | 5 | 12 | 12 | 32453.8779
2026 | 2008 | 5 | 12 | 13 | 32199.6505
2026 | 2008 | 5 | 12 | 14 | 33585.1808
2026 | 2008 | 5 | 12 | 15 | 32396.9023
2026 | 2008 | 5 | 12 | 16 | 31053.5412
2026 | 2008 | 5 | 12 | 17 | 28741.077
2026 | 2008 | 5 | 12 | 18 | 24191.9736
2026 | 2008 | 5 | 12 | 19 | 18921.9194
2026 | 2008 | 5 | 12 | 20 | 6362.6653
2026 | 2008 | 5 | 12 | 21 | 0
2026 | 2008 | 5 | 12 | 22 | 0
2026 | 2008 | 5 | 12 | 23 | 0
2026 | 2008 | 5 | 12 | 24 | 0
2026 | 2008 | 5 | 13 | 1 | 0
2026 | 2008 | 5 | 13 | 2 | 0
2026 | 2008 | 5 | 13 | 3 | 0
2026 | 2008 | 5 | 13 | 4 | 0
2026 | 2008 | 5 | 13 | 5 | 0
2026 | 2008 | 5 | 13 | 6 | 0
2026 | 2008 | 5 | 13 | 7 | 0.19935
2026 | 2008 | 5 | 13 | 8 | 1410.9622
2026 | 2008 | 5 | 13 | 9 | 8543.5678
2026 | 2008 | 5 | 13 | 10 | 13936.1984
2026 | 2008 | 5 | 13 | 11 | 18912.6786
2026 | 2008 | 5 | 13 | 12 | 23070.4478
2026 | 2008 | 5 | 13 | 13 | 25523.4615
2026 | 2008 | 5 | 13 | 14 | 27120.6435
2026 | 2008 | 5 | 13 | 15 | 28466.2864
2026 | 2008 | 5 | 13 | 16 | 26974.6983
2026 | 2008 | 5 | 13 | 17 | 23412.1434
2026 | 2008 | 5 | 13 | 18 | 22562.7411
2026 | 2008 | 5 | 13 | 19 | 17924.5837
2026 | 2008 | 5 | 13 | 20 | 6552.0263
2026 | 2008 | 5 | 13 | 21 | 0
2026 | 2008 | 5 | 13 | 22 | 0
2026 | 2008 | 5 | 13 | 23 | 0
2026 | 2008 | 5 | 13 | 24 | 0
2026 | 2008 | 5 | 14 | 1 | 0
2026 | 2008 | 5 | 14 | 2 | 0
2026 | 2008 | 5 | 14 | 3 | 0
2026 | 2008 | 5 | 14 | 4 | 0
2026 | 2008 | 5 | 14 | 5 | 0
2026 | 2008 | 5 | 14 | 6 | 0
2026 | 2008 | 5 | 14 | 7 | 1.4897
2026 | 2008 | 5 | 14 | 8 | 2651.6604
2026 | 2008 | 5 | 14 | 9 | 10639.7057
2026 | 2008 | 5 | 14 | 10 | 16222.9833
2026 | 2008 | 5 | 14 | 11 | 18725.314
2026 | 2008 | 5 | 14 | 12 | 24269.4456
2026 | 2008 | 5 | 14 | 13 | 26121.8977
2026 | 2008 | 5 | 14 | 14 | 27273.4282
2026 | 2008 | 5 | 14 | 15 | 25666.4968
2026 | 2008 | 5 | 14 | 16 | 24504.9252
2026 | 2008 | 5 | 14 | 17 | 22048.9797
2026 | 2008 | 5 | 14 | 18 | 19680.9943
2026 | 2008 | 5 | 14 | 19 | 15935.3299
2026 | 2008 | 5 | 14 | 20 | 6816.0272
2026 | 2008 | 5 | 14 | 21 | 8.797
2026 | 2008 | 5 | 14 | 22 | 0
2026 | 2008 | 5 | 14 | 23 | 0
2026 | 2008 | 5 | 14 | 24 | 0
2026 | 2008 | 5 | 15 | 1 | 0
2026 | 2008 | 5 | 15 | 2 | 0
2026 | 2008 | 5 | 15 | 3 | 0
2026 | 2008 | 5 | 15 | 4 | 0
2026 | 2008 | 5 | 15 | 5 | 0
2026 | 2008 | 5 | 15 | 6 | 0
2026 | 2008 | 5 | 15 | 7 | 0.18588
2026 | 2008 | 5 | 15 | 8 | 2204.3343
2026 | 2008 | 5 | 15 | 9 | 13361.111
2026 | 2008 | 5 | 15 | 10 | 24336.1999
2026 | 2008 | 5 | 15 | 11 | 27902.6776
2026 | 2008 | 5 | 15 | 12 | 29673.8688
2026 | 2008 | 5 | 15 | 13 | 29953.538
2026 | 2008 | 5 | 15 | 14 | 30317.7953
2026 | 2008 | 5 | 15 | 15 | 28711.055
2026 | 2008 | 5 | 15 | 16 | 26667.4939
2026 | 2008 | 5 | 15 | 17 | 23830.0033
2026 | 2008 | 5 | 15 | 18 | 22179.8985
2026 | 2008 | 5 | 15 | 19 | 16963.9269
2026 | 2008 | 5 | 15 | 20 | 6300.9618
2026 | 2008 | 5 | 15 | 21 | 19.971
2026 | 2008 | 5 | 15 | 22 | 0
2026 | 2008 | 5 | 15 | 23 | 0
2026 | 2008 | 5 | 15 | 24 | 0
2026 | 2008 | 5 | 16 | 1 | 0
2026 | 2008 | 5 | 16 | 2 | 0
2026 | 2008 | 5 | 16 | 3 | 0
2026 | 2008 | 5 | 16 | 4 | 0
2026 | 2008 | 5 | 16 | 5 | 0
2026 | 2008 | 5 | 16 | 6 | 0
2026 | 2008 | 5 | 16 | 7 | 19.2342
2026 | 2008 | 5 | 16 | 8 | 5232.5315
2026 | 2008 | 5 | 16 | 9 | 16561.9858
2026 | 2008 | 5 | 16 | 10 | 24096.1396
2026 | 2008 | 5 | 16 | 11 | 27442.0243
2026 | 2008 | 5 | 16 | 12 | 30400.3158
2026 | 2008 | 5 | 16 | 13 | 31918.3448
2026 | 2008 | 5 | 16 | 14 | 33208.8832
2026 | 2008 | 5 | 16 | 15 | 32510.826
2026 | 2008 | 5 | 16 | 16 | 31230.0808
2026 | 2008 | 5 | 16 | 17 | 28100.3765
2026 | 2008 | 5 | 16 | 18 | 26485.5439
2026 | 2008 | 5 | 16 | 19 | 19452.2534
2026 | 2008 | 5 | 16 | 20 | 5829.9688
2026 | 2008 | 5 | 16 | 21 | 20.0071
2026 | 2008 | 5 | 16 | 22 | 0
2026 | 2008 | 5 | 16 | 23 | 0
2026 | 2008 | 5 | 16 | 24 | 0
2026 | 2008 | 5 | 17 | 1 | 0
2026 | 2008 | 5 | 17 | 2 | 0
2026 | 2008 | 5 | 17 | 3 | 0
2026 | 2008 | 5 | 17 | 4 | 0
2026 | 2008 | 5 | 17 | 5 | 0
2026 | 2008 | 5 | 17 | 6 | 0
2026 | 2008 | 5 | 17 | 7 | 20.8243
2026 | 2008 | 5 | 17 | 8 | 7064.3477
2026 | 2008 | 5 | 17 | 9 | 22345.962
2026 | 2008 | 5 | 17 | 10 | 29392.5457
2026 | 2008 | 5 | 17 | 11 | 29902.9518
2026 | 2008 | 5 | 17 | 12 | 30221.282
2026 | 2008 | 5 | 17 | 13 | 29532.9298
2026 | 2008 | 5 | 17 | 14 | 29276.2376
2026 | 2008 | 5 | 17 | 15 | 27415.4408
2026 | 2008 | 5 | 17 | 16 | 25609.4369
2026 | 2008 | 5 | 17 | 17 | 22605.1623
2026 | 2008 | 5 | 17 | 18 | 22731.1912
2026 | 2008 | 5 | 17 | 19 | 18210.6417
2026 | 2008 | 5 | 17 | 20 | 7108.0834
2026 | 2008 | 5 | 17 | 21 | 32.9858
2026 | 2008 | 5 | 17 | 22 | 0
2026 | 2008 | 5 | 17 | 23 | 0
2026 | 2008 | 5 | 17 | 24 | 0
2026 | 2008 | 5 | 18 | 1 | 0
2026 | 2008 | 5 | 18 | 2 | 0
2026 | 2008 | 5 | 18 | 3 | 0
2026 | 2008 | 5 | 18 | 4 | 0
2026 | 2008 | 5 | 18 | 5 | 0
2026 | 2008 | 5 | 18 | 6 | 0
2026 | 2008 | 5 | 18 | 7 | 43.7616
2026 | 2008 | 5 | 18 | 8 | 11609.34
2026 | 2008 | 5 | 18 | 9 | 30534.5197
2026 | 2008 | 5 | 18 | 10 | 34937.3929
2026 | 2008 | 5 | 18 | 11 | 34696.4601
2026 | 2008 | 5 | 18 | 12 | 33974.5026
2026 | 2008 | 5 | 18 | 13 | 34232.4403
2026 | 2008 | 5 | 18 | 14 | 34426.8216
2026 | 2008 | 5 | 18 | 15 | 33463.5895
2026 | 2008 | 5 | 18 | 16 | 32630.6813
2026 | 2008 | 5 | 18 | 17 | 30617.0612
2026 | 2008 | 5 | 18 | 18 | 28675.1637
2026 | 2008 | 5 | 18 | 19 | 20490.0482
2026 | 2008 | 5 | 18 | 20 | 7481.0366
2026 | 2008 | 5 | 18 | 21 | 43.7266
2026 | 2008 | 5 | 18 | 22 | 0
2026 | 2008 | 5 | 18 | 23 | 0
2026 | 2008 | 5 | 18 | 24 | 0
2026 | 2008 | 5 | 19 | 1 | 0
2026 | 2008 | 5 | 19 | 2 | 0
2026 | 2008 | 5 | 19 | 3 | 0
2026 | 2008 | 5 | 19 | 4 | 0
2026 | 2008 | 5 | 19 | 5 | 0
2026 | 2008 | 5 | 19 | 6 | 0
2026 | 2008 | 5 | 19 | 7 | 34.175
2026 | 2008 | 5 | 19 | 8 | 11542.7373
2026 | 2008 | 5 | 19 | 9 | 31199.0494
2026 | 2008 | 5 | 19 | 10 | 35313.0863
2026 | 2008 | 5 | 19 | 11 | 34319.9434
2026 | 2008 | 5 | 19 | 12 | 33974.9948
2026 | 2008 | 5 | 19 | 13 | 34337.3674
2026 | 2008 | 5 | 19 | 14 | 34164.7998
2026 | 2008 | 5 | 19 | 15 | 33204.4972
2026 | 2008 | 5 | 19 | 16 | 32308.8617
2026 | 2008 | 5 | 19 | 17 | 30738.1949
2026 | 2008 | 5 | 19 | 18 | 28113.0916
2026 | 2008 | 5 | 19 | 19 | 20698.8313
2026 | 2008 | 5 | 19 | 20 | 7455.0206
2026 | 2008 | 5 | 19 | 21 | 76.8667
2026 | 2008 | 5 | 19 | 22 | 0
2026 | 2008 | 5 | 19 | 23 | 0
2026 | 2008 | 5 | 19 | 24 | 0
2026 | 2008 | 5 | 20 | 1 | 0
2026 | 2008 | 5 | 20 | 2 | 0
2026 | 2008 | 5 | 20 | 3 | 0
2026 | 2008 | 5 | 20 | 4 | 0
2026 | 2008 | 5 | 20 | 5 | 0
2026 | 2008 | 5 | 20 | 6 | 0
2026 | 2008 | 5 | 20 | 7 | 38.4267
2026 | 2008 | 5 | 20 | 8 | 10597.7866
2026 | 2008 | 5 | 20 | 9 | 26035.8638
2026 | 2008 | 5 | 20 | 10 | 31028.3952
2026 | 2008 | 5 | 20 | 11 | 32322.4659
2026 | 2008 | 5 | 20 | 12 | 33040.6013
2026 | 2008 | 5 | 20 | 13 | 33572.1797
2026 | 2008 | 5 | 20 | 14 | 34022.9175
2026 | 2008 | 5 | 20 | 15 | 32676.6654
2026 | 2008 | 5 | 20 | 16 | 31599.8924
2026 | 2008 | 5 | 20 | 17 | 30282.357
2026 | 2008 | 5 | 20 | 18 | 28328.1883
2026 | 2008 | 5 | 20 | 19 | 20203.5296
2026 | 2008 | 5 | 20 | 20 | 7096.9806
2026 | 2008 | 5 | 20 | 21 | 79.1864
2026 | 2008 | 5 | 20 | 22 | 0
2026 | 2008 | 5 | 20 | 23 | 0
2026 | 2008 | 5 | 20 | 24 | 0
2026 | 2008 | 5 | 21 | 1 | 0
2026 | 2008 | 5 | 21 | 2 | 0
2026 | 2008 | 5 | 21 | 3 | 0
2026 | 2008 | 5 | 21 | 4 | 0
2026 | 2008 | 5 | 21 | 5 | 0
2026 | 2008 | 5 | 21 | 6 | 0
2026 | 2008 | 5 | 21 | 7 | 30.238
2026 | 2008 | 5 | 21 | 8 | 4515.7648
2026 | 2008 | 5 | 21 | 9 | 16332.6851
2026 | 2008 | 5 | 21 | 10 | 22135.2982
2026 | 2008 | 5 | 21 | 11 | 25797.4479
2026 | 2008 | 5 | 21 | 12 | 32628.7665
2026 | 2008 | 5 | 21 | 13 | 33795.3404
2026 | 2008 | 5 | 21 | 14 | 34497.6396
2026 | 2008 | 5 | 21 | 15 | 32841.0023
2026 | 2008 | 5 | 21 | 16 | 32306.3432
2026 | 2008 | 5 | 21 | 17 | 30260.5352
2026 | 2008 | 5 | 21 | 18 | 27407.6403
2026 | 2008 | 5 | 21 | 19 | 20053.0993
2026 | 2008 | 5 | 21 | 20 | 7002.1513
2026 | 2008 | 5 | 21 | 21 | 69.4103
2026 | 2008 | 5 | 21 | 22 | 0
2026 | 2008 | 5 | 21 | 23 | 0
2026 | 2008 | 5 | 21 | 24 | 0
2026 | 2008 | 5 | 22 | 1 | 0
2026 | 2008 | 5 | 22 | 2 | 0
2026 | 2008 | 5 | 22 | 3 | 0
2026 | 2008 | 5 | 22 | 4 | 0
2026 | 2008 | 5 | 22 | 5 | 0
2026 | 2008 | 5 | 22 | 6 | 0
2026 | 2008 | 5 | 22 | 7 | 3.0327
2026 | 2008 | 5 | 22 | 8 | 2407.0718
2026 | 2008 | 5 | 22 | 9 | 12514.5723
2026 | 2008 | 5 | 22 | 10 | 22609.4039
2026 | 2008 | 5 | 22 | 11 | 27324.7524
2026 | 2008 | 5 | 22 | 12 | 31948.2052
2026 | 2008 | 5 | 22 | 13 | 33480.3231
2026 | 2008 | 5 | 22 | 14 | 33843.2538
2026 | 2008 | 5 | 22 | 15 | 32594.3595
2026 | 2008 | 5 | 22 | 16 | 30578.3767
2026 | 2008 | 5 | 22 | 17 | 27592.9825
2026 | 2008 | 5 | 22 | 18 | 25222.7611
2026 | 2008 | 5 | 22 | 19 | 20485.3268
2026 | 2008 | 5 | 22 | 20 | 7563.2147
2026 | 2008 | 5 | 22 | 21 | 141.2976
2026 | 2008 | 5 | 22 | 22 | 0
2026 | 2008 | 5 | 22 | 23 | 0
2026 | 2008 | 5 | 22 | 24 | 0
2026 | 2008 | 5 | 23 | 1 | 0
2026 | 2008 | 5 | 23 | 2 | 0
2026 | 2008 | 5 | 23 | 3 | 0
2026 | 2008 | 5 | 23 | 4 | 0
2026 | 2008 | 5 | 23 | 5 | 0
2026 | 2008 | 5 | 23 | 6 | 0
2026 | 2008 | 5 | 23 | 7 | 4.8648
2026 | 2008 | 5 | 23 | 8 | 3491.3622
2026 | 2008 | 5 | 23 | 9 | 14494.9704
2026 | 2008 | 5 | 23 | 10 | 23537.749
2026 | 2008 | 5 | 23 | 11 | 30223.2045
2026 | 2008 | 5 | 23 | 12 | 32785.4883
2026 | 2008 | 5 | 23 | 13 | 33172.1927
2026 | 2008 | 5 | 23 | 14 | 33911.7224
2026 | 2008 | 5 | 23 | 15 | 33449.6975
2026 | 2008 | 5 | 23 | 16 | 32041.7908
2026 | 2008 | 5 | 23 | 17 | 30184.9199
2026 | 2008 | 5 | 23 | 18 | 28472.9818
2026 | 2008 | 5 | 23 | 19 | 20686.6613
2026 | 2008 | 5 | 23 | 20 | 7198.8554
2026 | 2008 | 5 | 23 | 21 | 195.5477
2026 | 2008 | 5 | 23 | 22 | 0
2026 | 2008 | 5 | 23 | 23 | 0
2026 | 2008 | 5 | 23 | 24 | 0
2026 | 2008 | 5 | 24 | 1 | 0
2026 | 2008 | 5 | 24 | 2 | 0
2026 | 2008 | 5 | 24 | 3 | 0
2026 | 2008 | 5 | 24 | 4 | 0
2026 | 2008 | 5 | 24 | 5 | 0
2026 | 2008 | 5 | 24 | 6 | 0
2026 | 2008 | 5 | 24 | 7 | 5.9061
2026 | 2008 | 5 | 24 | 8 | 3215.7805
2026 | 2008 | 5 | 24 | 9 | 12404.5518
2026 | 2008 | 5 | 24 | 10 | 21019.8001
2026 | 2008 | 5 | 24 | 11 | 30885.6142
2026 | 2008 | 5 | 24 | 12 | 32914.0819
2026 | 2008 | 5 | 24 | 13 | 34170.7462
2026 | 2008 | 5 | 24 | 14 | 33677.6088
2026 | 2008 | 5 | 24 | 15 | 33296.8975
2026 | 2008 | 5 | 24 | 16 | 32509.7283
2026 | 2008 | 5 | 24 | 17 | 30532.4957
2026 | 2008 | 5 | 24 | 18 | 27215.5674
2026 | 2008 | 5 | 24 | 19 | 20360.6959
2026 | 2008 | 5 | 24 | 20 | 7632.0196
2026 | 2008 | 5 | 24 | 21 | 311.8844
2026 | 2008 | 5 | 24 | 22 | 0
2026 | 2008 | 5 | 24 | 23 | 0
2026 | 2008 | 5 | 24 | 24 | 0
2026 | 2008 | 5 | 25 | 1 | 0
2026 | 2008 | 5 | 25 | 2 | 0
2026 | 2008 | 5 | 25 | 3 | 0
2026 | 2008 | 5 | 25 | 4 | 0
2026 | 2008 | 5 | 25 | 5 | 0
2026 | 2008 | 5 | 25 | 6 | 0
2026 | 2008 | 5 | 25 | 7 | 7.3296
2026 | 2008 | 5 | 25 | 8 | 2846.7156
2026 | 2008 | 5 | 25 | 9 | 9538.4575
2026 | 2008 | 5 | 25 | 10 | 20354.9254
2026 | 2008 | 5 | 25 | 11 | 27664.1704
2026 | 2008 | 5 | 25 | 12 | 33123.537
2026 | 2008 | 5 | 25 | 13 | 33327.921
2026 | 2008 | 5 | 25 | 14 | 34141.9943
2026 | 2008 | 5 | 25 | 15 | 33409.282
2026 | 2008 | 5 | 25 | 16 | 31653.7661
2026 | 2008 | 5 | 25 | 17 | 30182.663
2026 | 2008 | 5 | 25 | 18 | 27715.5187
2026 | 2008 | 5 | 25 | 19 | 20351.0937
2026 | 2008 | 5 | 25 | 20 | 7499.7308
2026 | 2008 | 5 | 25 | 21 | 381.2831
2026 | 2008 | 5 | 25 | 22 | 0
2026 | 2008 | 5 | 25 | 23 | 0
2026 | 2008 | 5 | 25 | 24 | 0
2026 | 2008 | 5 | 26 | 1 | 0
2026 | 2008 | 5 | 26 | 2 | 0
2026 | 2008 | 5 | 26 | 3 | 0
2026 | 2008 | 5 | 26 | 4 | 0
2026 | 2008 | 5 | 26 | 5 | 0
2026 | 2008 | 5 | 26 | 6 | 0
2026 | 2008 | 5 | 26 | 7 | 12.3992
2026 | 2008 | 5 | 26 | 8 | 2038.7941
2026 | 2008 | 5 | 26 | 9 | 10001.3484
2026 | 2008 | 5 | 26 | 10 | 22632.7067
2026 | 2008 | 5 | 26 | 11 | 29330.2436
2026 | 2008 | 5 | 26 | 12 | 32697.9728
2026 | 2008 | 5 | 26 | 13 | 33488.9865
2026 | 2008 | 5 | 26 | 14 | 33778.1826
2026 | 2008 | 5 | 26 | 15 | 33321.8986
2026 | 2008 | 5 | 26 | 16 | 32029.1676
2026 | 2008 | 5 | 26 | 17 | 30425.2983
2026 | 2008 | 5 | 26 | 18 | 27131.7647
2026 | 2008 | 5 | 26 | 19 | 19556.553
2026 | 2008 | 5 | 26 | 20 | 6762.5171
2026 | 2008 | 5 | 26 | 21 | 410.7736
2026 | 2008 | 5 | 26 | 22 | 0
2026 | 2008 | 5 | 26 | 23 | 0
2026 | 2008 | 5 | 26 | 24 | 0
2026 | 2008 | 5 | 27 | 1 | 0
2026 | 2008 | 5 | 27 | 2 | 0
2026 | 2008 | 5 | 27 | 3 | 0
2026 | 2008 | 5 | 27 | 4 | 0
2026 | 2008 | 5 | 27 | 5 | 0
2026 | 2008 | 5 | 27 | 6 | 0
2026 | 2008 | 5 | 27 | 7 | 5.6416
2026 | 2008 | 5 | 27 | 8 | 2211.6265
2026 | 2008 | 5 | 27 | 9 | 12298.1473
2026 | 2008 | 5 | 27 | 10 | 21995.0901
2026 | 2008 | 5 | 27 | 11 | 30694.1222
2026 | 2008 | 5 | 27 | 12 | 33038.0207
2026 | 2008 | 5 | 27 | 13 | 33248.3147
2026 | 2008 | 5 | 27 | 14 | 33371.3766
2026 | 2008 | 5 | 27 | 15 | 33470.5669
2026 | 2008 | 5 | 27 | 16 | 31940.4891
2026 | 2008 | 5 | 27 | 17 | 30090.0928
2026 | 2008 | 5 | 27 | 18 | 27505.3856
2026 | 2008 | 5 | 27 | 19 | 20467.3183
2026 | 2008 | 5 | 27 | 20 | 7595.0626
2026 | 2008 | 5 | 27 | 21 | 470.5755
2026 | 2008 | 5 | 27 | 22 | 0
2026 | 2008 | 5 | 27 | 23 | 0
2026 | 2008 | 5 | 27 | 24 | 0
2026 | 2008 | 5 | 28 | 1 | 0
2026 | 2008 | 5 | 28 | 2 | 0
2026 | 2008 | 5 | 28 | 3 | 0
2026 | 2008 | 5 | 28 | 4 | 0
2026 | 2008 | 5 | 28 | 5 | 0
2026 | 2008 | 5 | 28 | 6 | 0
2026 | 2008 | 5 | 28 | 7 | 40.5889
2026 | 2008 | 5 | 28 | 8 | 5966.7097
2026 | 2008 | 5 | 28 | 9 | 16089.8454
2026 | 2008 | 5 | 28 | 10 | 22673.3468
2026 | 2008 | 5 | 28 | 11 | 28663.5413
2026 | 2008 | 5 | 28 | 12 | 30507.2861
2026 | 2008 | 5 | 28 | 13 | 30612.7993
2026 | 2008 | 5 | 28 | 14 | 31589.9373
2026 | 2008 | 5 | 28 | 15 | 30494.3353
2026 | 2008 | 5 | 28 | 16 | 28821.6454
2026 | 2008 | 5 | 28 | 17 | 27002.3894
2026 | 2008 | 5 | 28 | 18 | 25305.4723
2026 | 2008 | 5 | 28 | 19 | 20027.8468
2026 | 2008 | 5 | 28 | 20 | 8019.7978
2026 | 2008 | 5 | 28 | 21 | 551.7621
2026 | 2008 | 5 | 28 | 22 | 0
2026 | 2008 | 5 | 28 | 23 | 0
2026 | 2008 | 5 | 28 | 24 | 0
2026 | 2008 | 5 | 29 | 1 | 0
2026 | 2008 | 5 | 29 | 2 | 0
2026 | 2008 | 5 | 29 | 3 | 0
2026 | 2008 | 5 | 29 | 4 | 0
2026 | 2008 | 5 | 29 | 5 | 0
2026 | 2008 | 5 | 29 | 6 | 0
2026 | 2008 | 5 | 29 | 7 | 34.994
2026 | 2008 | 5 | 29 | 8 | 8993.7839
2026 | 2008 | 5 | 29 | 9 | 23070.0819
2026 | 2008 | 5 | 29 | 10 | 29244.7257
2026 | 2008 | 5 | 29 | 11 | 31068.8459
2026 | 2008 | 5 | 29 | 12 | 31343.8331
2026 | 2008 | 5 | 29 | 13 | 31673.3343
2026 | 2008 | 5 | 29 | 14 | 31706.8165
2026 | 2008 | 5 | 29 | 15 | 31706.2886
2026 | 2008 | 5 | 29 | 16 | 30521.6324
2026 | 2008 | 5 | 29 | 17 | 29267.5257
2026 | 2008 | 5 | 29 | 18 | 25901.0451
2026 | 2008 | 5 | 29 | 19 | 20457.7428
2026 | 2008 | 5 | 29 | 20 | 7241.33
2026 | 2008 | 5 | 29 | 21 | 522.0392
2026 | 2008 | 5 | 29 | 22 | 0
2026 | 2008 | 5 | 29 | 23 | 0
2026 | 2008 | 5 | 29 | 24 | 0
2026 | 2008 | 5 | 30 | 1 | 0
2026 | 2008 | 5 | 30 | 2 | 0
2026 | 2008 | 5 | 30 | 3 | 0
2026 | 2008 | 5 | 30 | 4 | 0
2026 | 2008 | 5 | 30 | 5 | 0
2026 | 2008 | 5 | 30 | 6 | 0
2026 | 2008 | 5 | 30 | 7 | 55.0789
2026 | 2008 | 5 | 30 | 8 | 9779.3868
2026 | 2008 | 5 | 30 | 9 | 26163.6636
2026 | 2008 | 5 | 30 | 10 | 32621.3814
2026 | 2008 | 5 | 30 | 11 | 33927.7372
2026 | 2008 | 5 | 30 | 12 | 33366.6648
2026 | 2008 | 5 | 30 | 13 | 33916.6169
2026 | 2008 | 5 | 30 | 14 | 34241.445
2026 | 2008 | 5 | 30 | 15 | 33435.7947
2026 | 2008 | 5 | 30 | 16 | 32482.2788
2026 | 2008 | 5 | 30 | 17 | 30386.6466
2026 | 2008 | 5 | 30 | 18 | 28160.7195
2026 | 2008 | 5 | 30 | 19 | 20500.7373
2026 | 2008 | 5 | 30 | 20 | 8182.7829
2026 | 2008 | 5 | 30 | 21 | 650.3018
2026 | 2008 | 5 | 30 | 22 | 0
2026 | 2008 | 5 | 30 | 23 | 0
2026 | 2008 | 5 | 30 | 24 | 0
2026 | 2008 | 5 | 31 | 1 | 0
2026 | 2008 | 5 | 31 | 2 | 0
2026 | 2008 | 5 | 31 | 3 | 0
2026 | 2008 | 5 | 31 | 4 | 0
2026 | 2008 | 5 | 31 | 5 | 0
2026 | 2008 | 5 | 31 | 6 | 0
2026 | 2008 | 5 | 31 | 7 | 48.7982
2026 | 2008 | 5 | 31 | 8 | 6941.4901
2026 | 2008 | 5 | 31 | 9 | 19504.0897
2026 | 2008 | 5 | 31 | 10 | 25558.2474
2026 | 2008 | 5 | 31 | 11 | 31917.233
2026 | 2008 | 5 | 31 | 12 | 32737.973
2026 | 2008 | 5 | 31 | 13 | 33036.8436
2026 | 2008 | 5 | 31 | 14 | 32955.9316
2026 | 2008 | 5 | 31 | 15 | 32518.1305
2026 | 2008 | 5 | 31 | 16 | 31723.187
2026 | 2008 | 5 | 31 | 17 | 30325.1133
2026 | 2008 | 5 | 31 | 18 | 27891.2096
2026 | 2008 | 5 | 31 | 19 | 21212.3018
2026 | 2008 | 5 | 31 | 20 | 8602.6447
2026 | 2008 | 5 | 31 | 21 | 302.4009
2026 | 2008 | 5 | 31 | 22 | 0
2026 | 2008 | 5 | 31 | 23 | 0
2026 | 2008 | 5 | 31 | 24 | 0
2027 | 2008 | 5 | 1 | 1 | 0
2027 | 2008 | 5 | 1 | 2 | 0
2027 | 2008 | 5 | 1 | 3 | 0
2027 | 2008 | 5 | 1 | 4 | 0
2027 | 2008 | 5 | 1 | 5 | 0
2027 | 2008 | 5 | 1 | 6 | 0
2027 | 2008 | 5 | 1 | 7 | 0.040681
2027 | 2008 | 5 | 1 | 8 | 2836.7458
2027 | 2008 | 5 | 1 | 9 | 18260.6731
2027 | 2008 | 5 | 1 | 10 | 25454.0728
2027 | 2008 | 5 | 1 | 11 | 27050.3248
2027 | 2008 | 5 | 1 | 12 | 29694.2986
2027 | 2008 | 5 | 1 | 13 | 33059.5733
2027 | 2008 | 5 | 1 | 14 | 36121.6264
2027 | 2008 | 5 | 1 | 15 | 37546.1147
2027 | 2008 | 5 | 1 | 16 | 34305.3184
2027 | 2008 | 5 | 1 | 17 | 35431.8949
2027 | 2008 | 5 | 1 | 18 | 33515.3287
2027 | 2008 | 5 | 1 | 19 | 25722.7303
2027 | 2008 | 5 | 1 | 20 | 10342.3512
2027 | 2008 | 5 | 1 | 21 | 0
2027 | 2008 | 5 | 1 | 22 | 0
2027 | 2008 | 5 | 1 | 23 | 0
2027 | 2008 | 5 | 1 | 24 | 0
2027 | 2008 | 5 | 2 | 1 | 0
2027 | 2008 | 5 | 2 | 2 | 0
2027 | 2008 | 5 | 2 | 3 | 0
2027 | 2008 | 5 | 2 | 4 | 0
2027 | 2008 | 5 | 2 | 5 | 0
2027 | 2008 | 5 | 2 | 6 | 0
2027 | 2008 | 5 | 2 | 7 | 0.4491
2027 | 2008 | 5 | 2 | 8 | 5465.2223
2027 | 2008 | 5 | 2 | 9 | 26906.9466
2027 | 2008 | 5 | 2 | 10 | 33427.4138
2027 | 2008 | 5 | 2 | 11 | 37126.3342
2027 | 2008 | 5 | 2 | 12 | 39246.136
2027 | 2008 | 5 | 2 | 13 | 40530.031
2027 | 2008 | 5 | 2 | 14 | 43678.6286
2027 | 2008 | 5 | 2 | 15 | 41084.7395
2027 | 2008 | 5 | 2 | 16 | 40677.4354
2027 | 2008 | 5 | 2 | 17 | 39152.4077
2027 | 2008 | 5 | 2 | 18 | 35980.0455
2027 | 2008 | 5 | 2 | 19 | 27253.0941
2027 | 2008 | 5 | 2 | 20 | 11094.3096
2027 | 2008 | 5 | 2 | 21 | 0
2027 | 2008 | 5 | 2 | 22 | 0
2027 | 2008 | 5 | 2 | 23 | 0
2027 | 2008 | 5 | 2 | 24 | 0
2027 | 2008 | 5 | 3 | 1 | 0
2027 | 2008 | 5 | 3 | 2 | 0
2027 | 2008 | 5 | 3 | 3 | 0
2027 | 2008 | 5 | 3 | 4 | 0
2027 | 2008 | 5 | 3 | 5 | 0
2027 | 2008 | 5 | 3 | 6 | 0
2027 | 2008 | 5 | 3 | 7 | 5.3963
2027 | 2008 | 5 | 3 | 8 | 9341.5697
2027 | 2008 | 5 | 3 | 9 | 32547.2779
2027 | 2008 | 5 | 3 | 10 | 39993.9433
2027 | 2008 | 5 | 3 | 11 | 40312.0046
2027 | 2008 | 5 | 3 | 12 | 43774.4629
2027 | 2008 | 5 | 3 | 13 | 44339.915
2027 | 2008 | 5 | 3 | 14 | 44945.3756
2027 | 2008 | 5 | 3 | 15 | 44168.9951
2027 | 2008 | 5 | 3 | 16 | 42699.8742
2027 | 2008 | 5 | 3 | 17 | 39612.8423
2027 | 2008 | 5 | 3 | 18 | 36431.3671
2027 | 2008 | 5 | 3 | 19 | 27199.8489
2027 | 2008 | 5 | 3 | 20 | 10949.6652
2027 | 2008 | 5 | 3 | 21 | 0
2027 | 2008 | 5 | 3 | 22 | 0
2027 | 2008 | 5 | 3 | 23 | 0
2027 | 2008 | 5 | 3 | 24 | 0
2027 | 2008 | 5 | 4 | 1 | 0
2027 | 2008 | 5 | 4 | 2 | 0
2027 | 2008 | 5 | 4 | 3 | 0
2027 | 2008 | 5 | 4 | 4 | 0
2027 | 2008 | 5 | 4 | 5 | 0
2027 | 2008 | 5 | 4 | 6 | 0
2027 | 2008 | 5 | 4 | 7 | 6.1047
2027 | 2008 | 5 | 4 | 8 | 9091.3608
2027 | 2008 | 5 | 4 | 9 | 31720.539
2027 | 2008 | 5 | 4 | 10 | 40729.8579
2027 | 2008 | 5 | 4 | 11 | 41209.7632
2027 | 2008 | 5 | 4 | 12 | 40652.4501
2027 | 2008 | 5 | 4 | 13 | 39355.4114
2027 | 2008 | 5 | 4 | 14 | 39577.3021
2027 | 2008 | 5 | 4 | 15 | 36738.9756
2027 | 2008 | 5 | 4 | 16 | 35874.4359
2027 | 2008 | 5 | 4 | 17 | 30626.7013
2027 | 2008 | 5 | 4 | 18 | 26648.3544
2027 | 2008 | 5 | 4 | 19 | 20506.3782
2027 | 2008 | 5 | 4 | 20 | 8579.5431
2027 | 2008 | 5 | 4 | 21 | 0
2027 | 2008 | 5 | 4 | 22 | 0
2027 | 2008 | 5 | 4 | 23 | 0
2027 | 2008 | 5 | 4 | 24 | 0
2027 | 2008 | 5 | 5 | 1 | 0
2027 | 2008 | 5 | 5 | 2 | 0
2027 | 2008 | 5 | 5 | 3 | 0
2027 | 2008 | 5 | 5 | 4 | 0
2027 | 2008 | 5 | 5 | 5 | 0
2027 | 2008 | 5 | 5 | 6 | 0
2027 | 2008 | 5 | 5 | 7 | 4.6217
2027 | 2008 | 5 | 5 | 8 | 1316.2469
2027 | 2008 | 5 | 5 | 9 | 9799.1651
2027 | 2008 | 5 | 5 | 10 | 16762.9586
2027 | 2008 | 5 | 5 | 11 | 20296.2993
2027 | 2008 | 5 | 5 | 12 | 23459.3133
2027 | 2008 | 5 | 5 | 13 | 28286.7717
2027 | 2008 | 5 | 5 | 14 | 28601.4587
2027 | 2008 | 5 | 5 | 15 | 30350.4447
2027 | 2008 | 5 | 5 | 16 | 28694.5724
2027 | 2008 | 5 | 5 | 17 | 27197.3772
2027 | 2008 | 5 | 5 | 18 | 26865.9606
2027 | 2008 | 5 | 5 | 19 | 23205.5908
2027 | 2008 | 5 | 5 | 20 | 8335.7718
2027 | 2008 | 5 | 5 | 21 | 0
2027 | 2008 | 5 | 5 | 22 | 0
2027 | 2008 | 5 | 5 | 23 | 0
2027 | 2008 | 5 | 5 | 24 | 0
2027 | 2008 | 5 | 6 | 1 | 0
2027 | 2008 | 5 | 6 | 2 | 0
2027 | 2008 | 5 | 6 | 3 | 0
2027 | 2008 | 5 | 6 | 4 | 0
2027 | 2008 | 5 | 6 | 5 | 0
2027 | 2008 | 5 | 6 | 6 | 0
2027 | 2008 | 5 | 6 | 7 | 0.76052
2027 | 2008 | 5 | 6 | 8 | 765.554
2027 | 2008 | 5 | 6 | 9 | 7299.8225
2027 | 2008 | 5 | 6 | 10 | 16498.1349
2027 | 2008 | 5 | 6 | 11 | 23224.0834
2027 | 2008 | 5 | 6 | 12 | 28667.7961
2027 | 2008 | 5 | 6 | 13 | 33948.8461
2027 | 2008 | 5 | 6 | 14 | 36190.7713
2027 | 2008 | 5 | 6 | 15 | 35978.7108
2027 | 2008 | 5 | 6 | 16 | 34909.1665
2027 | 2008 | 5 | 6 | 17 | 34638.0056
2027 | 2008 | 5 | 6 | 18 | 33188.1521
2027 | 2008 | 5 | 6 | 19 | 23520.6751
2027 | 2008 | 5 | 6 | 20 | 9481.5789
2027 | 2008 | 5 | 6 | 21 | 0
2027 | 2008 | 5 | 6 | 22 | 0
2027 | 2008 | 5 | 6 | 23 | 0
2027 | 2008 | 5 | 6 | 24 | 0
2027 | 2008 | 5 | 7 | 1 | 0
2027 | 2008 | 5 | 7 | 2 | 0
2027 | 2008 | 5 | 7 | 3 | 0
2027 | 2008 | 5 | 7 | 4 | 0
2027 | 2008 | 5 | 7 | 5 | 0
2027 | 2008 | 5 | 7 | 6 | 0
2027 | 2008 | 5 | 7 | 7 | 0
2027 | 2008 | 5 | 7 | 8 | 2542.5175
2027 | 2008 | 5 | 7 | 9 | 14589.6248
2027 | 2008 | 5 | 7 | 10 | 24351.4923
2027 | 2008 | 5 | 7 | 11 | 29072.0952
2027 | 2008 | 5 | 7 | 12 | 30794.8309
2027 | 2008 | 5 | 7 | 13 | 32482.9389
2027 | 2008 | 5 | 7 | 14 | 38881.8325
2027 | 2008 | 5 | 7 | 15 | 38306.8731
2027 | 2008 | 5 | 7 | 16 | 37214.4308
2027 | 2008 | 5 | 7 | 17 | 36087.8226
2027 | 2008 | 5 | 7 | 18 | 35305.592
2027 | 2008 | 5 | 7 | 19 | 26774.1877
2027 | 2008 | 5 | 7 | 20 | 9740.089
2027 | 2008 | 5 | 7 | 21 | 0
2027 | 2008 | 5 | 7 | 22 | 0
2027 | 2008 | 5 | 7 | 23 | 0
2027 | 2008 | 5 | 7 | 24 | 0
2027 | 2008 | 5 | 8 | 1 | 0
2027 | 2008 | 5 | 8 | 2 | 0
2027 | 2008 | 5 | 8 | 3 | 0
2027 | 2008 | 5 | 8 | 4 | 0
2027 | 2008 | 5 | 8 | 5 | 0
2027 | 2008 | 5 | 8 | 6 | 0
2027 | 2008 | 5 | 8 | 7 | 11.6985
2027 | 2008 | 5 | 8 | 8 | 9565.893
2027 | 2008 | 5 | 8 | 9 | 30260.5453
2027 | 2008 | 5 | 8 | 10 | 37930.8805
2027 | 2008 | 5 | 8 | 11 | 42031.5117
2027 | 2008 | 5 | 8 | 12 | 44348.8794
2027 | 2008 | 5 | 8 | 13 | 43922.9956
2027 | 2008 | 5 | 8 | 14 | 44271.304
2027 | 2008 | 5 | 8 | 15 | 43114.9142
2027 | 2008 | 5 | 8 | 16 | 40476.625
2027 | 2008 | 5 | 8 | 17 | 38510.9489
2027 | 2008 | 5 | 8 | 18 | 34972.6798
2027 | 2008 | 5 | 8 | 19 | 25525.1774
2027 | 2008 | 5 | 8 | 20 | 10803.3977
2027 | 2008 | 5 | 8 | 21 | 0
2027 | 2008 | 5 | 8 | 22 | 0
2027 | 2008 | 5 | 8 | 23 | 0
2027 | 2008 | 5 | 8 | 24 | 0
2027 | 2008 | 5 | 9 | 1 | 0
2027 | 2008 | 5 | 9 | 2 | 0
2027 | 2008 | 5 | 9 | 3 | 0
2027 | 2008 | 5 | 9 | 4 | 0
2027 | 2008 | 5 | 9 | 5 | 0
2027 | 2008 | 5 | 9 | 6 | 0
2027 | 2008 | 5 | 9 | 7 | 11.6492
2027 | 2008 | 5 | 9 | 8 | 8039.6596
2027 | 2008 | 5 | 9 | 9 | 27107.4985
2027 | 2008 | 5 | 9 | 10 | 34353.0972
2027 | 2008 | 5 | 9 | 11 | 39534.4772
2027 | 2008 | 5 | 9 | 12 | 41149.5671
2027 | 2008 | 5 | 9 | 13 | 43842.6565
2027 | 2008 | 5 | 9 | 14 | 43768.8035
2027 | 2008 | 5 | 9 | 15 | 42285.0655
2027 | 2008 | 5 | 9 | 16 | 40655.4782
2027 | 2008 | 5 | 9 | 17 | 38888.6362
2027 | 2008 | 5 | 9 | 18 | 34432.1568
2027 | 2008 | 5 | 9 | 19 | 24689.4173
2027 | 2008 | 5 | 9 | 20 | 9877.2509
2027 | 2008 | 5 | 9 | 21 | 0
2027 | 2008 | 5 | 9 | 22 | 0
2027 | 2008 | 5 | 9 | 23 | 0
2027 | 2008 | 5 | 9 | 24 | 0
2027 | 2008 | 5 | 10 | 1 | 0
2027 | 2008 | 5 | 10 | 2 | 0
2027 | 2008 | 5 | 10 | 3 | 0
2027 | 2008 | 5 | 10 | 4 | 0
2027 | 2008 | 5 | 10 | 5 | 0
2027 | 2008 | 5 | 10 | 6 | 0
2027 | 2008 | 5 | 10 | 7 | 0.7841
2027 | 2008 | 5 | 10 | 8 | 4654.7236
2027 | 2008 | 5 | 10 | 9 | 20843.48
2027 | 2008 | 5 | 10 | 10 | 28626.1726
2027 | 2008 | 5 | 10 | 11 | 33670.2227
2027 | 2008 | 5 | 10 | 12 | 40495.6685
2027 | 2008 | 5 | 10 | 13 | 43470.2374
2027 | 2008 | 5 | 10 | 14 | 43854.6353
2027 | 2008 | 5 | 10 | 15 | 41471.2997
2027 | 2008 | 5 | 10 | 16 | 39885.4879
2027 | 2008 | 5 | 10 | 17 | 34671.599
2027 | 2008 | 5 | 10 | 18 | 31426.9383
2027 | 2008 | 5 | 10 | 19 | 24639.4098
2027 | 2008 | 5 | 10 | 20 | 9164.9164
2027 | 2008 | 5 | 10 | 21 | 0
2027 | 2008 | 5 | 10 | 22 | 0
2027 | 2008 | 5 | 10 | 23 | 0
2027 | 2008 | 5 | 10 | 24 | 0
2027 | 2008 | 5 | 11 | 1 | 0
2027 | 2008 | 5 | 11 | 2 | 0
2027 | 2008 | 5 | 11 | 3 | 0
2027 | 2008 | 5 | 11 | 4 | 0
2027 | 2008 | 5 | 11 | 5 | 0
2027 | 2008 | 5 | 11 | 6 | 0
2027 | 2008 | 5 | 11 | 7 | 21.0823
2027 | 2008 | 5 | 11 | 8 | 12001.3812
2027 | 2008 | 5 | 11 | 9 | 34540.9815
2027 | 2008 | 5 | 11 | 10 | 40830.6509
2027 | 2008 | 5 | 11 | 11 | 42097.0338
2027 | 2008 | 5 | 11 | 12 | 43466.0489
2027 | 2008 | 5 | 11 | 13 | 43873.7499
2027 | 2008 | 5 | 11 | 14 | 44411.711
2027 | 2008 | 5 | 11 | 15 | 42452.1926
2027 | 2008 | 5 | 11 | 16 | 40460.8671
2027 | 2008 | 5 | 11 | 17 | 37653.6798
2027 | 2008 | 5 | 11 | 18 | 33232.2674
2027 | 2008 | 5 | 11 | 19 | 25818.1307
2027 | 2008 | 5 | 11 | 20 | 10027.2454
2027 | 2008 | 5 | 11 | 21 | 0
2027 | 2008 | 5 | 11 | 22 | 0
2027 | 2008 | 5 | 11 | 23 | 0
2027 | 2008 | 5 | 11 | 24 | 0
2027 | 2008 | 5 | 12 | 1 | 0
2027 | 2008 | 5 | 12 | 2 | 0
2027 | 2008 | 5 | 12 | 3 | 0
2027 | 2008 | 5 | 12 | 4 | 0
2027 | 2008 | 5 | 12 | 5 | 0
2027 | 2008 | 5 | 12 | 6 | 0
2027 | 2008 | 5 | 12 | 7 | 22.4307
2027 | 2008 | 5 | 12 | 8 | 10941.3334
2027 | 2008 | 5 | 12 | 9 | 31611.1786
2027 | 2008 | 5 | 12 | 10 | 38902.3675
2027 | 2008 | 5 | 12 | 11 | 40341.8317
2027 | 2008 | 5 | 12 | 12 | 42235.8789
2027 | 2008 | 5 | 12 | 13 | 42094.8762
2027 | 2008 | 5 | 12 | 14 | 43918.3181
2027 | 2008 | 5 | 12 | 15 | 42689.6565
2027 | 2008 | 5 | 12 | 16 | 40650.9888
2027 | 2008 | 5 | 12 | 17 | 37770.7319
2027 | 2008 | 5 | 12 | 18 | 31841.047
2027 | 2008 | 5 | 12 | 19 | 24983.7474
2027 | 2008 | 5 | 12 | 20 | 8353.0641
2027 | 2008 | 5 | 12 | 21 | 0
2027 | 2008 | 5 | 12 | 22 | 0
2027 | 2008 | 5 | 12 | 23 | 0
2027 | 2008 | 5 | 12 | 24 | 0
2027 | 2008 | 5 | 13 | 1 | 0
2027 | 2008 | 5 | 13 | 2 | 0
2027 | 2008 | 5 | 13 | 3 | 0
2027 | 2008 | 5 | 13 | 4 | 0
2027 | 2008 | 5 | 13 | 5 | 0
2027 | 2008 | 5 | 13 | 6 | 0
2027 | 2008 | 5 | 13 | 7 | 0.19935
2027 | 2008 | 5 | 13 | 8 | 2087.0777
2027 | 2008 | 5 | 13 | 9 | 11479.6674
2027 | 2008 | 5 | 13 | 10 | 18569.9742
2027 | 2008 | 5 | 13 | 11 | 25392.5248
2027 | 2008 | 5 | 13 | 12 | 30885.3662
2027 | 2008 | 5 | 13 | 13 | 32811.684
2027 | 2008 | 5 | 13 | 14 | 35095.45
2027 | 2008 | 5 | 13 | 15 | 36719.9841
2027 | 2008 | 5 | 13 | 16 | 35282.161
2027 | 2008 | 5 | 13 | 17 | 31336.8926
2027 | 2008 | 5 | 13 | 18 | 30506.6824
2027 | 2008 | 5 | 13 | 19 | 23829.5237
2027 | 2008 | 5 | 13 | 20 | 8758.5945
2027 | 2008 | 5 | 13 | 21 | 0
2027 | 2008 | 5 | 13 | 22 | 0
2027 | 2008 | 5 | 13 | 23 | 0
2027 | 2008 | 5 | 13 | 24 | 0
2027 | 2008 | 5 | 14 | 1 | 0
2027 | 2008 | 5 | 14 | 2 | 0
2027 | 2008 | 5 | 14 | 3 | 0
2027 | 2008 | 5 | 14 | 4 | 0
2027 | 2008 | 5 | 14 | 5 | 0
2027 | 2008 | 5 | 14 | 6 | 0
2027 | 2008 | 5 | 14 | 7 | 1.4897
2027 | 2008 | 5 | 14 | 8 | 3238.3273
2027 | 2008 | 5 | 14 | 9 | 13499.1532
2027 | 2008 | 5 | 14 | 10 | 20396.606
2027 | 2008 | 5 | 14 | 11 | 23760.6926
2027 | 2008 | 5 | 14 | 12 | 29964.7035
2027 | 2008 | 5 | 14 | 13 | 33243.1225
2027 | 2008 | 5 | 14 | 14 | 34234.4056
2027 | 2008 | 5 | 14 | 15 | 32061.9666
2027 | 2008 | 5 | 14 | 16 | 30804.3581
2027 | 2008 | 5 | 14 | 17 | 27691.5851
2027 | 2008 | 5 | 14 | 18 | 24813.4021
2027 | 2008 | 5 | 14 | 19 | 20831.5013
2027 | 2008 | 5 | 14 | 20 | 8646.8303
2027 | 2008 | 5 | 14 | 21 | 8.797
2027 | 2008 | 5 | 14 | 22 | 0
2027 | 2008 | 5 | 14 | 23 | 0
2027 | 2008 | 5 | 14 | 24 | 0
2027 | 2008 | 5 | 15 | 1 | 0
2027 | 2008 | 5 | 15 | 2 | 0
2027 | 2008 | 5 | 15 | 3 | 0
2027 | 2008 | 5 | 15 | 4 | 0
2027 | 2008 | 5 | 15 | 5 | 0
2027 | 2008 | 5 | 15 | 6 | 0
2027 | 2008 | 5 | 15 | 7 | 0.18588
2027 | 2008 | 5 | 15 | 8 | 3096.436
2027 | 2008 | 5 | 15 | 9 | 17918.4653
2027 | 2008 | 5 | 15 | 10 | 32039.8652
2027 | 2008 | 5 | 15 | 11 | 37104.8877
2027 | 2008 | 5 | 15 | 12 | 39596.4613
2027 | 2008 | 5 | 15 | 13 | 40187.2497
2027 | 2008 | 5 | 15 | 14 | 39346.1727
2027 | 2008 | 5 | 15 | 15 | 37377.5373
2027 | 2008 | 5 | 15 | 16 | 34438.4418
2027 | 2008 | 5 | 15 | 17 | 30839.7226
2027 | 2008 | 5 | 15 | 18 | 28875.3367
2027 | 2008 | 5 | 15 | 19 | 22277.8417
2027 | 2008 | 5 | 15 | 20 | 8242.1982
2027 | 2008 | 5 | 15 | 21 | 19.971
2027 | 2008 | 5 | 15 | 22 | 0
2027 | 2008 | 5 | 15 | 23 | 0
2027 | 2008 | 5 | 15 | 24 | 0
2027 | 2008 | 5 | 16 | 1 | 0
2027 | 2008 | 5 | 16 | 2 | 0
2027 | 2008 | 5 | 16 | 3 | 0
2027 | 2008 | 5 | 16 | 4 | 0
2027 | 2008 | 5 | 16 | 5 | 0
2027 | 2008 | 5 | 16 | 6 | 0
2027 | 2008 | 5 | 16 | 7 | 19.2342
2027 | 2008 | 5 | 16 | 8 | 6578.5152
2027 | 2008 | 5 | 16 | 9 | 21634.6909
2027 | 2008 | 5 | 16 | 10 | 31840.2252
2027 | 2008 | 5 | 16 | 11 | 36110.8249
2027 | 2008 | 5 | 16 | 12 | 39917.0496
2027 | 2008 | 5 | 16 | 13 | 42248.0954
2027 | 2008 | 5 | 16 | 14 | 43805.1186
2027 | 2008 | 5 | 16 | 15 | 42648.6418
2027 | 2008 | 5 | 16 | 16 | 41099.7828
2027 | 2008 | 5 | 16 | 17 | 37255.1902
2027 | 2008 | 5 | 16 | 18 | 35173.712
2027 | 2008 | 5 | 16 | 19 | 25756.0165
2027 | 2008 | 5 | 16 | 20 | 7880.5109
2027 | 2008 | 5 | 16 | 21 | 20.0071
2027 | 2008 | 5 | 16 | 22 | 0
2027 | 2008 | 5 | 16 | 23 | 0
2027 | 2008 | 5 | 16 | 24 | 0
2027 | 2008 | 5 | 17 | 1 | 0
2027 | 2008 | 5 | 17 | 2 | 0
2027 | 2008 | 5 | 17 | 3 | 0
2027 | 2008 | 5 | 17 | 4 | 0
2027 | 2008 | 5 | 17 | 5 | 0
2027 | 2008 | 5 | 17 | 6 | 0
2027 | 2008 | 5 | 17 | 7 | 20.8243
2027 | 2008 | 5 | 17 | 8 | 8418.3156
2027 | 2008 | 5 | 17 | 9 | 29101.5531
2027 | 2008 | 5 | 17 | 10 | 38666.9909
2027 | 2008 | 5 | 17 | 11 | 39617.3392
2027 | 2008 | 5 | 17 | 12 | 38991.4674
2027 | 2008 | 5 | 17 | 13 | 37679.5394
2027 | 2008 | 5 | 17 | 14 | 37297.0916
2027 | 2008 | 5 | 17 | 15 | 35518.2763
2027 | 2008 | 5 | 17 | 16 | 32835.8723
2027 | 2008 | 5 | 17 | 17 | 28683.8256
2027 | 2008 | 5 | 17 | 18 | 28659.2317
2027 | 2008 | 5 | 17 | 19 | 23916.8858
2027 | 2008 | 5 | 17 | 20 | 9247.7695
2027 | 2008 | 5 | 17 | 21 | 32.9858
2027 | 2008 | 5 | 17 | 22 | 0
2027 | 2008 | 5 | 17 | 23 | 0
2027 | 2008 | 5 | 17 | 24 | 0
2027 | 2008 | 5 | 18 | 1 | 0
2027 | 2008 | 5 | 18 | 2 | 0
2027 | 2008 | 5 | 18 | 3 | 0
2027 | 2008 | 5 | 18 | 4 | 0
2027 | 2008 | 5 | 18 | 5 | 0
2027 | 2008 | 5 | 18 | 6 | 0
2027 | 2008 | 5 | 18 | 7 | 43.7616
2027 | 2008 | 5 | 18 | 8 | 14728.9567
2027 | 2008 | 5 | 18 | 9 | 39828.8353
2027 | 2008 | 5 | 18 | 10 | 45743.9833
2027 | 2008 | 5 | 18 | 11 | 45610.146
2027 | 2008 | 5 | 18 | 12 | 44470.758
2027 | 2008 | 5 | 18 | 13 | 44995.4256
2027 | 2008 | 5 | 18 | 14 | 45426.6609
2027 | 2008 | 5 | 18 | 15 | 43990.575
2027 | 2008 | 5 | 18 | 16 | 42703.907
2027 | 2008 | 5 | 18 | 17 | 40188.1995
2027 | 2008 | 5 | 18 | 18 | 37756.8441
2027 | 2008 | 5 | 18 | 19 | 26803.9198
2027 | 2008 | 5 | 18 | 20 | 9865.958
2027 | 2008 | 5 | 18 | 21 | 43.7266
2027 | 2008 | 5 | 18 | 22 | 0
2027 | 2008 | 5 | 18 | 23 | 0
2027 | 2008 | 5 | 18 | 24 | 0
2027 | 2008 | 5 | 19 | 1 | 0
2027 | 2008 | 5 | 19 | 2 | 0
2027 | 2008 | 5 | 19 | 3 | 0
2027 | 2008 | 5 | 19 | 4 | 0
2027 | 2008 | 5 | 19 | 5 | 0
2027 | 2008 | 5 | 19 | 6 | 0
2027 | 2008 | 5 | 19 | 7 | 34.175
2027 | 2008 | 5 | 19 | 8 | 14695.7786
2027 | 2008 | 5 | 19 | 9 | 40706.4258
2027 | 2008 | 5 | 19 | 10 | 46519.043
2027 | 2008 | 5 | 19 | 11 | 45119.2095
2027 | 2008 | 5 | 19 | 12 | 44837.5256
2027 | 2008 | 5 | 19 | 13 | 45264.0503
2027 | 2008 | 5 | 19 | 14 | 44820.8347
2027 | 2008 | 5 | 19 | 15 | 43573.439
2027 | 2008 | 5 | 19 | 16 | 42534.9654
2027 | 2008 | 5 | 19 | 17 | 40015.5228
2027 | 2008 | 5 | 19 | 18 | 36866.474
2027 | 2008 | 5 | 19 | 19 | 27271.4761
2027 | 2008 | 5 | 19 | 20 | 9899.8287
2027 | 2008 | 5 | 19 | 21 | 114.6037
2027 | 2008 | 5 | 19 | 22 | 0
2027 | 2008 | 5 | 19 | 23 | 0
2027 | 2008 | 5 | 19 | 24 | 0
2027 | 2008 | 5 | 20 | 1 | 0
2027 | 2008 | 5 | 20 | 2 | 0
2027 | 2008 | 5 | 20 | 3 | 0
2027 | 2008 | 5 | 20 | 4 | 0
2027 | 2008 | 5 | 20 | 5 | 0
2027 | 2008 | 5 | 20 | 6 | 0
2027 | 2008 | 5 | 20 | 7 | 38.4267
2027 | 2008 | 5 | 20 | 8 | 13020.9199
2027 | 2008 | 5 | 20 | 9 | 33497.7392
2027 | 2008 | 5 | 20 | 10 | 40552.9727
2027 | 2008 | 5 | 20 | 11 | 42428.1871
2027 | 2008 | 5 | 20 | 12 | 43485.7191
2027 | 2008 | 5 | 20 | 13 | 44181.8732
2027 | 2008 | 5 | 20 | 14 | 44566.4994
2027 | 2008 | 5 | 20 | 15 | 42679.2714
2027 | 2008 | 5 | 20 | 16 | 41189.3207
2027 | 2008 | 5 | 20 | 17 | 39918.7035
2027 | 2008 | 5 | 20 | 18 | 37508.9839
2027 | 2008 | 5 | 20 | 19 | 26485.1369
2027 | 2008 | 5 | 20 | 20 | 9423.9717
2027 | 2008 | 5 | 20 | 21 | 124.066
2027 | 2008 | 5 | 20 | 22 | 0
2027 | 2008 | 5 | 20 | 23 | 0
2027 | 2008 | 5 | 20 | 24 | 0
2027 | 2008 | 5 | 21 | 1 | 0
2027 | 2008 | 5 | 21 | 2 | 0
2027 | 2008 | 5 | 21 | 3 | 0
2027 | 2008 | 5 | 21 | 4 | 0
2027 | 2008 | 5 | 21 | 5 | 0
2027 | 2008 | 5 | 21 | 6 | 0
2027 | 2008 | 5 | 21 | 7 | 30.238
2027 | 2008 | 5 | 21 | 8 | 5772.4603
2027 | 2008 | 5 | 21 | 9 | 20766.022
2027 | 2008 | 5 | 21 | 10 | 28855.2687
2027 | 2008 | 5 | 21 | 11 | 33985.2903
2027 | 2008 | 5 | 21 | 12 | 42899.0499
2027 | 2008 | 5 | 21 | 13 | 44408.1759
2027 | 2008 | 5 | 21 | 14 | 45204.4529
2027 | 2008 | 5 | 21 | 15 | 43310.8008
2027 | 2008 | 5 | 21 | 16 | 42311.7129
2027 | 2008 | 5 | 21 | 17 | 39608.4452
2027 | 2008 | 5 | 21 | 18 | 35987.9854
2027 | 2008 | 5 | 21 | 19 | 26398.1367
2027 | 2008 | 5 | 21 | 20 | 9523.6365
2027 | 2008 | 5 | 21 | 21 | 112.748
2027 | 2008 | 5 | 21 | 22 | 0
2027 | 2008 | 5 | 21 | 23 | 0
2027 | 2008 | 5 | 21 | 24 | 0
2027 | 2008 | 5 | 22 | 1 | 0
2027 | 2008 | 5 | 22 | 2 | 0
2027 | 2008 | 5 | 22 | 3 | 0
2027 | 2008 | 5 | 22 | 4 | 0
2027 | 2008 | 5 | 22 | 5 | 0
2027 | 2008 | 5 | 22 | 6 | 0
2027 | 2008 | 5 | 22 | 7 | 3.0327
2027 | 2008 | 5 | 22 | 8 | 3305.7428
2027 | 2008 | 5 | 22 | 9 | 16512.5475
2027 | 2008 | 5 | 22 | 10 | 30154.3735
2027 | 2008 | 5 | 22 | 11 | 36976.4786
2027 | 2008 | 5 | 22 | 12 | 41923.5929
2027 | 2008 | 5 | 22 | 13 | 44011.5584
2027 | 2008 | 5 | 22 | 14 | 44400.1891
2027 | 2008 | 5 | 22 | 15 | 42763.1264
2027 | 2008 | 5 | 22 | 16 | 39831.7643
2027 | 2008 | 5 | 22 | 17 | 36636.0424
2027 | 2008 | 5 | 22 | 18 | 33513.2116
2027 | 2008 | 5 | 22 | 19 | 27073.6066
2027 | 2008 | 5 | 22 | 20 | 10058.2209
2027 | 2008 | 5 | 22 | 21 | 226.0529
2027 | 2008 | 5 | 22 | 22 | 0
2027 | 2008 | 5 | 22 | 23 | 0
2027 | 2008 | 5 | 22 | 24 | 0
2027 | 2008 | 5 | 23 | 1 | 0
2027 | 2008 | 5 | 23 | 2 | 0
2027 | 2008 | 5 | 23 | 3 | 0
2027 | 2008 | 5 | 23 | 4 | 0
2027 | 2008 | 5 | 23 | 5 | 0
2027 | 2008 | 5 | 23 | 6 | 0
2027 | 2008 | 5 | 23 | 7 | 4.8648
2027 | 2008 | 5 | 23 | 8 | 4643.9182
2027 | 2008 | 5 | 23 | 9 | 19518.7144
2027 | 2008 | 5 | 23 | 10 | 31586.7273
2027 | 2008 | 5 | 23 | 11 | 40012.4166
2027 | 2008 | 5 | 23 | 12 | 43294.869
2027 | 2008 | 5 | 23 | 13 | 43725.4778
2027 | 2008 | 5 | 23 | 14 | 44750.3895
2027 | 2008 | 5 | 23 | 15 | 44000.8444
2027 | 2008 | 5 | 23 | 16 | 41930.4395
2027 | 2008 | 5 | 23 | 17 | 39714.4487
2027 | 2008 | 5 | 23 | 18 | 37245.5933
2027 | 2008 | 5 | 23 | 19 | 27251.3928
2027 | 2008 | 5 | 23 | 20 | 9566.825
2027 | 2008 | 5 | 23 | 21 | 289.5678
2027 | 2008 | 5 | 23 | 22 | 0
2027 | 2008 | 5 | 23 | 23 | 0
2027 | 2008 | 5 | 23 | 24 | 0
2027 | 2008 | 5 | 24 | 1 | 0
2027 | 2008 | 5 | 24 | 2 | 0
2027 | 2008 | 5 | 24 | 3 | 0
2027 | 2008 | 5 | 24 | 4 | 0
2027 | 2008 | 5 | 24 | 5 | 0
2027 | 2008 | 5 | 24 | 6 | 0
2027 | 2008 | 5 | 24 | 7 | 5.9061
2027 | 2008 | 5 | 24 | 8 | 4204.6286
2027 | 2008 | 5 | 24 | 9 | 16642.3453
2027 | 2008 | 5 | 24 | 10 | 27201.9999
2027 | 2008 | 5 | 24 | 11 | 40774.3343
2027 | 2008 | 5 | 24 | 12 | 43566.7477
2027 | 2008 | 5 | 24 | 13 | 44891.995
2027 | 2008 | 5 | 24 | 14 | 44353.0698
2027 | 2008 | 5 | 24 | 15 | 43715.364
2027 | 2008 | 5 | 24 | 16 | 42510.1606
2027 | 2008 | 5 | 24 | 17 | 40106.3792
2027 | 2008 | 5 | 24 | 18 | 35566.2562
2027 | 2008 | 5 | 24 | 19 | 26714.7069
2027 | 2008 | 5 | 24 | 20 | 10089.6723
2027 | 2008 | 5 | 24 | 21 | 406.1327
2027 | 2008 | 5 | 24 | 22 | 0
2027 | 2008 | 5 | 24 | 23 | 0
2027 | 2008 | 5 | 24 | 24 | 0
2027 | 2008 | 5 | 25 | 1 | 0
2027 | 2008 | 5 | 25 | 2 | 0
2027 | 2008 | 5 | 25 | 3 | 0
2027 | 2008 | 5 | 25 | 4 | 0
2027 | 2008 | 5 | 25 | 5 | 0
2027 | 2008 | 5 | 25 | 6 | 0
2027 | 2008 | 5 | 25 | 7 | 7.3296
2027 | 2008 | 5 | 25 | 8 | 3476.784
2027 | 2008 | 5 | 25 | 9 | 11770.8977
2027 | 2008 | 5 | 25 | 10 | 26815.2783
2027 | 2008 | 5 | 25 | 11 | 37183.0208
2027 | 2008 | 5 | 25 | 12 | 43649.4165
2027 | 2008 | 5 | 25 | 13 | 43995.8631
2027 | 2008 | 5 | 25 | 14 | 44927.4857
2027 | 2008 | 5 | 25 | 15 | 43949.378
2027 | 2008 | 5 | 25 | 16 | 41623.6304
2027 | 2008 | 5 | 25 | 17 | 39903.0196
2027 | 2008 | 5 | 25 | 18 | 36384.5566
2027 | 2008 | 5 | 25 | 19 | 26818.2754
2027 | 2008 | 5 | 25 | 20 | 10026.2823
2027 | 2008 | 5 | 25 | 21 | 530.3762
2027 | 2008 | 5 | 25 | 22 | 0
2027 | 2008 | 5 | 25 | 23 | 0
2027 | 2008 | 5 | 25 | 24 | 0
2027 | 2008 | 5 | 26 | 1 | 0
2027 | 2008 | 5 | 26 | 2 | 0
2027 | 2008 | 5 | 26 | 3 | 0
2027 | 2008 | 5 | 26 | 4 | 0
2027 | 2008 | 5 | 26 | 5 | 0
2027 | 2008 | 5 | 26 | 6 | 0
2027 | 2008 | 5 | 26 | 7 | 12.3992
2027 | 2008 | 5 | 26 | 8 | 2832.1268
2027 | 2008 | 5 | 26 | 9 | 13192.9242
2027 | 2008 | 5 | 26 | 10 | 31379.4166
2027 | 2008 | 5 | 26 | 11 | 39332.0382
2027 | 2008 | 5 | 26 | 12 | 42956.1912
2027 | 2008 | 5 | 26 | 13 | 44376.7821
2027 | 2008 | 5 | 26 | 14 | 44259.1674
2027 | 2008 | 5 | 26 | 15 | 43803.3205
2027 | 2008 | 5 | 26 | 16 | 42025.1819
2027 | 2008 | 5 | 26 | 17 | 40054.0027
2027 | 2008 | 5 | 26 | 18 | 35627.2883
2027 | 2008 | 5 | 26 | 19 | 25838.4573
2027 | 2008 | 5 | 26 | 20 | 9011.0183
2027 | 2008 | 5 | 26 | 21 | 559.8964
2027 | 2008 | 5 | 26 | 22 | 0
2027 | 2008 | 5 | 26 | 23 | 0
2027 | 2008 | 5 | 26 | 24 | 0
2027 | 2008 | 5 | 27 | 1 | 0
2027 | 2008 | 5 | 27 | 2 | 0
2027 | 2008 | 5 | 27 | 3 | 0
2027 | 2008 | 5 | 27 | 4 | 0
2027 | 2008 | 5 | 27 | 5 | 0
2027 | 2008 | 5 | 27 | 6 | 0
2027 | 2008 | 5 | 27 | 7 | 5.6416
2027 | 2008 | 5 | 27 | 8 | 3155.6506
2027 | 2008 | 5 | 27 | 9 | 16615.831
2027 | 2008 | 5 | 27 | 10 | 28839.7645
2027 | 2008 | 5 | 27 | 11 | 40275.1079
2027 | 2008 | 5 | 27 | 12 | 43431.8078
2027 | 2008 | 5 | 27 | 13 | 43957.2989
2027 | 2008 | 5 | 27 | 14 | 43874.4023
2027 | 2008 | 5 | 27 | 15 | 44037.0633
2027 | 2008 | 5 | 27 | 16 | 41893.5413
2027 | 2008 | 5 | 27 | 17 | 39243.6489
2027 | 2008 | 5 | 27 | 18 | 35817.9253
2027 | 2008 | 5 | 27 | 19 | 26777.3067
2027 | 2008 | 5 | 27 | 20 | 9981.0336
2027 | 2008 | 5 | 27 | 21 | 611.6354
2027 | 2008 | 5 | 27 | 22 | 0
2027 | 2008 | 5 | 27 | 23 | 0
2027 | 2008 | 5 | 27 | 24 | 0
2027 | 2008 | 5 | 28 | 1 | 0
2027 | 2008 | 5 | 28 | 2 | 0
2027 | 2008 | 5 | 28 | 3 | 0
2027 | 2008 | 5 | 28 | 4 | 0
2027 | 2008 | 5 | 28 | 5 | 0
2027 | 2008 | 5 | 28 | 6 | 0
2027 | 2008 | 5 | 28 | 7 | 40.5889
2027 | 2008 | 5 | 28 | 8 | 7443.444
2027 | 2008 | 5 | 28 | 9 | 20487.8353
2027 | 2008 | 5 | 28 | 10 | 29624.3599
2027 | 2008 | 5 | 28 | 11 | 36666.2392
2027 | 2008 | 5 | 28 | 12 | 39782.4703
2027 | 2008 | 5 | 28 | 13 | 39759.4733
2027 | 2008 | 5 | 28 | 14 | 41797.8159
2027 | 2008 | 5 | 28 | 15 | 40773.1936
2027 | 2008 | 5 | 28 | 16 | 37546.0613
2027 | 2008 | 5 | 28 | 17 | 36393.3767
2027 | 2008 | 5 | 28 | 18 | 33421.7145
2027 | 2008 | 5 | 28 | 19 | 26625.963
2027 | 2008 | 5 | 28 | 20 | 10616.1735
2027 | 2008 | 5 | 28 | 21 | 724.8672
2027 | 2008 | 5 | 28 | 22 | 0
2027 | 2008 | 5 | 28 | 23 | 0
2027 | 2008 | 5 | 28 | 24 | 0
2027 | 2008 | 5 | 29 | 1 | 0
2027 | 2008 | 5 | 29 | 2 | 0
2027 | 2008 | 5 | 29 | 3 | 0
2027 | 2008 | 5 | 29 | 4 | 0
2027 | 2008 | 5 | 29 | 5 | 0
2027 | 2008 | 5 | 29 | 6 | 0
2027 | 2008 | 5 | 29 | 7 | 34.994
2027 | 2008 | 5 | 29 | 8 | 11487.3691
2027 | 2008 | 5 | 29 | 9 | 30695.5363
2027 | 2008 | 5 | 29 | 10 | 38626.7299
2027 | 2008 | 5 | 29 | 11 | 41028.0621
2027 | 2008 | 5 | 29 | 12 | 41328.5459
2027 | 2008 | 5 | 29 | 13 | 41650.1857
2027 | 2008 | 5 | 29 | 14 | 41467.5637
2027 | 2008 | 5 | 29 | 15 | 41867.6883
2027 | 2008 | 5 | 29 | 16 | 40485.3489
2027 | 2008 | 5 | 29 | 17 | 38240.2047
2027 | 2008 | 5 | 29 | 18 | 34486.9371
2027 | 2008 | 5 | 29 | 19 | 26980.3488
2027 | 2008 | 5 | 29 | 20 | 9640.4906
2027 | 2008 | 5 | 29 | 21 | 686.4556
2027 | 2008 | 5 | 29 | 22 | 0
2027 | 2008 | 5 | 29 | 23 | 0
2027 | 2008 | 5 | 29 | 24 | 0
2027 | 2008 | 5 | 30 | 1 | 0
2027 | 2008 | 5 | 30 | 2 | 0
2027 | 2008 | 5 | 30 | 3 | 0
2027 | 2008 | 5 | 30 | 4 | 0
2027 | 2008 | 5 | 30 | 5 | 0
2027 | 2008 | 5 | 30 | 6 | 0
2027 | 2008 | 5 | 30 | 7 | 55.0789
2027 | 2008 | 5 | 30 | 8 | 12558.6202
2027 | 2008 | 5 | 30 | 9 | 34280.1485
2027 | 2008 | 5 | 30 | 10 | 42952.7434
2027 | 2008 | 5 | 30 | 11 | 44797.896
2027 | 2008 | 5 | 30 | 12 | 43647.3615
2027 | 2008 | 5 | 30 | 13 | 44452.4935
2027 | 2008 | 5 | 30 | 14 | 44937.1176
2027 | 2008 | 5 | 30 | 15 | 44017.0788
2027 | 2008 | 5 | 30 | 16 | 42477.0613
2027 | 2008 | 5 | 30 | 17 | 39742.4649
2027 | 2008 | 5 | 30 | 18 | 37001.4405
2027 | 2008 | 5 | 30 | 19 | 26818.9701
2027 | 2008 | 5 | 30 | 20 | 10801.6576
2027 | 2008 | 5 | 30 | 21 | 866.1167
2027 | 2008 | 5 | 30 | 22 | 0
2027 | 2008 | 5 | 30 | 23 | 0
2027 | 2008 | 5 | 30 | 24 | 0
2027 | 2008 | 5 | 31 | 1 | 0
2027 | 2008 | 5 | 31 | 2 | 0
2027 | 2008 | 5 | 31 | 3 | 0
2027 | 2008 | 5 | 31 | 4 | 0
2027 | 2008 | 5 | 31 | 5 | 0
2027 | 2008 | 5 | 31 | 6 | 0
2027 | 2008 | 5 | 31 | 7 | 48.7982
2027 | 2008 | 5 | 31 | 8 | 8824.6319
2027 | 2008 | 5 | 31 | 9 | 25466.4112
2027 | 2008 | 5 | 31 | 10 | 33189.047
2027 | 2008 | 5 | 31 | 11 | 41730.0882
2027 | 2008 | 5 | 31 | 12 | 43100.1673
2027 | 2008 | 5 | 31 | 13 | 43190.4833
2027 | 2008 | 5 | 31 | 14 | 43384.5466
2027 | 2008 | 5 | 31 | 15 | 42705.8864
2027 | 2008 | 5 | 31 | 16 | 41569.8579
2027 | 2008 | 5 | 31 | 17 | 39868.5898
2027 | 2008 | 5 | 31 | 18 | 36636.4294
2027 | 2008 | 5 | 31 | 19 | 27780.9035
2027 | 2008 | 5 | 31 | 20 | 11375.5734
2027 | 2008 | 5 | 31 | 21 | 407.7966
2027 | 2008 | 5 | 31 | 22 | 0
2027 | 2008 | 5 | 31 | 23 | 0
2027 | 2008 | 5 | 31 | 24 | 0
2028 | 2008 | 5 | 1 | 1 | 0
2028 | 2008 | 5 | 1 | 2 | 0
2028 | 2008 | 5 | 1 | 3 | 0
2028 | 2008 | 5 | 1 | 4 | 0
2028 | 2008 | 5 | 1 | 5 | 0
2028 | 2008 | 5 | 1 | 6 | 0
2028 | 2008 | 5 | 1 | 7 | 0.040681
2028 | 2008 | 5 | 1 | 8 | 3418.6586
2028 | 2008 | 5 | 1 | 9 | 21822.8656
2028 | 2008 | 5 | 1 | 10 | 30484.2395
2028 | 2008 | 5 | 1 | 11 | 32259.542
2028 | 2008 | 5 | 1 | 12 | 35323.794
2028 | 2008 | 5 | 1 | 13 | 38791.1077
2028 | 2008 | 5 | 1 | 14 | 42316.4428
2028 | 2008 | 5 | 1 | 15 | 45115.9386
2028 | 2008 | 5 | 1 | 16 | 40355.2901
2028 | 2008 | 5 | 1 | 17 | 42097.8186
2028 | 2008 | 5 | 1 | 18 | 40179.9384
2028 | 2008 | 5 | 1 | 19 | 30684.6163
2028 | 2008 | 5 | 1 | 20 | 12272.7121
2028 | 2008 | 5 | 1 | 21 | 0
2028 | 2008 | 5 | 1 | 22 | 0
2028 | 2008 | 5 | 1 | 23 | 0
2028 | 2008 | 5 | 1 | 24 | 0
2028 | 2008 | 5 | 2 | 1 | 0
2028 | 2008 | 5 | 2 | 2 | 0
2028 | 2008 | 5 | 2 | 3 | 0
2028 | 2008 | 5 | 2 | 4 | 0
2028 | 2008 | 5 | 2 | 5 | 0
2028 | 2008 | 5 | 2 | 6 | 0
2028 | 2008 | 5 | 2 | 7 | 0.4491
2028 | 2008 | 5 | 2 | 8 | 6369.1142
2028 | 2008 | 5 | 2 | 9 | 31441.8472
2028 | 2008 | 5 | 2 | 10 | 39160.877
2028 | 2008 | 5 | 2 | 11 | 43977.6071
2028 | 2008 | 5 | 2 | 12 | 46071.4811
2028 | 2008 | 5 | 2 | 13 | 48377.5661
2028 | 2008 | 5 | 2 | 14 | 51573.1305
2028 | 2008 | 5 | 2 | 15 | 48059.4629
2028 | 2008 | 5 | 2 | 16 | 48702.7266
2028 | 2008 | 5 | 2 | 17 | 46699.2203
2028 | 2008 | 5 | 2 | 18 | 43019.5692
2028 | 2008 | 5 | 2 | 19 | 32489.8112
2028 | 2008 | 5 | 2 | 20 | 13144.8158
2028 | 2008 | 5 | 2 | 21 | 0
2028 | 2008 | 5 | 2 | 22 | 0
2028 | 2008 | 5 | 2 | 23 | 0
2028 | 2008 | 5 | 2 | 24 | 0
2028 | 2008 | 5 | 3 | 1 | 0
2028 | 2008 | 5 | 3 | 2 | 0
2028 | 2008 | 5 | 3 | 3 | 0
2028 | 2008 | 5 | 3 | 4 | 0
2028 | 2008 | 5 | 3 | 5 | 0
2028 | 2008 | 5 | 3 | 6 | 0
2028 | 2008 | 5 | 3 | 7 | 5.3963
2028 | 2008 | 5 | 3 | 8 | 10854.9128
2028 | 2008 | 5 | 3 | 9 | 37760.7858
2028 | 2008 | 5 | 3 | 10 | 46921.5972
2028 | 2008 | 5 | 3 | 11 | 47541.9517
2028 | 2008 | 5 | 3 | 12 | 52282.6618
2028 | 2008 | 5 | 3 | 13 | 53353.6876
2028 | 2008 | 5 | 3 | 14 | 54078.8989
2028 | 2008 | 5 | 3 | 15 | 53058.3087
2028 | 2008 | 5 | 3 | 16 | 51464.393
2028 | 2008 | 5 | 3 | 17 | 47372.2489
2028 | 2008 | 5 | 3 | 18 | 43817.5714
2028 | 2008 | 5 | 3 | 19 | 32425.5005
2028 | 2008 | 5 | 3 | 20 | 13035.6628
2028 | 2008 | 5 | 3 | 21 | 0
2028 | 2008 | 5 | 3 | 22 | 0
2028 | 2008 | 5 | 3 | 23 | 0
2028 | 2008 | 5 | 3 | 24 | 0
2028 | 2008 | 5 | 4 | 1 | 0
2028 | 2008 | 5 | 4 | 2 | 0
2028 | 2008 | 5 | 4 | 3 | 0
2028 | 2008 | 5 | 4 | 4 | 0
2028 | 2008 | 5 | 4 | 5 | 0
2028 | 2008 | 5 | 4 | 6 | 0
2028 | 2008 | 5 | 4 | 7 | 6.1047
2028 | 2008 | 5 | 4 | 8 | 10487.7875
2028 | 2008 | 5 | 4 | 9 | 37840.588
2028 | 2008 | 5 | 4 | 10 | 48816.9724
2028 | 2008 | 5 | 4 | 11 | 49880.9549
2028 | 2008 | 5 | 4 | 12 | 49046.9322
2028 | 2008 | 5 | 4 | 13 | 47357.4078
2028 | 2008 | 5 | 4 | 14 | 47672.4608
2028 | 2008 | 5 | 4 | 15 | 43941.1088
2028 | 2008 | 5 | 4 | 16 | 42842.4582
2028 | 2008 | 5 | 4 | 17 | 36417.921
2028 | 2008 | 5 | 4 | 18 | 32021.2875
2028 | 2008 | 5 | 4 | 19 | 24690.9454
2028 | 2008 | 5 | 4 | 20 | 10230.2243
2028 | 2008 | 5 | 4 | 21 | 0
2028 | 2008 | 5 | 4 | 22 | 0
2028 | 2008 | 5 | 4 | 23 | 0
2028 | 2008 | 5 | 4 | 24 | 0
2028 | 2008 | 5 | 5 | 1 | 0
2028 | 2008 | 5 | 5 | 2 | 0
2028 | 2008 | 5 | 5 | 3 | 0
2028 | 2008 | 5 | 5 | 4 | 0
2028 | 2008 | 5 | 5 | 5 | 0
2028 | 2008 | 5 | 5 | 6 | 0
2028 | 2008 | 5 | 5 | 7 | 4.6217
2028 | 2008 | 5 | 5 | 8 | 1423.8236
2028 | 2008 | 5 | 5 | 9 | 11062.7021
2028 | 2008 | 5 | 5 | 10 | 19990.8983
2028 | 2008 | 5 | 5 | 11 | 25104.5762
2028 | 2008 | 5 | 5 | 12 | 29133.0881
2028 | 2008 | 5 | 5 | 13 | 34716.8578
2028 | 2008 | 5 | 5 | 14 | 35927.0682
2028 | 2008 | 5 | 5 | 15 | 37533.9214
2028 | 2008 | 5 | 5 | 16 | 35099.114
2028 | 2008 | 5 | 5 | 17 | 33307.6838
2028 | 2008 | 5 | 5 | 18 | 33057.2111
2028 | 2008 | 5 | 5 | 19 | 28175.8854
2028 | 2008 | 5 | 5 | 20 | 9946.4578
2028 | 2008 | 5 | 5 | 21 | 0
2028 | 2008 | 5 | 5 | 22 | 0
2028 | 2008 | 5 | 5 | 23 | 0
2028 | 2008 | 5 | 5 | 24 | 0
2028 | 2008 | 5 | 6 | 1 | 0
2028 | 2008 | 5 | 6 | 2 | 0
2028 | 2008 | 5 | 6 | 3 | 0
2028 | 2008 | 5 | 6 | 4 | 0
2028 | 2008 | 5 | 6 | 5 | 0
2028 | 2008 | 5 | 6 | 6 | 0
2028 | 2008 | 5 | 6 | 7 | 0.76052
2028 | 2008 | 5 | 6 | 8 | 880.9843
2028 | 2008 | 5 | 6 | 9 | 8551.1961
2028 | 2008 | 5 | 6 | 10 | 19817.9321
2028 | 2008 | 5 | 6 | 11 | 27932.4747
2028 | 2008 | 5 | 6 | 12 | 34314.1548
2028 | 2008 | 5 | 6 | 13 | 40847.427
2028 | 2008 | 5 | 6 | 14 | 43738.8546
2028 | 2008 | 5 | 6 | 15 | 43155.0658
2028 | 2008 | 5 | 6 | 16 | 41529.5656
2028 | 2008 | 5 | 6 | 17 | 41264.0165
2028 | 2008 | 5 | 6 | 18 | 39567.11
2028 | 2008 | 5 | 6 | 19 | 28052.0617
2028 | 2008 | 5 | 6 | 20 | 11278.0469
2028 | 2008 | 5 | 6 | 21 | 0
2028 | 2008 | 5 | 6 | 22 | 0
2028 | 2008 | 5 | 6 | 23 | 0
2028 | 2008 | 5 | 6 | 24 | 0
2028 | 2008 | 5 | 7 | 1 | 0
2028 | 2008 | 5 | 7 | 2 | 0
2028 | 2008 | 5 | 7 | 3 | 0
2028 | 2008 | 5 | 7 | 4 | 0
2028 | 2008 | 5 | 7 | 5 | 0
2028 | 2008 | 5 | 7 | 6 | 0
2028 | 2008 | 5 | 7 | 7 | 0
2028 | 2008 | 5 | 7 | 8 | 3139.2801
2028 | 2008 | 5 | 7 | 9 | 18423.8885
2028 | 2008 | 5 | 7 | 10 | 29983.1554
2028 | 2008 | 5 | 7 | 11 | 36045.6561
2028 | 2008 | 5 | 7 | 12 | 37396.2551
2028 | 2008 | 5 | 7 | 13 | 39970.1554
2028 | 2008 | 5 | 7 | 14 | 46938.9705
2028 | 2008 | 5 | 7 | 15 | 46345.5007
2028 | 2008 | 5 | 7 | 16 | 44706.0957
2028 | 2008 | 5 | 7 | 17 | 42815.3616
2028 | 2008 | 5 | 7 | 18 | 41768.2567
2028 | 2008 | 5 | 7 | 19 | 32041.4627
2028 | 2008 | 5 | 7 | 20 | 11691.515
2028 | 2008 | 5 | 7 | 21 | 0
2028 | 2008 | 5 | 7 | 22 | 0
2028 | 2008 | 5 | 7 | 23 | 0
2028 | 2008 | 5 | 7 | 24 | 0
2028 | 2008 | 5 | 8 | 1 | 0
2028 | 2008 | 5 | 8 | 2 | 0
2028 | 2008 | 5 | 8 | 3 | 0
2028 | 2008 | 5 | 8 | 4 | 0
2028 | 2008 | 5 | 8 | 5 | 0
2028 | 2008 | 5 | 8 | 6 | 0
2028 | 2008 | 5 | 8 | 7 | 11.6985
2028 | 2008 | 5 | 8 | 8 | 11118.8407
2028 | 2008 | 5 | 8 | 9 | 35507.131
2028 | 2008 | 5 | 8 | 10 | 45241.2727
2028 | 2008 | 5 | 8 | 11 | 50209.0054
2028 | 2008 | 5 | 8 | 12 | 53426.572
2028 | 2008 | 5 | 8 | 13 | 52770.9659
2028 | 2008 | 5 | 8 | 14 | 53369.5508
2028 | 2008 | 5 | 8 | 15 | 51701.6198
2028 | 2008 | 5 | 8 | 16 | 48709.1704
2028 | 2008 | 5 | 8 | 17 | 46145.5286
2028 | 2008 | 5 | 8 | 18 | 42010.5643
2028 | 2008 | 5 | 8 | 19 | 30755.0898
2028 | 2008 | 5 | 8 | 20 | 12886.0945
2028 | 2008 | 5 | 8 | 21 | 0
2028 | 2008 | 5 | 8 | 22 | 0
2028 | 2008 | 5 | 8 | 23 | 0
2028 | 2008 | 5 | 8 | 24 | 0
2028 | 2008 | 5 | 9 | 1 | 0
2028 | 2008 | 5 | 9 | 2 | 0
2028 | 2008 | 5 | 9 | 3 | 0
2028 | 2008 | 5 | 9 | 4 | 0
2028 | 2008 | 5 | 9 | 5 | 0
2028 | 2008 | 5 | 9 | 6 | 0
2028 | 2008 | 5 | 9 | 7 | 11.6492
2028 | 2008 | 5 | 9 | 8 | 9251.1942
2028 | 2008 | 5 | 9 | 9 | 31837.003
2028 | 2008 | 5 | 9 | 10 | 40574.7017
2028 | 2008 | 5 | 9 | 11 | 46821.1589
2028 | 2008 | 5 | 9 | 12 | 49127.8641
2028 | 2008 | 5 | 9 | 13 | 53058.2468
2028 | 2008 | 5 | 9 | 14 | 52831.9482
2028 | 2008 | 5 | 9 | 15 | 51270.8354
2028 | 2008 | 5 | 9 | 16 | 49003.1646
2028 | 2008 | 5 | 9 | 17 | 46345.6377
2028 | 2008 | 5 | 9 | 18 | 41252.3788
2028 | 2008 | 5 | 9 | 19 | 29581.0025
2028 | 2008 | 5 | 9 | 20 | 11869.4726
2028 | 2008 | 5 | 9 | 21 | 0
2028 | 2008 | 5 | 9 | 22 | 0
2028 | 2008 | 5 | 9 | 23 | 0
2028 | 2008 | 5 | 9 | 24 | 0
2028 | 2008 | 5 | 10 | 1 | 0
2028 | 2008 | 5 | 10 | 2 | 0
2028 | 2008 | 5 | 10 | 3 | 0
2028 | 2008 | 5 | 10 | 4 | 0
2028 | 2008 | 5 | 10 | 5 | 0
2028 | 2008 | 5 | 10 | 6 | 0
2028 | 2008 | 5 | 10 | 7 | 0.7841
2028 | 2008 | 5 | 10 | 8 | 5324.003
2028 | 2008 | 5 | 10 | 9 | 24321.9803
2028 | 2008 | 5 | 10 | 10 | 33823.0942
2028 | 2008 | 5 | 10 | 11 | 40303.616
2028 | 2008 | 5 | 10 | 12 | 48401.2576
2028 | 2008 | 5 | 10 | 13 | 51667.9073
2028 | 2008 | 5 | 10 | 14 | 52816.9841
2028 | 2008 | 5 | 10 | 15 | 49505.2722
2028 | 2008 | 5 | 10 | 16 | 47719.7256
2028 | 2008 | 5 | 10 | 17 | 41816.5169
2028 | 2008 | 5 | 10 | 18 | 37520.2053
2028 | 2008 | 5 | 10 | 19 | 29366.5507
2028 | 2008 | 5 | 10 | 20 | 10919.508
2028 | 2008 | 5 | 10 | 21 | 0
2028 | 2008 | 5 | 10 | 22 | 0
2028 | 2008 | 5 | 10 | 23 | 0
2028 | 2008 | 5 | 10 | 24 | 0
2028 | 2008 | 5 | 11 | 1 | 0
2028 | 2008 | 5 | 11 | 2 | 0
2028 | 2008 | 5 | 11 | 3 | 0
2028 | 2008 | 5 | 11 | 4 | 0
2028 | 2008 | 5 | 11 | 5 | 0
2028 | 2008 | 5 | 11 | 6 | 0
2028 | 2008 | 5 | 11 | 7 | 21.0823
2028 | 2008 | 5 | 11 | 8 | 13699.9754
2028 | 2008 | 5 | 11 | 9 | 41155.6681
2028 | 2008 | 5 | 11 | 10 | 48136.2672
2028 | 2008 | 5 | 11 | 11 | 51207.4864
2028 | 2008 | 5 | 11 | 12 | 52484.7422
2028 | 2008 | 5 | 11 | 13 | 52893.4321
2028 | 2008 | 5 | 11 | 14 | 53705.5623
2028 | 2008 | 5 | 11 | 15 | 50996.6389
2028 | 2008 | 5 | 11 | 16 | 48782.9574
2028 | 2008 | 5 | 11 | 17 | 45358.6515
2028 | 2008 | 5 | 11 | 18 | 40111.7069
2028 | 2008 | 5 | 11 | 19 | 31075.7545
2028 | 2008 | 5 | 11 | 20 | 12047.9101
2028 | 2008 | 5 | 11 | 21 | 0
2028 | 2008 | 5 | 11 | 22 | 0
2028 | 2008 | 5 | 11 | 23 | 0
2028 | 2008 | 5 | 11 | 24 | 0
2028 | 2008 | 5 | 12 | 1 | 0
2028 | 2008 | 5 | 12 | 2 | 0
2028 | 2008 | 5 | 12 | 3 | 0
2028 | 2008 | 5 | 12 | 4 | 0
2028 | 2008 | 5 | 12 | 5 | 0
2028 | 2008 | 5 | 12 | 6 | 0
2028 | 2008 | 5 | 12 | 7 | 22.4307
2028 | 2008 | 5 | 12 | 8 | 13129.4648
2028 | 2008 | 5 | 12 | 9 | 37656.7197
2028 | 2008 | 5 | 12 | 10 | 47201.0728
2028 | 2008 | 5 | 12 | 11 | 49003.1358
2028 | 2008 | 5 | 12 | 12 | 50921.1458
2028 | 2008 | 5 | 12 | 13 | 50562.7936
2028 | 2008 | 5 | 12 | 14 | 53116.2485
2028 | 2008 | 5 | 12 | 15 | 51576.8298
2028 | 2008 | 5 | 12 | 16 | 49068.5267
2028 | 2008 | 5 | 12 | 17 | 45661.0838
2028 | 2008 | 5 | 12 | 18 | 38496.3118
2028 | 2008 | 5 | 12 | 19 | 30092.2413
2028 | 2008 | 5 | 12 | 20 | 9875.6233
2028 | 2008 | 5 | 12 | 21 | 0
2028 | 2008 | 5 | 12 | 22 | 0
2028 | 2008 | 5 | 12 | 23 | 0
2028 | 2008 | 5 | 12 | 24 | 0
2028 | 2008 | 5 | 13 | 1 | 0
2028 | 2008 | 5 | 13 | 2 | 0
2028 | 2008 | 5 | 13 | 3 | 0
2028 | 2008 | 5 | 13 | 4 | 0
2028 | 2008 | 5 | 13 | 5 | 0
2028 | 2008 | 5 | 13 | 6 | 0
2028 | 2008 | 5 | 13 | 7 | 0.19935
2028 | 2008 | 5 | 13 | 8 | 2196.9401
2028 | 2008 | 5 | 13 | 9 | 12766.6675
2028 | 2008 | 5 | 13 | 10 | 21843.3621
2028 | 2008 | 5 | 13 | 11 | 30350.9197
2028 | 2008 | 5 | 13 | 12 | 36795.3358
2028 | 2008 | 5 | 13 | 13 | 39055.2521
2028 | 2008 | 5 | 13 | 14 | 41233.5138
2028 | 2008 | 5 | 13 | 15 | 43277.4338
2028 | 2008 | 5 | 13 | 16 | 42510.8127
2028 | 2008 | 5 | 13 | 17 | 37636.2115
2028 | 2008 | 5 | 13 | 18 | 37132.6518
2028 | 2008 | 5 | 13 | 19 | 28660.5411
2028 | 2008 | 5 | 13 | 20 | 10253.349
2028 | 2008 | 5 | 13 | 21 | 0
2028 | 2008 | 5 | 13 | 22 | 0
2028 | 2008 | 5 | 13 | 23 | 0
2028 | 2008 | 5 | 13 | 24 | 0
2028 | 2008 | 5 | 14 | 1 | 0
2028 | 2008 | 5 | 14 | 2 | 0
2028 | 2008 | 5 | 14 | 3 | 0
2028 | 2008 | 5 | 14 | 4 | 0
2028 | 2008 | 5 | 14 | 5 | 0
2028 | 2008 | 5 | 14 | 6 | 0
2028 | 2008 | 5 | 14 | 7 | 1.4897
2028 | 2008 | 5 | 14 | 8 | 3914.8693
2028 | 2008 | 5 | 14 | 9 | 15942.9912
2028 | 2008 | 5 | 14 | 10 | 23737.7213
2028 | 2008 | 5 | 14 | 11 | 27468.8876
2028 | 2008 | 5 | 14 | 12 | 34917.7341
2028 | 2008 | 5 | 14 | 13 | 39239.7348
2028 | 2008 | 5 | 14 | 14 | 39955.7309
2028 | 2008 | 5 | 14 | 15 | 37685.7146
2028 | 2008 | 5 | 14 | 16 | 35845.3531
2028 | 2008 | 5 | 14 | 17 | 33222.7174
2028 | 2008 | 5 | 14 | 18 | 29240.9238
2028 | 2008 | 5 | 14 | 19 | 24659.1232
2028 | 2008 | 5 | 14 | 20 | 10079.9581
2028 | 2008 | 5 | 14 | 21 | 8.797
2028 | 2008 | 5 | 14 | 22 | 0
2028 | 2008 | 5 | 14 | 23 | 0
2028 | 2008 | 5 | 14 | 24 | 0
2028 | 2008 | 5 | 15 | 1 | 0
2028 | 2008 | 5 | 15 | 2 | 0
2028 | 2008 | 5 | 15 | 3 | 0
2028 | 2008 | 5 | 15 | 4 | 0
2028 | 2008 | 5 | 15 | 5 | 0
2028 | 2008 | 5 | 15 | 6 | 0
2028 | 2008 | 5 | 15 | 7 | 0.18588
2028 | 2008 | 5 | 15 | 8 | 3843.1177
2028 | 2008 | 5 | 15 | 9 | 22076.9197
2028 | 2008 | 5 | 15 | 10 | 38771.0972
2028 | 2008 | 5 | 15 | 11 | 45493.1699
2028 | 2008 | 5 | 15 | 12 | 48173.4378
2028 | 2008 | 5 | 15 | 13 | 48606.3274
2028 | 2008 | 5 | 15 | 14 | 46755.4817
2028 | 2008 | 5 | 15 | 15 | 44513.0417
2028 | 2008 | 5 | 15 | 16 | 40632.0299
2028 | 2008 | 5 | 15 | 17 | 36681.5585
2028 | 2008 | 5 | 15 | 18 | 34136.0947
2028 | 2008 | 5 | 15 | 19 | 26509.0839
2028 | 2008 | 5 | 15 | 20 | 9693.3164
2028 | 2008 | 5 | 15 | 21 | 19.971
2028 | 2008 | 5 | 15 | 22 | 0
2028 | 2008 | 5 | 15 | 23 | 0
2028 | 2008 | 5 | 15 | 24 | 0
2028 | 2008 | 5 | 16 | 1 | 0
2028 | 2008 | 5 | 16 | 2 | 0
2028 | 2008 | 5 | 16 | 3 | 0
2028 | 2008 | 5 | 16 | 4 | 0
2028 | 2008 | 5 | 16 | 5 | 0
2028 | 2008 | 5 | 16 | 6 | 0
2028 | 2008 | 5 | 16 | 7 | 19.2342
2028 | 2008 | 5 | 16 | 8 | 7684.4992
2028 | 2008 | 5 | 16 | 9 | 25706.1355
2028 | 2008 | 5 | 16 | 10 | 37603.987
2028 | 2008 | 5 | 16 | 11 | 43113.9176
2028 | 2008 | 5 | 16 | 12 | 47894.4201
2028 | 2008 | 5 | 16 | 13 | 50796.5193
2028 | 2008 | 5 | 16 | 14 | 52793.7742
2028 | 2008 | 5 | 16 | 15 | 51461.0039
2028 | 2008 | 5 | 16 | 16 | 49492.7407
2028 | 2008 | 5 | 16 | 17 | 45351.8918
2028 | 2008 | 5 | 16 | 18 | 42745.9777
2028 | 2008 | 5 | 16 | 19 | 30934.1801
2028 | 2008 | 5 | 16 | 20 | 9414.1103
2028 | 2008 | 5 | 16 | 21 | 20.0071
2028 | 2008 | 5 | 16 | 22 | 0
2028 | 2008 | 5 | 16 | 23 | 0
2028 | 2008 | 5 | 16 | 24 | 0
2028 | 2008 | 5 | 17 | 1 | 0
2028 | 2008 | 5 | 17 | 2 | 0
2028 | 2008 | 5 | 17 | 3 | 0
2028 | 2008 | 5 | 17 | 4 | 0
2028 | 2008 | 5 | 17 | 5 | 0
2028 | 2008 | 5 | 17 | 6 | 0
2028 | 2008 | 5 | 17 | 7 | 20.8243
2028 | 2008 | 5 | 17 | 8 | 9519.1853
2028 | 2008 | 5 | 17 | 9 | 33349.5754
2028 | 2008 | 5 | 17 | 10 | 45543.4021
2028 | 2008 | 5 | 17 | 11 | 47109.2386
2028 | 2008 | 5 | 17 | 12 | 47065.2815
2028 | 2008 | 5 | 17 | 13 | 44684.6971
2028 | 2008 | 5 | 17 | 14 | 43911.4447
2028 | 2008 | 5 | 17 | 15 | 41255.9897
2028 | 2008 | 5 | 17 | 16 | 38207.4484
2028 | 2008 | 5 | 17 | 17 | 33411.7928
2028 | 2008 | 5 | 17 | 18 | 33033.2639
2028 | 2008 | 5 | 17 | 19 | 28675.6631
2028 | 2008 | 5 | 17 | 20 | 10726.4036
2028 | 2008 | 5 | 17 | 21 | 32.9858
2028 | 2008 | 5 | 17 | 22 | 0
2028 | 2008 | 5 | 17 | 23 | 0
2028 | 2008 | 5 | 17 | 24 | 0
2028 | 2008 | 5 | 18 | 1 | 0
2028 | 2008 | 5 | 18 | 2 | 0
2028 | 2008 | 5 | 18 | 3 | 0
2028 | 2008 | 5 | 18 | 4 | 0
2028 | 2008 | 5 | 18 | 5 | 0
2028 | 2008 | 5 | 18 | 6 | 0
2028 | 2008 | 5 | 18 | 7 | 43.7616
2028 | 2008 | 5 | 18 | 8 | 17344.4352
2028 | 2008 | 5 | 18 | 9 | 47344.1009
2028 | 2008 | 5 | 18 | 10 | 54900.5291
2028 | 2008 | 5 | 18 | 11 | 54823.0565
2028 | 2008 | 5 | 18 | 12 | 53298.1427
2028 | 2008 | 5 | 18 | 13 | 54049.657
2028 | 2008 | 5 | 18 | 14 | 54712.6837
2028 | 2008 | 5 | 18 | 15 | 52749.9526
2028 | 2008 | 5 | 18 | 16 | 51413.9605
2028 | 2008 | 5 | 18 | 17 | 48452.9995
2028 | 2008 | 5 | 18 | 18 | 45644.3452
2028 | 2008 | 5 | 18 | 19 | 32027.5121
2028 | 2008 | 5 | 18 | 20 | 11611.4344
2028 | 2008 | 5 | 18 | 21 | 43.7266
2028 | 2008 | 5 | 18 | 22 | 0
2028 | 2008 | 5 | 18 | 23 | 0
2028 | 2008 | 5 | 18 | 24 | 0
2028 | 2008 | 5 | 19 | 1 | 0
2028 | 2008 | 5 | 19 | 2 | 0
2028 | 2008 | 5 | 19 | 3 | 0
2028 | 2008 | 5 | 19 | 4 | 0
2028 | 2008 | 5 | 19 | 5 | 0
2028 | 2008 | 5 | 19 | 6 | 0
2028 | 2008 | 5 | 19 | 7 | 34.175
2028 | 2008 | 5 | 19 | 8 | 17308.1234
2028 | 2008 | 5 | 19 | 9 | 48601.0511
2028 | 2008 | 5 | 19 | 10 | 55884.3611
2028 | 2008 | 5 | 19 | 11 | 54247.1189
2028 | 2008 | 5 | 19 | 12 | 53958.6832
2028 | 2008 | 5 | 19 | 13 | 54542.3405
2028 | 2008 | 5 | 19 | 14 | 53862.6179
2028 | 2008 | 5 | 19 | 15 | 52413.8241
2028 | 2008 | 5 | 19 | 16 | 51276.0793
2028 | 2008 | 5 | 19 | 17 | 48103.729
2028 | 2008 | 5 | 19 | 18 | 44095.7194
2028 | 2008 | 5 | 19 | 19 | 32769.1382
2028 | 2008 | 5 | 19 | 20 | 11763.0669
2028 | 2008 | 5 | 19 | 21 | 114.6037
2028 | 2008 | 5 | 19 | 22 | 0
2028 | 2008 | 5 | 19 | 23 | 0
2028 | 2008 | 5 | 19 | 24 | 0
2028 | 2008 | 5 | 20 | 1 | 0
2028 | 2008 | 5 | 20 | 2 | 0
2028 | 2008 | 5 | 20 | 3 | 0
2028 | 2008 | 5 | 20 | 4 | 0
2028 | 2008 | 5 | 20 | 5 | 0
2028 | 2008 | 5 | 20 | 6 | 0
2028 | 2008 | 5 | 20 | 7 | 38.4267
2028 | 2008 | 5 | 20 | 8 | 15310.8129
2028 | 2008 | 5 | 20 | 9 | 40333.7475
2028 | 2008 | 5 | 20 | 10 | 48713.9509
2028 | 2008 | 5 | 20 | 11 | 51441.2458
2028 | 2008 | 5 | 20 | 12 | 52563.4201
2028 | 2008 | 5 | 20 | 13 | 53153.894
2028 | 2008 | 5 | 20 | 14 | 53350.6572
2028 | 2008 | 5 | 20 | 15 | 51490.6693
2028 | 2008 | 5 | 20 | 16 | 49400.029
2028 | 2008 | 5 | 20 | 17 | 47969.9908
2028 | 2008 | 5 | 20 | 18 | 45256.3173
2028 | 2008 | 5 | 20 | 19 | 31676.3396
2028 | 2008 | 5 | 20 | 20 | 11090.2349
2028 | 2008 | 5 | 20 | 21 | 124.066
2028 | 2008 | 5 | 20 | 22 | 0
2028 | 2008 | 5 | 20 | 23 | 0
2028 | 2008 | 5 | 20 | 24 | 0
2028 | 2008 | 5 | 21 | 1 | 0
2028 | 2008 | 5 | 21 | 2 | 0
2028 | 2008 | 5 | 21 | 3 | 0
2028 | 2008 | 5 | 21 | 4 | 0
2028 | 2008 | 5 | 21 | 5 | 0
2028 | 2008 | 5 | 21 | 6 | 0
2028 | 2008 | 5 | 21 | 7 | 30.238
2028 | 2008 | 5 | 21 | 8 | 6670.618
2028 | 2008 | 5 | 21 | 9 | 23983.8755
2028 | 2008 | 5 | 21 | 10 | 33847.1063
2028 | 2008 | 5 | 21 | 11 | 40648.4444
2028 | 2008 | 5 | 21 | 12 | 51355.3639
2028 | 2008 | 5 | 21 | 13 | 53280.6475
2028 | 2008 | 5 | 21 | 14 | 54122.3306
2028 | 2008 | 5 | 21 | 15 | 52160.7735
2028 | 2008 | 5 | 21 | 16 | 50651.9236
2028 | 2008 | 5 | 21 | 17 | 47611.4977
2028 | 2008 | 5 | 21 | 18 | 43350.1852
2028 | 2008 | 5 | 21 | 19 | 31503.0594
2028 | 2008 | 5 | 21 | 20 | 11204.1398
2028 | 2008 | 5 | 21 | 21 | 112.748
2028 | 2008 | 5 | 21 | 22 | 0
2028 | 2008 | 5 | 21 | 23 | 0
2028 | 2008 | 5 | 21 | 24 | 0
2028 | 2008 | 5 | 22 | 1 | 0
2028 | 2008 | 5 | 22 | 2 | 0
2028 | 2008 | 5 | 22 | 3 | 0
2028 | 2008 | 5 | 22 | 4 | 0
2028 | 2008 | 5 | 22 | 5 | 0
2028 | 2008 | 5 | 22 | 6 | 0
2028 | 2008 | 5 | 22 | 7 | 3.0327
2028 | 2008 | 5 | 22 | 8 | 3988.0777
2028 | 2008 | 5 | 22 | 9 | 20151.9975
2028 | 2008 | 5 | 22 | 10 | 36112.5839
2028 | 2008 | 5 | 22 | 11 | 45068.6176
2028 | 2008 | 5 | 22 | 12 | 50500.2153
2028 | 2008 | 5 | 22 | 13 | 52791.056
2028 | 2008 | 5 | 22 | 14 | 53212.783
2028 | 2008 | 5 | 22 | 15 | 51028.3468
2028 | 2008 | 5 | 22 | 16 | 47848.3184
2028 | 2008 | 5 | 22 | 17 | 44480.3893
2028 | 2008 | 5 | 22 | 18 | 40543.1342
2028 | 2008 | 5 | 22 | 19 | 32339.6801
2028 | 2008 | 5 | 22 | 20 | 11689.5643
2028 | 2008 | 5 | 22 | 21 | 226.0529
2028 | 2008 | 5 | 22 | 22 | 0
2028 | 2008 | 5 | 22 | 23 | 0
2028 | 2008 | 5 | 22 | 24 | 0
2028 | 2008 | 5 | 23 | 1 | 0
2028 | 2008 | 5 | 23 | 2 | 0
2028 | 2008 | 5 | 23 | 3 | 0
2028 | 2008 | 5 | 23 | 4 | 0
2028 | 2008 | 5 | 23 | 5 | 0
2028 | 2008 | 5 | 23 | 6 | 0
2028 | 2008 | 5 | 23 | 7 | 4.8648
2028 | 2008 | 5 | 23 | 8 | 5111.5419
2028 | 2008 | 5 | 23 | 9 | 23188.5325
2028 | 2008 | 5 | 23 | 10 | 38140.241
2028 | 2008 | 5 | 23 | 11 | 48182.4825
2028 | 2008 | 5 | 23 | 12 | 51914.8683
2028 | 2008 | 5 | 23 | 13 | 52693.0291
2028 | 2008 | 5 | 23 | 14 | 53989.8164
2028 | 2008 | 5 | 23 | 15 | 52742.8197
2028 | 2008 | 5 | 23 | 16 | 50400.7949
2028 | 2008 | 5 | 23 | 17 | 48013.0275
2028 | 2008 | 5 | 23 | 18 | 44555.1797
2028 | 2008 | 5 | 23 | 19 | 32541.9608
2028 | 2008 | 5 | 23 | 20 | 11161.1828
2028 | 2008 | 5 | 23 | 21 | 289.5678
2028 | 2008 | 5 | 23 | 22 | 0
2028 | 2008 | 5 | 23 | 23 | 0
2028 | 2008 | 5 | 23 | 24 | 0
2028 | 2008 | 5 | 24 | 1 | 0
2028 | 2008 | 5 | 24 | 2 | 0
2028 | 2008 | 5 | 24 | 3 | 0
2028 | 2008 | 5 | 24 | 4 | 0
2028 | 2008 | 5 | 24 | 5 | 0
2028 | 2008 | 5 | 24 | 6 | 0
2028 | 2008 | 5 | 24 | 7 | 5.9061
2028 | 2008 | 5 | 24 | 8 | 4649.6177
2028 | 2008 | 5 | 24 | 9 | 19177.503
2028 | 2008 | 5 | 24 | 10 | 31953.4653
2028 | 2008 | 5 | 24 | 11 | 48794.2276
2028 | 2008 | 5 | 24 | 12 | 52291.6681
2028 | 2008 | 5 | 24 | 13 | 53995.1305
2028 | 2008 | 5 | 24 | 14 | 53624.0617
2028 | 2008 | 5 | 24 | 15 | 52518.9667
2028 | 2008 | 5 | 24 | 16 | 51002.1879
2028 | 2008 | 5 | 24 | 17 | 48091.2517
2028 | 2008 | 5 | 24 | 18 | 42612.4326
2028 | 2008 | 5 | 24 | 19 | 31958.7392
2028 | 2008 | 5 | 24 | 20 | 11861.0994
2028 | 2008 | 5 | 24 | 21 | 406.1327
2028 | 2008 | 5 | 24 | 22 | 0
2028 | 2008 | 5 | 24 | 23 | 0
2028 | 2008 | 5 | 24 | 24 | 0
2028 | 2008 | 5 | 25 | 1 | 0
2028 | 2008 | 5 | 25 | 2 | 0
2028 | 2008 | 5 | 25 | 3 | 0
2028 | 2008 | 5 | 25 | 4 | 0
2028 | 2008 | 5 | 25 | 5 | 0
2028 | 2008 | 5 | 25 | 6 | 0
2028 | 2008 | 5 | 25 | 7 | 7.3296
2028 | 2008 | 5 | 25 | 8 | 3757.4558
2028 | 2008 | 5 | 25 | 9 | 13693.8837
2028 | 2008 | 5 | 25 | 10 | 32153.6534
2028 | 2008 | 5 | 25 | 11 | 45130.8977
2028 | 2008 | 5 | 25 | 12 | 52268.4118
2028 | 2008 | 5 | 25 | 13 | 53180.6372
2028 | 2008 | 5 | 25 | 14 | 54220.1779
2028 | 2008 | 5 | 25 | 15 | 52988.6904
2028 | 2008 | 5 | 25 | 16 | 50154.7116
2028 | 2008 | 5 | 25 | 17 | 48229.2453
2028 | 2008 | 5 | 25 | 18 | 43621.3338
2028 | 2008 | 5 | 25 | 19 | 32113.1978
2028 | 2008 | 5 | 25 | 20 | 11814.4502
2028 | 2008 | 5 | 25 | 21 | 530.3762
2028 | 2008 | 5 | 25 | 22 | 0
2028 | 2008 | 5 | 25 | 23 | 0
2028 | 2008 | 5 | 25 | 24 | 0
2028 | 2008 | 5 | 26 | 1 | 0
2028 | 2008 | 5 | 26 | 2 | 0
2028 | 2008 | 5 | 26 | 3 | 0
2028 | 2008 | 5 | 26 | 4 | 0
2028 | 2008 | 5 | 26 | 5 | 0
2028 | 2008 | 5 | 26 | 6 | 0
2028 | 2008 | 5 | 26 | 7 | 12.3992
2028 | 2008 | 5 | 26 | 8 | 3520.3819
2028 | 2008 | 5 | 26 | 9 | 16266.5317
2028 | 2008 | 5 | 26 | 10 | 39040.4059
2028 | 2008 | 5 | 26 | 11 | 47615.3569
2028 | 2008 | 5 | 26 | 12 | 51758.9373
2028 | 2008 | 5 | 26 | 13 | 53714.8421
2028 | 2008 | 5 | 26 | 14 | 52923.6485
2028 | 2008 | 5 | 26 | 15 | 52847.8356
2028 | 2008 | 5 | 26 | 16 | 50664.8357
2028 | 2008 | 5 | 26 | 17 | 48067.4035
2028 | 2008 | 5 | 26 | 18 | 42846.8694
2028 | 2008 | 5 | 26 | 19 | 30909.2603
2028 | 2008 | 5 | 26 | 20 | 10778.4551
2028 | 2008 | 5 | 26 | 21 | 559.8964
2028 | 2008 | 5 | 26 | 22 | 0
2028 | 2008 | 5 | 26 | 23 | 0
2028 | 2008 | 5 | 26 | 24 | 0
2028 | 2008 | 5 | 27 | 1 | 0
2028 | 2008 | 5 | 27 | 2 | 0
2028 | 2008 | 5 | 27 | 3 | 0
2028 | 2008 | 5 | 27 | 4 | 0
2028 | 2008 | 5 | 27 | 5 | 0
2028 | 2008 | 5 | 27 | 6 | 0
2028 | 2008 | 5 | 27 | 7 | 5.6416
2028 | 2008 | 5 | 27 | 8 | 3805.4258
2028 | 2008 | 5 | 27 | 9 | 18914.4552
2028 | 2008 | 5 | 27 | 10 | 34320.2031
2028 | 2008 | 5 | 27 | 11 | 48195.2158
2028 | 2008 | 5 | 27 | 12 | 51855.4463
2028 | 2008 | 5 | 27 | 13 | 52737.7487
2028 | 2008 | 5 | 27 | 14 | 52637.1573
2028 | 2008 | 5 | 27 | 15 | 52635.5863
2028 | 2008 | 5 | 27 | 16 | 50262.0351
2028 | 2008 | 5 | 27 | 17 | 46958.3443
2028 | 2008 | 5 | 27 | 18 | 42701.7304
2028 | 2008 | 5 | 27 | 19 | 32067.9099
2028 | 2008 | 5 | 27 | 20 | 11765.0477
2028 | 2008 | 5 | 27 | 21 | 611.6354
2028 | 2008 | 5 | 27 | 22 | 0
2028 | 2008 | 5 | 27 | 23 | 0
2028 | 2008 | 5 | 27 | 24 | 0
2028 | 2008 | 5 | 28 | 1 | 0
2028 | 2008 | 5 | 28 | 2 | 0
2028 | 2008 | 5 | 28 | 3 | 0
2028 | 2008 | 5 | 28 | 4 | 0
2028 | 2008 | 5 | 28 | 5 | 0
2028 | 2008 | 5 | 28 | 6 | 0
2028 | 2008 | 5 | 28 | 7 | 40.5889
2028 | 2008 | 5 | 28 | 8 | 8884.941
2028 | 2008 | 5 | 28 | 9 | 24940.8461
2028 | 2008 | 5 | 28 | 10 | 35948.5788
2028 | 2008 | 5 | 28 | 11 | 44044.6236
2028 | 2008 | 5 | 28 | 12 | 47831.981
2028 | 2008 | 5 | 28 | 13 | 48522.7206
2028 | 2008 | 5 | 28 | 14 | 50613.2949
2028 | 2008 | 5 | 28 | 15 | 49923.5364
2028 | 2008 | 5 | 28 | 16 | 44374.9104
2028 | 2008 | 5 | 28 | 17 | 44514.3553
2028 | 2008 | 5 | 28 | 18 | 39995.1845
2028 | 2008 | 5 | 28 | 19 | 31888.4304
2028 | 2008 | 5 | 28 | 20 | 12507.5387
2028 | 2008 | 5 | 28 | 21 | 724.8672
2028 | 2008 | 5 | 28 | 22 | 0
2028 | 2008 | 5 | 28 | 23 | 0
2028 | 2008 | 5 | 28 | 24 | 0
2028 | 2008 | 5 | 29 | 1 | 0
2028 | 2008 | 5 | 29 | 2 | 0
2028 | 2008 | 5 | 29 | 3 | 0
2028 | 2008 | 5 | 29 | 4 | 0
2028 | 2008 | 5 | 29 | 5 | 0
2028 | 2008 | 5 | 29 | 6 | 0
2028 | 2008 | 5 | 29 | 7 | 34.994
2028 | 2008 | 5 | 29 | 8 | 13655.3635
2028 | 2008 | 5 | 29 | 9 | 36850.0549
2028 | 2008 | 5 | 29 | 10 | 46529.2495
2028 | 2008 | 5 | 29 | 11 | 49559.0733
2028 | 2008 | 5 | 29 | 12 | 49726.0988
2028 | 2008 | 5 | 29 | 13 | 50072.0567
2028 | 2008 | 5 | 29 | 14 | 49626.9215
2028 | 2008 | 5 | 29 | 15 | 50151.8095
2028 | 2008 | 5 | 29 | 16 | 48721.9076
2028 | 2008 | 5 | 29 | 17 | 45228.9152
2028 | 2008 | 5 | 29 | 18 | 41706.5936
2028 | 2008 | 5 | 29 | 19 | 32152.6949
2028 | 2008 | 5 | 29 | 20 | 11323.8476
2028 | 2008 | 5 | 29 | 21 | 686.4556
2028 | 2008 | 5 | 29 | 22 | 0
2028 | 2008 | 5 | 29 | 23 | 0
2028 | 2008 | 5 | 29 | 24 | 0
2028 | 2008 | 5 | 30 | 1 | 0
2028 | 2008 | 5 | 30 | 2 | 0
2028 | 2008 | 5 | 30 | 3 | 0
2028 | 2008 | 5 | 30 | 4 | 0
2028 | 2008 | 5 | 30 | 5 | 0
2028 | 2008 | 5 | 30 | 6 | 0
2028 | 2008 | 5 | 30 | 7 | 55.0789
2028 | 2008 | 5 | 30 | 8 | 15237.7249
2028 | 2008 | 5 | 30 | 9 | 41849.7833
2028 | 2008 | 5 | 30 | 10 | 52133.6519
2028 | 2008 | 5 | 30 | 11 | 54185.3418
2028 | 2008 | 5 | 30 | 12 | 52039.3786
2028 | 2008 | 5 | 30 | 13 | 53364.9253
2028 | 2008 | 5 | 30 | 14 | 54019.7213
2028 | 2008 | 5 | 30 | 15 | 53057.2683
2028 | 2008 | 5 | 30 | 16 | 50889.6906
2028 | 2008 | 5 | 30 | 17 | 47679.437
2028 | 2008 | 5 | 30 | 18 | 44386.5816
2028 | 2008 | 5 | 30 | 19 | 31961.292
2028 | 2008 | 5 | 30 | 20 | 12702.9277
2028 | 2008 | 5 | 30 | 21 | 866.1167
2028 | 2008 | 5 | 30 | 22 | 0
2028 | 2008 | 5 | 30 | 23 | 0
2028 | 2008 | 5 | 30 | 24 | 0
2028 | 2008 | 5 | 31 | 1 | 0
2028 | 2008 | 5 | 31 | 2 | 0
2028 | 2008 | 5 | 31 | 3 | 0
2028 | 2008 | 5 | 31 | 4 | 0
2028 | 2008 | 5 | 31 | 5 | 0
2028 | 2008 | 5 | 31 | 6 | 0
2028 | 2008 | 5 | 31 | 7 | 48.7982
2028 | 2008 | 5 | 31 | 8 | 10218.4011
2028 | 2008 | 5 | 31 | 9 | 30282.8425
2028 | 2008 | 5 | 31 | 10 | 39545.9879
2028 | 2008 | 5 | 31 | 11 | 49581.3959
2028 | 2008 | 5 | 31 | 12 | 51784.1839
2028 | 2008 | 5 | 31 | 13 | 51642.0419
2028 | 2008 | 5 | 31 | 14 | 51900.844
2028 | 2008 | 5 | 31 | 15 | 51072.7388
2028 | 2008 | 5 | 31 | 16 | 49954.14
2028 | 2008 | 5 | 31 | 17 | 47966.009
2028 | 2008 | 5 | 31 | 18 | 43871.7575
2028 | 2008 | 5 | 31 | 19 | 33180.0863
2028 | 2008 | 5 | 31 | 20 | 13368.8873
2028 | 2008 | 5 | 31 | 21 | 407.7966
2028 | 2008 | 5 | 31 | 22 | 0
2028 | 2008 | 5 | 31 | 23 | 0
2028 | 2008 | 5 | 31 | 24 | 0
2029 | 2008 | 5 | 1 | 1 | 0
2029 | 2008 | 5 | 1 | 2 | 0
2029 | 2008 | 5 | 1 | 3 | 0
2029 | 2008 | 5 | 1 | 4 | 0
2029 | 2008 | 5 | 1 | 5 | 0
2029 | 2008 | 5 | 1 | 6 | 0
2029 | 2008 | 5 | 1 | 7 | 0.040681
2029 | 2008 | 5 | 1 | 8 | 3708.3417
2029 | 2008 | 5 | 1 | 9 | 23239.8709
2029 | 2008 | 5 | 1 | 10 | 32237.2886
2029 | 2008 | 5 | 1 | 11 | 33946.615
2029 | 2008 | 5 | 1 | 12 | 37028.7203
2029 | 2008 | 5 | 1 | 13 | 40523.2509
2029 | 2008 | 5 | 1 | 14 | 44083.7623
2029 | 2008 | 5 | 1 | 15 | 46601.1856
2029 | 2008 | 5 | 1 | 16 | 41953.006
2029 | 2008 | 5 | 1 | 17 | 43644.6085
2029 | 2008 | 5 | 1 | 18 | 41624.3001
2029 | 2008 | 5 | 1 | 19 | 31866.0755
2029 | 2008 | 5 | 1 | 20 | 12691.3469
2029 | 2008 | 5 | 1 | 21 | 0
2029 | 2008 | 5 | 1 | 22 | 0
2029 | 2008 | 5 | 1 | 23 | 0
2029 | 2008 | 5 | 1 | 24 | 0
2029 | 2008 | 5 | 2 | 1 | 0
2029 | 2008 | 5 | 2 | 2 | 0
2029 | 2008 | 5 | 2 | 3 | 0
2029 | 2008 | 5 | 2 | 4 | 0
2029 | 2008 | 5 | 2 | 5 | 0
2029 | 2008 | 5 | 2 | 6 | 0
2029 | 2008 | 5 | 2 | 7 | 0.4491
2029 | 2008 | 5 | 2 | 8 | 6699.3754
2029 | 2008 | 5 | 2 | 9 | 33007.3523
2029 | 2008 | 5 | 2 | 10 | 40984.5336
2029 | 2008 | 5 | 2 | 11 | 45779.3599
2029 | 2008 | 5 | 2 | 12 | 47824.8713
2029 | 2008 | 5 | 2 | 13 | 50156.4303
2029 | 2008 | 5 | 2 | 14 | 53383.3816
2029 | 2008 | 5 | 2 | 15 | 49853.9994
2029 | 2008 | 5 | 2 | 16 | 50325.9858
2029 | 2008 | 5 | 2 | 17 | 48309.3788
2029 | 2008 | 5 | 2 | 18 | 44482.0926
2029 | 2008 | 5 | 2 | 19 | 33762.2016
2029 | 2008 | 5 | 2 | 20 | 13618.7536
2029 | 2008 | 5 | 2 | 21 | 0
2029 | 2008 | 5 | 2 | 22 | 0
2029 | 2008 | 5 | 2 | 23 | 0
2029 | 2008 | 5 | 2 | 24 | 0
2029 | 2008 | 5 | 3 | 1 | 0
2029 | 2008 | 5 | 3 | 2 | 0
2029 | 2008 | 5 | 3 | 3 | 0
2029 | 2008 | 5 | 3 | 4 | 0
2029 | 2008 | 5 | 3 | 5 | 0
2029 | 2008 | 5 | 3 | 6 | 0
2029 | 2008 | 5 | 3 | 7 | 5.3963
2029 | 2008 | 5 | 3 | 8 | 11196.739
2029 | 2008 | 5 | 3 | 9 | 39253.4011
2029 | 2008 | 5 | 3 | 10 | 48729.4445
2029 | 2008 | 5 | 3 | 11 | 49260.5216
2029 | 2008 | 5 | 3 | 12 | 54091.9734
2029 | 2008 | 5 | 3 | 13 | 55117.7223
2029 | 2008 | 5 | 3 | 14 | 55865.4228
2029 | 2008 | 5 | 3 | 15 | 54837.0553
2029 | 2008 | 5 | 3 | 16 | 53159.0749
2029 | 2008 | 5 | 3 | 17 | 48842.5264
2029 | 2008 | 5 | 3 | 18 | 45307.0292
2029 | 2008 | 5 | 3 | 19 | 33602.2903
2029 | 2008 | 5 | 3 | 20 | 13507.7521
2029 | 2008 | 5 | 3 | 21 | 0
2029 | 2008 | 5 | 3 | 22 | 0
2029 | 2008 | 5 | 3 | 23 | 0
2029 | 2008 | 5 | 3 | 24 | 0
2029 | 2008 | 5 | 4 | 1 | 0
2029 | 2008 | 5 | 4 | 2 | 0
2029 | 2008 | 5 | 4 | 3 | 0
2029 | 2008 | 5 | 4 | 4 | 0
2029 | 2008 | 5 | 4 | 5 | 0
2029 | 2008 | 5 | 4 | 6 | 0
2029 | 2008 | 5 | 4 | 7 | 6.1047
2029 | 2008 | 5 | 4 | 8 | 10660.865
2029 | 2008 | 5 | 4 | 9 | 38958.8248
2029 | 2008 | 5 | 4 | 10 | 50343.3592
2029 | 2008 | 5 | 4 | 11 | 51499.8458
2029 | 2008 | 5 | 4 | 12 | 50393.766
2029 | 2008 | 5 | 4 | 13 | 48683.0229
2029 | 2008 | 5 | 4 | 14 | 49154.4185
2029 | 2008 | 5 | 4 | 15 | 45355.5281
2029 | 2008 | 5 | 4 | 16 | 44200.0554
2029 | 2008 | 5 | 4 | 17 | 37758.6669
2029 | 2008 | 5 | 4 | 18 | 33333.2945
2029 | 2008 | 5 | 4 | 19 | 25747.1222
2029 | 2008 | 5 | 4 | 20 | 10664.3746
2029 | 2008 | 5 | 4 | 21 | 0
2029 | 2008 | 5 | 4 | 22 | 0
2029 | 2008 | 5 | 4 | 23 | 0
2029 | 2008 | 5 | 4 | 24 | 0
2029 | 2008 | 5 | 5 | 1 | 0
2029 | 2008 | 5 | 5 | 2 | 0
2029 | 2008 | 5 | 5 | 3 | 0
2029 | 2008 | 5 | 5 | 4 | 0
2029 | 2008 | 5 | 5 | 5 | 0
2029 | 2008 | 5 | 5 | 6 | 0
2029 | 2008 | 5 | 5 | 7 | 4.6217
2029 | 2008 | 5 | 5 | 8 | 1432.2503
2029 | 2008 | 5 | 5 | 9 | 11210.5105
2029 | 2008 | 5 | 5 | 10 | 20891.147
2029 | 2008 | 5 | 5 | 11 | 25671.8685
2029 | 2008 | 5 | 5 | 12 | 30331.712
2029 | 2008 | 5 | 5 | 13 | 35944.7365
2029 | 2008 | 5 | 5 | 14 | 37024.5982
2029 | 2008 | 5 | 5 | 15 | 38841.2829
2029 | 2008 | 5 | 5 | 16 | 36455.1734
2029 | 2008 | 5 | 5 | 17 | 34533.2867
2029 | 2008 | 5 | 5 | 18 | 34304.9835
2029 | 2008 | 5 | 5 | 19 | 29172.287
2029 | 2008 | 5 | 5 | 20 | 10342.4462
2029 | 2008 | 5 | 5 | 21 | 0
2029 | 2008 | 5 | 5 | 22 | 0
2029 | 2008 | 5 | 5 | 23 | 0
2029 | 2008 | 5 | 5 | 24 | 0
2029 | 2008 | 5 | 6 | 1 | 0
2029 | 2008 | 5 | 6 | 2 | 0
2029 | 2008 | 5 | 6 | 3 | 0
2029 | 2008 | 5 | 6 | 4 | 0
2029 | 2008 | 5 | 6 | 5 | 0
2029 | 2008 | 5 | 6 | 6 | 0
2029 | 2008 | 5 | 6 | 7 | 0.76052
2029 | 2008 | 5 | 6 | 8 | 896.286
2029 | 2008 | 5 | 6 | 9 | 8879.2797
2029 | 2008 | 5 | 6 | 10 | 20434.8514
2029 | 2008 | 5 | 6 | 11 | 28764.5879
2029 | 2008 | 5 | 6 | 12 | 35614.6408
2029 | 2008 | 5 | 6 | 13 | 42187.7446
2029 | 2008 | 5 | 6 | 14 | 45375.6964
2029 | 2008 | 5 | 6 | 15 | 44910.9549
2029 | 2008 | 5 | 6 | 16 | 43070.0771
2029 | 2008 | 5 | 6 | 17 | 42650.257
2029 | 2008 | 5 | 6 | 18 | 40841.2517
2029 | 2008 | 5 | 6 | 19 | 29158.6056
2029 | 2008 | 5 | 6 | 20 | 11725.7159
2029 | 2008 | 5 | 6 | 21 | 0
2029 | 2008 | 5 | 6 | 22 | 0
2029 | 2008 | 5 | 6 | 23 | 0
2029 | 2008 | 5 | 6 | 24 | 0
2029 | 2008 | 5 | 7 | 1 | 0
2029 | 2008 | 5 | 7 | 2 | 0
2029 | 2008 | 5 | 7 | 3 | 0
2029 | 2008 | 5 | 7 | 4 | 0
2029 | 2008 | 5 | 7 | 5 | 0
2029 | 2008 | 5 | 7 | 6 | 0
2029 | 2008 | 5 | 7 | 7 | 0
2029 | 2008 | 5 | 7 | 8 | 3316.4561
2029 | 2008 | 5 | 7 | 9 | 19550.6865
2029 | 2008 | 5 | 7 | 10 | 31445.6215
2029 | 2008 | 5 | 7 | 11 | 37704.9402
2029 | 2008 | 5 | 7 | 12 | 39066.2912
2029 | 2008 | 5 | 7 | 13 | 41759.1456
2029 | 2008 | 5 | 7 | 14 | 48786.9079
2029 | 2008 | 5 | 7 | 15 | 48113.2672
2029 | 2008 | 5 | 7 | 16 | 46369.6977
2029 | 2008 | 5 | 7 | 17 | 44443.6138
2029 | 2008 | 5 | 7 | 18 | 43263.5019
2029 | 2008 | 5 | 7 | 19 | 33195.0041
2029 | 2008 | 5 | 7 | 20 | 12135.8266
2029 | 2008 | 5 | 7 | 21 | 0
2029 | 2008 | 5 | 7 | 22 | 0
2029 | 2008 | 5 | 7 | 23 | 0
2029 | 2008 | 5 | 7 | 24 | 0
2029 | 2008 | 5 | 8 | 1 | 0
2029 | 2008 | 5 | 8 | 2 | 0
2029 | 2008 | 5 | 8 | 3 | 0
2029 | 2008 | 5 | 8 | 4 | 0
2029 | 2008 | 5 | 8 | 5 | 0
2029 | 2008 | 5 | 8 | 6 | 0
2029 | 2008 | 5 | 8 | 7 | 11.6985
2029 | 2008 | 5 | 8 | 8 | 11504.9955
2029 | 2008 | 5 | 8 | 9 | 37021.1222
2029 | 2008 | 5 | 8 | 10 | 47053.174
2029 | 2008 | 5 | 8 | 11 | 51983.9221
2029 | 2008 | 5 | 8 | 12 | 55179.8203
2029 | 2008 | 5 | 8 | 13 | 54579.26
2029 | 2008 | 5 | 8 | 14 | 55138.2979
2029 | 2008 | 5 | 8 | 15 | 53403.8457
2029 | 2008 | 5 | 8 | 16 | 50252.167
2029 | 2008 | 5 | 8 | 17 | 47668.9943
2029 | 2008 | 5 | 8 | 18 | 43350.2766
2029 | 2008 | 5 | 8 | 19 | 32004.1694
2029 | 2008 | 5 | 8 | 20 | 13406.2403
2029 | 2008 | 5 | 8 | 21 | 0
2029 | 2008 | 5 | 8 | 22 | 0
2029 | 2008 | 5 | 8 | 23 | 0
2029 | 2008 | 5 | 8 | 24 | 0
2029 | 2008 | 5 | 9 | 1 | 0
2029 | 2008 | 5 | 9 | 2 | 0
2029 | 2008 | 5 | 9 | 3 | 0
2029 | 2008 | 5 | 9 | 4 | 0
2029 | 2008 | 5 | 9 | 5 | 0
2029 | 2008 | 5 | 9 | 6 | 0
2029 | 2008 | 5 | 9 | 7 | 11.6492
2029 | 2008 | 5 | 9 | 8 | 9693.9404
2029 | 2008 | 5 | 9 | 9 | 33417.3951
2029 | 2008 | 5 | 9 | 10 | 42370.2754
2029 | 2008 | 5 | 9 | 11 | 48553.0373
2029 | 2008 | 5 | 9 | 12 | 50824.2809
2029 | 2008 | 5 | 9 | 13 | 54794.9716
2029 | 2008 | 5 | 9 | 14 | 54700.3366
2029 | 2008 | 5 | 9 | 15 | 52863.5448
2029 | 2008 | 5 | 9 | 16 | 50556.6803
2029 | 2008 | 5 | 9 | 17 | 47766.1699
2029 | 2008 | 5 | 9 | 18 | 42379.3193
2029 | 2008 | 5 | 9 | 19 | 30641.6509
2029 | 2008 | 5 | 9 | 20 | 12241.816
2029 | 2008 | 5 | 9 | 21 | 0
2029 | 2008 | 5 | 9 | 22 | 0
2029 | 2008 | 5 | 9 | 23 | 0
2029 | 2008 | 5 | 9 | 24 | 0
2029 | 2008 | 5 | 10 | 1 | 0
2029 | 2008 | 5 | 10 | 2 | 0
2029 | 2008 | 5 | 10 | 3 | 0
2029 | 2008 | 5 | 10 | 4 | 0
2029 | 2008 | 5 | 10 | 5 | 0
2029 | 2008 | 5 | 10 | 6 | 0
2029 | 2008 | 5 | 10 | 7 | 0.7841
2029 | 2008 | 5 | 10 | 8 | 5499.1248
2029 | 2008 | 5 | 10 | 9 | 25590.8676
2029 | 2008 | 5 | 10 | 10 | 35400.5432
2029 | 2008 | 5 | 10 | 11 | 41975.1169
2029 | 2008 | 5 | 10 | 12 | 50098.614
2029 | 2008 | 5 | 10 | 13 | 53451.3844
2029 | 2008 | 5 | 10 | 14 | 54581.2681
2029 | 2008 | 5 | 10 | 15 | 51193.4619
2029 | 2008 | 5 | 10 | 16 | 49332.9915
2029 | 2008 | 5 | 10 | 17 | 43313.6047
2029 | 2008 | 5 | 10 | 18 | 38851.0732
2029 | 2008 | 5 | 10 | 19 | 30460.407
2029 | 2008 | 5 | 10 | 20 | 11431.704
2029 | 2008 | 5 | 10 | 21 | 0
2029 | 2008 | 5 | 10 | 22 | 0
2029 | 2008 | 5 | 10 | 23 | 0
2029 | 2008 | 5 | 10 | 24 | 0
2029 | 2008 | 5 | 11 | 1 | 0
2029 | 2008 | 5 | 11 | 2 | 0
2029 | 2008 | 5 | 11 | 3 | 0
2029 | 2008 | 5 | 11 | 4 | 0
2029 | 2008 | 5 | 11 | 5 | 0
2029 | 2008 | 5 | 11 | 6 | 0
2029 | 2008 | 5 | 11 | 7 | 21.0823
2029 | 2008 | 5 | 11 | 8 | 14150.2717
2029 | 2008 | 5 | 11 | 9 | 42592.2682
2029 | 2008 | 5 | 11 | 10 | 49987.1891
2029 | 2008 | 5 | 11 | 11 | 53079.6589
2029 | 2008 | 5 | 11 | 12 | 54279.7224
2029 | 2008 | 5 | 11 | 13 | 54618.0915
2029 | 2008 | 5 | 11 | 14 | 55535.4984
2029 | 2008 | 5 | 11 | 15 | 52581.4473
2029 | 2008 | 5 | 11 | 16 | 50310.8009
2029 | 2008 | 5 | 11 | 17 | 46779.8885
2029 | 2008 | 5 | 11 | 18 | 41260.8892
2029 | 2008 | 5 | 11 | 19 | 32145.5511
2029 | 2008 | 5 | 11 | 20 | 12508.0683
2029 | 2008 | 5 | 11 | 21 | 0
2029 | 2008 | 5 | 11 | 22 | 0
2029 | 2008 | 5 | 11 | 23 | 0
2029 | 2008 | 5 | 11 | 24 | 0
2029 | 2008 | 5 | 12 | 1 | 0
2029 | 2008 | 5 | 12 | 2 | 0
2029 | 2008 | 5 | 12 | 3 | 0
2029 | 2008 | 5 | 12 | 4 | 0
2029 | 2008 | 5 | 12 | 5 | 0
2029 | 2008 | 5 | 12 | 6 | 0
2029 | 2008 | 5 | 12 | 7 | 22.4307
2029 | 2008 | 5 | 12 | 8 | 13367.518
2029 | 2008 | 5 | 12 | 9 | 38701.2491
2029 | 2008 | 5 | 12 | 10 | 48677.3897
2029 | 2008 | 5 | 12 | 11 | 50518.5807
2029 | 2008 | 5 | 12 | 12 | 52378.842
2029 | 2008 | 5 | 12 | 13 | 52171.4162
2029 | 2008 | 5 | 12 | 14 | 54788.6298
2029 | 2008 | 5 | 12 | 15 | 53186.8225
2029 | 2008 | 5 | 12 | 16 | 50798.6134
2029 | 2008 | 5 | 12 | 17 | 47224.6923
2029 | 2008 | 5 | 12 | 18 | 39709.5467
2029 | 2008 | 5 | 12 | 19 | 31174.1897
2029 | 2008 | 5 | 12 | 20 | 10344.8141
2029 | 2008 | 5 | 12 | 21 | 0
2029 | 2008 | 5 | 12 | 22 | 0
2029 | 2008 | 5 | 12 | 23 | 0
2029 | 2008 | 5 | 12 | 24 | 0
2029 | 2008 | 5 | 13 | 1 | 0
2029 | 2008 | 5 | 13 | 2 | 0
2029 | 2008 | 5 | 13 | 3 | 0
2029 | 2008 | 5 | 13 | 4 | 0
2029 | 2008 | 5 | 13 | 5 | 0
2029 | 2008 | 5 | 13 | 6 | 0
2029 | 2008 | 5 | 13 | 7 | 0.19935
2029 | 2008 | 5 | 13 | 8 | 2393.0384
2029 | 2008 | 5 | 13 | 9 | 13655.4472
2029 | 2008 | 5 | 13 | 10 | 23283.6467
2029 | 2008 | 5 | 13 | 11 | 31804.806
2029 | 2008 | 5 | 13 | 12 | 38498.2509
2029 | 2008 | 5 | 13 | 13 | 40778.2922
2029 | 2008 | 5 | 13 | 14 | 42879.7919
2029 | 2008 | 5 | 13 | 15 | 44907.1541
2029 | 2008 | 5 | 13 | 16 | 44173.7157
2029 | 2008 | 5 | 13 | 17 | 39171.6022
2029 | 2008 | 5 | 13 | 18 | 38559.9033
2029 | 2008 | 5 | 13 | 19 | 29635.5908
2029 | 2008 | 5 | 13 | 20 | 10655.4116
2029 | 2008 | 5 | 13 | 21 | 0
2029 | 2008 | 5 | 13 | 22 | 0
2029 | 2008 | 5 | 13 | 23 | 0
2029 | 2008 | 5 | 13 | 24 | 0
2029 | 2008 | 5 | 14 | 1 | 0
2029 | 2008 | 5 | 14 | 2 | 0
2029 | 2008 | 5 | 14 | 3 | 0
2029 | 2008 | 5 | 14 | 4 | 0
2029 | 2008 | 5 | 14 | 5 | 0
2029 | 2008 | 5 | 14 | 6 | 0
2029 | 2008 | 5 | 14 | 7 | 1.4897
2029 | 2008 | 5 | 14 | 8 | 3967.3232
2029 | 2008 | 5 | 14 | 9 | 16255.6587
2029 | 2008 | 5 | 14 | 10 | 24367.6339
2029 | 2008 | 5 | 14 | 11 | 28188.3477
2029 | 2008 | 5 | 14 | 12 | 35657.164
2029 | 2008 | 5 | 14 | 13 | 40193.5534
2029 | 2008 | 5 | 14 | 14 | 41162.6747
2029 | 2008 | 5 | 14 | 15 | 38730.3249
2029 | 2008 | 5 | 14 | 16 | 36838.5243
2029 | 2008 | 5 | 14 | 17 | 34099.8271
2029 | 2008 | 5 | 14 | 18 | 29909.3693
2029 | 2008 | 5 | 14 | 19 | 25529.3847
2029 | 2008 | 5 | 14 | 20 | 10407.1697
2029 | 2008 | 5 | 14 | 21 | 8.797
2029 | 2008 | 5 | 14 | 22 | 0
2029 | 2008 | 5 | 14 | 23 | 0
2029 | 2008 | 5 | 14 | 24 | 0
2029 | 2008 | 5 | 15 | 1 | 0
2029 | 2008 | 5 | 15 | 2 | 0
2029 | 2008 | 5 | 15 | 3 | 0
2029 | 2008 | 5 | 15 | 4 | 0
2029 | 2008 | 5 | 15 | 5 | 0
2029 | 2008 | 5 | 15 | 6 | 0
2029 | 2008 | 5 | 15 | 7 | 0.18588
2029 | 2008 | 5 | 15 | 8 | 4168.7634
2029 | 2008 | 5 | 15 | 9 | 23110.3428
2029 | 2008 | 5 | 15 | 10 | 40279.3502
2029 | 2008 | 5 | 15 | 11 | 47087.992
2029 | 2008 | 5 | 15 | 12 | 49817.4263
2029 | 2008 | 5 | 15 | 13 | 50358.3587
2029 | 2008 | 5 | 15 | 14 | 48122.2259
2029 | 2008 | 5 | 15 | 15 | 45719.9267
2029 | 2008 | 5 | 15 | 16 | 41632.1246
2029 | 2008 | 5 | 15 | 17 | 37477.7487
2029 | 2008 | 5 | 15 | 18 | 35019.2796
2029 | 2008 | 5 | 15 | 19 | 27317.2836
2029 | 2008 | 5 | 15 | 20 | 10089.5034
2029 | 2008 | 5 | 15 | 21 | 19.971
2029 | 2008 | 5 | 15 | 22 | 0
2029 | 2008 | 5 | 15 | 23 | 0
2029 | 2008 | 5 | 15 | 24 | 0
2029 | 2008 | 5 | 16 | 1 | 0
2029 | 2008 | 5 | 16 | 2 | 0
2029 | 2008 | 5 | 16 | 3 | 0
2029 | 2008 | 5 | 16 | 4 | 0
2029 | 2008 | 5 | 16 | 5 | 0
2029 | 2008 | 5 | 16 | 6 | 0
2029 | 2008 | 5 | 16 | 7 | 19.2342
2029 | 2008 | 5 | 16 | 8 | 8080.5276
2029 | 2008 | 5 | 16 | 9 | 26846.366
2029 | 2008 | 5 | 16 | 10 | 39091.3065
2029 | 2008 | 5 | 16 | 11 | 44763.7611
2029 | 2008 | 5 | 16 | 12 | 49601.6735
2029 | 2008 | 5 | 16 | 13 | 52514.9107
2029 | 2008 | 5 | 16 | 14 | 54568.6793
2029 | 2008 | 5 | 16 | 15 | 52992.855
2029 | 2008 | 5 | 16 | 16 | 50896.0385
2029 | 2008 | 5 | 16 | 17 | 46756.8693
2029 | 2008 | 5 | 16 | 18 | 44073.9772
2029 | 2008 | 5 | 16 | 19 | 32030.9889
2029 | 2008 | 5 | 16 | 20 | 9811.4201
2029 | 2008 | 5 | 16 | 21 | 20.0071
2029 | 2008 | 5 | 16 | 22 | 0
2029 | 2008 | 5 | 16 | 23 | 0
2029 | 2008 | 5 | 16 | 24 | 0
2029 | 2008 | 5 | 17 | 1 | 0
2029 | 2008 | 5 | 17 | 2 | 0
2029 | 2008 | 5 | 17 | 3 | 0
2029 | 2008 | 5 | 17 | 4 | 0
2029 | 2008 | 5 | 17 | 5 | 0
2029 | 2008 | 5 | 17 | 6 | 0
2029 | 2008 | 5 | 17 | 7 | 20.8243
2029 | 2008 | 5 | 17 | 8 | 9854.8926
2029 | 2008 | 5 | 17 | 9 | 34328.5733
2029 | 2008 | 5 | 17 | 10 | 46917.7066
2029 | 2008 | 5 | 17 | 11 | 48829.1253
2029 | 2008 | 5 | 17 | 12 | 48813.3224
2029 | 2008 | 5 | 17 | 13 | 46249.5606
2029 | 2008 | 5 | 17 | 14 | 45153.935
2029 | 2008 | 5 | 17 | 15 | 42497.2907
2029 | 2008 | 5 | 17 | 16 | 39322.4195
2029 | 2008 | 5 | 17 | 17 | 34353.2617
2029 | 2008 | 5 | 17 | 18 | 34006.2725
2029 | 2008 | 5 | 17 | 19 | 29562.7635
2029 | 2008 | 5 | 17 | 20 | 11197.1564
2029 | 2008 | 5 | 17 | 21 | 32.9858
2029 | 2008 | 5 | 17 | 22 | 0
2029 | 2008 | 5 | 17 | 23 | 0
2029 | 2008 | 5 | 17 | 24 | 0
2029 | 2008 | 5 | 18 | 1 | 0
2029 | 2008 | 5 | 18 | 2 | 0
2029 | 2008 | 5 | 18 | 3 | 0
2029 | 2008 | 5 | 18 | 4 | 0
2029 | 2008 | 5 | 18 | 5 | 0
2029 | 2008 | 5 | 18 | 6 | 0
2029 | 2008 | 5 | 18 | 7 | 43.7616
2029 | 2008 | 5 | 18 | 8 | 17854.8646
2029 | 2008 | 5 | 18 | 9 | 48957.7742
2029 | 2008 | 5 | 18 | 10 | 56711.0215
2029 | 2008 | 5 | 18 | 11 | 56676.5116
2029 | 2008 | 5 | 18 | 12 | 55132.2242
2029 | 2008 | 5 | 18 | 13 | 55851.8981
2029 | 2008 | 5 | 18 | 14 | 56577.0374
2029 | 2008 | 5 | 18 | 15 | 54541.735
2029 | 2008 | 5 | 18 | 16 | 53101.4924
2029 | 2008 | 5 | 18 | 17 | 50099.6742
2029 | 2008 | 5 | 18 | 18 | 47133.2465
2029 | 2008 | 5 | 18 | 19 | 33211.8546
2029 | 2008 | 5 | 18 | 20 | 12176.4879
2029 | 2008 | 5 | 18 | 21 | 67.2796
2029 | 2008 | 5 | 18 | 22 | 0
2029 | 2008 | 5 | 18 | 23 | 0
2029 | 2008 | 5 | 18 | 24 | 0
2029 | 2008 | 5 | 19 | 1 | 0
2029 | 2008 | 5 | 19 | 2 | 0
2029 | 2008 | 5 | 19 | 3 | 0
2029 | 2008 | 5 | 19 | 4 | 0
2029 | 2008 | 5 | 19 | 5 | 0
2029 | 2008 | 5 | 19 | 6 | 0
2029 | 2008 | 5 | 19 | 7 | 34.175
2029 | 2008 | 5 | 19 | 8 | 17791.0005
2029 | 2008 | 5 | 19 | 9 | 50271.5831
2029 | 2008 | 5 | 19 | 10 | 57773.9336
2029 | 2008 | 5 | 19 | 11 | 56165.028
2029 | 2008 | 5 | 19 | 12 | 55848.9368
2029 | 2008 | 5 | 19 | 13 | 56349.424
2029 | 2008 | 5 | 19 | 14 | 55679.2658
2029 | 2008 | 5 | 19 | 15 | 54105.536
2029 | 2008 | 5 | 19 | 16 | 53001.6936
2029 | 2008 | 5 | 19 | 17 | 49717.8303
2029 | 2008 | 5 | 19 | 18 | 45656.2357
2029 | 2008 | 5 | 19 | 19 | 33965.5161
2029 | 2008 | 5 | 19 | 20 | 12310.398
2029 | 2008 | 5 | 19 | 21 | 140.7847
2029 | 2008 | 5 | 19 | 22 | 0
2029 | 2008 | 5 | 19 | 23 | 0
2029 | 2008 | 5 | 19 | 24 | 0
2029 | 2008 | 5 | 20 | 1 | 0
2029 | 2008 | 5 | 20 | 2 | 0
2029 | 2008 | 5 | 20 | 3 | 0
2029 | 2008 | 5 | 20 | 4 | 0
2029 | 2008 | 5 | 20 | 5 | 0
2029 | 2008 | 5 | 20 | 6 | 0
2029 | 2008 | 5 | 20 | 7 | 38.4267
2029 | 2008 | 5 | 20 | 8 | 15845.8291
2029 | 2008 | 5 | 20 | 9 | 41724.6274
2029 | 2008 | 5 | 20 | 10 | 50475.6763
2029 | 2008 | 5 | 20 | 11 | 53306.093
2029 | 2008 | 5 | 20 | 12 | 54265.461
2029 | 2008 | 5 | 20 | 13 | 54991.9239
2029 | 2008 | 5 | 20 | 14 | 55146.8428
2029 | 2008 | 5 | 20 | 15 | 53239.1639
2029 | 2008 | 5 | 20 | 16 | 51052.8724
2029 | 2008 | 5 | 20 | 17 | 49597.3303
2029 | 2008 | 5 | 20 | 18 | 46803.3389
2029 | 2008 | 5 | 20 | 19 | 32835.5795
2029 | 2008 | 5 | 20 | 20 | 11673.7415
2029 | 2008 | 5 | 20 | 21 | 154.3178
2029 | 2008 | 5 | 20 | 22 | 0
2029 | 2008 | 5 | 20 | 23 | 0
2029 | 2008 | 5 | 20 | 24 | 0
2029 | 2008 | 5 | 21 | 1 | 0
2029 | 2008 | 5 | 21 | 2 | 0
2029 | 2008 | 5 | 21 | 3 | 0
2029 | 2008 | 5 | 21 | 4 | 0
2029 | 2008 | 5 | 21 | 5 | 0
2029 | 2008 | 5 | 21 | 6 | 0
2029 | 2008 | 5 | 21 | 7 | 30.238
2029 | 2008 | 5 | 21 | 8 | 7089.5538
2029 | 2008 | 5 | 21 | 9 | 25273.3815
2029 | 2008 | 5 | 21 | 10 | 35433.9096
2029 | 2008 | 5 | 21 | 11 | 42299.3514
2029 | 2008 | 5 | 21 | 12 | 53120.0884
2029 | 2008 | 5 | 21 | 13 | 55108.8291
2029 | 2008 | 5 | 21 | 14 | 55930.2593
2029 | 2008 | 5 | 21 | 15 | 53922.8159
2029 | 2008 | 5 | 21 | 16 | 52365.2164
2029 | 2008 | 5 | 21 | 17 | 49220.2267
2029 | 2008 | 5 | 21 | 18 | 44848.1585
2029 | 2008 | 5 | 21 | 19 | 32682.1299
2029 | 2008 | 5 | 21 | 20 | 11797.4301
2029 | 2008 | 5 | 21 | 21 | 139.6412
2029 | 2008 | 5 | 21 | 22 | 0
2029 | 2008 | 5 | 21 | 23 | 0
2029 | 2008 | 5 | 21 | 24 | 0
2029 | 2008 | 5 | 22 | 1 | 0
2029 | 2008 | 5 | 22 | 2 | 0
2029 | 2008 | 5 | 22 | 3 | 0
2029 | 2008 | 5 | 22 | 4 | 0
2029 | 2008 | 5 | 22 | 5 | 0
2029 | 2008 | 5 | 22 | 6 | 0
2029 | 2008 | 5 | 22 | 7 | 3.0327
2029 | 2008 | 5 | 22 | 8 | 4257.449
2029 | 2008 | 5 | 22 | 9 | 20937.5643
2029 | 2008 | 5 | 22 | 10 | 37536.081
2029 | 2008 | 5 | 22 | 11 | 46649.0276
2029 | 2008 | 5 | 22 | 12 | 52144.9445
2029 | 2008 | 5 | 22 | 13 | 54588.0847
2029 | 2008 | 5 | 22 | 14 | 54946.5682
2029 | 2008 | 5 | 22 | 15 | 52826.4312
2029 | 2008 | 5 | 22 | 16 | 49608.6382
2029 | 2008 | 5 | 22 | 17 | 46023.5536
2029 | 2008 | 5 | 22 | 18 | 41987.0359
2029 | 2008 | 5 | 22 | 19 | 33475.8261
2029 | 2008 | 5 | 22 | 20 | 12251.236
2029 | 2008 | 5 | 22 | 21 | 254.0206
2029 | 2008 | 5 | 22 | 22 | 0
2029 | 2008 | 5 | 22 | 23 | 0
2029 | 2008 | 5 | 22 | 24 | 0
2029 | 2008 | 5 | 23 | 1 | 0
2029 | 2008 | 5 | 23 | 2 | 0
2029 | 2008 | 5 | 23 | 3 | 0
2029 | 2008 | 5 | 23 | 4 | 0
2029 | 2008 | 5 | 23 | 5 | 0
2029 | 2008 | 5 | 23 | 6 | 0
2029 | 2008 | 5 | 23 | 7 | 4.8648
2029 | 2008 | 5 | 23 | 8 | 5563.259
2029 | 2008 | 5 | 23 | 9 | 24614.83
2029 | 2008 | 5 | 23 | 10 | 39843.8768
2029 | 2008 | 5 | 23 | 11 | 50010.3939
2029 | 2008 | 5 | 23 | 12 | 53725.7084
2029 | 2008 | 5 | 23 | 13 | 54546.6323
2029 | 2008 | 5 | 23 | 14 | 55849.9413
2029 | 2008 | 5 | 23 | 15 | 54482.751
2029 | 2008 | 5 | 23 | 16 | 52166.8977
2029 | 2008 | 5 | 23 | 17 | 49613.8478
2029 | 2008 | 5 | 23 | 18 | 46047.5305
2029 | 2008 | 5 | 23 | 19 | 33772.5664
2029 | 2008 | 5 | 23 | 20 | 11739.696
2029 | 2008 | 5 | 23 | 21 | 323.5711
2029 | 2008 | 5 | 23 | 22 | 0
2029 | 2008 | 5 | 23 | 23 | 0
2029 | 2008 | 5 | 23 | 24 | 0
2029 | 2008 | 5 | 24 | 1 | 0
2029 | 2008 | 5 | 24 | 2 | 0
2029 | 2008 | 5 | 24 | 3 | 0
2029 | 2008 | 5 | 24 | 4 | 0
2029 | 2008 | 5 | 24 | 5 | 0
2029 | 2008 | 5 | 24 | 6 | 0
2029 | 2008 | 5 | 24 | 7 | 5.9061
2029 | 2008 | 5 | 24 | 8 | 4994.9887
2029 | 2008 | 5 | 24 | 9 | 20483.0521
2029 | 2008 | 5 | 24 | 10 | 33609.3952
2029 | 2008 | 5 | 24 | 11 | 50653.5467
2029 | 2008 | 5 | 24 | 12 | 54073.8244
2029 | 2008 | 5 | 24 | 13 | 55842.2362
2029 | 2008 | 5 | 24 | 14 | 55400.9303
2029 | 2008 | 5 | 24 | 15 | 54288.9577
2029 | 2008 | 5 | 24 | 16 | 52694.3861
2029 | 2008 | 5 | 24 | 17 | 49693.2843
2029 | 2008 | 5 | 24 | 18 | 44097.5715
2029 | 2008 | 5 | 24 | 19 | 33075.3522
2029 | 2008 | 5 | 24 | 20 | 12436.8922
2029 | 2008 | 5 | 24 | 21 | 439.9825
2029 | 2008 | 5 | 24 | 22 | 0
2029 | 2008 | 5 | 24 | 23 | 0
2029 | 2008 | 5 | 24 | 24 | 0
2029 | 2008 | 5 | 25 | 1 | 0
2029 | 2008 | 5 | 25 | 2 | 0
2029 | 2008 | 5 | 25 | 3 | 0
2029 | 2008 | 5 | 25 | 4 | 0
2029 | 2008 | 5 | 25 | 5 | 0
2029 | 2008 | 5 | 25 | 6 | 0
2029 | 2008 | 5 | 25 | 7 | 7.3296
2029 | 2008 | 5 | 25 | 8 | 4024.2987
2029 | 2008 | 5 | 25 | 9 | 14611.9171
2029 | 2008 | 5 | 25 | 10 | 33852.7025
2029 | 2008 | 5 | 25 | 11 | 46951.7077
2029 | 2008 | 5 | 25 | 12 | 54095.2123
2029 | 2008 | 5 | 25 | 13 | 55059.8317
2029 | 2008 | 5 | 25 | 14 | 56047.7935
2029 | 2008 | 5 | 25 | 15 | 54769.8288
2029 | 2008 | 5 | 25 | 16 | 51819.676
2029 | 2008 | 5 | 25 | 17 | 49878.0917
2029 | 2008 | 5 | 25 | 18 | 45111.1463
2029 | 2008 | 5 | 25 | 19 | 33278.9704
2029 | 2008 | 5 | 25 | 20 | 12372.4613
2029 | 2008 | 5 | 25 | 21 | 567.867
2029 | 2008 | 5 | 25 | 22 | 0
2029 | 2008 | 5 | 25 | 23 | 0
2029 | 2008 | 5 | 25 | 24 | 0
2029 | 2008 | 5 | 26 | 1 | 0
2029 | 2008 | 5 | 26 | 2 | 0
2029 | 2008 | 5 | 26 | 3 | 0
2029 | 2008 | 5 | 26 | 4 | 0
2029 | 2008 | 5 | 26 | 5 | 0
2029 | 2008 | 5 | 26 | 6 | 0
2029 | 2008 | 5 | 26 | 7 | 12.3992
2029 | 2008 | 5 | 26 | 8 | 3784.5114
2029 | 2008 | 5 | 26 | 9 | 16740.2322
2029 | 2008 | 5 | 26 | 10 | 40491.4453
2029 | 2008 | 5 | 26 | 11 | 49463.451
2029 | 2008 | 5 | 26 | 12 | 53386.8981
2029 | 2008 | 5 | 26 | 13 | 55564.0239
2029 | 2008 | 5 | 26 | 14 | 54625.3193
2029 | 2008 | 5 | 26 | 15 | 54602.0782
2029 | 2008 | 5 | 26 | 16 | 52385.3689
2029 | 2008 | 5 | 26 | 17 | 49745.0688
2029 | 2008 | 5 | 26 | 18 | 44333.0528
2029 | 2008 | 5 | 26 | 19 | 32144.9265
2029 | 2008 | 5 | 26 | 20 | 11351.403
2029 | 2008 | 5 | 26 | 21 | 599.8187
2029 | 2008 | 5 | 26 | 22 | 0
2029 | 2008 | 5 | 26 | 23 | 0
2029 | 2008 | 5 | 26 | 24 | 0
2029 | 2008 | 5 | 27 | 1 | 0
2029 | 2008 | 5 | 27 | 2 | 0
2029 | 2008 | 5 | 27 | 3 | 0
2029 | 2008 | 5 | 27 | 4 | 0
2029 | 2008 | 5 | 27 | 5 | 0
2029 | 2008 | 5 | 27 | 6 | 0
2029 | 2008 | 5 | 27 | 7 | 5.6416
2029 | 2008 | 5 | 27 | 8 | 3999.8598
2029 | 2008 | 5 | 27 | 9 | 19413.4422
2029 | 2008 | 5 | 27 | 10 | 35065.9175
2029 | 2008 | 5 | 27 | 11 | 49476.6608
2029 | 2008 | 5 | 27 | 12 | 53677.177
2029 | 2008 | 5 | 27 | 13 | 54515.4999
2029 | 2008 | 5 | 27 | 14 | 54473.302
2029 | 2008 | 5 | 27 | 15 | 54352.3572
2029 | 2008 | 5 | 27 | 16 | 51784.9475
2029 | 2008 | 5 | 27 | 17 | 48560.4392
2029 | 2008 | 5 | 27 | 18 | 44128.7318
2029 | 2008 | 5 | 27 | 19 | 33241.8278
2029 | 2008 | 5 | 27 | 20 | 12249.7752
2029 | 2008 | 5 | 27 | 21 | 646.9833
2029 | 2008 | 5 | 27 | 22 | 0
2029 | 2008 | 5 | 27 | 23 | 0
2029 | 2008 | 5 | 27 | 24 | 0
2029 | 2008 | 5 | 28 | 1 | 0
2029 | 2008 | 5 | 28 | 2 | 0
2029 | 2008 | 5 | 28 | 3 | 0
2029 | 2008 | 5 | 28 | 4 | 0
2029 | 2008 | 5 | 28 | 5 | 0
2029 | 2008 | 5 | 28 | 6 | 0
2029 | 2008 | 5 | 28 | 7 | 40.5889
2029 | 2008 | 5 | 28 | 8 | 9092.6496
2029 | 2008 | 5 | 28 | 9 | 25612.9375
2029 | 2008 | 5 | 28 | 10 | 36949.3683
2029 | 2008 | 5 | 28 | 11 | 45172.5227
2029 | 2008 | 5 | 28 | 12 | 49420.3977
2029 | 2008 | 5 | 28 | 13 | 50246.1985
2029 | 2008 | 5 | 28 | 14 | 52489.1979
2029 | 2008 | 5 | 28 | 15 | 51753.4579
2029 | 2008 | 5 | 28 | 16 | 45980.3803
2029 | 2008 | 5 | 28 | 17 | 46084.8909
2029 | 2008 | 5 | 28 | 18 | 41475.9732
2029 | 2008 | 5 | 28 | 19 | 33060.2697
2029 | 2008 | 5 | 28 | 20 | 13057.8828
2029 | 2008 | 5 | 28 | 21 | 763.6106
2029 | 2008 | 5 | 28 | 22 | 0
2029 | 2008 | 5 | 28 | 23 | 0
2029 | 2008 | 5 | 28 | 24 | 0
2029 | 2008 | 5 | 29 | 1 | 0
2029 | 2008 | 5 | 29 | 2 | 0
2029 | 2008 | 5 | 29 | 3 | 0
2029 | 2008 | 5 | 29 | 4 | 0
2029 | 2008 | 5 | 29 | 5 | 0
2029 | 2008 | 5 | 29 | 6 | 0
2029 | 2008 | 5 | 29 | 7 | 34.994
2029 | 2008 | 5 | 29 | 8 | 14144.5096
2029 | 2008 | 5 | 29 | 9 | 38265.6097
2029 | 2008 | 5 | 29 | 10 | 48336.1045
2029 | 2008 | 5 | 29 | 11 | 51408.7676
2029 | 2008 | 5 | 29 | 12 | 51451.6522
2029 | 2008 | 5 | 29 | 13 | 51848.7738
2029 | 2008 | 5 | 29 | 14 | 51405.5265
2029 | 2008 | 5 | 29 | 15 | 51913.7074
2029 | 2008 | 5 | 29 | 16 | 50471.0127
2029 | 2008 | 5 | 29 | 17 | 46791.4833
2029 | 2008 | 5 | 29 | 18 | 43176.282
2029 | 2008 | 5 | 29 | 19 | 33297.8516
2029 | 2008 | 5 | 29 | 20 | 11870.2362
2029 | 2008 | 5 | 29 | 21 | 719.3783
2029 | 2008 | 5 | 29 | 22 | 0
2029 | 2008 | 5 | 29 | 23 | 0
2029 | 2008 | 5 | 29 | 24 | 0
2029 | 2008 | 5 | 30 | 1 | 0
2029 | 2008 | 5 | 30 | 2 | 0
2029 | 2008 | 5 | 30 | 3 | 0
2029 | 2008 | 5 | 30 | 4 | 0
2029 | 2008 | 5 | 30 | 5 | 0
2029 | 2008 | 5 | 30 | 6 | 0
2029 | 2008 | 5 | 30 | 7 | 55.0789
2029 | 2008 | 5 | 30 | 8 | 15713.5488
2029 | 2008 | 5 | 30 | 9 | 43320.0206
2029 | 2008 | 5 | 30 | 10 | 53916.1017
2029 | 2008 | 5 | 30 | 11 | 56037.4933
2029 | 2008 | 5 | 30 | 12 | 53703.2936
2029 | 2008 | 5 | 30 | 13 | 55192.4934
2029 | 2008 | 5 | 30 | 14 | 55796.2914
2029 | 2008 | 5 | 30 | 15 | 54892.0509
2029 | 2008 | 5 | 30 | 16 | 52658.5915
2029 | 2008 | 5 | 30 | 17 | 49320.5884
2029 | 2008 | 5 | 30 | 18 | 45932.7361
2029 | 2008 | 5 | 30 | 19 | 33124.6559
2029 | 2008 | 5 | 30 | 20 | 13315.7078
2029 | 2008 | 5 | 30 | 21 | 931.6545
2029 | 2008 | 5 | 30 | 22 | 0
2029 | 2008 | 5 | 30 | 23 | 0
2029 | 2008 | 5 | 30 | 24 | 0
2029 | 2008 | 5 | 31 | 1 | 0
2029 | 2008 | 5 | 31 | 2 | 0
2029 | 2008 | 5 | 31 | 3 | 0
2029 | 2008 | 5 | 31 | 4 | 0
2029 | 2008 | 5 | 31 | 5 | 0
2029 | 2008 | 5 | 31 | 6 | 0
2029 | 2008 | 5 | 31 | 7 | 48.7982
2029 | 2008 | 5 | 31 | 8 | 10679.7273
2029 | 2008 | 5 | 31 | 9 | 31719.8476
2029 | 2008 | 5 | 31 | 10 | 41273.3923
2029 | 2008 | 5 | 31 | 11 | 51383.0523
2029 | 2008 | 5 | 31 | 12 | 53579.9033
2029 | 2008 | 5 | 31 | 13 | 53453.2472
2029 | 2008 | 5 | 31 | 14 | 53708.5725
2029 | 2008 | 5 | 31 | 15 | 52819.2597
2029 | 2008 | 5 | 31 | 16 | 51630.7924
2029 | 2008 | 5 | 31 | 17 | 49628.5155
2029 | 2008 | 5 | 31 | 18 | 45292.3384
2029 | 2008 | 5 | 31 | 19 | 34361.1501
2029 | 2008 | 5 | 31 | 20 | 13994.841
2029 | 2008 | 5 | 31 | 21 | 439.3671
2029 | 2008 | 5 | 31 | 22 | 0
2029 | 2008 | 5 | 31 | 23 | 0
2029 | 2008 | 5 | 31 | 24 | 0
2030 | 2008 | 5 | 1 | 1 | 0
2030 | 2008 | 5 | 1 | 2 | 0
2030 | 2008 | 5 | 1 | 3 | 0
2030 | 2008 | 5 | 1 | 4 | 0
2030 | 2008 | 5 | 1 | 5 | 0
2030 | 2008 | 5 | 1 | 6 | 0
2030 | 2008 | 5 | 1 | 7 | 0.040681
2030 | 2008 | 5 | 1 | 8 | 3828.8917
2030 | 2008 | 5 | 1 | 9 | 23734.9334
2030 | 2008 | 5 | 1 | 10 | 32846.8636
2030 | 2008 | 5 | 1 | 11 | 34567.59
2030 | 2008 | 5 | 1 | 12 | 37603.7453
2030 | 2008 | 5 | 1 | 13 | 41077.4384
2030 | 2008 | 5 | 1 | 14 | 44623.8623
2030 | 2008 | 5 | 1 | 15 | 47189.8981
2030 | 2008 | 5 | 1 | 16 | 42244.306
2030 | 2008 | 5 | 1 | 17 | 43850.246
2030 | 2008 | 5 | 1 | 18 | 42125.8376
2030 | 2008 | 5 | 1 | 19 | 32218.5505
2030 | 2008 | 5 | 1 | 20 | 12783.4344
2030 | 2008 | 5 | 1 | 21 | 0
2030 | 2008 | 5 | 1 | 22 | 0
2030 | 2008 | 5 | 1 | 23 | 0
2030 | 2008 | 5 | 1 | 24 | 0
2030 | 2008 | 5 | 2 | 1 | 0
2030 | 2008 | 5 | 2 | 2 | 0
2030 | 2008 | 5 | 2 | 3 | 0
2030 | 2008 | 5 | 2 | 4 | 0
2030 | 2008 | 5 | 2 | 5 | 0
2030 | 2008 | 5 | 2 | 6 | 0
2030 | 2008 | 5 | 2 | 7 | 0.4491
2030 | 2008 | 5 | 2 | 8 | 6847.0754
2030 | 2008 | 5 | 2 | 9 | 33529.2898
2030 | 2008 | 5 | 2 | 10 | 41526.2211
2030 | 2008 | 5 | 2 | 11 | 46394.0849
2030 | 2008 | 5 | 2 | 12 | 48394.6463
2030 | 2008 | 5 | 2 | 13 | 50732.7553
2030 | 2008 | 5 | 2 | 14 | 53986.4191
2030 | 2008 | 5 | 2 | 15 | 50432.8744
2030 | 2008 | 5 | 2 | 16 | 50934.9983
2030 | 2008 | 5 | 2 | 17 | 48791.8663
2030 | 2008 | 5 | 2 | 18 | 44939.8676
2030 | 2008 | 5 | 2 | 19 | 34150.0891
2030 | 2008 | 5 | 2 | 20 | 13704.7286
2030 | 2008 | 5 | 2 | 21 | 0
2030 | 2008 | 5 | 2 | 22 | 0
2030 | 2008 | 5 | 2 | 23 | 0
2030 | 2008 | 5 | 2 | 24 | 0
2030 | 2008 | 5 | 3 | 1 | 0
2030 | 2008 | 5 | 3 | 2 | 0
2030 | 2008 | 5 | 3 | 3 | 0
2030 | 2008 | 5 | 3 | 4 | 0
2030 | 2008 | 5 | 3 | 5 | 0
2030 | 2008 | 5 | 3 | 6 | 0
2030 | 2008 | 5 | 3 | 7 | 5.3963
2030 | 2008 | 5 | 3 | 8 | 11334.389
2030 | 2008 | 5 | 3 | 9 | 39820.7261
2030 | 2008 | 5 | 3 | 10 | 49325.3695
2030 | 2008 | 5 | 3 | 11 | 49834.3716
2030 | 2008 | 5 | 3 | 12 | 54642.7859
2030 | 2008 | 5 | 3 | 13 | 55715.2723
2030 | 2008 | 5 | 3 | 14 | 56426.9978
2030 | 2008 | 5 | 3 | 15 | 55436.9553
2030 | 2008 | 5 | 3 | 16 | 53685.9374
2030 | 2008 | 5 | 3 | 17 | 49307.7764
2030 | 2008 | 5 | 3 | 18 | 45713.6042
2030 | 2008 | 5 | 3 | 19 | 34012.2403
2030 | 2008 | 5 | 3 | 20 | 13612.7271
2030 | 2008 | 5 | 3 | 21 | 0
2030 | 2008 | 5 | 3 | 22 | 0
2030 | 2008 | 5 | 3 | 23 | 0
2030 | 2008 | 5 | 3 | 24 | 0
2030 | 2008 | 5 | 4 | 1 | 0
2030 | 2008 | 5 | 4 | 2 | 0
2030 | 2008 | 5 | 4 | 3 | 0
2030 | 2008 | 5 | 4 | 4 | 0
2030 | 2008 | 5 | 4 | 5 | 0
2030 | 2008 | 5 | 4 | 6 | 0
2030 | 2008 | 5 | 4 | 7 | 6.1047
2030 | 2008 | 5 | 4 | 8 | 10783.7025
2030 | 2008 | 5 | 4 | 9 | 39476.1498
2030 | 2008 | 5 | 4 | 10 | 50954.6217
2030 | 2008 | 5 | 4 | 11 | 52067.6833
2030 | 2008 | 5 | 4 | 12 | 50901.616
2030 | 2008 | 5 | 4 | 13 | 49259.0479
2030 | 2008 | 5 | 4 | 14 | 49733.581
2030 | 2008 | 5 | 4 | 15 | 45869.5781
2030 | 2008 | 5 | 4 | 16 | 44527.5929
2030 | 2008 | 5 | 4 | 17 | 38353.4419
2030 | 2008 | 5 | 4 | 18 | 33804.432
2030 | 2008 | 5 | 4 | 19 | 26086.9597
2030 | 2008 | 5 | 4 | 20 | 10755.4371
2030 | 2008 | 5 | 4 | 21 | 0
2030 | 2008 | 5 | 4 | 22 | 0
2030 | 2008 | 5 | 4 | 23 | 0
2030 | 2008 | 5 | 4 | 24 | 0
2030 | 2008 | 5 | 5 | 1 | 0
2030 | 2008 | 5 | 5 | 2 | 0
2030 | 2008 | 5 | 5 | 3 | 0
2030 | 2008 | 5 | 5 | 4 | 0
2030 | 2008 | 5 | 5 | 5 | 0
2030 | 2008 | 5 | 5 | 6 | 0
2030 | 2008 | 5 | 5 | 7 | 4.6217
2030 | 2008 | 5 | 5 | 8 | 1445.7253
2030 | 2008 | 5 | 5 | 9 | 11360.7855
2030 | 2008 | 5 | 5 | 10 | 21007.3095
2030 | 2008 | 5 | 5 | 11 | 25790.981
2030 | 2008 | 5 | 5 | 12 | 30897.287
2030 | 2008 | 5 | 5 | 13 | 36540.1615
2030 | 2008 | 5 | 5 | 14 | 37456.8482
2030 | 2008 | 5 | 5 | 15 | 39099.8704
2030 | 2008 | 5 | 5 | 16 | 36806.5109
2030 | 2008 | 5 | 5 | 17 | 34850.2242
2030 | 2008 | 5 | 5 | 18 | 34611.4835
2030 | 2008 | 5 | 5 | 19 | 29437.3995
2030 | 2008 | 5 | 5 | 20 | 10419.4837
2030 | 2008 | 5 | 5 | 21 | 0
2030 | 2008 | 5 | 5 | 22 | 0
2030 | 2008 | 5 | 5 | 23 | 0
2030 | 2008 | 5 | 5 | 24 | 0
2030 | 2008 | 5 | 6 | 1 | 0
2030 | 2008 | 5 | 6 | 2 | 0
2030 | 2008 | 5 | 6 | 3 | 0
2030 | 2008 | 5 | 6 | 4 | 0
2030 | 2008 | 5 | 6 | 5 | 0
2030 | 2008 | 5 | 6 | 6 | 0
2030 | 2008 | 5 | 6 | 7 | 0.76052
2030 | 2008 | 5 | 6 | 8 | 922.4735
2030 | 2008 | 5 | 6 | 9 | 9000.6297
2030 | 2008 | 5 | 6 | 10 | 20631.7139
2030 | 2008 | 5 | 6 | 11 | 29050.7004
2030 | 2008 | 5 | 6 | 12 | 36093.7408
2030 | 2008 | 5 | 6 | 13 | 42762.4696
2030 | 2008 | 5 | 6 | 14 | 45942.4589
2030 | 2008 | 5 | 6 | 15 | 45504.2924
2030 | 2008 | 5 | 6 | 16 | 43525.0021
2030 | 2008 | 5 | 6 | 17 | 42971.582
2030 | 2008 | 5 | 6 | 18 | 41154.8517
2030 | 2008 | 5 | 6 | 19 | 29457.1681
2030 | 2008 | 5 | 6 | 20 | 11818.7409
2030 | 2008 | 5 | 6 | 21 | 0
2030 | 2008 | 5 | 6 | 22 | 0
2030 | 2008 | 5 | 6 | 23 | 0
2030 | 2008 | 5 | 6 | 24 | 0
2030 | 2008 | 5 | 7 | 1 | 0
2030 | 2008 | 5 | 7 | 2 | 0
2030 | 2008 | 5 | 7 | 3 | 0
2030 | 2008 | 5 | 7 | 4 | 0
2030 | 2008 | 5 | 7 | 5 | 0
2030 | 2008 | 5 | 7 | 6 | 0
2030 | 2008 | 5 | 7 | 7 | 0
2030 | 2008 | 5 | 7 | 8 | 3322.9811
2030 | 2008 | 5 | 7 | 9 | 19615.5615
2030 | 2008 | 5 | 7 | 10 | 32008.2715
2030 | 2008 | 5 | 7 | 11 | 38012.8277
2030 | 2008 | 5 | 7 | 12 | 39472.5787
2030 | 2008 | 5 | 7 | 13 | 42338.7331
2030 | 2008 | 5 | 7 | 14 | 49345.6454
2030 | 2008 | 5 | 7 | 15 | 48632.3922
2030 | 2008 | 5 | 7 | 16 | 46882.4977
2030 | 2008 | 5 | 7 | 17 | 44485.8513
2030 | 2008 | 5 | 7 | 18 | 43775.7269
2030 | 2008 | 5 | 7 | 19 | 33558.2666
2030 | 2008 | 5 | 7 | 20 | 12237.6141
2030 | 2008 | 5 | 7 | 21 | 0
2030 | 2008 | 5 | 7 | 22 | 0
2030 | 2008 | 5 | 7 | 23 | 0
2030 | 2008 | 5 | 7 | 24 | 0
2030 | 2008 | 5 | 8 | 1 | 0
2030 | 2008 | 5 | 8 | 2 | 0
2030 | 2008 | 5 | 8 | 3 | 0
2030 | 2008 | 5 | 8 | 4 | 0
2030 | 2008 | 5 | 8 | 5 | 0
2030 | 2008 | 5 | 8 | 6 | 0
2030 | 2008 | 5 | 8 | 7 | 11.6985
2030 | 2008 | 5 | 8 | 8 | 11700.983
2030 | 2008 | 5 | 8 | 9 | 37510.3597
2030 | 2008 | 5 | 8 | 10 | 47669.574
2030 | 2008 | 5 | 8 | 11 | 52475.5096
2030 | 2008 | 5 | 8 | 12 | 55696.3953
2030 | 2008 | 5 | 8 | 13 | 55074.5225
2030 | 2008 | 5 | 8 | 14 | 55591.7854
2030 | 2008 | 5 | 8 | 15 | 53837.9082
2030 | 2008 | 5 | 8 | 16 | 50627.7295
2030 | 2008 | 5 | 8 | 17 | 48003.8068
2030 | 2008 | 5 | 8 | 18 | 43671.5641
2030 | 2008 | 5 | 8 | 19 | 32278.7694
2030 | 2008 | 5 | 8 | 20 | 13492.3653
2030 | 2008 | 5 | 8 | 21 | 0
2030 | 2008 | 5 | 8 | 22 | 0
2030 | 2008 | 5 | 8 | 23 | 0
2030 | 2008 | 5 | 8 | 24 | 0
2030 | 2008 | 5 | 9 | 1 | 0
2030 | 2008 | 5 | 9 | 2 | 0
2030 | 2008 | 5 | 9 | 3 | 0
2030 | 2008 | 5 | 9 | 4 | 0
2030 | 2008 | 5 | 9 | 5 | 0
2030 | 2008 | 5 | 9 | 6 | 0
2030 | 2008 | 5 | 9 | 7 | 11.6492
2030 | 2008 | 5 | 9 | 8 | 9867.3404
2030 | 2008 | 5 | 9 | 9 | 33959.7576
2030 | 2008 | 5 | 9 | 10 | 42995.2754
2030 | 2008 | 5 | 9 | 11 | 49131.7623
2030 | 2008 | 5 | 9 | 12 | 51377.8934
2030 | 2008 | 5 | 9 | 13 | 55409.0716
2030 | 2008 | 5 | 9 | 14 | 55312.4116
2030 | 2008 | 5 | 9 | 15 | 53461.8323
2030 | 2008 | 5 | 9 | 16 | 51101.3678
2030 | 2008 | 5 | 9 | 17 | 48313.4199
2030 | 2008 | 5 | 9 | 18 | 42564.2318
2030 | 2008 | 5 | 9 | 19 | 30824.2384
2030 | 2008 | 5 | 9 | 20 | 12337.7035
2030 | 2008 | 5 | 9 | 21 | 0
2030 | 2008 | 5 | 9 | 22 | 0
2030 | 2008 | 5 | 9 | 23 | 0
2030 | 2008 | 5 | 9 | 24 | 0
2030 | 2008 | 5 | 10 | 1 | 0
2030 | 2008 | 5 | 10 | 2 | 0
2030 | 2008 | 5 | 10 | 3 | 0
2030 | 2008 | 5 | 10 | 4 | 0
2030 | 2008 | 5 | 10 | 5 | 0
2030 | 2008 | 5 | 10 | 6 | 0
2030 | 2008 | 5 | 10 | 7 | 0.7841
2030 | 2008 | 5 | 10 | 8 | 5525.1498
2030 | 2008 | 5 | 10 | 9 | 25973.9176
2030 | 2008 | 5 | 10 | 10 | 35891.2182
2030 | 2008 | 5 | 10 | 11 | 42574.9669
2030 | 2008 | 5 | 10 | 12 | 50692.764
2030 | 2008 | 5 | 10 | 13 | 54063.1594
2030 | 2008 | 5 | 10 | 14 | 55206.2681
2030 | 2008 | 5 | 10 | 15 | 51758.0119
2030 | 2008 | 5 | 10 | 16 | 49839.5915
2030 | 2008 | 5 | 10 | 17 | 43851.3297
2030 | 2008 | 5 | 10 | 18 | 39274.5732
2030 | 2008 | 5 | 10 | 19 | 30833.257
2030 | 2008 | 5 | 10 | 20 | 11548.4165
2030 | 2008 | 5 | 10 | 21 | 0
2030 | 2008 | 5 | 10 | 22 | 0
2030 | 2008 | 5 | 10 | 23 | 0
2030 | 2008 | 5 | 10 | 24 | 0
2030 | 2008 | 5 | 11 | 1 | 0
2030 | 2008 | 5 | 11 | 2 | 0
2030 | 2008 | 5 | 11 | 3 | 0
2030 | 2008 | 5 | 11 | 4 | 0
2030 | 2008 | 5 | 11 | 5 | 0
2030 | 2008 | 5 | 11 | 6 | 0
2030 | 2008 | 5 | 11 | 7 | 21.0823
2030 | 2008 | 5 | 11 | 8 | 14341.0467
2030 | 2008 | 5 | 11 | 9 | 43193.9682
2030 | 2008 | 5 | 11 | 10 | 50601.9266
2030 | 2008 | 5 | 11 | 11 | 53614.4339
2030 | 2008 | 5 | 11 | 12 | 54855.3474
2030 | 2008 | 5 | 11 | 13 | 55212.8415
2030 | 2008 | 5 | 11 | 14 | 56091.8359
2030 | 2008 | 5 | 11 | 15 | 53118.2598
2030 | 2008 | 5 | 11 | 16 | 50871.9259
2030 | 2008 | 5 | 11 | 17 | 47340.151
2030 | 2008 | 5 | 11 | 18 | 41758.0767
2030 | 2008 | 5 | 11 | 19 | 32532.0886
2030 | 2008 | 5 | 11 | 20 | 12603.5183
2030 | 2008 | 5 | 11 | 21 | 0
2030 | 2008 | 5 | 11 | 22 | 0
2030 | 2008 | 5 | 11 | 23 | 0
2030 | 2008 | 5 | 11 | 24 | 0
2030 | 2008 | 5 | 12 | 1 | 0
2030 | 2008 | 5 | 12 | 2 | 0
2030 | 2008 | 5 | 12 | 3 | 0
2030 | 2008 | 5 | 12 | 4 | 0
2030 | 2008 | 5 | 12 | 5 | 0
2030 | 2008 | 5 | 12 | 6 | 0
2030 | 2008 | 5 | 12 | 7 | 22.4307
2030 | 2008 | 5 | 12 | 8 | 13541.218
2030 | 2008 | 5 | 12 | 9 | 39210.3741
2030 | 2008 | 5 | 12 | 10 | 49302.3897
2030 | 2008 | 5 | 12 | 11 | 51076.1557
2030 | 2008 | 5 | 12 | 12 | 52978.6045
2030 | 2008 | 5 | 12 | 13 | 52784.4787
2030 | 2008 | 5 | 12 | 14 | 55389.2673
2030 | 2008 | 5 | 12 | 15 | 53751.085
2030 | 2008 | 5 | 12 | 16 | 51303.0134
2030 | 2008 | 5 | 12 | 17 | 47749.0923
2030 | 2008 | 5 | 12 | 18 | 40184.7967
2030 | 2008 | 5 | 12 | 19 | 31542.2022
2030 | 2008 | 5 | 12 | 20 | 10461.6641
2030 | 2008 | 5 | 12 | 21 | 0
2030 | 2008 | 5 | 12 | 22 | 0
2030 | 2008 | 5 | 12 | 23 | 0
2030 | 2008 | 5 | 12 | 24 | 0
2030 | 2008 | 5 | 13 | 1 | 0
2030 | 2008 | 5 | 13 | 2 | 0
2030 | 2008 | 5 | 13 | 3 | 0
2030 | 2008 | 5 | 13 | 4 | 0
2030 | 2008 | 5 | 13 | 5 | 0
2030 | 2008 | 5 | 13 | 6 | 0
2030 | 2008 | 5 | 13 | 7 | 0.19935
2030 | 2008 | 5 | 13 | 8 | 2399.4759
2030 | 2008 | 5 | 13 | 9 | 13707.3972
2030 | 2008 | 5 | 13 | 10 | 23507.4217
2030 | 2008 | 5 | 13 | 11 | 32340.956
2030 | 2008 | 5 | 13 | 12 | 38869.2134
2030 | 2008 | 5 | 13 | 13 | 41328.2547
2030 | 2008 | 5 | 13 | 14 | 43264.2669
2030 | 2008 | 5 | 13 | 15 | 45216.7291
2030 | 2008 | 5 | 13 | 16 | 44539.0782
2030 | 2008 | 5 | 13 | 17 | 39713.0022
2030 | 2008 | 5 | 13 | 18 | 39033.8533
2030 | 2008 | 5 | 13 | 19 | 30022.4158
2030 | 2008 | 5 | 13 | 20 | 10777.3866
2030 | 2008 | 5 | 13 | 21 | 0
2030 | 2008 | 5 | 13 | 22 | 0
2030 | 2008 | 5 | 13 | 23 | 0
2030 | 2008 | 5 | 13 | 24 | 0
2030 | 2008 | 5 | 14 | 1 | 0
2030 | 2008 | 5 | 14 | 2 | 0
2030 | 2008 | 5 | 14 | 3 | 0
2030 | 2008 | 5 | 14 | 4 | 0
2030 | 2008 | 5 | 14 | 5 | 0
2030 | 2008 | 5 | 14 | 6 | 0
2030 | 2008 | 5 | 14 | 7 | 1.4897
2030 | 2008 | 5 | 14 | 8 | 3967.3232
2030 | 2008 | 5 | 14 | 9 | 16292.5587
2030 | 2008 | 5 | 14 | 10 | 24411.4839
2030 | 2008 | 5 | 14 | 11 | 28226.4477
2030 | 2008 | 5 | 14 | 12 | 35702.389
2030 | 2008 | 5 | 14 | 13 | 40226.1034
2030 | 2008 | 5 | 14 | 14 | 41201.4872
2030 | 2008 | 5 | 14 | 15 | 38793.2124
2030 | 2008 | 5 | 14 | 16 | 36918.3743
2030 | 2008 | 5 | 14 | 17 | 34180.9146
2030 | 2008 | 5 | 14 | 18 | 30046.8818
2030 | 2008 | 5 | 14 | 19 | 25677.5722
2030 | 2008 | 5 | 14 | 20 | 10476.0572
2030 | 2008 | 5 | 14 | 21 | 8.797
2030 | 2008 | 5 | 14 | 22 | 0
2030 | 2008 | 5 | 14 | 23 | 0
2030 | 2008 | 5 | 14 | 24 | 0
2030 | 2008 | 5 | 15 | 1 | 0
2030 | 2008 | 5 | 15 | 2 | 0
2030 | 2008 | 5 | 15 | 3 | 0
2030 | 2008 | 5 | 15 | 4 | 0
2030 | 2008 | 5 | 15 | 5 | 0
2030 | 2008 | 5 | 15 | 6 | 0
2030 | 2008 | 5 | 15 | 7 | 0.18588
2030 | 2008 | 5 | 15 | 8 | 4335.8259
2030 | 2008 | 5 | 15 | 9 | 23625.4928
2030 | 2008 | 5 | 15 | 10 | 40890.4002
2030 | 2008 | 5 | 15 | 11 | 47621.217
2030 | 2008 | 5 | 15 | 12 | 50367.9638
2030 | 2008 | 5 | 15 | 13 | 50919.7837
2030 | 2008 | 5 | 15 | 14 | 48698.1134
2030 | 2008 | 5 | 15 | 15 | 46209.9767
2030 | 2008 | 5 | 15 | 16 | 42035.3746
2030 | 2008 | 5 | 15 | 17 | 37856.4112
2030 | 2008 | 5 | 15 | 18 | 35284.7171
2030 | 2008 | 5 | 15 | 19 | 27741.5086
2030 | 2008 | 5 | 15 | 20 | 10214.0909
2030 | 2008 | 5 | 15 | 21 | 19.971
2030 | 2008 | 5 | 15 | 22 | 0
2030 | 2008 | 5 | 15 | 23 | 0
2030 | 2008 | 5 | 15 | 24 | 0
2030 | 2008 | 5 | 16 | 1 | 0
2030 | 2008 | 5 | 16 | 2 | 0
2030 | 2008 | 5 | 16 | 3 | 0
2030 | 2008 | 5 | 16 | 4 | 0
2030 | 2008 | 5 | 16 | 5 | 0
2030 | 2008 | 5 | 16 | 6 | 0
2030 | 2008 | 5 | 16 | 7 | 19.2342
2030 | 2008 | 5 | 16 | 8 | 8278.9651
2030 | 2008 | 5 | 16 | 9 | 27359.816
2030 | 2008 | 5 | 16 | 10 | 39707.0315
2030 | 2008 | 5 | 16 | 11 | 45316.6486
2030 | 2008 | 5 | 16 | 12 | 50226.6735
2030 | 2008 | 5 | 16 | 13 | 53056.7232
2030 | 2008 | 5 | 16 | 14 | 55125.5418
2030 | 2008 | 5 | 16 | 15 | 53566.8925
2030 | 2008 | 5 | 16 | 16 | 51435.6635
2030 | 2008 | 5 | 16 | 17 | 47288.3068
2030 | 2008 | 5 | 16 | 18 | 44555.4772
2030 | 2008 | 5 | 16 | 19 | 32400.6014
2030 | 2008 | 5 | 16 | 20 | 9931.3951
2030 | 2008 | 5 | 16 | 21 | 20.0071
2030 | 2008 | 5 | 16 | 22 | 0
2030 | 2008 | 5 | 16 | 23 | 0
2030 | 2008 | 5 | 16 | 24 | 0
2030 | 2008 | 5 | 17 | 1 | 0
2030 | 2008 | 5 | 17 | 2 | 0
2030 | 2008 | 5 | 17 | 3 | 0
2030 | 2008 | 5 | 17 | 4 | 0
2030 | 2008 | 5 | 17 | 5 | 0
2030 | 2008 | 5 | 17 | 6 | 0
2030 | 2008 | 5 | 17 | 7 | 20.8243
2030 | 2008 | 5 | 17 | 8 | 9911.3551
2030 | 2008 | 5 | 17 | 9 | 34578.3483
2030 | 2008 | 5 | 17 | 10 | 47195.8066
2030 | 2008 | 5 | 17 | 11 | 49187.7003
2030 | 2008 | 5 | 17 | 12 | 49286.1099
2030 | 2008 | 5 | 17 | 13 | 46803.0356
2030 | 2008 | 5 | 17 | 14 | 45482.7725
2030 | 2008 | 5 | 17 | 15 | 42747.2157
2030 | 2008 | 5 | 17 | 16 | 39604.7945
2030 | 2008 | 5 | 17 | 17 | 34548.3742
2030 | 2008 | 5 | 17 | 18 | 34166.7475
2030 | 2008 | 5 | 17 | 19 | 29780.5635
2030 | 2008 | 5 | 17 | 20 | 11272.1939
2030 | 2008 | 5 | 17 | 21 | 32.9858
2030 | 2008 | 5 | 17 | 22 | 0
2030 | 2008 | 5 | 17 | 23 | 0
2030 | 2008 | 5 | 17 | 24 | 0
2030 | 2008 | 5 | 18 | 1 | 0
2030 | 2008 | 5 | 18 | 2 | 0
2030 | 2008 | 5 | 18 | 3 | 0
2030 | 2008 | 5 | 18 | 4 | 0
2030 | 2008 | 5 | 18 | 5 | 0
2030 | 2008 | 5 | 18 | 6 | 0
2030 | 2008 | 5 | 18 | 7 | 43.7616
2030 | 2008 | 5 | 18 | 8 | 18025.0771
2030 | 2008 | 5 | 18 | 9 | 49438.7242
2030 | 2008 | 5 | 18 | 10 | 57325.2465
2030 | 2008 | 5 | 18 | 11 | 57283.2241
2030 | 2008 | 5 | 18 | 12 | 55707.7992
2030 | 2008 | 5 | 18 | 13 | 56449.2481
2030 | 2008 | 5 | 18 | 14 | 57149.0374
2030 | 2008 | 5 | 18 | 15 | 55071.4975
2030 | 2008 | 5 | 18 | 16 | 53651.7924
2030 | 2008 | 5 | 18 | 17 | 50591.0492
2030 | 2008 | 5 | 18 | 18 | 47643.609
2030 | 2008 | 5 | 18 | 19 | 33574.1796
2030 | 2008 | 5 | 18 | 20 | 12304.9754
2030 | 2008 | 5 | 18 | 21 | 67.2796
2030 | 2008 | 5 | 18 | 22 | 0
2030 | 2008 | 5 | 18 | 23 | 0
2030 | 2008 | 5 | 18 | 24 | 0
2030 | 2008 | 5 | 19 | 1 | 0
2030 | 2008 | 5 | 19 | 2 | 0
2030 | 2008 | 5 | 19 | 3 | 0
2030 | 2008 | 5 | 19 | 4 | 0
2030 | 2008 | 5 | 19 | 5 | 0
2030 | 2008 | 5 | 19 | 6 | 0
2030 | 2008 | 5 | 19 | 7 | 34.175
2030 | 2008 | 5 | 19 | 8 | 17996.863
2030 | 2008 | 5 | 19 | 9 | 50756.5831
2030 | 2008 | 5 | 19 | 10 | 58398.9336
2030 | 2008 | 5 | 19 | 11 | 56749.7405
2030 | 2008 | 5 | 19 | 12 | 56448.6868
2030 | 2008 | 5 | 19 | 13 | 56922.5115
2030 | 2008 | 5 | 19 | 14 | 56284.3658
2030 | 2008 | 5 | 19 | 15 | 54695.211
2030 | 2008 | 5 | 19 | 16 | 53524.7186
2030 | 2008 | 5 | 19 | 17 | 50212.7053
2030 | 2008 | 5 | 19 | 18 | 46126.2482
2030 | 2008 | 5 | 19 | 19 | 34266.1911
2030 | 2008 | 5 | 19 | 20 | 12426.5105
2030 | 2008 | 5 | 19 | 21 | 140.7847
2030 | 2008 | 5 | 19 | 22 | 0
2030 | 2008 | 5 | 19 | 23 | 0
2030 | 2008 | 5 | 19 | 24 | 0
2030 | 2008 | 5 | 20 | 1 | 0
2030 | 2008 | 5 | 20 | 2 | 0
2030 | 2008 | 5 | 20 | 3 | 0
2030 | 2008 | 5 | 20 | 4 | 0
2030 | 2008 | 5 | 20 | 5 | 0
2030 | 2008 | 5 | 20 | 6 | 0
2030 | 2008 | 5 | 20 | 7 | 38.4267
2030 | 2008 | 5 | 20 | 8 | 16013.7291
2030 | 2008 | 5 | 20 | 9 | 42161.7899
2030 | 2008 | 5 | 20 | 10 | 51013.7513
2030 | 2008 | 5 | 20 | 11 | 53892.1805
2030 | 2008 | 5 | 20 | 12 | 54824.2485
2030 | 2008 | 5 | 20 | 13 | 55577.0864
2030 | 2008 | 5 | 20 | 14 | 55771.8428
2030 | 2008 | 5 | 20 | 15 | 53804.8264
2030 | 2008 | 5 | 20 | 16 | 51669.8224
2030 | 2008 | 5 | 20 | 17 | 50108.5553
2030 | 2008 | 5 | 20 | 18 | 47301.1639
2030 | 2008 | 5 | 20 | 19 | 33192.817
2030 | 2008 | 5 | 20 | 20 | 11800.1165
2030 | 2008 | 5 | 20 | 21 | 154.3178
2030 | 2008 | 5 | 20 | 22 | 0
2030 | 2008 | 5 | 20 | 23 | 0
2030 | 2008 | 5 | 20 | 24 | 0
2030 | 2008 | 5 | 21 | 1 | 0
2030 | 2008 | 5 | 21 | 2 | 0
2030 | 2008 | 5 | 21 | 3 | 0
2030 | 2008 | 5 | 21 | 4 | 0
2030 | 2008 | 5 | 21 | 5 | 0
2030 | 2008 | 5 | 21 | 6 | 0
2030 | 2008 | 5 | 21 | 7 | 30.238
2030 | 2008 | 5 | 21 | 8 | 7268.7913
2030 | 2008 | 5 | 21 | 9 | 25730.2565
2030 | 2008 | 5 | 21 | 10 | 36004.7721
2030 | 2008 | 5 | 21 | 11 | 42536.5764
2030 | 2008 | 5 | 21 | 12 | 53675.0759
2030 | 2008 | 5 | 21 | 13 | 55687.4541
2030 | 2008 | 5 | 21 | 14 | 56553.9843
2030 | 2008 | 5 | 21 | 15 | 54486.2659
2030 | 2008 | 5 | 21 | 16 | 52919.4664
2030 | 2008 | 5 | 21 | 17 | 49735.0892
2030 | 2008 | 5 | 21 | 18 | 45390.921
2030 | 2008 | 5 | 21 | 19 | 33074.4799
2030 | 2008 | 5 | 21 | 20 | 11943.5051
2030 | 2008 | 5 | 21 | 21 | 139.6412
2030 | 2008 | 5 | 21 | 22 | 0
2030 | 2008 | 5 | 21 | 23 | 0
2030 | 2008 | 5 | 21 | 24 | 0
2030 | 2008 | 5 | 22 | 1 | 0
2030 | 2008 | 5 | 22 | 2 | 0
2030 | 2008 | 5 | 22 | 3 | 0
2030 | 2008 | 5 | 22 | 4 | 0
2030 | 2008 | 5 | 22 | 5 | 0
2030 | 2008 | 5 | 22 | 6 | 0
2030 | 2008 | 5 | 22 | 7 | 3.0327
2030 | 2008 | 5 | 22 | 8 | 4264.5865
2030 | 2008 | 5 | 22 | 9 | 21280.8518
2030 | 2008 | 5 | 22 | 10 | 37776.5185
2030 | 2008 | 5 | 22 | 11 | 47219.7276
2030 | 2008 | 5 | 22 | 12 | 52745.907
2030 | 2008 | 5 | 22 | 13 | 55206.3472
2030 | 2008 | 5 | 22 | 14 | 55345.6932
2030 | 2008 | 5 | 22 | 15 | 53255.2937
2030 | 2008 | 5 | 22 | 16 | 50164.7882
2030 | 2008 | 5 | 22 | 17 | 46484.0536
2030 | 2008 | 5 | 22 | 18 | 42447.9609
2030 | 2008 | 5 | 22 | 19 | 33812.0011
2030 | 2008 | 5 | 22 | 20 | 12381.0735
2030 | 2008 | 5 | 22 | 21 | 254.0206
2030 | 2008 | 5 | 22 | 22 | 0
2030 | 2008 | 5 | 22 | 23 | 0
2030 | 2008 | 5 | 22 | 24 | 0
2030 | 2008 | 5 | 23 | 1 | 0
2030 | 2008 | 5 | 23 | 2 | 0
2030 | 2008 | 5 | 23 | 3 | 0
2030 | 2008 | 5 | 23 | 4 | 0
2030 | 2008 | 5 | 23 | 5 | 0
2030 | 2008 | 5 | 23 | 6 | 0
2030 | 2008 | 5 | 23 | 7 | 4.8648
2030 | 2008 | 5 | 23 | 8 | 5577.634
2030 | 2008 | 5 | 23 | 9 | 24746.18
2030 | 2008 | 5 | 23 | 10 | 40437.0268
2030 | 2008 | 5 | 23 | 11 | 50594.1314
2030 | 2008 | 5 | 23 | 12 | 54254.7709
2030 | 2008 | 5 | 23 | 13 | 55112.9573
2030 | 2008 | 5 | 23 | 14 | 56446.0913
2030 | 2008 | 5 | 23 | 15 | 55050.1135
2030 | 2008 | 5 | 23 | 16 | 52690.1352
2030 | 2008 | 5 | 23 | 17 | 50185.6978
2030 | 2008 | 5 | 23 | 18 | 46556.7555
2030 | 2008 | 5 | 23 | 19 | 34079.4664
2030 | 2008 | 5 | 23 | 20 | 11851.6835
2030 | 2008 | 5 | 23 | 21 | 323.5711
2030 | 2008 | 5 | 23 | 22 | 0
2030 | 2008 | 5 | 23 | 23 | 0
2030 | 2008 | 5 | 23 | 24 | 0
2030 | 2008 | 5 | 24 | 1 | 0
2030 | 2008 | 5 | 24 | 2 | 0
2030 | 2008 | 5 | 24 | 3 | 0
2030 | 2008 | 5 | 24 | 4 | 0
2030 | 2008 | 5 | 24 | 5 | 0
2030 | 2008 | 5 | 24 | 6 | 0
2030 | 2008 | 5 | 24 | 7 | 5.9061
2030 | 2008 | 5 | 24 | 8 | 5017.7762
2030 | 2008 | 5 | 24 | 9 | 20921.8521
2030 | 2008 | 5 | 24 | 10 | 34172.5827
2030 | 2008 | 5 | 24 | 11 | 51252.7967
2030 | 2008 | 5 | 24 | 12 | 54677.6619
2030 | 2008 | 5 | 24 | 13 | 56387.4612
2030 | 2008 | 5 | 24 | 14 | 55989.0303
2030 | 2008 | 5 | 24 | 15 | 54779.8827
2030 | 2008 | 5 | 24 | 16 | 53223.0111
2030 | 2008 | 5 | 24 | 17 | 50247.7218
2030 | 2008 | 5 | 24 | 18 | 44575.3715
2030 | 2008 | 5 | 24 | 19 | 33404.5647
2030 | 2008 | 5 | 24 | 20 | 12569.0797
2030 | 2008 | 5 | 24 | 21 | 439.9825
2030 | 2008 | 5 | 24 | 22 | 0
2030 | 2008 | 5 | 24 | 23 | 0
2030 | 2008 | 5 | 24 | 24 | 0
2030 | 2008 | 5 | 25 | 1 | 0
2030 | 2008 | 5 | 25 | 2 | 0
2030 | 2008 | 5 | 25 | 3 | 0
2030 | 2008 | 5 | 25 | 4 | 0
2030 | 2008 | 5 | 25 | 5 | 0
2030 | 2008 | 5 | 25 | 6 | 0
2030 | 2008 | 5 | 25 | 7 | 7.3296
2030 | 2008 | 5 | 25 | 8 | 4213.6862
2030 | 2008 | 5 | 25 | 9 | 14698.4296
2030 | 2008 | 5 | 25 | 10 | 34073.69
2030 | 2008 | 5 | 25 | 11 | 47576.7077
2030 | 2008 | 5 | 25 | 12 | 54691.8373
2030 | 2008 | 5 | 25 | 13 | 55648.3942
2030 | 2008 | 5 | 25 | 14 | 56630.731
2030 | 2008 | 5 | 25 | 15 | 55358.6288
2030 | 2008 | 5 | 25 | 16 | 52318.8635
2030 | 2008 | 5 | 25 | 17 | 50398.4542
2030 | 2008 | 5 | 25 | 18 | 45658.6713
2030 | 2008 | 5 | 25 | 19 | 33655.4579
2030 | 2008 | 5 | 25 | 20 | 12523.3238
2030 | 2008 | 5 | 25 | 21 | 567.867
2030 | 2008 | 5 | 25 | 22 | 0
2030 | 2008 | 5 | 25 | 23 | 0
2030 | 2008 | 5 | 25 | 24 | 0
2030 | 2008 | 5 | 26 | 1 | 0
2030 | 2008 | 5 | 26 | 2 | 0
2030 | 2008 | 5 | 26 | 3 | 0
2030 | 2008 | 5 | 26 | 4 | 0
2030 | 2008 | 5 | 26 | 5 | 0
2030 | 2008 | 5 | 26 | 6 | 0
2030 | 2008 | 5 | 26 | 7 | 12.3992
2030 | 2008 | 5 | 26 | 8 | 3953.6114
2030 | 2008 | 5 | 26 | 9 | 17206.6072
2030 | 2008 | 5 | 26 | 10 | 41079.2078
2030 | 2008 | 5 | 26 | 11 | 50019.801
2030 | 2008 | 5 | 26 | 12 | 53991.6856
2030 | 2008 | 5 | 26 | 13 | 56130.7614
2030 | 2008 | 5 | 26 | 14 | 55204.8443
2030 | 2008 | 5 | 26 | 15 | 55132.4782
2030 | 2008 | 5 | 26 | 16 | 52913.1814
2030 | 2008 | 5 | 26 | 17 | 50283.2688
2030 | 2008 | 5 | 26 | 18 | 44818.5528
2030 | 2008 | 5 | 26 | 19 | 32502.4015
2030 | 2008 | 5 | 26 | 20 | 11466.153
2030 | 2008 | 5 | 26 | 21 | 599.8187
2030 | 2008 | 5 | 26 | 22 | 0
2030 | 2008 | 5 | 26 | 23 | 0
2030 | 2008 | 5 | 26 | 24 | 0
2030 | 2008 | 5 | 27 | 1 | 0
2030 | 2008 | 5 | 27 | 2 | 0
2030 | 2008 | 5 | 27 | 3 | 0
2030 | 2008 | 5 | 27 | 4 | 0
2030 | 2008 | 5 | 27 | 5 | 0
2030 | 2008 | 5 | 27 | 6 | 0
2030 | 2008 | 5 | 27 | 7 | 5.6416
2030 | 2008 | 5 | 27 | 8 | 4181.0598
2030 | 2008 | 5 | 27 | 9 | 19872.0922
2030 | 2008 | 5 | 27 | 10 | 35235.955
2030 | 2008 | 5 | 27 | 11 | 50092.9233
2030 | 2008 | 5 | 27 | 12 | 53953.477
2030 | 2008 | 5 | 27 | 13 | 55083.8874
2030 | 2008 | 5 | 27 | 14 | 55043.0645
2030 | 2008 | 5 | 27 | 15 | 54828.8572
2030 | 2008 | 5 | 27 | 16 | 52128.4475
2030 | 2008 | 5 | 27 | 17 | 48939.2267
2030 | 2008 | 5 | 27 | 18 | 44646.2818
2030 | 2008 | 5 | 27 | 19 | 33579.9903
2030 | 2008 | 5 | 27 | 20 | 12416.3127
2030 | 2008 | 5 | 27 | 21 | 646.9833
2030 | 2008 | 5 | 27 | 22 | 0
2030 | 2008 | 5 | 27 | 23 | 0
2030 | 2008 | 5 | 27 | 24 | 0
2030 | 2008 | 5 | 28 | 1 | 0
2030 | 2008 | 5 | 28 | 2 | 0
2030 | 2008 | 5 | 28 | 3 | 0
2030 | 2008 | 5 | 28 | 4 | 0
2030 | 2008 | 5 | 28 | 5 | 0
2030 | 2008 | 5 | 28 | 6 | 0
2030 | 2008 | 5 | 28 | 7 | 40.5889
2030 | 2008 | 5 | 28 | 8 | 9128.3746
2030 | 2008 | 5 | 28 | 9 | 25636.025
2030 | 2008 | 5 | 28 | 10 | 37458.0433
2030 | 2008 | 5 | 28 | 11 | 45718.7227
2030 | 2008 | 5 | 28 | 12 | 49611.4852
2030 | 2008 | 5 | 28 | 13 | 50782.7235
2030 | 2008 | 5 | 28 | 14 | 53074.2229
2030 | 2008 | 5 | 28 | 15 | 52320.2079
2030 | 2008 | 5 | 28 | 16 | 46528.7928
2030 | 2008 | 5 | 28 | 17 | 46602.4534
2030 | 2008 | 5 | 28 | 18 | 41619.2982
2030 | 2008 | 5 | 28 | 19 | 33437.2572
2030 | 2008 | 5 | 28 | 20 | 13221.4953
2030 | 2008 | 5 | 28 | 21 | 763.6106
2030 | 2008 | 5 | 28 | 22 | 0
2030 | 2008 | 5 | 28 | 23 | 0
2030 | 2008 | 5 | 28 | 24 | 0
2030 | 2008 | 5 | 29 | 1 | 0
2030 | 2008 | 5 | 29 | 2 | 0
2030 | 2008 | 5 | 29 | 3 | 0
2030 | 2008 | 5 | 29 | 4 | 0
2030 | 2008 | 5 | 29 | 5 | 0
2030 | 2008 | 5 | 29 | 6 | 0
2030 | 2008 | 5 | 29 | 7 | 34.994
2030 | 2008 | 5 | 29 | 8 | 14156.0346
2030 | 2008 | 5 | 29 | 9 | 38341.7347
2030 | 2008 | 5 | 29 | 10 | 48486.1045
2030 | 2008 | 5 | 29 | 11 | 52011.5676
2030 | 2008 | 5 | 29 | 12 | 52055.0147
2030 | 2008 | 5 | 29 | 13 | 52455.1238
2030 | 2008 | 5 | 29 | 14 | 51996.989
2030 | 2008 | 5 | 29 | 15 | 52453.4949
2030 | 2008 | 5 | 29 | 16 | 50990.4377
2030 | 2008 | 5 | 29 | 17 | 47282.3583
2030 | 2008 | 5 | 29 | 18 | 43620.382
2030 | 2008 | 5 | 29 | 19 | 33644.8516
2030 | 2008 | 5 | 29 | 20 | 12003.0362
2030 | 2008 | 5 | 29 | 21 | 719.3783
2030 | 2008 | 5 | 29 | 22 | 0
2030 | 2008 | 5 | 29 | 23 | 0
2030 | 2008 | 5 | 29 | 24 | 0
2030 | 2008 | 5 | 30 | 1 | 0
2030 | 2008 | 5 | 30 | 2 | 0
2030 | 2008 | 5 | 30 | 3 | 0
2030 | 2008 | 5 | 30 | 4 | 0
2030 | 2008 | 5 | 30 | 5 | 0
2030 | 2008 | 5 | 30 | 6 | 0
2030 | 2008 | 5 | 30 | 7 | 55.0789
2030 | 2008 | 5 | 30 | 8 | 15895.1988
2030 | 2008 | 5 | 30 | 9 | 43850.5831
2030 | 2008 | 5 | 30 | 10 | 54493.7392
2030 | 2008 | 5 | 30 | 11 | 56629.9933
2030 | 2008 | 5 | 30 | 12 | 54310.8186
2030 | 2008 | 5 | 30 | 13 | 55778.4559
2030 | 2008 | 5 | 30 | 14 | 56410.1914
2030 | 2008 | 5 | 30 | 15 | 55465.6759
2030 | 2008 | 5 | 30 | 16 | 53244.2415
2030 | 2008 | 5 | 30 | 17 | 49838.5134
2030 | 2008 | 5 | 30 | 18 | 46435.1486
2030 | 2008 | 5 | 30 | 19 | 33458.5934
2030 | 2008 | 5 | 30 | 20 | 13482.9453
2030 | 2008 | 5 | 30 | 21 | 931.6545
2030 | 2008 | 5 | 30 | 22 | 0
2030 | 2008 | 5 | 30 | 23 | 0
2030 | 2008 | 5 | 30 | 24 | 0
2030 | 2008 | 5 | 31 | 1 | 0
2030 | 2008 | 5 | 31 | 2 | 0
2030 | 2008 | 5 | 31 | 3 | 0
2030 | 2008 | 5 | 31 | 4 | 0
2030 | 2008 | 5 | 31 | 5 | 0
2030 | 2008 | 5 | 31 | 6 | 0
2030 | 2008 | 5 | 31 | 7 | 48.7982
2030 | 2008 | 5 | 31 | 8 | 10830.3398
2030 | 2008 | 5 | 31 | 9 | 32225.1601
2030 | 2008 | 5 | 31 | 10 | 41816.3423
2030 | 2008 | 5 | 31 | 11 | 51981.8898
2030 | 2008 | 5 | 31 | 12 | 54204.9033
2030 | 2008 | 5 | 31 | 13 | 54045.4847
2030 | 2008 | 5 | 31 | 14 | 54328.3725
2030 | 2008 | 5 | 31 | 15 | 53411.2347
2030 | 2008 | 5 | 31 | 16 | 52180.7799
2030 | 2008 | 5 | 31 | 17 | 50139.0655
2030 | 2008 | 5 | 31 | 18 | 45775.5384
2030 | 2008 | 5 | 31 | 19 | 34692.1376
2030 | 2008 | 5 | 31 | 20 | 14116.266
2030 | 2008 | 5 | 31 | 21 | 439.3671
2030 | 2008 | 5 | 31 | 22 | 0
2030 | 2008 | 5 | 31 | 23 | 0
2030 | 2008 | 5 | 31 | 24 | 0
2026 | 2008 | 10 | 1 | 1 | 0
2026 | 2008 | 10 | 1 | 2 | 0
2026 | 2008 | 10 | 1 | 3 | 0
2026 | 2008 | 10 | 1 | 4 | 0
2026 | 2008 | 10 | 1 | 5 | 0
2026 | 2008 | 10 | 1 | 6 | 0
2026 | 2008 | 10 | 1 | 7 | 0
2026 | 2008 | 10 | 1 | 8 | 48.6855
2026 | 2008 | 10 | 1 | 9 | 15128.4589
2026 | 2008 | 10 | 1 | 10 | 37842.2201
2026 | 2008 | 10 | 1 | 11 | 41812.1087
2026 | 2008 | 10 | 1 | 12 | 42184.2813
2026 | 2008 | 10 | 1 | 13 | 41441.365
2026 | 2008 | 10 | 1 | 14 | 40838.7713
2026 | 2008 | 10 | 1 | 15 | 40140.8322
2026 | 2008 | 10 | 1 | 16 | 40547.6244
2026 | 2008 | 10 | 1 | 17 | 39740.8839
2026 | 2008 | 10 | 1 | 18 | 31382.1764
2026 | 2008 | 10 | 1 | 19 | 10662.7751
2026 | 2008 | 10 | 1 | 20 | 0
2026 | 2008 | 10 | 1 | 21 | 0
2026 | 2008 | 10 | 1 | 22 | 0
2026 | 2008 | 10 | 1 | 23 | 0
2026 | 2008 | 10 | 1 | 24 | 0
2026 | 2008 | 10 | 2 | 1 | 0
2026 | 2008 | 10 | 2 | 2 | 0
2026 | 2008 | 10 | 2 | 3 | 0
2026 | 2008 | 10 | 2 | 4 | 0
2026 | 2008 | 10 | 2 | 5 | 0
2026 | 2008 | 10 | 2 | 6 | 0
2026 | 2008 | 10 | 2 | 7 | 0
2026 | 2008 | 10 | 2 | 8 | 60.204
2026 | 2008 | 10 | 2 | 9 | 15309.4241
2026 | 2008 | 10 | 2 | 10 | 36394.6964
2026 | 2008 | 10 | 2 | 11 | 41892.5824
2026 | 2008 | 10 | 2 | 12 | 42267.602
2026 | 2008 | 10 | 2 | 13 | 40766.6069
2026 | 2008 | 10 | 2 | 14 | 40128.3554
2026 | 2008 | 10 | 2 | 15 | 39300.3565
2026 | 2008 | 10 | 2 | 16 | 40039.8681
2026 | 2008 | 10 | 2 | 17 | 39457.8268
2026 | 2008 | 10 | 2 | 18 | 31053.9507
2026 | 2008 | 10 | 2 | 19 | 10584.5907
2026 | 2008 | 10 | 2 | 20 | 0
2026 | 2008 | 10 | 2 | 21 | 0
2026 | 2008 | 10 | 2 | 22 | 0
2026 | 2008 | 10 | 2 | 23 | 0
2026 | 2008 | 10 | 2 | 24 | 0
2026 | 2008 | 10 | 3 | 1 | 0
2026 | 2008 | 10 | 3 | 2 | 0
2026 | 2008 | 10 | 3 | 3 | 0
2026 | 2008 | 10 | 3 | 4 | 0
2026 | 2008 | 10 | 3 | 5 | 0
2026 | 2008 | 10 | 3 | 6 | 0
2026 | 2008 | 10 | 3 | 7 | 0
2026 | 2008 | 10 | 3 | 8 | 57.8862
2026 | 2008 | 10 | 3 | 9 | 12291.7645
2026 | 2008 | 10 | 3 | 10 | 34328.9848
2026 | 2008 | 10 | 3 | 11 | 39543.0092
2026 | 2008 | 10 | 3 | 12 | 39187.7515
2026 | 2008 | 10 | 3 | 13 | 38107.751
2026 | 2008 | 10 | 3 | 14 | 37219.4125
2026 | 2008 | 10 | 3 | 15 | 37327.0963
2026 | 2008 | 10 | 3 | 16 | 37354.9912
2026 | 2008 | 10 | 3 | 17 | 35527.1958
2026 | 2008 | 10 | 3 | 18 | 28707.5133
2026 | 2008 | 10 | 3 | 19 | 9878.7452
2026 | 2008 | 10 | 3 | 20 | 0
2026 | 2008 | 10 | 3 | 21 | 0
2026 | 2008 | 10 | 3 | 22 | 0
2026 | 2008 | 10 | 3 | 23 | 0
2026 | 2008 | 10 | 3 | 24 | 0
2026 | 2008 | 10 | 4 | 1 | 0
2026 | 2008 | 10 | 4 | 2 | 0
2026 | 2008 | 10 | 4 | 3 | 0
2026 | 2008 | 10 | 4 | 4 | 0
2026 | 2008 | 10 | 4 | 5 | 0
2026 | 2008 | 10 | 4 | 6 | 0
2026 | 2008 | 10 | 4 | 7 | 0
2026 | 2008 | 10 | 4 | 8 | 37.5899
2026 | 2008 | 10 | 4 | 9 | 9113.4289
2026 | 2008 | 10 | 4 | 10 | 28531.8973
2026 | 2008 | 10 | 4 | 11 | 35832.3027
2026 | 2008 | 10 | 4 | 12 | 39129.9003
2026 | 2008 | 10 | 4 | 13 | 39158.9813
2026 | 2008 | 10 | 4 | 14 | 38099.3115
2026 | 2008 | 10 | 4 | 15 | 37882.3343
2026 | 2008 | 10 | 4 | 16 | 37276.5492
2026 | 2008 | 10 | 4 | 17 | 36776.3799
2026 | 2008 | 10 | 4 | 18 | 27823.4657
2026 | 2008 | 10 | 4 | 19 | 9629.149
2026 | 2008 | 10 | 4 | 20 | 0
2026 | 2008 | 10 | 4 | 21 | 0
2026 | 2008 | 10 | 4 | 22 | 0
2026 | 2008 | 10 | 4 | 23 | 0
2026 | 2008 | 10 | 4 | 24 | 0
2026 | 2008 | 10 | 5 | 1 | 0
2026 | 2008 | 10 | 5 | 2 | 0
2026 | 2008 | 10 | 5 | 3 | 0
2026 | 2008 | 10 | 5 | 4 | 0
2026 | 2008 | 10 | 5 | 5 | 0
2026 | 2008 | 10 | 5 | 6 | 0
2026 | 2008 | 10 | 5 | 7 | 0
2026 | 2008 | 10 | 5 | 8 | 39.1087
2026 | 2008 | 10 | 5 | 9 | 9114.1276
2026 | 2008 | 10 | 5 | 10 | 24719.6446
2026 | 2008 | 10 | 5 | 11 | 27560.9411
2026 | 2008 | 10 | 5 | 12 | 30737.9833
2026 | 2008 | 10 | 5 | 13 | 31740.9583
2026 | 2008 | 10 | 5 | 14 | 29514.5415
2026 | 2008 | 10 | 5 | 15 | 28017.6184
2026 | 2008 | 10 | 5 | 16 | 28193.8012
2026 | 2008 | 10 | 5 | 17 | 27101.0264
2026 | 2008 | 10 | 5 | 18 | 22708.5055
2026 | 2008 | 10 | 5 | 19 | 7961.8132
2026 | 2008 | 10 | 5 | 20 | 0
2026 | 2008 | 10 | 5 | 21 | 0
2026 | 2008 | 10 | 5 | 22 | 0
2026 | 2008 | 10 | 5 | 23 | 0
2026 | 2008 | 10 | 5 | 24 | 0
2026 | 2008 | 10 | 6 | 1 | 0
2026 | 2008 | 10 | 6 | 2 | 0
2026 | 2008 | 10 | 6 | 3 | 0
2026 | 2008 | 10 | 6 | 4 | 0
2026 | 2008 | 10 | 6 | 5 | 0
2026 | 2008 | 10 | 6 | 6 | 0
2026 | 2008 | 10 | 6 | 7 | 0
2026 | 2008 | 10 | 6 | 8 | 18.5113
2026 | 2008 | 10 | 6 | 9 | 7327.5038
2026 | 2008 | 10 | 6 | 10 | 23336.218
2026 | 2008 | 10 | 6 | 11 | 31280.1531
2026 | 2008 | 10 | 6 | 12 | 34334.3778
2026 | 2008 | 10 | 6 | 13 | 34637.5015
2026 | 2008 | 10 | 6 | 14 | 34794.3067
2026 | 2008 | 10 | 6 | 15 | 34887.5473
2026 | 2008 | 10 | 6 | 16 | 36210.8793
2026 | 2008 | 10 | 6 | 17 | 36023.8726
2026 | 2008 | 10 | 6 | 18 | 27991.1497
2026 | 2008 | 10 | 6 | 19 | 9139.1066
2026 | 2008 | 10 | 6 | 20 | 0
2026 | 2008 | 10 | 6 | 21 | 0
2026 | 2008 | 10 | 6 | 22 | 0
2026 | 2008 | 10 | 6 | 23 | 0
2026 | 2008 | 10 | 6 | 24 | 0
2026 | 2008 | 10 | 7 | 1 | 0
2026 | 2008 | 10 | 7 | 2 | 0
2026 | 2008 | 10 | 7 | 3 | 0
2026 | 2008 | 10 | 7 | 4 | 0
2026 | 2008 | 10 | 7 | 5 | 0
2026 | 2008 | 10 | 7 | 6 | 0
2026 | 2008 | 10 | 7 | 7 | 0
2026 | 2008 | 10 | 7 | 8 | 23.6528
2026 | 2008 | 10 | 7 | 9 | 9797.5958
2026 | 2008 | 10 | 7 | 10 | 30426.3013
2026 | 2008 | 10 | 7 | 11 | 35082.2754
2026 | 2008 | 10 | 7 | 12 | 38316.1748
2026 | 2008 | 10 | 7 | 13 | 38568.3116
2026 | 2008 | 10 | 7 | 14 | 38765.1921
2026 | 2008 | 10 | 7 | 15 | 38238.345
2026 | 2008 | 10 | 7 | 16 | 39382.8737
2026 | 2008 | 10 | 7 | 17 | 36603.2854
2026 | 2008 | 10 | 7 | 18 | 27529.419
2026 | 2008 | 10 | 7 | 19 | 9833.1304
2026 | 2008 | 10 | 7 | 20 | 0
2026 | 2008 | 10 | 7 | 21 | 0
2026 | 2008 | 10 | 7 | 22 | 0
2026 | 2008 | 10 | 7 | 23 | 0
2026 | 2008 | 10 | 7 | 24 | 0
2026 | 2008 | 10 | 8 | 1 | 0
2026 | 2008 | 10 | 8 | 2 | 0
2026 | 2008 | 10 | 8 | 3 | 0
2026 | 2008 | 10 | 8 | 4 | 0
2026 | 2008 | 10 | 8 | 5 | 0
2026 | 2008 | 10 | 8 | 6 | 0
2026 | 2008 | 10 | 8 | 7 | 0
2026 | 2008 | 10 | 8 | 8 | 32.2666
2026 | 2008 | 10 | 8 | 9 | 14429.3145
2026 | 2008 | 10 | 8 | 10 | 38812.8137
2026 | 2008 | 10 | 8 | 11 | 42784.4339
2026 | 2008 | 10 | 8 | 12 | 42238.1135
2026 | 2008 | 10 | 8 | 13 | 41563.1281
2026 | 2008 | 10 | 8 | 14 | 40964.7372
2026 | 2008 | 10 | 8 | 15 | 41067.1161
2026 | 2008 | 10 | 8 | 16 | 40231.3629
2026 | 2008 | 10 | 8 | 17 | 37982.9491
2026 | 2008 | 10 | 8 | 18 | 29859.8903
2026 | 2008 | 10 | 8 | 19 | 9247.5072
2026 | 2008 | 10 | 8 | 20 | 0
2026 | 2008 | 10 | 8 | 21 | 0
2026 | 2008 | 10 | 8 | 22 | 0
2026 | 2008 | 10 | 8 | 23 | 0
2026 | 2008 | 10 | 8 | 24 | 0
2026 | 2008 | 10 | 9 | 1 | 0
2026 | 2008 | 10 | 9 | 2 | 0
2026 | 2008 | 10 | 9 | 3 | 0
2026 | 2008 | 10 | 9 | 4 | 0
2026 | 2008 | 10 | 9 | 5 | 0
2026 | 2008 | 10 | 9 | 6 | 0
2026 | 2008 | 10 | 9 | 7 | 0
2026 | 2008 | 10 | 9 | 8 | 33.4365
2026 | 2008 | 10 | 9 | 9 | 14625.1316
2026 | 2008 | 10 | 9 | 10 | 37954.0812
2026 | 2008 | 10 | 9 | 11 | 42534.9691
2026 | 2008 | 10 | 9 | 12 | 42440.5002
2026 | 2008 | 10 | 9 | 13 | 40866.8286
2026 | 2008 | 10 | 9 | 14 | 40779.8399
2026 | 2008 | 10 | 9 | 15 | 40194.5638
2026 | 2008 | 10 | 9 | 16 | 40067.9817
2026 | 2008 | 10 | 9 | 17 | 37141.9178
2026 | 2008 | 10 | 9 | 18 | 29814.6792
2026 | 2008 | 10 | 9 | 19 | 9033.9156
2026 | 2008 | 10 | 9 | 20 | 0
2026 | 2008 | 10 | 9 | 21 | 0
2026 | 2008 | 10 | 9 | 22 | 0
2026 | 2008 | 10 | 9 | 23 | 0
2026 | 2008 | 10 | 9 | 24 | 0
2026 | 2008 | 10 | 10 | 1 | 0
2026 | 2008 | 10 | 10 | 2 | 0
2026 | 2008 | 10 | 10 | 3 | 0
2026 | 2008 | 10 | 10 | 4 | 0
2026 | 2008 | 10 | 10 | 5 | 0
2026 | 2008 | 10 | 10 | 6 | 0
2026 | 2008 | 10 | 10 | 7 | 0
2026 | 2008 | 10 | 10 | 8 | 24.1782
2026 | 2008 | 10 | 10 | 9 | 10538.1298
2026 | 2008 | 10 | 10 | 10 | 28339.8245
2026 | 2008 | 10 | 10 | 11 | 37030.6213
2026 | 2008 | 10 | 10 | 12 | 38254.4663
2026 | 2008 | 10 | 10 | 13 | 36109.094
2026 | 2008 | 10 | 10 | 14 | 37054.438
2026 | 2008 | 10 | 10 | 15 | 36156.3312
2026 | 2008 | 10 | 10 | 16 | 36585.4912
2026 | 2008 | 10 | 10 | 17 | 36408.4316
2026 | 2008 | 10 | 10 | 18 | 26976.2902
2026 | 2008 | 10 | 10 | 19 | 8153.8765
2026 | 2008 | 10 | 10 | 20 | 0
2026 | 2008 | 10 | 10 | 21 | 0
2026 | 2008 | 10 | 10 | 22 | 0
2026 | 2008 | 10 | 10 | 23 | 0
2026 | 2008 | 10 | 10 | 24 | 0
2026 | 2008 | 10 | 11 | 1 | 0
2026 | 2008 | 10 | 11 | 2 | 0
2026 | 2008 | 10 | 11 | 3 | 0
2026 | 2008 | 10 | 11 | 4 | 0
2026 | 2008 | 10 | 11 | 5 | 0
2026 | 2008 | 10 | 11 | 6 | 0
2026 | 2008 | 10 | 11 | 7 | 0
2026 | 2008 | 10 | 11 | 8 | 12.945
2026 | 2008 | 10 | 11 | 9 | 5041.5116
2026 | 2008 | 10 | 11 | 10 | 14501.2953
2026 | 2008 | 10 | 11 | 11 | 19314.1528
2026 | 2008 | 10 | 11 | 12 | 23372.1543
2026 | 2008 | 10 | 11 | 13 | 25445.6992
2026 | 2008 | 10 | 11 | 14 | 28989.3546
2026 | 2008 | 10 | 11 | 15 | 31019.6801
2026 | 2008 | 10 | 11 | 16 | 32775.3132
2026 | 2008 | 10 | 11 | 17 | 30914.3203
2026 | 2008 | 10 | 11 | 18 | 24677.0019
2026 | 2008 | 10 | 11 | 19 | 7143.3353
2026 | 2008 | 10 | 11 | 20 | 0
2026 | 2008 | 10 | 11 | 21 | 0
2026 | 2008 | 10 | 11 | 22 | 0
2026 | 2008 | 10 | 11 | 23 | 0
2026 | 2008 | 10 | 11 | 24 | 0
2026 | 2008 | 10 | 12 | 1 | 0
2026 | 2008 | 10 | 12 | 2 | 0
2026 | 2008 | 10 | 12 | 3 | 0
2026 | 2008 | 10 | 12 | 4 | 0
2026 | 2008 | 10 | 12 | 5 | 0
2026 | 2008 | 10 | 12 | 6 | 0
2026 | 2008 | 10 | 12 | 7 | 0
2026 | 2008 | 10 | 12 | 8 | 16.8739
2026 | 2008 | 10 | 12 | 9 | 4420.2088
2026 | 2008 | 10 | 12 | 10 | 15348.7748
2026 | 2008 | 10 | 12 | 11 | 21928.9495
2026 | 2008 | 10 | 12 | 12 | 26221.8415
2026 | 2008 | 10 | 12 | 13 | 26989.4248
2026 | 2008 | 10 | 12 | 14 | 26752.9564
2026 | 2008 | 10 | 12 | 15 | 25138.7813
2026 | 2008 | 10 | 12 | 16 | 23897.7486
2026 | 2008 | 10 | 12 | 17 | 22555.9634
2026 | 2008 | 10 | 12 | 18 | 19174.3709
2026 | 2008 | 10 | 12 | 19 | 4920.4605
2026 | 2008 | 10 | 12 | 20 | 0
2026 | 2008 | 10 | 12 | 21 | 0
2026 | 2008 | 10 | 12 | 22 | 0
2026 | 2008 | 10 | 12 | 23 | 0
2026 | 2008 | 10 | 12 | 24 | 0
2026 | 2008 | 10 | 13 | 1 | 0
2026 | 2008 | 10 | 13 | 2 | 0
2026 | 2008 | 10 | 13 | 3 | 0
2026 | 2008 | 10 | 13 | 4 | 0
2026 | 2008 | 10 | 13 | 5 | 0
2026 | 2008 | 10 | 13 | 6 | 0
2026 | 2008 | 10 | 13 | 7 | 0
2026 | 2008 | 10 | 13 | 8 | 17.7923
2026 | 2008 | 10 | 13 | 9 | 4121.9276
2026 | 2008 | 10 | 13 | 10 | 13009.5693
2026 | 2008 | 10 | 13 | 11 | 17283.9157
2026 | 2008 | 10 | 13 | 12 | 21129.5869
2026 | 2008 | 10 | 13 | 13 | 23665.6628
2026 | 2008 | 10 | 13 | 14 | 25028.3587
2026 | 2008 | 10 | 13 | 15 | 24099.6496
2026 | 2008 | 10 | 13 | 16 | 23777.8697
2026 | 2008 | 10 | 13 | 17 | 24553.5409
2026 | 2008 | 10 | 13 | 18 | 18956.9833
2026 | 2008 | 10 | 13 | 19 | 4448.9643
2026 | 2008 | 10 | 13 | 20 | 0
2026 | 2008 | 10 | 13 | 21 | 0
2026 | 2008 | 10 | 13 | 22 | 0
2026 | 2008 | 10 | 13 | 23 | 0
2026 | 2008 | 10 | 13 | 24 | 0
2026 | 2008 | 10 | 14 | 1 | 0
2026 | 2008 | 10 | 14 | 2 | 0
2026 | 2008 | 10 | 14 | 3 | 0
2026 | 2008 | 10 | 14 | 4 | 0
2026 | 2008 | 10 | 14 | 5 | 0
2026 | 2008 | 10 | 14 | 6 | 0
2026 | 2008 | 10 | 14 | 7 | 0
2026 | 2008 | 10 | 14 | 8 | 1.4228
2026 | 2008 | 10 | 14 | 9 | 1131.7524
2026 | 2008 | 10 | 14 | 10 | 5189.5624
2026 | 2008 | 10 | 14 | 11 | 9942.0828
2026 | 2008 | 10 | 14 | 12 | 16317.6741
2026 | 2008 | 10 | 14 | 13 | 19468.0104
2026 | 2008 | 10 | 14 | 14 | 20805.4406
2026 | 2008 | 10 | 14 | 15 | 22509.3373
2026 | 2008 | 10 | 14 | 16 | 22909.4589
2026 | 2008 | 10 | 14 | 17 | 21704.2537
2026 | 2008 | 10 | 14 | 18 | 18447.887
2026 | 2008 | 10 | 14 | 19 | 4165.0588
2026 | 2008 | 10 | 14 | 20 | 0
2026 | 2008 | 10 | 14 | 21 | 0
2026 | 2008 | 10 | 14 | 22 | 0
2026 | 2008 | 10 | 14 | 23 | 0
2026 | 2008 | 10 | 14 | 24 | 0
2026 | 2008 | 10 | 15 | 1 | 0
2026 | 2008 | 10 | 15 | 2 | 0
2026 | 2008 | 10 | 15 | 3 | 0
2026 | 2008 | 10 | 15 | 4 | 0
2026 | 2008 | 10 | 15 | 5 | 0
2026 | 2008 | 10 | 15 | 6 | 0
2026 | 2008 | 10 | 15 | 7 | 0
2026 | 2008 | 10 | 15 | 8 | 6.4361
2026 | 2008 | 10 | 15 | 9 | 2078.5455
2026 | 2008 | 10 | 15 | 10 | 10230.6641
2026 | 2008 | 10 | 15 | 11 | 14928.6482
2026 | 2008 | 10 | 15 | 12 | 18871.9232
2026 | 2008 | 10 | 15 | 13 | 20925.8007
2026 | 2008 | 10 | 15 | 14 | 22045.9115
2026 | 2008 | 10 | 15 | 15 | 22108.5954
2026 | 2008 | 10 | 15 | 16 | 20596.3755
2026 | 2008 | 10 | 15 | 17 | 20299.1316
2026 | 2008 | 10 | 15 | 18 | 18755.5797
2026 | 2008 | 10 | 15 | 19 | 4921.7051
2026 | 2008 | 10 | 15 | 20 | 0
2026 | 2008 | 10 | 15 | 21 | 0
2026 | 2008 | 10 | 15 | 22 | 0
2026 | 2008 | 10 | 15 | 23 | 0
2026 | 2008 | 10 | 15 | 24 | 0
2026 | 2008 | 10 | 16 | 1 | 0
2026 | 2008 | 10 | 16 | 2 | 0
2026 | 2008 | 10 | 16 | 3 | 0
2026 | 2008 | 10 | 16 | 4 | 0
2026 | 2008 | 10 | 16 | 5 | 0
2026 | 2008 | 10 | 16 | 6 | 0
2026 | 2008 | 10 | 16 | 7 | 0
2026 | 2008 | 10 | 16 | 8 | 0.48227
2026 | 2008 | 10 | 16 | 9 | 1310.4117
2026 | 2008 | 10 | 16 | 10 | 7257.2833
2026 | 2008 | 10 | 16 | 11 | 12274.6795
2026 | 2008 | 10 | 16 | 12 | 19349.0455
2026 | 2008 | 10 | 16 | 13 | 22044.2633
2026 | 2008 | 10 | 16 | 14 | 23564.0538
2026 | 2008 | 10 | 16 | 15 | 24119.5615
2026 | 2008 | 10 | 16 | 16 | 24336.3003
2026 | 2008 | 10 | 16 | 17 | 20669.2304
2026 | 2008 | 10 | 16 | 18 | 19819.9634
2026 | 2008 | 10 | 16 | 19 | 4656.1253
2026 | 2008 | 10 | 16 | 20 | 0
2026 | 2008 | 10 | 16 | 21 | 0
2026 | 2008 | 10 | 16 | 22 | 0
2026 | 2008 | 10 | 16 | 23 | 0
2026 | 2008 | 10 | 16 | 24 | 0
2026 | 2008 | 10 | 17 | 1 | 0
2026 | 2008 | 10 | 17 | 2 | 0
2026 | 2008 | 10 | 17 | 3 | 0
2026 | 2008 | 10 | 17 | 4 | 0
2026 | 2008 | 10 | 17 | 5 | 0
2026 | 2008 | 10 | 17 | 6 | 0
2026 | 2008 | 10 | 17 | 7 | 0
2026 | 2008 | 10 | 17 | 8 | 2.332
2026 | 2008 | 10 | 17 | 9 | 6280.9125
2026 | 2008 | 10 | 17 | 10 | 21613.4681
2026 | 2008 | 10 | 17 | 11 | 25370.3116
2026 | 2008 | 10 | 17 | 12 | 26844.8317
2026 | 2008 | 10 | 17 | 13 | 27695.6874
2026 | 2008 | 10 | 17 | 14 | 27930.9013
2026 | 2008 | 10 | 17 | 15 | 27063.7894
2026 | 2008 | 10 | 17 | 16 | 26995.3837
2026 | 2008 | 10 | 17 | 17 | 26337.9012
2026 | 2008 | 10 | 17 | 18 | 20718.1915
2026 | 2008 | 10 | 17 | 19 | 4634.6912
2026 | 2008 | 10 | 17 | 20 | 0
2026 | 2008 | 10 | 17 | 21 | 0
2026 | 2008 | 10 | 17 | 22 | 0
2026 | 2008 | 10 | 17 | 23 | 0
2026 | 2008 | 10 | 17 | 24 | 0
2026 | 2008 | 10 | 18 | 1 | 0
2026 | 2008 | 10 | 18 | 2 | 0
2026 | 2008 | 10 | 18 | 3 | 0
2026 | 2008 | 10 | 18 | 4 | 0
2026 | 2008 | 10 | 18 | 5 | 0
2026 | 2008 | 10 | 18 | 6 | 0
2026 | 2008 | 10 | 18 | 7 | 0
2026 | 2008 | 10 | 18 | 8 | 20.7526
2026 | 2008 | 10 | 18 | 9 | 11816.5916
2026 | 2008 | 10 | 18 | 10 | 33558.6802
2026 | 2008 | 10 | 18 | 11 | 39289.1081
2026 | 2008 | 10 | 18 | 12 | 39402.7821
2026 | 2008 | 10 | 18 | 13 | 38961.9281
2026 | 2008 | 10 | 18 | 14 | 37487.9984
2026 | 2008 | 10 | 18 | 15 | 37794.2333
2026 | 2008 | 10 | 18 | 16 | 37120.8968
2026 | 2008 | 10 | 18 | 17 | 34836.6744
2026 | 2008 | 10 | 18 | 18 | 26350.2915
2026 | 2008 | 10 | 18 | 19 | 5360.715
2026 | 2008 | 10 | 18 | 20 | 0
2026 | 2008 | 10 | 18 | 21 | 0
2026 | 2008 | 10 | 18 | 22 | 0
2026 | 2008 | 10 | 18 | 23 | 0
2026 | 2008 | 10 | 18 | 24 | 0
2026 | 2008 | 10 | 19 | 1 | 0
2026 | 2008 | 10 | 19 | 2 | 0
2026 | 2008 | 10 | 19 | 3 | 0
2026 | 2008 | 10 | 19 | 4 | 0
2026 | 2008 | 10 | 19 | 5 | 0
2026 | 2008 | 10 | 19 | 6 | 0
2026 | 2008 | 10 | 19 | 7 | 0
2026 | 2008 | 10 | 19 | 8 | 19.9747
2026 | 2008 | 10 | 19 | 9 | 11830.9026
2026 | 2008 | 10 | 19 | 10 | 34702.6424
2026 | 2008 | 10 | 19 | 11 | 38927.6831
2026 | 2008 | 10 | 19 | 12 | 39958.1002
2026 | 2008 | 10 | 19 | 13 | 38769.0579
2026 | 2008 | 10 | 19 | 14 | 37784.4565
2026 | 2008 | 10 | 19 | 15 | 37496.3588
2026 | 2008 | 10 | 19 | 16 | 35090.1644
2026 | 2008 | 10 | 19 | 17 | 34197.5783
2026 | 2008 | 10 | 19 | 18 | 23857.1398
2026 | 2008 | 10 | 19 | 19 | 4809.3575
2026 | 2008 | 10 | 19 | 20 | 0
2026 | 2008 | 10 | 19 | 21 | 0
2026 | 2008 | 10 | 19 | 22 | 0
2026 | 2008 | 10 | 19 | 23 | 0
2026 | 2008 | 10 | 19 | 24 | 0
2026 | 2008 | 10 | 20 | 1 | 0
2026 | 2008 | 10 | 20 | 2 | 0
2026 | 2008 | 10 | 20 | 3 | 0
2026 | 2008 | 10 | 20 | 4 | 0
2026 | 2008 | 10 | 20 | 5 | 0
2026 | 2008 | 10 | 20 | 6 | 0
2026 | 2008 | 10 | 20 | 7 | 0
2026 | 2008 | 10 | 20 | 8 | 15.5983
2026 | 2008 | 10 | 20 | 9 | 10253.7547
2026 | 2008 | 10 | 20 | 10 | 31531.1697
2026 | 2008 | 10 | 20 | 11 | 36429.0664
2026 | 2008 | 10 | 20 | 12 | 36755.0313
2026 | 2008 | 10 | 20 | 13 | 37103.2083
2026 | 2008 | 10 | 20 | 14 | 36040.1525
2026 | 2008 | 10 | 20 | 15 | 35760.1196
2026 | 2008 | 10 | 20 | 16 | 34530.6152
2026 | 2008 | 10 | 20 | 17 | 31722.8529
2026 | 2008 | 10 | 20 | 18 | 23631.2215
2026 | 2008 | 10 | 20 | 19 | 4439.1621
2026 | 2008 | 10 | 20 | 20 | 0
2026 | 2008 | 10 | 20 | 21 | 0
2026 | 2008 | 10 | 20 | 22 | 0
2026 | 2008 | 10 | 20 | 23 | 0
2026 | 2008 | 10 | 20 | 24 | 0
2026 | 2008 | 10 | 21 | 1 | 0
2026 | 2008 | 10 | 21 | 2 | 0
2026 | 2008 | 10 | 21 | 3 | 0
2026 | 2008 | 10 | 21 | 4 | 0
2026 | 2008 | 10 | 21 | 5 | 0
2026 | 2008 | 10 | 21 | 6 | 0
2026 | 2008 | 10 | 21 | 7 | 0
2026 | 2008 | 10 | 21 | 8 | 9.6645
2026 | 2008 | 10 | 21 | 9 | 5923.0692
2026 | 2008 | 10 | 21 | 10 | 18358.3165
2026 | 2008 | 10 | 21 | 11 | 24523.2048
2026 | 2008 | 10 | 21 | 12 | 27218.4648
2026 | 2008 | 10 | 21 | 13 | 29745.0796
2026 | 2008 | 10 | 21 | 14 | 30781.7708
2026 | 2008 | 10 | 21 | 15 | 30740.3731
2026 | 2008 | 10 | 21 | 16 | 30826.2367
2026 | 2008 | 10 | 21 | 17 | 29165.1663
2026 | 2008 | 10 | 21 | 18 | 21386.8158
2026 | 2008 | 10 | 21 | 19 | 3837.9477
2026 | 2008 | 10 | 21 | 20 | 0
2026 | 2008 | 10 | 21 | 21 | 0
2026 | 2008 | 10 | 21 | 22 | 0
2026 | 2008 | 10 | 21 | 23 | 0
2026 | 2008 | 10 | 21 | 24 | 0
2026 | 2008 | 10 | 22 | 1 | 0
2026 | 2008 | 10 | 22 | 2 | 0
2026 | 2008 | 10 | 22 | 3 | 0
2026 | 2008 | 10 | 22 | 4 | 0
2026 | 2008 | 10 | 22 | 5 | 0
2026 | 2008 | 10 | 22 | 6 | 0
2026 | 2008 | 10 | 22 | 7 | 0
2026 | 2008 | 10 | 22 | 8 | 8.5606
2026 | 2008 | 10 | 22 | 9 | 4479.5935
2026 | 2008 | 10 | 22 | 10 | 14795.7771
2026 | 2008 | 10 | 22 | 11 | 21175.0046
2026 | 2008 | 10 | 22 | 12 | 24775.8587
2026 | 2008 | 10 | 22 | 13 | 27648.8424
2026 | 2008 | 10 | 22 | 14 | 27637.8611
2026 | 2008 | 10 | 22 | 15 | 26460.8839
2026 | 2008 | 10 | 22 | 16 | 27957.3391
2026 | 2008 | 10 | 22 | 17 | 24170.3847
2026 | 2008 | 10 | 22 | 18 | 18982.2316
2026 | 2008 | 10 | 22 | 19 | 3409.1658
2026 | 2008 | 10 | 22 | 20 | 0
2026 | 2008 | 10 | 22 | 21 | 0
2026 | 2008 | 10 | 22 | 22 | 0
2026 | 2008 | 10 | 22 | 23 | 0
2026 | 2008 | 10 | 22 | 24 | 0
2026 | 2008 | 10 | 23 | 1 | 0
2026 | 2008 | 10 | 23 | 2 | 0
2026 | 2008 | 10 | 23 | 3 | 0
2026 | 2008 | 10 | 23 | 4 | 0
2026 | 2008 | 10 | 23 | 5 | 0
2026 | 2008 | 10 | 23 | 6 | 0
2026 | 2008 | 10 | 23 | 7 | 0
2026 | 2008 | 10 | 23 | 8 | 7.7832
2026 | 2008 | 10 | 23 | 9 | 11010.8656
2026 | 2008 | 10 | 23 | 10 | 32970.686
2026 | 2008 | 10 | 23 | 11 | 38920.1556
2026 | 2008 | 10 | 23 | 12 | 39426.2325
2026 | 2008 | 10 | 23 | 13 | 38827.5777
2026 | 2008 | 10 | 23 | 14 | 38430.5684
2026 | 2008 | 10 | 23 | 15 | 37860.4242
2026 | 2008 | 10 | 23 | 16 | 37482.2844
2026 | 2008 | 10 | 23 | 17 | 34766.0923
2026 | 2008 | 10 | 23 | 18 | 25339.7442
2026 | 2008 | 10 | 23 | 19 | 3505.3029
2026 | 2008 | 10 | 23 | 20 | 0
2026 | 2008 | 10 | 23 | 21 | 0
2026 | 2008 | 10 | 23 | 22 | 0
2026 | 2008 | 10 | 23 | 23 | 0
2026 | 2008 | 10 | 23 | 24 | 0
2026 | 2008 | 10 | 24 | 1 | 0
2026 | 2008 | 10 | 24 | 2 | 0
2026 | 2008 | 10 | 24 | 3 | 0
2026 | 2008 | 10 | 24 | 4 | 0
2026 | 2008 | 10 | 24 | 5 | 0
2026 | 2008 | 10 | 24 | 6 | 0
2026 | 2008 | 10 | 24 | 7 | 0
2026 | 2008 | 10 | 24 | 8 | 11.3728
2026 | 2008 | 10 | 24 | 9 | 11135.2486
2026 | 2008 | 10 | 24 | 10 | 34980.1205
2026 | 2008 | 10 | 24 | 11 | 40318.5358
2026 | 2008 | 10 | 24 | 12 | 40838.8235
2026 | 2008 | 10 | 24 | 13 | 39026.1418
2026 | 2008 | 10 | 24 | 14 | 38474.5437
2026 | 2008 | 10 | 24 | 15 | 38089.0719
2026 | 2008 | 10 | 24 | 16 | 36105.1615
2026 | 2008 | 10 | 24 | 17 | 34629.4642
2026 | 2008 | 10 | 24 | 18 | 22166.8335
2026 | 2008 | 10 | 24 | 19 | 2992.1833
2026 | 2008 | 10 | 24 | 20 | 0
2026 | 2008 | 10 | 24 | 21 | 0
2026 | 2008 | 10 | 24 | 22 | 0
2026 | 2008 | 10 | 24 | 23 | 0
2026 | 2008 | 10 | 24 | 24 | 0
2026 | 2008 | 10 | 25 | 1 | 0
2026 | 2008 | 10 | 25 | 2 | 0
2026 | 2008 | 10 | 25 | 3 | 0
2026 | 2008 | 10 | 25 | 4 | 0
2026 | 2008 | 10 | 25 | 5 | 0
2026 | 2008 | 10 | 25 | 6 | 0
2026 | 2008 | 10 | 25 | 7 | 0
2026 | 2008 | 10 | 25 | 8 | 10.3332
2026 | 2008 | 10 | 25 | 9 | 10015.2867
2026 | 2008 | 10 | 25 | 10 | 32395.3463
2026 | 2008 | 10 | 25 | 11 | 37525.4154
2026 | 2008 | 10 | 25 | 12 | 38422.3041
2026 | 2008 | 10 | 25 | 13 | 37214.6854
2026 | 2008 | 10 | 25 | 14 | 36010.1265
2026 | 2008 | 10 | 25 | 15 | 36117.6825
2026 | 2008 | 10 | 25 | 16 | 35268.4914
2026 | 2008 | 10 | 25 | 17 | 32519.2573
2026 | 2008 | 10 | 25 | 18 | 20884.9065
2026 | 2008 | 10 | 25 | 19 | 2501.9476
2026 | 2008 | 10 | 25 | 20 | 0
2026 | 2008 | 10 | 25 | 21 | 0
2026 | 2008 | 10 | 25 | 22 | 0
2026 | 2008 | 10 | 25 | 23 | 0
2026 | 2008 | 10 | 25 | 24 | 0
2026 | 2008 | 10 | 26 | 1 | 0
2026 | 2008 | 10 | 26 | 2 | 0
2026 | 2008 | 10 | 26 | 3 | 0
2026 | 2008 | 10 | 26 | 4 | 0
2026 | 2008 | 10 | 26 | 5 | 0
2026 | 2008 | 10 | 26 | 6 | 0
2026 | 2008 | 10 | 26 | 7 | 0
2026 | 2008 | 10 | 26 | 8 | 8.289
2026 | 2008 | 10 | 26 | 9 | 8421.5818
2026 | 2008 | 10 | 26 | 10 | 26842.7186
2026 | 2008 | 10 | 26 | 11 | 30530.9596
2026 | 2008 | 10 | 26 | 12 | 31233.8425
2026 | 2008 | 10 | 26 | 13 | 32162.4111
2026 | 2008 | 10 | 26 | 14 | 32891.0966
2026 | 2008 | 10 | 26 | 15 | 31543.6788
2026 | 2008 | 10 | 26 | 16 | 29544.1609
2026 | 2008 | 10 | 26 | 17 | 29150.7545
2026 | 2008 | 10 | 26 | 18 | 22251.103
2026 | 2008 | 10 | 26 | 19 | 2264.4997
2026 | 2008 | 10 | 26 | 20 | 0
2026 | 2008 | 10 | 26 | 21 | 0
2026 | 2008 | 10 | 26 | 22 | 0
2026 | 2008 | 10 | 26 | 23 | 0
2026 | 2008 | 10 | 26 | 24 | 0
2026 | 2008 | 10 | 27 | 1 | 0
2026 | 2008 | 10 | 27 | 2 | 0
2026 | 2008 | 10 | 27 | 3 | 0
2026 | 2008 | 10 | 27 | 4 | 0
2026 | 2008 | 10 | 27 | 5 | 0
2026 | 2008 | 10 | 27 | 6 | 0
2026 | 2008 | 10 | 27 | 7 | 0
2026 | 2008 | 10 | 27 | 8 | 2.3435
2026 | 2008 | 10 | 27 | 9 | 9904.2465
2026 | 2008 | 10 | 27 | 10 | 33191.4481
2026 | 2008 | 10 | 27 | 11 | 39293.2053
2026 | 2008 | 10 | 27 | 12 | 40932.769
2026 | 2008 | 10 | 27 | 13 | 39200.4905
2026 | 2008 | 10 | 27 | 14 | 38954.0764
2026 | 2008 | 10 | 27 | 15 | 38819.8407
2026 | 2008 | 10 | 27 | 16 | 37107.7998
2026 | 2008 | 10 | 27 | 17 | 34605.0502
2026 | 2008 | 10 | 27 | 18 | 21741.4862
2026 | 2008 | 10 | 27 | 19 | 2242.9438
2026 | 2008 | 10 | 27 | 20 | 0
2026 | 2008 | 10 | 27 | 21 | 0
2026 | 2008 | 10 | 27 | 22 | 0
2026 | 2008 | 10 | 27 | 23 | 0
2026 | 2008 | 10 | 27 | 24 | 0
2026 | 2008 | 10 | 28 | 1 | 0
2026 | 2008 | 10 | 28 | 2 | 0
2026 | 2008 | 10 | 28 | 3 | 0
2026 | 2008 | 10 | 28 | 4 | 0
2026 | 2008 | 10 | 28 | 5 | 0
2026 | 2008 | 10 | 28 | 6 | 0
2026 | 2008 | 10 | 28 | 7 | 0
2026 | 2008 | 10 | 28 | 8 | 4.1892
2026 | 2008 | 10 | 28 | 9 | 10773.4174
2026 | 2008 | 10 | 28 | 10 | 33653.2394
2026 | 2008 | 10 | 28 | 11 | 38289.7692
2026 | 2008 | 10 | 28 | 12 | 39198.1253
2026 | 2008 | 10 | 28 | 13 | 37677.5338
2026 | 2008 | 10 | 28 | 14 | 36674.1158
2026 | 2008 | 10 | 28 | 15 | 36525.0268
2026 | 2008 | 10 | 28 | 16 | 35168.4711
2026 | 2008 | 10 | 28 | 17 | 31794.2887
2026 | 2008 | 10 | 28 | 18 | 22600.1916
2026 | 2008 | 10 | 28 | 19 | 2071.2997
2026 | 2008 | 10 | 28 | 20 | 0
2026 | 2008 | 10 | 28 | 21 | 0
2026 | 2008 | 10 | 28 | 22 | 0
2026 | 2008 | 10 | 28 | 23 | 0
2026 | 2008 | 10 | 28 | 24 | 0
2026 | 2008 | 10 | 29 | 1 | 0
2026 | 2008 | 10 | 29 | 2 | 0
2026 | 2008 | 10 | 29 | 3 | 0
2026 | 2008 | 10 | 29 | 4 | 0
2026 | 2008 | 10 | 29 | 5 | 0
2026 | 2008 | 10 | 29 | 6 | 0
2026 | 2008 | 10 | 29 | 7 | 0
2026 | 2008 | 10 | 29 | 8 | 5.4891
2026 | 2008 | 10 | 29 | 9 | 9213.075
2026 | 2008 | 10 | 29 | 10 | 31549.3503
2026 | 2008 | 10 | 29 | 11 | 37438.8946
2026 | 2008 | 10 | 29 | 12 | 37501.8688
2026 | 2008 | 10 | 29 | 13 | 36322.345
2026 | 2008 | 10 | 29 | 14 | 35727.0419
2026 | 2008 | 10 | 29 | 15 | 35002.7127
2026 | 2008 | 10 | 29 | 16 | 34022.6344
2026 | 2008 | 10 | 29 | 17 | 32608.4484
2026 | 2008 | 10 | 29 | 18 | 20651.3364
2026 | 2008 | 10 | 29 | 19 | 1825.5267
2026 | 2008 | 10 | 29 | 20 | 0
2026 | 2008 | 10 | 29 | 21 | 0
2026 | 2008 | 10 | 29 | 22 | 0
2026 | 2008 | 10 | 29 | 23 | 0
2026 | 2008 | 10 | 29 | 24 | 0
2026 | 2008 | 10 | 30 | 1 | 0
2026 | 2008 | 10 | 30 | 2 | 0
2026 | 2008 | 10 | 30 | 3 | 0
2026 | 2008 | 10 | 30 | 4 | 0
2026 | 2008 | 10 | 30 | 5 | 0
2026 | 2008 | 10 | 30 | 6 | 0
2026 | 2008 | 10 | 30 | 7 | 0
2026 | 2008 | 10 | 30 | 8 | 2.4384
2026 | 2008 | 10 | 30 | 9 | 5803.4628
2026 | 2008 | 10 | 30 | 10 | 18997.3119
2026 | 2008 | 10 | 30 | 11 | 23603.6012
2026 | 2008 | 10 | 30 | 12 | 26229.7252
2026 | 2008 | 10 | 30 | 13 | 29056.8275
2026 | 2008 | 10 | 30 | 14 | 31198.7246
2026 | 2008 | 10 | 30 | 15 | 31060.8417
2026 | 2008 | 10 | 30 | 16 | 32443.4008
2026 | 2008 | 10 | 30 | 17 | 29067.6726
2026 | 2008 | 10 | 30 | 18 | 18503.7712
2026 | 2008 | 10 | 30 | 19 | 1609.2495
2026 | 2008 | 10 | 30 | 20 | 0
2026 | 2008 | 10 | 30 | 21 | 0
2026 | 2008 | 10 | 30 | 22 | 0
2026 | 2008 | 10 | 30 | 23 | 0
2026 | 2008 | 10 | 30 | 24 | 0
2026 | 2008 | 10 | 31 | 1 | 0
2026 | 2008 | 10 | 31 | 2 | 0
2026 | 2008 | 10 | 31 | 3 | 0
2026 | 2008 | 10 | 31 | 4 | 0
2026 | 2008 | 10 | 31 | 5 | 0
2026 | 2008 | 10 | 31 | 6 | 0
2026 | 2008 | 10 | 31 | 7 | 0
2026 | 2008 | 10 | 31 | 8 | 2.1371
2026 | 2008 | 10 | 31 | 9 | 4660.7062
2026 | 2008 | 10 | 31 | 10 | 16339.3689
2026 | 2008 | 10 | 31 | 11 | 21133.1295
2026 | 2008 | 10 | 31 | 12 | 25926.6289
2026 | 2008 | 10 | 31 | 13 | 28145.2418
2026 | 2008 | 10 | 31 | 14 | 29706.9677
2026 | 2008 | 10 | 31 | 15 | 30596.5222
2026 | 2008 | 10 | 31 | 16 | 29592.1989
2026 | 2008 | 10 | 31 | 17 | 29406.2872
2026 | 2008 | 10 | 31 | 18 | 17351.7323
2026 | 2008 | 10 | 31 | 19 | 2451.3487
2026 | 2008 | 10 | 31 | 20 | 0
2026 | 2008 | 10 | 31 | 21 | 0
2026 | 2008 | 10 | 31 | 22 | 0
2026 | 2008 | 10 | 31 | 23 | 0
2026 | 2008 | 10 | 31 | 24 | 0
2027 | 2008 | 10 | 1 | 1 | 0
2027 | 2008 | 10 | 1 | 2 | 0
2027 | 2008 | 10 | 1 | 3 | 0
2027 | 2008 | 10 | 1 | 4 | 0
2027 | 2008 | 10 | 1 | 5 | 0
2027 | 2008 | 10 | 1 | 6 | 0
2027 | 2008 | 10 | 1 | 7 | 0
2027 | 2008 | 10 | 1 | 8 | 48.6855
2027 | 2008 | 10 | 1 | 9 | 19144.4848
2027 | 2008 | 10 | 1 | 10 | 48160.1679
2027 | 2008 | 10 | 1 | 11 | 53254.0516
2027 | 2008 | 10 | 1 | 12 | 53804.8485
2027 | 2008 | 10 | 1 | 13 | 52743.2263
2027 | 2008 | 10 | 1 | 14 | 52130.4787
2027 | 2008 | 10 | 1 | 15 | 51041.1675
2027 | 2008 | 10 | 1 | 16 | 51799.1474
2027 | 2008 | 10 | 1 | 17 | 50703.647
2027 | 2008 | 10 | 1 | 18 | 39746.5916
2027 | 2008 | 10 | 1 | 19 | 13557.2116
2027 | 2008 | 10 | 1 | 20 | 0
2027 | 2008 | 10 | 1 | 21 | 0
2027 | 2008 | 10 | 1 | 22 | 0
2027 | 2008 | 10 | 1 | 23 | 0
2027 | 2008 | 10 | 1 | 24 | 0
2027 | 2008 | 10 | 2 | 1 | 0
2027 | 2008 | 10 | 2 | 2 | 0
2027 | 2008 | 10 | 2 | 3 | 0
2027 | 2008 | 10 | 2 | 4 | 0
2027 | 2008 | 10 | 2 | 5 | 0
2027 | 2008 | 10 | 2 | 6 | 0
2027 | 2008 | 10 | 2 | 7 | 0
2027 | 2008 | 10 | 2 | 8 | 60.204
2027 | 2008 | 10 | 2 | 9 | 19423.354
2027 | 2008 | 10 | 2 | 10 | 46424.1429
2027 | 2008 | 10 | 2 | 11 | 53546.1576
2027 | 2008 | 10 | 2 | 12 | 53748.4824
2027 | 2008 | 10 | 2 | 13 | 51997.2515
2027 | 2008 | 10 | 2 | 14 | 51358.3469
2027 | 2008 | 10 | 2 | 15 | 50086.0504
2027 | 2008 | 10 | 2 | 16 | 50993.7796
2027 | 2008 | 10 | 2 | 17 | 50083.5248
2027 | 2008 | 10 | 2 | 18 | 39411.8473
2027 | 2008 | 10 | 2 | 19 | 13381.9058
2027 | 2008 | 10 | 2 | 20 | 0
2027 | 2008 | 10 | 2 | 21 | 0
2027 | 2008 | 10 | 2 | 22 | 0
2027 | 2008 | 10 | 2 | 23 | 0
2027 | 2008 | 10 | 2 | 24 | 0
2027 | 2008 | 10 | 3 | 1 | 0
2027 | 2008 | 10 | 3 | 2 | 0
2027 | 2008 | 10 | 3 | 3 | 0
2027 | 2008 | 10 | 3 | 4 | 0
2027 | 2008 | 10 | 3 | 5 | 0
2027 | 2008 | 10 | 3 | 6 | 0
2027 | 2008 | 10 | 3 | 7 | 0
2027 | 2008 | 10 | 3 | 8 | 57.8862
2027 | 2008 | 10 | 3 | 9 | 15633.426
2027 | 2008 | 10 | 3 | 10 | 43461.3452
2027 | 2008 | 10 | 3 | 11 | 50295.9607
2027 | 2008 | 10 | 3 | 12 | 49600.0398
2027 | 2008 | 10 | 3 | 13 | 48605.2566
2027 | 2008 | 10 | 3 | 14 | 47455.5968
2027 | 2008 | 10 | 3 | 15 | 47800.0402
2027 | 2008 | 10 | 3 | 16 | 46638.0193
2027 | 2008 | 10 | 3 | 17 | 45402.2199
2027 | 2008 | 10 | 3 | 18 | 36786.5964
2027 | 2008 | 10 | 3 | 19 | 12534.6745
2027 | 2008 | 10 | 3 | 20 | 0
2027 | 2008 | 10 | 3 | 21 | 0
2027 | 2008 | 10 | 3 | 22 | 0
2027 | 2008 | 10 | 3 | 23 | 0
2027 | 2008 | 10 | 3 | 24 | 0
2027 | 2008 | 10 | 4 | 1 | 0
2027 | 2008 | 10 | 4 | 2 | 0
2027 | 2008 | 10 | 4 | 3 | 0
2027 | 2008 | 10 | 4 | 4 | 0
2027 | 2008 | 10 | 4 | 5 | 0
2027 | 2008 | 10 | 4 | 6 | 0
2027 | 2008 | 10 | 4 | 7 | 0
2027 | 2008 | 10 | 4 | 8 | 37.5899
2027 | 2008 | 10 | 4 | 9 | 11537.0993
2027 | 2008 | 10 | 4 | 10 | 36348.7193
2027 | 2008 | 10 | 4 | 11 | 46084.4037
2027 | 2008 | 10 | 4 | 12 | 50094.8268
2027 | 2008 | 10 | 4 | 13 | 50032.2642
2027 | 2008 | 10 | 4 | 14 | 48717.5716
2027 | 2008 | 10 | 4 | 15 | 48216.2926
2027 | 2008 | 10 | 4 | 16 | 47712.7075
2027 | 2008 | 10 | 4 | 17 | 46660.7291
2027 | 2008 | 10 | 4 | 18 | 35581.5713
2027 | 2008 | 10 | 4 | 19 | 12187.7834
2027 | 2008 | 10 | 4 | 20 | 0
2027 | 2008 | 10 | 4 | 21 | 0
2027 | 2008 | 10 | 4 | 22 | 0
2027 | 2008 | 10 | 4 | 23 | 0
2027 | 2008 | 10 | 4 | 24 | 0
2027 | 2008 | 10 | 5 | 1 | 0
2027 | 2008 | 10 | 5 | 2 | 0
2027 | 2008 | 10 | 5 | 3 | 0
2027 | 2008 | 10 | 5 | 4 | 0
2027 | 2008 | 10 | 5 | 5 | 0
2027 | 2008 | 10 | 5 | 6 | 0
2027 | 2008 | 10 | 5 | 7 | 0
2027 | 2008 | 10 | 5 | 8 | 39.1087
2027 | 2008 | 10 | 5 | 9 | 11875.1732
2027 | 2008 | 10 | 5 | 10 | 32118.0148
2027 | 2008 | 10 | 5 | 11 | 35090.9529
2027 | 2008 | 10 | 5 | 12 | 39721.3755
2027 | 2008 | 10 | 5 | 13 | 40645.4408
2027 | 2008 | 10 | 5 | 14 | 37916.1158
2027 | 2008 | 10 | 5 | 15 | 36321.2998
2027 | 2008 | 10 | 5 | 16 | 36376.0728
2027 | 2008 | 10 | 5 | 17 | 34741.4757
2027 | 2008 | 10 | 5 | 18 | 29299.5823
2027 | 2008 | 10 | 5 | 19 | 10256.3501
2027 | 2008 | 10 | 5 | 20 | 0
2027 | 2008 | 10 | 5 | 21 | 0
2027 | 2008 | 10 | 5 | 22 | 0
2027 | 2008 | 10 | 5 | 23 | 0
2027 | 2008 | 10 | 5 | 24 | 0
2027 | 2008 | 10 | 6 | 1 | 0
2027 | 2008 | 10 | 6 | 2 | 0
2027 | 2008 | 10 | 6 | 3 | 0
2027 | 2008 | 10 | 6 | 4 | 0
2027 | 2008 | 10 | 6 | 5 | 0
2027 | 2008 | 10 | 6 | 6 | 0
2027 | 2008 | 10 | 6 | 7 | 0
2027 | 2008 | 10 | 6 | 8 | 18.5113
2027 | 2008 | 10 | 6 | 9 | 9110.0031
2027 | 2008 | 10 | 6 | 10 | 29219.0169
2027 | 2008 | 10 | 6 | 11 | 39504.021
2027 | 2008 | 10 | 6 | 12 | 43773.2937
2027 | 2008 | 10 | 6 | 13 | 44603.9954
2027 | 2008 | 10 | 6 | 14 | 44519.568
2027 | 2008 | 10 | 6 | 15 | 44548.1374
2027 | 2008 | 10 | 6 | 16 | 46123.2329
2027 | 2008 | 10 | 6 | 17 | 45796.9594
2027 | 2008 | 10 | 6 | 18 | 35749.2562
2027 | 2008 | 10 | 6 | 19 | 11616.6969
2027 | 2008 | 10 | 6 | 20 | 0
2027 | 2008 | 10 | 6 | 21 | 0
2027 | 2008 | 10 | 6 | 22 | 0
2027 | 2008 | 10 | 6 | 23 | 0
2027 | 2008 | 10 | 6 | 24 | 0
2027 | 2008 | 10 | 7 | 1 | 0
2027 | 2008 | 10 | 7 | 2 | 0
2027 | 2008 | 10 | 7 | 3 | 0
2027 | 2008 | 10 | 7 | 4 | 0
2027 | 2008 | 10 | 7 | 5 | 0
2027 | 2008 | 10 | 7 | 6 | 0
2027 | 2008 | 10 | 7 | 7 | 0
2027 | 2008 | 10 | 7 | 8 | 23.6528
2027 | 2008 | 10 | 7 | 9 | 12257.4184
2027 | 2008 | 10 | 7 | 10 | 38460.8682
2027 | 2008 | 10 | 7 | 11 | 44336.7451
2027 | 2008 | 10 | 7 | 12 | 48527.0801
2027 | 2008 | 10 | 7 | 13 | 49283.3208
2027 | 2008 | 10 | 7 | 14 | 49363.9084
2027 | 2008 | 10 | 7 | 15 | 48749.6996
2027 | 2008 | 10 | 7 | 16 | 50172.3537
2027 | 2008 | 10 | 7 | 17 | 46635.5
2027 | 2008 | 10 | 7 | 18 | 35171.3841
2027 | 2008 | 10 | 7 | 19 | 12438.1404
2027 | 2008 | 10 | 7 | 20 | 0
2027 | 2008 | 10 | 7 | 21 | 0
2027 | 2008 | 10 | 7 | 22 | 0
2027 | 2008 | 10 | 7 | 23 | 0
2027 | 2008 | 10 | 7 | 24 | 0
2027 | 2008 | 10 | 8 | 1 | 0
2027 | 2008 | 10 | 8 | 2 | 0
2027 | 2008 | 10 | 8 | 3 | 0
2027 | 2008 | 10 | 8 | 4 | 0
2027 | 2008 | 10 | 8 | 5 | 0
2027 | 2008 | 10 | 8 | 6 | 0
2027 | 2008 | 10 | 8 | 7 | 0
2027 | 2008 | 10 | 8 | 8 | 32.2666
2027 | 2008 | 10 | 8 | 9 | 18375.8363
2027 | 2008 | 10 | 8 | 10 | 49649.3904
2027 | 2008 | 10 | 8 | 11 | 54411.6663
2027 | 2008 | 10 | 8 | 12 | 53867.552
2027 | 2008 | 10 | 8 | 13 | 53162.5292
2027 | 2008 | 10 | 8 | 14 | 52228.0815
2027 | 2008 | 10 | 8 | 15 | 52465.9227
2027 | 2008 | 10 | 8 | 16 | 51348.6731
2027 | 2008 | 10 | 8 | 17 | 48339.0457
2027 | 2008 | 10 | 8 | 18 | 38091.4907
2027 | 2008 | 10 | 8 | 19 | 11932.5127
2027 | 2008 | 10 | 8 | 20 | 0
2027 | 2008 | 10 | 8 | 21 | 0
2027 | 2008 | 10 | 8 | 22 | 0
2027 | 2008 | 10 | 8 | 23 | 0
2027 | 2008 | 10 | 8 | 24 | 0
2027 | 2008 | 10 | 9 | 1 | 0
2027 | 2008 | 10 | 9 | 2 | 0
2027 | 2008 | 10 | 9 | 3 | 0
2027 | 2008 | 10 | 9 | 4 | 0
2027 | 2008 | 10 | 9 | 5 | 0
2027 | 2008 | 10 | 9 | 6 | 0
2027 | 2008 | 10 | 9 | 7 | 0
2027 | 2008 | 10 | 9 | 8 | 33.4365
2027 | 2008 | 10 | 9 | 9 | 18645.7937
2027 | 2008 | 10 | 9 | 10 | 48347.6561
2027 | 2008 | 10 | 9 | 11 | 54152.9774
2027 | 2008 | 10 | 9 | 12 | 54060.6993
2027 | 2008 | 10 | 9 | 13 | 52177.6855
2027 | 2008 | 10 | 9 | 14 | 52110.8745
2027 | 2008 | 10 | 9 | 15 | 51458.0216
2027 | 2008 | 10 | 9 | 16 | 51245.4027
2027 | 2008 | 10 | 9 | 17 | 47094.5093
2027 | 2008 | 10 | 9 | 18 | 38205.0166
2027 | 2008 | 10 | 9 | 19 | 11654.2259
2027 | 2008 | 10 | 9 | 20 | 0
2027 | 2008 | 10 | 9 | 21 | 0
2027 | 2008 | 10 | 9 | 22 | 0
2027 | 2008 | 10 | 9 | 23 | 0
2027 | 2008 | 10 | 9 | 24 | 0
2027 | 2008 | 10 | 10 | 1 | 0
2027 | 2008 | 10 | 10 | 2 | 0
2027 | 2008 | 10 | 10 | 3 | 0
2027 | 2008 | 10 | 10 | 4 | 0
2027 | 2008 | 10 | 10 | 5 | 0
2027 | 2008 | 10 | 10 | 6 | 0
2027 | 2008 | 10 | 10 | 7 | 0
2027 | 2008 | 10 | 10 | 8 | 24.1782
2027 | 2008 | 10 | 10 | 9 | 13299.4755
2027 | 2008 | 10 | 10 | 10 | 35987.5494
2027 | 2008 | 10 | 10 | 11 | 47133.0376
2027 | 2008 | 10 | 10 | 12 | 48831.8699
2027 | 2008 | 10 | 10 | 13 | 46012.2727
2027 | 2008 | 10 | 10 | 14 | 47094.9517
2027 | 2008 | 10 | 10 | 15 | 45909.6763
2027 | 2008 | 10 | 10 | 16 | 46088.2908
2027 | 2008 | 10 | 10 | 17 | 46202.6327
2027 | 2008 | 10 | 10 | 18 | 34398.4868
2027 | 2008 | 10 | 10 | 19 | 10584.9365
2027 | 2008 | 10 | 10 | 20 | 0
2027 | 2008 | 10 | 10 | 21 | 0
2027 | 2008 | 10 | 10 | 22 | 0
2027 | 2008 | 10 | 10 | 23 | 0
2027 | 2008 | 10 | 10 | 24 | 0
2027 | 2008 | 10 | 11 | 1 | 0
2027 | 2008 | 10 | 11 | 2 | 0
2027 | 2008 | 10 | 11 | 3 | 0
2027 | 2008 | 10 | 11 | 4 | 0
2027 | 2008 | 10 | 11 | 5 | 0
2027 | 2008 | 10 | 11 | 6 | 0
2027 | 2008 | 10 | 11 | 7 | 0
2027 | 2008 | 10 | 11 | 8 | 12.945
2027 | 2008 | 10 | 11 | 9 | 6254.9173
2027 | 2008 | 10 | 11 | 10 | 17758.8149
2027 | 2008 | 10 | 11 | 11 | 24329.6848
2027 | 2008 | 10 | 11 | 12 | 29465.9933
2027 | 2008 | 10 | 11 | 13 | 31759.5755
2027 | 2008 | 10 | 11 | 14 | 36213.9922
2027 | 2008 | 10 | 11 | 15 | 39427.4251
2027 | 2008 | 10 | 11 | 16 | 42016.511
2027 | 2008 | 10 | 11 | 17 | 40043.9747
2027 | 2008 | 10 | 11 | 18 | 31651.464
2027 | 2008 | 10 | 11 | 19 | 9293.7279
2027 | 2008 | 10 | 11 | 20 | 0
2027 | 2008 | 10 | 11 | 21 | 0
2027 | 2008 | 10 | 11 | 22 | 0
2027 | 2008 | 10 | 11 | 23 | 0
2027 | 2008 | 10 | 11 | 24 | 0
2027 | 2008 | 10 | 12 | 1 | 0
2027 | 2008 | 10 | 12 | 2 | 0
2027 | 2008 | 10 | 12 | 3 | 0
2027 | 2008 | 10 | 12 | 4 | 0
2027 | 2008 | 10 | 12 | 5 | 0
2027 | 2008 | 10 | 12 | 6 | 0
2027 | 2008 | 10 | 12 | 7 | 0
2027 | 2008 | 10 | 12 | 8 | 16.8739
2027 | 2008 | 10 | 12 | 9 | 6080.7426
2027 | 2008 | 10 | 12 | 10 | 21179.6661
2027 | 2008 | 10 | 12 | 11 | 27911.5975
2027 | 2008 | 10 | 12 | 12 | 34806.6141
2027 | 2008 | 10 | 12 | 13 | 34912.0594
2027 | 2008 | 10 | 12 | 14 | 35328.2747
2027 | 2008 | 10 | 12 | 15 | 32110.6001
2027 | 2008 | 10 | 12 | 16 | 31697.4842
2027 | 2008 | 10 | 12 | 17 | 30005.2786
2027 | 2008 | 10 | 12 | 18 | 24876.3648
2027 | 2008 | 10 | 12 | 19 | 6409.1341
2027 | 2008 | 10 | 12 | 20 | 0
2027 | 2008 | 10 | 12 | 21 | 0
2027 | 2008 | 10 | 12 | 22 | 0
2027 | 2008 | 10 | 12 | 23 | 0
2027 | 2008 | 10 | 12 | 24 | 0
2027 | 2008 | 10 | 13 | 1 | 0
2027 | 2008 | 10 | 13 | 2 | 0
2027 | 2008 | 10 | 13 | 3 | 0
2027 | 2008 | 10 | 13 | 4 | 0
2027 | 2008 | 10 | 13 | 5 | 0
2027 | 2008 | 10 | 13 | 6 | 0
2027 | 2008 | 10 | 13 | 7 | 0
2027 | 2008 | 10 | 13 | 8 | 17.7923
2027 | 2008 | 10 | 13 | 9 | 5063.0627
2027 | 2008 | 10 | 13 | 10 | 16357.8768
2027 | 2008 | 10 | 13 | 11 | 21572.4914
2027 | 2008 | 10 | 13 | 12 | 25800.5534
2027 | 2008 | 10 | 13 | 13 | 29281.0417
2027 | 2008 | 10 | 13 | 14 | 31692.1212
2027 | 2008 | 10 | 13 | 15 | 30233.9968
2027 | 2008 | 10 | 13 | 16 | 30315.8587
2027 | 2008 | 10 | 13 | 17 | 31244.7735
2027 | 2008 | 10 | 13 | 18 | 23968.1181
2027 | 2008 | 10 | 13 | 19 | 5640.8544
2027 | 2008 | 10 | 13 | 20 | 0
2027 | 2008 | 10 | 13 | 21 | 0
2027 | 2008 | 10 | 13 | 22 | 0
2027 | 2008 | 10 | 13 | 23 | 0
2027 | 2008 | 10 | 13 | 24 | 0
2027 | 2008 | 10 | 14 | 1 | 0
2027 | 2008 | 10 | 14 | 2 | 0
2027 | 2008 | 10 | 14 | 3 | 0
2027 | 2008 | 10 | 14 | 4 | 0
2027 | 2008 | 10 | 14 | 5 | 0
2027 | 2008 | 10 | 14 | 6 | 0
2027 | 2008 | 10 | 14 | 7 | 0
2027 | 2008 | 10 | 14 | 8 | 1.4228
2027 | 2008 | 10 | 14 | 9 | 1470.4894
2027 | 2008 | 10 | 14 | 10 | 6737.6217
2027 | 2008 | 10 | 14 | 11 | 13007.4279
2027 | 2008 | 10 | 14 | 12 | 20765.1582
2027 | 2008 | 10 | 14 | 13 | 26000.6
2027 | 2008 | 10 | 14 | 14 | 27162.1588
2027 | 2008 | 10 | 14 | 15 | 29364.0261
2027 | 2008 | 10 | 14 | 16 | 29719.9802
2027 | 2008 | 10 | 14 | 17 | 28754.3821
2027 | 2008 | 10 | 14 | 18 | 24099.7309
2027 | 2008 | 10 | 14 | 19 | 5490.0524
2027 | 2008 | 10 | 14 | 20 | 0
2027 | 2008 | 10 | 14 | 21 | 0
2027 | 2008 | 10 | 14 | 22 | 0
2027 | 2008 | 10 | 14 | 23 | 0
2027 | 2008 | 10 | 14 | 24 | 0
2027 | 2008 | 10 | 15 | 1 | 0
2027 | 2008 | 10 | 15 | 2 | 0
2027 | 2008 | 10 | 15 | 3 | 0
2027 | 2008 | 10 | 15 | 4 | 0
2027 | 2008 | 10 | 15 | 5 | 0
2027 | 2008 | 10 | 15 | 6 | 0
2027 | 2008 | 10 | 15 | 7 | 0
2027 | 2008 | 10 | 15 | 8 | 6.4361
2027 | 2008 | 10 | 15 | 9 | 2816.489
2027 | 2008 | 10 | 15 | 10 | 12766.1678
2027 | 2008 | 10 | 15 | 11 | 18791.8026
2027 | 2008 | 10 | 15 | 12 | 23506.7579
2027 | 2008 | 10 | 15 | 13 | 27238.8035
2027 | 2008 | 10 | 15 | 14 | 28861.083
2027 | 2008 | 10 | 15 | 15 | 28360.5533
2027 | 2008 | 10 | 15 | 16 | 26990.6323
2027 | 2008 | 10 | 15 | 17 | 26126.8703
2027 | 2008 | 10 | 15 | 18 | 23992.3921
2027 | 2008 | 10 | 15 | 19 | 6342.7189
2027 | 2008 | 10 | 15 | 20 | 0
2027 | 2008 | 10 | 15 | 21 | 0
2027 | 2008 | 10 | 15 | 22 | 0
2027 | 2008 | 10 | 15 | 23 | 0
2027 | 2008 | 10 | 15 | 24 | 0
2027 | 2008 | 10 | 16 | 1 | 0
2027 | 2008 | 10 | 16 | 2 | 0
2027 | 2008 | 10 | 16 | 3 | 0
2027 | 2008 | 10 | 16 | 4 | 0
2027 | 2008 | 10 | 16 | 5 | 0
2027 | 2008 | 10 | 16 | 6 | 0
2027 | 2008 | 10 | 16 | 7 | 0
2027 | 2008 | 10 | 16 | 8 | 0.48227
2027 | 2008 | 10 | 16 | 9 | 1469.4451
2027 | 2008 | 10 | 16 | 10 | 10381.0122
2027 | 2008 | 10 | 16 | 11 | 16393.0429
2027 | 2008 | 10 | 16 | 12 | 25580.2876
2027 | 2008 | 10 | 16 | 13 | 28753.869
2027 | 2008 | 10 | 16 | 14 | 30310.9243
2027 | 2008 | 10 | 16 | 15 | 30758.401
2027 | 2008 | 10 | 16 | 16 | 31264.1421
2027 | 2008 | 10 | 16 | 17 | 26594.2839
2027 | 2008 | 10 | 16 | 18 | 25043.0192
2027 | 2008 | 10 | 16 | 19 | 5871.7351
2027 | 2008 | 10 | 16 | 20 | 0
2027 | 2008 | 10 | 16 | 21 | 0
2027 | 2008 | 10 | 16 | 22 | 0
2027 | 2008 | 10 | 16 | 23 | 0
2027 | 2008 | 10 | 16 | 24 | 0
2027 | 2008 | 10 | 17 | 1 | 0
2027 | 2008 | 10 | 17 | 2 | 0
2027 | 2008 | 10 | 17 | 3 | 0
2027 | 2008 | 10 | 17 | 4 | 0
2027 | 2008 | 10 | 17 | 5 | 0
2027 | 2008 | 10 | 17 | 6 | 0
2027 | 2008 | 10 | 17 | 7 | 0
2027 | 2008 | 10 | 17 | 8 | 2.332
2027 | 2008 | 10 | 17 | 9 | 7858.3019
2027 | 2008 | 10 | 17 | 10 | 26865.1787
2027 | 2008 | 10 | 17 | 11 | 31611.3543
2027 | 2008 | 10 | 17 | 12 | 33312.4556
2027 | 2008 | 10 | 17 | 13 | 34944.4554
2027 | 2008 | 10 | 17 | 14 | 35322.2039
2027 | 2008 | 10 | 17 | 15 | 33867.8035
2027 | 2008 | 10 | 17 | 16 | 33444.1395
2027 | 2008 | 10 | 17 | 17 | 32560.4063
2027 | 2008 | 10 | 17 | 18 | 26007.0631
2027 | 2008 | 10 | 17 | 19 | 6033.0633
2027 | 2008 | 10 | 17 | 20 | 0
2027 | 2008 | 10 | 17 | 21 | 0
2027 | 2008 | 10 | 17 | 22 | 0
2027 | 2008 | 10 | 17 | 23 | 0
2027 | 2008 | 10 | 17 | 24 | 0
2027 | 2008 | 10 | 18 | 1 | 0
2027 | 2008 | 10 | 18 | 2 | 0
2027 | 2008 | 10 | 18 | 3 | 0
2027 | 2008 | 10 | 18 | 4 | 0
2027 | 2008 | 10 | 18 | 5 | 0
2027 | 2008 | 10 | 18 | 6 | 0
2027 | 2008 | 10 | 18 | 7 | 0
2027 | 2008 | 10 | 18 | 8 | 20.7526
2027 | 2008 | 10 | 18 | 9 | 14941.0016
2027 | 2008 | 10 | 18 | 10 | 42587.3705
2027 | 2008 | 10 | 18 | 11 | 49852.3803
2027 | 2008 | 10 | 18 | 12 | 49963.147
2027 | 2008 | 10 | 18 | 13 | 49611.4602
2027 | 2008 | 10 | 18 | 14 | 47989.8176
2027 | 2008 | 10 | 18 | 15 | 48447.2932
2027 | 2008 | 10 | 18 | 16 | 47245.1866
2027 | 2008 | 10 | 18 | 17 | 44128.6726
2027 | 2008 | 10 | 18 | 18 | 33545.8874
2027 | 2008 | 10 | 18 | 19 | 6910.0853
2027 | 2008 | 10 | 18 | 20 | 0
2027 | 2008 | 10 | 18 | 21 | 0
2027 | 2008 | 10 | 18 | 22 | 0
2027 | 2008 | 10 | 18 | 23 | 0
2027 | 2008 | 10 | 18 | 24 | 0
2027 | 2008 | 10 | 19 | 1 | 0
2027 | 2008 | 10 | 19 | 2 | 0
2027 | 2008 | 10 | 19 | 3 | 0
2027 | 2008 | 10 | 19 | 4 | 0
2027 | 2008 | 10 | 19 | 5 | 0
2027 | 2008 | 10 | 19 | 6 | 0
2027 | 2008 | 10 | 19 | 7 | 0
2027 | 2008 | 10 | 19 | 8 | 19.9747
2027 | 2008 | 10 | 19 | 9 | 15026.8377
2027 | 2008 | 10 | 19 | 10 | 44074.138
2027 | 2008 | 10 | 19 | 11 | 49544.0142
2027 | 2008 | 10 | 19 | 12 | 50814.357
2027 | 2008 | 10 | 19 | 13 | 49344.6272
2027 | 2008 | 10 | 19 | 14 | 48189.0835
2027 | 2008 | 10 | 19 | 15 | 47762.7359
2027 | 2008 | 10 | 19 | 16 | 44128.1339
2027 | 2008 | 10 | 19 | 17 | 43038.4051
2027 | 2008 | 10 | 19 | 18 | 30067.0191
2027 | 2008 | 10 | 19 | 19 | 6068.5266
2027 | 2008 | 10 | 19 | 20 | 0
2027 | 2008 | 10 | 19 | 21 | 0
2027 | 2008 | 10 | 19 | 22 | 0
2027 | 2008 | 10 | 19 | 23 | 0
2027 | 2008 | 10 | 19 | 24 | 0
2027 | 2008 | 10 | 20 | 1 | 0
2027 | 2008 | 10 | 20 | 2 | 0
2027 | 2008 | 10 | 20 | 3 | 0
2027 | 2008 | 10 | 20 | 4 | 0
2027 | 2008 | 10 | 20 | 5 | 0
2027 | 2008 | 10 | 20 | 6 | 0
2027 | 2008 | 10 | 20 | 7 | 0
2027 | 2008 | 10 | 20 | 8 | 15.5983
2027 | 2008 | 10 | 20 | 9 | 13310.3677
2027 | 2008 | 10 | 20 | 10 | 40457.1315
2027 | 2008 | 10 | 20 | 11 | 46709.9033
2027 | 2008 | 10 | 20 | 12 | 47078.2518
2027 | 2008 | 10 | 20 | 13 | 47204.5783
2027 | 2008 | 10 | 20 | 14 | 45722.3618
2027 | 2008 | 10 | 20 | 15 | 45501.4147
2027 | 2008 | 10 | 20 | 16 | 43908.7317
2027 | 2008 | 10 | 20 | 17 | 40082.5197
2027 | 2008 | 10 | 20 | 18 | 29808.4277
2027 | 2008 | 10 | 20 | 19 | 5612.5516
2027 | 2008 | 10 | 20 | 20 | 0
2027 | 2008 | 10 | 20 | 21 | 0
2027 | 2008 | 10 | 20 | 22 | 0
2027 | 2008 | 10 | 20 | 23 | 0
2027 | 2008 | 10 | 20 | 24 | 0
2027 | 2008 | 10 | 21 | 1 | 0
2027 | 2008 | 10 | 21 | 2 | 0
2027 | 2008 | 10 | 21 | 3 | 0
2027 | 2008 | 10 | 21 | 4 | 0
2027 | 2008 | 10 | 21 | 5 | 0
2027 | 2008 | 10 | 21 | 6 | 0
2027 | 2008 | 10 | 21 | 7 | 0
2027 | 2008 | 10 | 21 | 8 | 9.6645
2027 | 2008 | 10 | 21 | 9 | 7615.0252
2027 | 2008 | 10 | 21 | 10 | 24018.9089
2027 | 2008 | 10 | 21 | 11 | 31116.1286
2027 | 2008 | 10 | 21 | 12 | 35033.5493
2027 | 2008 | 10 | 21 | 13 | 37732.2456
2027 | 2008 | 10 | 21 | 14 | 39084.4293
2027 | 2008 | 10 | 21 | 15 | 38523.7422
2027 | 2008 | 10 | 21 | 16 | 38893.3623
2027 | 2008 | 10 | 21 | 17 | 36113.9562
2027 | 2008 | 10 | 21 | 18 | 26803.881
2027 | 2008 | 10 | 21 | 19 | 4691.3373
2027 | 2008 | 10 | 21 | 20 | 0
2027 | 2008 | 10 | 21 | 21 | 0
2027 | 2008 | 10 | 21 | 22 | 0
2027 | 2008 | 10 | 21 | 23 | 0
2027 | 2008 | 10 | 21 | 24 | 0
2027 | 2008 | 10 | 22 | 1 | 0
2027 | 2008 | 10 | 22 | 2 | 0
2027 | 2008 | 10 | 22 | 3 | 0
2027 | 2008 | 10 | 22 | 4 | 0
2027 | 2008 | 10 | 22 | 5 | 0
2027 | 2008 | 10 | 22 | 6 | 0
2027 | 2008 | 10 | 22 | 7 | 0
2027 | 2008 | 10 | 22 | 8 | 8.5606
2027 | 2008 | 10 | 22 | 9 | 5318.6888
2027 | 2008 | 10 | 22 | 10 | 17928.2287
2027 | 2008 | 10 | 22 | 11 | 26083.821
2027 | 2008 | 10 | 22 | 12 | 30454.999
2027 | 2008 | 10 | 22 | 13 | 34087.8404
2027 | 2008 | 10 | 22 | 14 | 35278.1595
2027 | 2008 | 10 | 22 | 15 | 34592.0843
2027 | 2008 | 10 | 22 | 16 | 36584.5826
2027 | 2008 | 10 | 22 | 17 | 30626.2971
2027 | 2008 | 10 | 22 | 18 | 23645.2698
2027 | 2008 | 10 | 22 | 19 | 4130.9834
2027 | 2008 | 10 | 22 | 20 | 0
2027 | 2008 | 10 | 22 | 21 | 0
2027 | 2008 | 10 | 22 | 22 | 0
2027 | 2008 | 10 | 22 | 23 | 0
2027 | 2008 | 10 | 22 | 24 | 0
2027 | 2008 | 10 | 23 | 1 | 0
2027 | 2008 | 10 | 23 | 2 | 0
2027 | 2008 | 10 | 23 | 3 | 0
2027 | 2008 | 10 | 23 | 4 | 0
2027 | 2008 | 10 | 23 | 5 | 0
2027 | 2008 | 10 | 23 | 6 | 0
2027 | 2008 | 10 | 23 | 7 | 0
2027 | 2008 | 10 | 23 | 8 | 7.7832
2027 | 2008 | 10 | 23 | 9 | 13954.5557
2027 | 2008 | 10 | 23 | 10 | 41398.978
2027 | 2008 | 10 | 23 | 11 | 48867.9381
2027 | 2008 | 10 | 23 | 12 | 49592.2283
2027 | 2008 | 10 | 23 | 13 | 49015.8177
2027 | 2008 | 10 | 23 | 14 | 48770.7858
2027 | 2008 | 10 | 23 | 15 | 48241.1058
2027 | 2008 | 10 | 23 | 16 | 47513.723
2027 | 2008 | 10 | 23 | 17 | 44126.0982
2027 | 2008 | 10 | 23 | 18 | 32088.639
2027 | 2008 | 10 | 23 | 19 | 4300.1566
2027 | 2008 | 10 | 23 | 20 | 0
2027 | 2008 | 10 | 23 | 21 | 0
2027 | 2008 | 10 | 23 | 22 | 0
2027 | 2008 | 10 | 23 | 23 | 0
2027 | 2008 | 10 | 23 | 24 | 0
2027 | 2008 | 10 | 24 | 1 | 0
2027 | 2008 | 10 | 24 | 2 | 0
2027 | 2008 | 10 | 24 | 3 | 0
2027 | 2008 | 10 | 24 | 4 | 0
2027 | 2008 | 10 | 24 | 5 | 0
2027 | 2008 | 10 | 24 | 6 | 0
2027 | 2008 | 10 | 24 | 7 | 0
2027 | 2008 | 10 | 24 | 8 | 11.3728
2027 | 2008 | 10 | 24 | 9 | 14272.6209
2027 | 2008 | 10 | 24 | 10 | 44626.0684
2027 | 2008 | 10 | 24 | 11 | 51403.8832
2027 | 2008 | 10 | 24 | 12 | 52061.4805
2027 | 2008 | 10 | 24 | 13 | 49515.9567
2027 | 2008 | 10 | 24 | 14 | 48877.7057
2027 | 2008 | 10 | 24 | 15 | 48474.8898
2027 | 2008 | 10 | 24 | 16 | 45579.1216
2027 | 2008 | 10 | 24 | 17 | 43859.2067
2027 | 2008 | 10 | 24 | 18 | 27929.6026
2027 | 2008 | 10 | 24 | 19 | 3553.1045
2027 | 2008 | 10 | 24 | 20 | 0
2027 | 2008 | 10 | 24 | 21 | 0
2027 | 2008 | 10 | 24 | 22 | 0
2027 | 2008 | 10 | 24 | 23 | 0
2027 | 2008 | 10 | 24 | 24 | 0
2027 | 2008 | 10 | 25 | 1 | 0
2027 | 2008 | 10 | 25 | 2 | 0
2027 | 2008 | 10 | 25 | 3 | 0
2027 | 2008 | 10 | 25 | 4 | 0
2027 | 2008 | 10 | 25 | 5 | 0
2027 | 2008 | 10 | 25 | 6 | 0
2027 | 2008 | 10 | 25 | 7 | 0
2027 | 2008 | 10 | 25 | 8 | 10.3332
2027 | 2008 | 10 | 25 | 9 | 12934.5518
2027 | 2008 | 10 | 25 | 10 | 41256.7227
2027 | 2008 | 10 | 25 | 11 | 47794.5952
2027 | 2008 | 10 | 25 | 12 | 48476.4159
2027 | 2008 | 10 | 25 | 13 | 47135.3368
2027 | 2008 | 10 | 25 | 14 | 45922.7367
2027 | 2008 | 10 | 25 | 15 | 45772.6333
2027 | 2008 | 10 | 25 | 16 | 44815.1384
2027 | 2008 | 10 | 25 | 17 | 41125.3217
2027 | 2008 | 10 | 25 | 18 | 26444.7064
2027 | 2008 | 10 | 25 | 19 | 2957.8095
2027 | 2008 | 10 | 25 | 20 | 0
2027 | 2008 | 10 | 25 | 21 | 0
2027 | 2008 | 10 | 25 | 22 | 0
2027 | 2008 | 10 | 25 | 23 | 0
2027 | 2008 | 10 | 25 | 24 | 0
2027 | 2008 | 10 | 26 | 1 | 0
2027 | 2008 | 10 | 26 | 2 | 0
2027 | 2008 | 10 | 26 | 3 | 0
2027 | 2008 | 10 | 26 | 4 | 0
2027 | 2008 | 10 | 26 | 5 | 0
2027 | 2008 | 10 | 26 | 6 | 0
2027 | 2008 | 10 | 26 | 7 | 0
2027 | 2008 | 10 | 26 | 8 | 8.289
2027 | 2008 | 10 | 26 | 9 | 10708.9922
2027 | 2008 | 10 | 26 | 10 | 34214.4059
2027 | 2008 | 10 | 26 | 11 | 39068.1053
2027 | 2008 | 10 | 26 | 12 | 38813.9037
2027 | 2008 | 10 | 26 | 13 | 39979.4136
2027 | 2008 | 10 | 26 | 14 | 41892.2334
2027 | 2008 | 10 | 26 | 15 | 40074.1666
2027 | 2008 | 10 | 26 | 16 | 37488.0161
2027 | 2008 | 10 | 26 | 17 | 36970.9888
2027 | 2008 | 10 | 26 | 18 | 28336.2827
2027 | 2008 | 10 | 26 | 19 | 2772.8256
2027 | 2008 | 10 | 26 | 20 | 0
2027 | 2008 | 10 | 26 | 21 | 0
2027 | 2008 | 10 | 26 | 22 | 0
2027 | 2008 | 10 | 26 | 23 | 0
2027 | 2008 | 10 | 26 | 24 | 0
2027 | 2008 | 10 | 27 | 1 | 0
2027 | 2008 | 10 | 27 | 2 | 0
2027 | 2008 | 10 | 27 | 3 | 0
2027 | 2008 | 10 | 27 | 4 | 0
2027 | 2008 | 10 | 27 | 5 | 0
2027 | 2008 | 10 | 27 | 6 | 0
2027 | 2008 | 10 | 27 | 7 | 0
2027 | 2008 | 10 | 27 | 8 | 2.3435
2027 | 2008 | 10 | 27 | 9 | 12645.4897
2027 | 2008 | 10 | 27 | 10 | 42224.0341
2027 | 2008 | 10 | 27 | 11 | 50391.1393
2027 | 2008 | 10 | 27 | 12 | 52174.3732
2027 | 2008 | 10 | 27 | 13 | 50043.2215
2027 | 2008 | 10 | 27 | 14 | 49912.0238
2027 | 2008 | 10 | 27 | 15 | 49467.8247
2027 | 2008 | 10 | 27 | 16 | 47366.2306
2027 | 2008 | 10 | 27 | 17 | 43905.9952
2027 | 2008 | 10 | 27 | 18 | 27623.4922
2027 | 2008 | 10 | 27 | 19 | 2674.7845
2027 | 2008 | 10 | 27 | 20 | 0
2027 | 2008 | 10 | 27 | 21 | 0
2027 | 2008 | 10 | 27 | 22 | 0
2027 | 2008 | 10 | 27 | 23 | 0
2027 | 2008 | 10 | 27 | 24 | 0
2027 | 2008 | 10 | 28 | 1 | 0
2027 | 2008 | 10 | 28 | 2 | 0
2027 | 2008 | 10 | 28 | 3 | 0
2027 | 2008 | 10 | 28 | 4 | 0
2027 | 2008 | 10 | 28 | 5 | 0
2027 | 2008 | 10 | 28 | 6 | 0
2027 | 2008 | 10 | 28 | 7 | 0
2027 | 2008 | 10 | 28 | 8 | 4.1892
2027 | 2008 | 10 | 28 | 9 | 13890.4099
2027 | 2008 | 10 | 28 | 10 | 42840.0724
2027 | 2008 | 10 | 28 | 11 | 48943.409
2027 | 2008 | 10 | 28 | 12 | 49754.188
2027 | 2008 | 10 | 28 | 13 | 48167.3851
2027 | 2008 | 10 | 28 | 14 | 46804.4474
2027 | 2008 | 10 | 28 | 15 | 46532.9426
2027 | 2008 | 10 | 28 | 16 | 44970.5697
2027 | 2008 | 10 | 28 | 17 | 40483.6198
2027 | 2008 | 10 | 28 | 18 | 28886.4379
2027 | 2008 | 10 | 28 | 19 | 2467.0442
2027 | 2008 | 10 | 28 | 20 | 0
2027 | 2008 | 10 | 28 | 21 | 0
2027 | 2008 | 10 | 28 | 22 | 0
2027 | 2008 | 10 | 28 | 23 | 0
2027 | 2008 | 10 | 28 | 24 | 0
2027 | 2008 | 10 | 29 | 1 | 0
2027 | 2008 | 10 | 29 | 2 | 0
2027 | 2008 | 10 | 29 | 3 | 0
2027 | 2008 | 10 | 29 | 4 | 0
2027 | 2008 | 10 | 29 | 5 | 0
2027 | 2008 | 10 | 29 | 6 | 0
2027 | 2008 | 10 | 29 | 7 | 0
2027 | 2008 | 10 | 29 | 8 | 5.4891
2027 | 2008 | 10 | 29 | 9 | 11993.648
2027 | 2008 | 10 | 29 | 10 | 39933.8383
2027 | 2008 | 10 | 29 | 11 | 47340.6038
2027 | 2008 | 10 | 29 | 12 | 47719.8557
2027 | 2008 | 10 | 29 | 13 | 46084.5706
2027 | 2008 | 10 | 29 | 14 | 45718.2756
2027 | 2008 | 10 | 29 | 15 | 44537.4426
2027 | 2008 | 10 | 29 | 16 | 43432.8996
2027 | 2008 | 10 | 29 | 17 | 41698.9654
2027 | 2008 | 10 | 29 | 18 | 26366.5788
2027 | 2008 | 10 | 29 | 19 | 2138.5108
2027 | 2008 | 10 | 29 | 20 | 0
2027 | 2008 | 10 | 29 | 21 | 0
2027 | 2008 | 10 | 29 | 22 | 0
2027 | 2008 | 10 | 29 | 23 | 0
2027 | 2008 | 10 | 29 | 24 | 0
2027 | 2008 | 10 | 30 | 1 | 0
2027 | 2008 | 10 | 30 | 2 | 0
2027 | 2008 | 10 | 30 | 3 | 0
2027 | 2008 | 10 | 30 | 4 | 0
2027 | 2008 | 10 | 30 | 5 | 0
2027 | 2008 | 10 | 30 | 6 | 0
2027 | 2008 | 10 | 30 | 7 | 0
2027 | 2008 | 10 | 30 | 8 | 2.4384
2027 | 2008 | 10 | 30 | 9 | 7318.7854
2027 | 2008 | 10 | 30 | 10 | 23178.3494
2027 | 2008 | 10 | 30 | 11 | 28900.0022
2027 | 2008 | 10 | 30 | 12 | 32261.1925
2027 | 2008 | 10 | 30 | 13 | 36370.3003
2027 | 2008 | 10 | 30 | 14 | 39149.8617
2027 | 2008 | 10 | 30 | 15 | 39143.095
2027 | 2008 | 10 | 30 | 16 | 41054.0885
2027 | 2008 | 10 | 30 | 17 | 36735.6594
2027 | 2008 | 10 | 30 | 18 | 23294.4121
2027 | 2008 | 10 | 30 | 19 | 1854.9339
2027 | 2008 | 10 | 30 | 20 | 0
2027 | 2008 | 10 | 30 | 21 | 0
2027 | 2008 | 10 | 30 | 22 | 0
2027 | 2008 | 10 | 30 | 23 | 0
2027 | 2008 | 10 | 30 | 24 | 0
2027 | 2008 | 10 | 31 | 1 | 0
2027 | 2008 | 10 | 31 | 2 | 0
2027 | 2008 | 10 | 31 | 3 | 0
2027 | 2008 | 10 | 31 | 4 | 0
2027 | 2008 | 10 | 31 | 5 | 0
2027 | 2008 | 10 | 31 | 6 | 0
2027 | 2008 | 10 | 31 | 7 | 0
2027 | 2008 | 10 | 31 | 8 | 2.1371
2027 | 2008 | 10 | 31 | 9 | 5912.2347
2027 | 2008 | 10 | 31 | 10 | 20520.4889
2027 | 2008 | 10 | 31 | 11 | 26384.5286
2027 | 2008 | 10 | 31 | 12 | 33070.1235
2027 | 2008 | 10 | 31 | 13 | 35921.8415
2027 | 2008 | 10 | 31 | 14 | 37561.3911
2027 | 2008 | 10 | 31 | 15 | 39126.7669
2027 | 2008 | 10 | 31 | 16 | 37792.8814
2027 | 2008 | 10 | 31 | 17 | 37334.7554
2027 | 2008 | 10 | 31 | 18 | 22175.87
2027 | 2008 | 10 | 31 | 19 | 2777.9442
2027 | 2008 | 10 | 31 | 20 | 0
2027 | 2008 | 10 | 31 | 21 | 0
2027 | 2008 | 10 | 31 | 22 | 0
2027 | 2008 | 10 | 31 | 23 | 0
2027 | 2008 | 10 | 31 | 24 | 0
2028 | 2008 | 10 | 1 | 1 | 0
2028 | 2008 | 10 | 1 | 2 | 0
2028 | 2008 | 10 | 1 | 3 | 0
2028 | 2008 | 10 | 1 | 4 | 0
2028 | 2008 | 10 | 1 | 5 | 0
2028 | 2008 | 10 | 1 | 6 | 0
2028 | 2008 | 10 | 1 | 7 | 0
2028 | 2008 | 10 | 1 | 8 | 48.6855
2028 | 2008 | 10 | 1 | 9 | 19847.3104
2028 | 2008 | 10 | 1 | 10 | 50150.749
2028 | 2008 | 10 | 1 | 11 | 55498.9878
2028 | 2008 | 10 | 1 | 12 | 56024.7323
2028 | 2008 | 10 | 1 | 13 | 54947.1088
2028 | 2008 | 10 | 1 | 14 | 54292.3991
2028 | 2008 | 10 | 1 | 15 | 53165.2906
2028 | 2008 | 10 | 1 | 16 | 53961.989
2028 | 2008 | 10 | 1 | 17 | 52903.2354
2028 | 2008 | 10 | 1 | 18 | 41456.44
2028 | 2008 | 10 | 1 | 19 | 14198.9317
2028 | 2008 | 10 | 1 | 20 | 0
2028 | 2008 | 10 | 1 | 21 | 0
2028 | 2008 | 10 | 1 | 22 | 0
2028 | 2008 | 10 | 1 | 23 | 0
2028 | 2008 | 10 | 1 | 24 | 0
2028 | 2008 | 10 | 2 | 1 | 0
2028 | 2008 | 10 | 2 | 2 | 0
2028 | 2008 | 10 | 2 | 3 | 0
2028 | 2008 | 10 | 2 | 4 | 0
2028 | 2008 | 10 | 2 | 5 | 0
2028 | 2008 | 10 | 2 | 6 | 0
2028 | 2008 | 10 | 2 | 7 | 0
2028 | 2008 | 10 | 2 | 8 | 60.204
2028 | 2008 | 10 | 2 | 9 | 20166.7151
2028 | 2008 | 10 | 2 | 10 | 48373.4743
2028 | 2008 | 10 | 2 | 11 | 55763.5038
2028 | 2008 | 10 | 2 | 12 | 55973.3599
2028 | 2008 | 10 | 2 | 13 | 54146.5859
2028 | 2008 | 10 | 2 | 14 | 53448.1105
2028 | 2008 | 10 | 2 | 15 | 52207.7683
2028 | 2008 | 10 | 2 | 16 | 53071.4989
2028 | 2008 | 10 | 2 | 17 | 52250.8516
2028 | 2008 | 10 | 2 | 18 | 41102.8121
2028 | 2008 | 10 | 2 | 19 | 13995.1115
2028 | 2008 | 10 | 2 | 20 | 0
2028 | 2008 | 10 | 2 | 21 | 0
2028 | 2008 | 10 | 2 | 22 | 0
2028 | 2008 | 10 | 2 | 23 | 0
2028 | 2008 | 10 | 2 | 24 | 0
2028 | 2008 | 10 | 3 | 1 | 0
2028 | 2008 | 10 | 3 | 2 | 0
2028 | 2008 | 10 | 3 | 3 | 0
2028 | 2008 | 10 | 3 | 4 | 0
2028 | 2008 | 10 | 3 | 5 | 0
2028 | 2008 | 10 | 3 | 6 | 0
2028 | 2008 | 10 | 3 | 7 | 0
2028 | 2008 | 10 | 3 | 8 | 57.8862
2028 | 2008 | 10 | 3 | 9 | 16294.408
2028 | 2008 | 10 | 3 | 10 | 45390.0057
2028 | 2008 | 10 | 3 | 11 | 52430.3277
2028 | 2008 | 10 | 3 | 12 | 51777.2266
2028 | 2008 | 10 | 3 | 13 | 50659.6886
2028 | 2008 | 10 | 3 | 14 | 49473.8987
2028 | 2008 | 10 | 3 | 15 | 49768.252
2028 | 2008 | 10 | 3 | 16 | 48545.6483
2028 | 2008 | 10 | 3 | 17 | 47194.5685
2028 | 2008 | 10 | 3 | 18 | 38389.4557
2028 | 2008 | 10 | 3 | 19 | 13066.8068
2028 | 2008 | 10 | 3 | 20 | 0
2028 | 2008 | 10 | 3 | 21 | 0
2028 | 2008 | 10 | 3 | 22 | 0
2028 | 2008 | 10 | 3 | 23 | 0
2028 | 2008 | 10 | 3 | 24 | 0
2028 | 2008 | 10 | 4 | 1 | 0
2028 | 2008 | 10 | 4 | 2 | 0
2028 | 2008 | 10 | 4 | 3 | 0
2028 | 2008 | 10 | 4 | 4 | 0
2028 | 2008 | 10 | 4 | 5 | 0
2028 | 2008 | 10 | 4 | 6 | 0
2028 | 2008 | 10 | 4 | 7 | 0
2028 | 2008 | 10 | 4 | 8 | 37.5899
2028 | 2008 | 10 | 4 | 9 | 12199.6316
2028 | 2008 | 10 | 4 | 10 | 38186.3362
2028 | 2008 | 10 | 4 | 11 | 47876.2055
2028 | 2008 | 10 | 4 | 12 | 52254.2402
2028 | 2008 | 10 | 4 | 13 | 52159.8629
2028 | 2008 | 10 | 4 | 14 | 50818.8763
2028 | 2008 | 10 | 4 | 15 | 50104.9494
2028 | 2008 | 10 | 4 | 16 | 49851.2983
2028 | 2008 | 10 | 4 | 17 | 48674.2261
2028 | 2008 | 10 | 4 | 18 | 37170.227
2028 | 2008 | 10 | 4 | 19 | 12793.2311
2028 | 2008 | 10 | 4 | 20 | 0
2028 | 2008 | 10 | 4 | 21 | 0
2028 | 2008 | 10 | 4 | 22 | 0
2028 | 2008 | 10 | 4 | 23 | 0
2028 | 2008 | 10 | 4 | 24 | 0
2028 | 2008 | 10 | 5 | 1 | 0
2028 | 2008 | 10 | 5 | 2 | 0
2028 | 2008 | 10 | 5 | 3 | 0
2028 | 2008 | 10 | 5 | 4 | 0
2028 | 2008 | 10 | 5 | 5 | 0
2028 | 2008 | 10 | 5 | 6 | 0
2028 | 2008 | 10 | 5 | 7 | 0
2028 | 2008 | 10 | 5 | 8 | 39.1087
2028 | 2008 | 10 | 5 | 9 | 12380.5087
2028 | 2008 | 10 | 5 | 10 | 33196.49
2028 | 2008 | 10 | 5 | 11 | 35994.92
2028 | 2008 | 10 | 5 | 12 | 41210.9754
2028 | 2008 | 10 | 5 | 13 | 42055.0611
2028 | 2008 | 10 | 5 | 14 | 39221.5696
2028 | 2008 | 10 | 5 | 15 | 37621.8597
2028 | 2008 | 10 | 5 | 16 | 37697.9175
2028 | 2008 | 10 | 5 | 17 | 36096.208
2028 | 2008 | 10 | 5 | 18 | 30317.3966
2028 | 2008 | 10 | 5 | 19 | 10612.7913
2028 | 2008 | 10 | 5 | 20 | 0
2028 | 2008 | 10 | 5 | 21 | 0
2028 | 2008 | 10 | 5 | 22 | 0
2028 | 2008 | 10 | 5 | 23 | 0
2028 | 2008 | 10 | 5 | 24 | 0
2028 | 2008 | 10 | 6 | 1 | 0
2028 | 2008 | 10 | 6 | 2 | 0
2028 | 2008 | 10 | 6 | 3 | 0
2028 | 2008 | 10 | 6 | 4 | 0
2028 | 2008 | 10 | 6 | 5 | 0
2028 | 2008 | 10 | 6 | 6 | 0
2028 | 2008 | 10 | 6 | 7 | 0
2028 | 2008 | 10 | 6 | 8 | 18.5113
2028 | 2008 | 10 | 6 | 9 | 9598.1374
2028 | 2008 | 10 | 6 | 10 | 30350.7236
2028 | 2008 | 10 | 6 | 11 | 41060.2286
2028 | 2008 | 10 | 6 | 12 | 45676.7309
2028 | 2008 | 10 | 6 | 13 | 46528.3574
2028 | 2008 | 10 | 6 | 14 | 46529.1346
2028 | 2008 | 10 | 6 | 15 | 46522.4124
2028 | 2008 | 10 | 6 | 16 | 48176.9183
2028 | 2008 | 10 | 6 | 17 | 47866.7224
2028 | 2008 | 10 | 6 | 18 | 37345.4184
2028 | 2008 | 10 | 6 | 19 | 12160.6824
2028 | 2008 | 10 | 6 | 20 | 0
2028 | 2008 | 10 | 6 | 21 | 0
2028 | 2008 | 10 | 6 | 22 | 0
2028 | 2008 | 10 | 6 | 23 | 0
2028 | 2008 | 10 | 6 | 24 | 0
2028 | 2008 | 10 | 7 | 1 | 0
2028 | 2008 | 10 | 7 | 2 | 0
2028 | 2008 | 10 | 7 | 3 | 0
2028 | 2008 | 10 | 7 | 4 | 0
2028 | 2008 | 10 | 7 | 5 | 0
2028 | 2008 | 10 | 7 | 6 | 0
2028 | 2008 | 10 | 7 | 7 | 0
2028 | 2008 | 10 | 7 | 8 | 23.6528
2028 | 2008 | 10 | 7 | 9 | 12831.9877
2028 | 2008 | 10 | 7 | 10 | 40116.3785
2028 | 2008 | 10 | 7 | 11 | 46229.0545
2028 | 2008 | 10 | 7 | 12 | 50415.4665
2028 | 2008 | 10 | 7 | 13 | 51192.8144
2028 | 2008 | 10 | 7 | 14 | 51405.8155
2028 | 2008 | 10 | 7 | 15 | 50737.6064
2028 | 2008 | 10 | 7 | 16 | 52243.9439
2028 | 2008 | 10 | 7 | 17 | 48328.596
2028 | 2008 | 10 | 7 | 18 | 36711.603
2028 | 2008 | 10 | 7 | 19 | 13044.6919
2028 | 2008 | 10 | 7 | 20 | 0
2028 | 2008 | 10 | 7 | 21 | 0
2028 | 2008 | 10 | 7 | 22 | 0
2028 | 2008 | 10 | 7 | 23 | 0
2028 | 2008 | 10 | 7 | 24 | 0
2028 | 2008 | 10 | 8 | 1 | 0
2028 | 2008 | 10 | 8 | 2 | 0
2028 | 2008 | 10 | 8 | 3 | 0
2028 | 2008 | 10 | 8 | 4 | 0
2028 | 2008 | 10 | 8 | 5 | 0
2028 | 2008 | 10 | 8 | 6 | 0
2028 | 2008 | 10 | 8 | 7 | 0
2028 | 2008 | 10 | 8 | 8 | 32.2666
2028 | 2008 | 10 | 8 | 9 | 19074.435
2028 | 2008 | 10 | 8 | 10 | 51659.09
2028 | 2008 | 10 | 8 | 11 | 56669.1517
2028 | 2008 | 10 | 8 | 12 | 56111.9989
2028 | 2008 | 10 | 8 | 13 | 55404.2048
2028 | 2008 | 10 | 8 | 14 | 54404.6001
2028 | 2008 | 10 | 8 | 15 | 54629.3807
2028 | 2008 | 10 | 8 | 16 | 53528.5919
2028 | 2008 | 10 | 8 | 17 | 50381.6381
2028 | 2008 | 10 | 8 | 18 | 39727.6652
2028 | 2008 | 10 | 8 | 19 | 12482.7212
2028 | 2008 | 10 | 8 | 20 | 0
2028 | 2008 | 10 | 8 | 21 | 0
2028 | 2008 | 10 | 8 | 22 | 0
2028 | 2008 | 10 | 8 | 23 | 0
2028 | 2008 | 10 | 8 | 24 | 0
2028 | 2008 | 10 | 9 | 1 | 0
2028 | 2008 | 10 | 9 | 2 | 0
2028 | 2008 | 10 | 9 | 3 | 0
2028 | 2008 | 10 | 9 | 4 | 0
2028 | 2008 | 10 | 9 | 5 | 0
2028 | 2008 | 10 | 9 | 6 | 0
2028 | 2008 | 10 | 9 | 7 | 0
2028 | 2008 | 10 | 9 | 8 | 33.4365
2028 | 2008 | 10 | 9 | 9 | 19393.5894
2028 | 2008 | 10 | 9 | 10 | 50285.5635
2028 | 2008 | 10 | 9 | 11 | 56423.3691
2028 | 2008 | 10 | 9 | 12 | 56340.2781
2028 | 2008 | 10 | 9 | 13 | 54376.4165
2028 | 2008 | 10 | 9 | 14 | 54257.3586
2028 | 2008 | 10 | 9 | 15 | 53522.2529
2028 | 2008 | 10 | 9 | 16 | 53375.8599
2028 | 2008 | 10 | 9 | 17 | 49087.5244
2028 | 2008 | 10 | 9 | 18 | 39830.5202
2028 | 2008 | 10 | 9 | 19 | 12171.2098
2028 | 2008 | 10 | 9 | 20 | 0
2028 | 2008 | 10 | 9 | 21 | 0
2028 | 2008 | 10 | 9 | 22 | 0
2028 | 2008 | 10 | 9 | 23 | 0
2028 | 2008 | 10 | 9 | 24 | 0
2028 | 2008 | 10 | 10 | 1 | 0
2028 | 2008 | 10 | 10 | 2 | 0
2028 | 2008 | 10 | 10 | 3 | 0
2028 | 2008 | 10 | 10 | 4 | 0
2028 | 2008 | 10 | 10 | 5 | 0
2028 | 2008 | 10 | 10 | 6 | 0
2028 | 2008 | 10 | 10 | 7 | 0
2028 | 2008 | 10 | 10 | 8 | 24.1782
2028 | 2008 | 10 | 10 | 9 | 13759.0664
2028 | 2008 | 10 | 10 | 10 | 37340.3672
2028 | 2008 | 10 | 10 | 11 | 49199.0141
2028 | 2008 | 10 | 10 | 12 | 50882.6907
2028 | 2008 | 10 | 10 | 13 | 47741.757
2028 | 2008 | 10 | 10 | 14 | 49016.6822
2028 | 2008 | 10 | 10 | 15 | 47779.546
2028 | 2008 | 10 | 10 | 16 | 47885.8665
2028 | 2008 | 10 | 10 | 17 | 48114.5872
2028 | 2008 | 10 | 10 | 18 | 35923.3023
2028 | 2008 | 10 | 10 | 19 | 11085.519
2028 | 2008 | 10 | 10 | 20 | 0
2028 | 2008 | 10 | 10 | 21 | 0
2028 | 2008 | 10 | 10 | 22 | 0
2028 | 2008 | 10 | 10 | 23 | 0
2028 | 2008 | 10 | 10 | 24 | 0
2028 | 2008 | 10 | 11 | 1 | 0
2028 | 2008 | 10 | 11 | 2 | 0
2028 | 2008 | 10 | 11 | 3 | 0
2028 | 2008 | 10 | 11 | 4 | 0
2028 | 2008 | 10 | 11 | 5 | 0
2028 | 2008 | 10 | 11 | 6 | 0
2028 | 2008 | 10 | 11 | 7 | 0
2028 | 2008 | 10 | 11 | 8 | 12.945
2028 | 2008 | 10 | 11 | 9 | 6623.8332
2028 | 2008 | 10 | 11 | 10 | 18545.8444
2028 | 2008 | 10 | 11 | 11 | 25336.9714
2028 | 2008 | 10 | 11 | 12 | 30643.2966
2028 | 2008 | 10 | 11 | 13 | 33045.0146
2028 | 2008 | 10 | 11 | 14 | 37743.5197
2028 | 2008 | 10 | 11 | 15 | 41176.187
2028 | 2008 | 10 | 11 | 16 | 43717.193
2028 | 2008 | 10 | 11 | 17 | 41835.4425
2028 | 2008 | 10 | 11 | 18 | 33046.3744
2028 | 2008 | 10 | 11 | 19 | 9758.1785
2028 | 2008 | 10 | 11 | 20 | 0
2028 | 2008 | 10 | 11 | 21 | 0
2028 | 2008 | 10 | 11 | 22 | 0
2028 | 2008 | 10 | 11 | 23 | 0
2028 | 2008 | 10 | 11 | 24 | 0
2028 | 2008 | 10 | 12 | 1 | 0
2028 | 2008 | 10 | 12 | 2 | 0
2028 | 2008 | 10 | 12 | 3 | 0
2028 | 2008 | 10 | 12 | 4 | 0
2028 | 2008 | 10 | 12 | 5 | 0
2028 | 2008 | 10 | 12 | 6 | 0
2028 | 2008 | 10 | 12 | 7 | 0
2028 | 2008 | 10 | 12 | 8 | 16.8739
2028 | 2008 | 10 | 12 | 9 | 6404.2734
2028 | 2008 | 10 | 12 | 10 | 22243.8046
2028 | 2008 | 10 | 12 | 11 | 29058.2152
2028 | 2008 | 10 | 12 | 12 | 36306.0562
2028 | 2008 | 10 | 12 | 13 | 36212.0957
2028 | 2008 | 10 | 12 | 14 | 36636.3626
2028 | 2008 | 10 | 12 | 15 | 33256.1181
2028 | 2008 | 10 | 12 | 16 | 32932.02
2028 | 2008 | 10 | 12 | 17 | 31378.1216
2028 | 2008 | 10 | 12 | 18 | 26023.8608
2028 | 2008 | 10 | 12 | 19 | 6776.841
2028 | 2008 | 10 | 12 | 20 | 0
2028 | 2008 | 10 | 12 | 21 | 0
2028 | 2008 | 10 | 12 | 22 | 0
2028 | 2008 | 10 | 12 | 23 | 0
2028 | 2008 | 10 | 12 | 24 | 0
2028 | 2008 | 10 | 13 | 1 | 0
2028 | 2008 | 10 | 13 | 2 | 0
2028 | 2008 | 10 | 13 | 3 | 0
2028 | 2008 | 10 | 13 | 4 | 0
2028 | 2008 | 10 | 13 | 5 | 0
2028 | 2008 | 10 | 13 | 6 | 0
2028 | 2008 | 10 | 13 | 7 | 0
2028 | 2008 | 10 | 13 | 8 | 17.7923
2028 | 2008 | 10 | 13 | 9 | 5316.5109
2028 | 2008 | 10 | 13 | 10 | 17262.7829
2028 | 2008 | 10 | 13 | 11 | 22653.3234
2028 | 2008 | 10 | 13 | 12 | 26885.8233
2028 | 2008 | 10 | 13 | 13 | 30520.7475
2028 | 2008 | 10 | 13 | 14 | 32951.5893
2028 | 2008 | 10 | 13 | 15 | 31327.9496
2028 | 2008 | 10 | 13 | 16 | 31310.76
2028 | 2008 | 10 | 13 | 17 | 32167.3339
2028 | 2008 | 10 | 13 | 18 | 24904.1355
2028 | 2008 | 10 | 13 | 19 | 5867.1787
2028 | 2008 | 10 | 13 | 20 | 0
2028 | 2008 | 10 | 13 | 21 | 0
2028 | 2008 | 10 | 13 | 22 | 0
2028 | 2008 | 10 | 13 | 23 | 0
2028 | 2008 | 10 | 13 | 24 | 0
2028 | 2008 | 10 | 14 | 1 | 0
2028 | 2008 | 10 | 14 | 2 | 0
2028 | 2008 | 10 | 14 | 3 | 0
2028 | 2008 | 10 | 14 | 4 | 0
2028 | 2008 | 10 | 14 | 5 | 0
2028 | 2008 | 10 | 14 | 6 | 0
2028 | 2008 | 10 | 14 | 7 | 0
2028 | 2008 | 10 | 14 | 8 | 1.4228
2028 | 2008 | 10 | 14 | 9 | 1581.0915
2028 | 2008 | 10 | 14 | 10 | 7115.3948
2028 | 2008 | 10 | 14 | 11 | 13625.6113
2028 | 2008 | 10 | 14 | 12 | 21669.8861
2028 | 2008 | 10 | 14 | 13 | 26919.3325
2028 | 2008 | 10 | 14 | 14 | 28129.3065
2028 | 2008 | 10 | 14 | 15 | 30441.6844
2028 | 2008 | 10 | 14 | 16 | 30622.5396
2028 | 2008 | 10 | 14 | 17 | 29636.2414
2028 | 2008 | 10 | 14 | 18 | 24955.3504
2028 | 2008 | 10 | 14 | 19 | 5686.9519
2028 | 2008 | 10 | 14 | 20 | 0
2028 | 2008 | 10 | 14 | 21 | 0
2028 | 2008 | 10 | 14 | 22 | 0
2028 | 2008 | 10 | 14 | 23 | 0
2028 | 2008 | 10 | 14 | 24 | 0
2028 | 2008 | 10 | 15 | 1 | 0
2028 | 2008 | 10 | 15 | 2 | 0
2028 | 2008 | 10 | 15 | 3 | 0
2028 | 2008 | 10 | 15 | 4 | 0
2028 | 2008 | 10 | 15 | 5 | 0
2028 | 2008 | 10 | 15 | 6 | 0
2028 | 2008 | 10 | 15 | 7 | 0
2028 | 2008 | 10 | 15 | 8 | 6.4361
2028 | 2008 | 10 | 15 | 9 | 2891.0837
2028 | 2008 | 10 | 15 | 10 | 13191.3838
2028 | 2008 | 10 | 15 | 11 | 19371.2062
2028 | 2008 | 10 | 15 | 12 | 24431.9944
2028 | 2008 | 10 | 15 | 13 | 28293.8314
2028 | 2008 | 10 | 15 | 14 | 30046.2649
2028 | 2008 | 10 | 15 | 15 | 29545.7799
2028 | 2008 | 10 | 15 | 16 | 28540.7716
2028 | 2008 | 10 | 15 | 17 | 27557.4295
2028 | 2008 | 10 | 15 | 18 | 25256.3081
2028 | 2008 | 10 | 15 | 19 | 6708.7562
2028 | 2008 | 10 | 15 | 20 | 0
2028 | 2008 | 10 | 15 | 21 | 0
2028 | 2008 | 10 | 15 | 22 | 0
2028 | 2008 | 10 | 15 | 23 | 0
2028 | 2008 | 10 | 15 | 24 | 0
2028 | 2008 | 10 | 16 | 1 | 0
2028 | 2008 | 10 | 16 | 2 | 0
2028 | 2008 | 10 | 16 | 3 | 0
2028 | 2008 | 10 | 16 | 4 | 0
2028 | 2008 | 10 | 16 | 5 | 0
2028 | 2008 | 10 | 16 | 6 | 0
2028 | 2008 | 10 | 16 | 7 | 0
2028 | 2008 | 10 | 16 | 8 | 0.48227
2028 | 2008 | 10 | 16 | 9 | 1500.4542
2028 | 2008 | 10 | 16 | 10 | 10642.4529
2028 | 2008 | 10 | 16 | 11 | 17147.7778
2028 | 2008 | 10 | 16 | 12 | 26617.8624
2028 | 2008 | 10 | 16 | 13 | 30183.1501
2028 | 2008 | 10 | 16 | 14 | 31682.8435
2028 | 2008 | 10 | 16 | 15 | 32211.6215
2028 | 2008 | 10 | 16 | 16 | 32797.4196
2028 | 2008 | 10 | 16 | 17 | 27889.0812
2028 | 2008 | 10 | 16 | 18 | 26160.6905
2028 | 2008 | 10 | 16 | 19 | 6168.7725
2028 | 2008 | 10 | 16 | 20 | 0
2028 | 2008 | 10 | 16 | 21 | 0
2028 | 2008 | 10 | 16 | 22 | 0
2028 | 2008 | 10 | 16 | 23 | 0
2028 | 2008 | 10 | 16 | 24 | 0
2028 | 2008 | 10 | 17 | 1 | 0
2028 | 2008 | 10 | 17 | 2 | 0
2028 | 2008 | 10 | 17 | 3 | 0
2028 | 2008 | 10 | 17 | 4 | 0
2028 | 2008 | 10 | 17 | 5 | 0
2028 | 2008 | 10 | 17 | 6 | 0
2028 | 2008 | 10 | 17 | 7 | 0
2028 | 2008 | 10 | 17 | 8 | 2.332
2028 | 2008 | 10 | 17 | 9 | 8181.5512
2028 | 2008 | 10 | 17 | 10 | 28074.6429
2028 | 2008 | 10 | 17 | 11 | 32990.1152
2028 | 2008 | 10 | 17 | 12 | 34822.8883
2028 | 2008 | 10 | 17 | 13 | 36728.5703
2028 | 2008 | 10 | 17 | 14 | 37014.0531
2028 | 2008 | 10 | 17 | 15 | 35510.4994
2028 | 2008 | 10 | 17 | 16 | 35028.2665
2028 | 2008 | 10 | 17 | 17 | 34029.2491
2028 | 2008 | 10 | 17 | 18 | 27236.5435
2028 | 2008 | 10 | 17 | 19 | 6387.7591
2028 | 2008 | 10 | 17 | 20 | 0
2028 | 2008 | 10 | 17 | 21 | 0
2028 | 2008 | 10 | 17 | 22 | 0
2028 | 2008 | 10 | 17 | 23 | 0
2028 | 2008 | 10 | 17 | 24 | 0
2028 | 2008 | 10 | 18 | 1 | 0
2028 | 2008 | 10 | 18 | 2 | 0
2028 | 2008 | 10 | 18 | 3 | 0
2028 | 2008 | 10 | 18 | 4 | 0
2028 | 2008 | 10 | 18 | 5 | 0
2028 | 2008 | 10 | 18 | 6 | 0
2028 | 2008 | 10 | 18 | 7 | 0
2028 | 2008 | 10 | 18 | 8 | 20.7526
2028 | 2008 | 10 | 18 | 9 | 15501.4433
2028 | 2008 | 10 | 18 | 10 | 44308.0741
2028 | 2008 | 10 | 18 | 11 | 51862.3038
2028 | 2008 | 10 | 18 | 12 | 52113.1794
2028 | 2008 | 10 | 18 | 13 | 51710.9681
2028 | 2008 | 10 | 18 | 14 | 49944.668
2028 | 2008 | 10 | 18 | 15 | 50521.755
2028 | 2008 | 10 | 18 | 16 | 49157.6943
2028 | 2008 | 10 | 18 | 17 | 46000.0145
2028 | 2008 | 10 | 18 | 18 | 35023.3021
2028 | 2008 | 10 | 18 | 19 | 7313.6259
2028 | 2008 | 10 | 18 | 20 | 0
2028 | 2008 | 10 | 18 | 21 | 0
2028 | 2008 | 10 | 18 | 22 | 0
2028 | 2008 | 10 | 18 | 23 | 0
2028 | 2008 | 10 | 18 | 24 | 0
2028 | 2008 | 10 | 19 | 1 | 0
2028 | 2008 | 10 | 19 | 2 | 0
2028 | 2008 | 10 | 19 | 3 | 0
2028 | 2008 | 10 | 19 | 4 | 0
2028 | 2008 | 10 | 19 | 5 | 0
2028 | 2008 | 10 | 19 | 6 | 0
2028 | 2008 | 10 | 19 | 7 | 0
2028 | 2008 | 10 | 19 | 8 | 19.9747
2028 | 2008 | 10 | 19 | 9 | 15590.6681
2028 | 2008 | 10 | 19 | 10 | 45898.1612
2028 | 2008 | 10 | 19 | 11 | 51598.7361
2028 | 2008 | 10 | 19 | 12 | 52929.4058
2028 | 2008 | 10 | 19 | 13 | 51417.9396
2028 | 2008 | 10 | 19 | 14 | 50244.6279
2028 | 2008 | 10 | 19 | 15 | 49703.3865
2028 | 2008 | 10 | 19 | 16 | 45969.7943
2028 | 2008 | 10 | 19 | 17 | 44806.8447
2028 | 2008 | 10 | 19 | 18 | 31380.4619
2028 | 2008 | 10 | 19 | 19 | 6414.8913
2028 | 2008 | 10 | 19 | 20 | 0
2028 | 2008 | 10 | 19 | 21 | 0
2028 | 2008 | 10 | 19 | 22 | 0
2028 | 2008 | 10 | 19 | 23 | 0
2028 | 2008 | 10 | 19 | 24 | 0
2028 | 2008 | 10 | 20 | 1 | 0
2028 | 2008 | 10 | 20 | 2 | 0
2028 | 2008 | 10 | 20 | 3 | 0
2028 | 2008 | 10 | 20 | 4 | 0
2028 | 2008 | 10 | 20 | 5 | 0
2028 | 2008 | 10 | 20 | 6 | 0
2028 | 2008 | 10 | 20 | 7 | 0
2028 | 2008 | 10 | 20 | 8 | 15.5983
2028 | 2008 | 10 | 20 | 9 | 13842.5765
2028 | 2008 | 10 | 20 | 10 | 42242.2487
2028 | 2008 | 10 | 20 | 11 | 48737.7862
2028 | 2008 | 10 | 20 | 12 | 49062.0708
2028 | 2008 | 10 | 20 | 13 | 49155.0596
2028 | 2008 | 10 | 20 | 14 | 47652.6223
2028 | 2008 | 10 | 20 | 15 | 47376.1279
2028 | 2008 | 10 | 20 | 16 | 45761.574
2028 | 2008 | 10 | 20 | 17 | 41703.9626
2028 | 2008 | 10 | 20 | 18 | 30952.5018
2028 | 2008 | 10 | 20 | 19 | 5899.3689
2028 | 2008 | 10 | 20 | 20 | 0
2028 | 2008 | 10 | 20 | 21 | 0
2028 | 2008 | 10 | 20 | 22 | 0
2028 | 2008 | 10 | 20 | 23 | 0
2028 | 2008 | 10 | 20 | 24 | 0
2028 | 2008 | 10 | 21 | 1 | 0
2028 | 2008 | 10 | 21 | 2 | 0
2028 | 2008 | 10 | 21 | 3 | 0
2028 | 2008 | 10 | 21 | 4 | 0
2028 | 2008 | 10 | 21 | 5 | 0
2028 | 2008 | 10 | 21 | 6 | 0
2028 | 2008 | 10 | 21 | 7 | 0
2028 | 2008 | 10 | 21 | 8 | 9.6645
2028 | 2008 | 10 | 21 | 9 | 7747.1492
2028 | 2008 | 10 | 21 | 10 | 24632.489
2028 | 2008 | 10 | 21 | 11 | 32023.3833
2028 | 2008 | 10 | 21 | 12 | 36045.3968
2028 | 2008 | 10 | 21 | 13 | 39072.4408
2028 | 2008 | 10 | 21 | 14 | 40516.7075
2028 | 2008 | 10 | 21 | 15 | 40116.6941
2028 | 2008 | 10 | 21 | 16 | 40200.7807
2028 | 2008 | 10 | 21 | 17 | 37363.6616
2028 | 2008 | 10 | 21 | 18 | 27818.5826
2028 | 2008 | 10 | 21 | 19 | 4935.6854
2028 | 2008 | 10 | 21 | 20 | 0
2028 | 2008 | 10 | 21 | 21 | 0
2028 | 2008 | 10 | 21 | 22 | 0
2028 | 2008 | 10 | 21 | 23 | 0
2028 | 2008 | 10 | 21 | 24 | 0
2028 | 2008 | 10 | 22 | 1 | 0
2028 | 2008 | 10 | 22 | 2 | 0
2028 | 2008 | 10 | 22 | 3 | 0
2028 | 2008 | 10 | 22 | 4 | 0
2028 | 2008 | 10 | 22 | 5 | 0
2028 | 2008 | 10 | 22 | 6 | 0
2028 | 2008 | 10 | 22 | 7 | 0
2028 | 2008 | 10 | 22 | 8 | 8.5606
2028 | 2008 | 10 | 22 | 9 | 5569.0351
2028 | 2008 | 10 | 22 | 10 | 18739.1406
2028 | 2008 | 10 | 22 | 11 | 27422.0888
2028 | 2008 | 10 | 22 | 12 | 31686.8404
2028 | 2008 | 10 | 22 | 13 | 35571.3126
2028 | 2008 | 10 | 22 | 14 | 36986.0164
2028 | 2008 | 10 | 22 | 15 | 36202.0776
2028 | 2008 | 10 | 22 | 16 | 38348.5472
2028 | 2008 | 10 | 22 | 17 | 32208.6083
2028 | 2008 | 10 | 22 | 18 | 24928.4185
2028 | 2008 | 10 | 22 | 19 | 4409.3716
2028 | 2008 | 10 | 22 | 20 | 0
2028 | 2008 | 10 | 22 | 21 | 0
2028 | 2008 | 10 | 22 | 22 | 0
2028 | 2008 | 10 | 22 | 23 | 0
2028 | 2008 | 10 | 22 | 24 | 0
2028 | 2008 | 10 | 23 | 1 | 0
2028 | 2008 | 10 | 23 | 2 | 0
2028 | 2008 | 10 | 23 | 3 | 0
2028 | 2008 | 10 | 23 | 4 | 0
2028 | 2008 | 10 | 23 | 5 | 0
2028 | 2008 | 10 | 23 | 6 | 0
2028 | 2008 | 10 | 23 | 7 | 0
2028 | 2008 | 10 | 23 | 8 | 7.7832
2028 | 2008 | 10 | 23 | 9 | 14416.1062
2028 | 2008 | 10 | 23 | 10 | 43104.2646
2028 | 2008 | 10 | 23 | 11 | 50949.6605
2028 | 2008 | 10 | 23 | 12 | 51714.6613
2028 | 2008 | 10 | 23 | 13 | 50961.5105
2028 | 2008 | 10 | 23 | 14 | 50793.7756
2028 | 2008 | 10 | 23 | 15 | 50243.046
2028 | 2008 | 10 | 23 | 16 | 49432.4783
2028 | 2008 | 10 | 23 | 17 | 45977.0081
2028 | 2008 | 10 | 23 | 18 | 33482.0393
2028 | 2008 | 10 | 23 | 19 | 4587.0906
2028 | 2008 | 10 | 23 | 20 | 0
2028 | 2008 | 10 | 23 | 21 | 0
2028 | 2008 | 10 | 23 | 22 | 0
2028 | 2008 | 10 | 23 | 23 | 0
2028 | 2008 | 10 | 23 | 24 | 0
2028 | 2008 | 10 | 24 | 1 | 0
2028 | 2008 | 10 | 24 | 2 | 0
2028 | 2008 | 10 | 24 | 3 | 0
2028 | 2008 | 10 | 24 | 4 | 0
2028 | 2008 | 10 | 24 | 5 | 0
2028 | 2008 | 10 | 24 | 6 | 0
2028 | 2008 | 10 | 24 | 7 | 0
2028 | 2008 | 10 | 24 | 8 | 11.3728
2028 | 2008 | 10 | 24 | 9 | 14813.6357
2028 | 2008 | 10 | 24 | 10 | 46516.9769
2028 | 2008 | 10 | 24 | 11 | 53508.5574
2028 | 2008 | 10 | 24 | 12 | 54159.9333
2028 | 2008 | 10 | 24 | 13 | 51475.3739
2028 | 2008 | 10 | 24 | 14 | 50854.1607
2028 | 2008 | 10 | 24 | 15 | 50412.0169
2028 | 2008 | 10 | 24 | 16 | 47483.6554
2028 | 2008 | 10 | 24 | 17 | 45642.526
2028 | 2008 | 10 | 24 | 18 | 29143.0727
2028 | 2008 | 10 | 24 | 19 | 3729.8537
2028 | 2008 | 10 | 24 | 20 | 0
2028 | 2008 | 10 | 24 | 21 | 0
2028 | 2008 | 10 | 24 | 22 | 0
2028 | 2008 | 10 | 24 | 23 | 0
2028 | 2008 | 10 | 24 | 24 | 0
2028 | 2008 | 10 | 25 | 1 | 0
2028 | 2008 | 10 | 25 | 2 | 0
2028 | 2008 | 10 | 25 | 3 | 0
2028 | 2008 | 10 | 25 | 4 | 0
2028 | 2008 | 10 | 25 | 5 | 0
2028 | 2008 | 10 | 25 | 6 | 0
2028 | 2008 | 10 | 25 | 7 | 0
2028 | 2008 | 10 | 25 | 8 | 10.3332
2028 | 2008 | 10 | 25 | 9 | 13399.5556
2028 | 2008 | 10 | 25 | 10 | 42889.057
2028 | 2008 | 10 | 25 | 11 | 49694.6435
2028 | 2008 | 10 | 25 | 12 | 50424.1431
2028 | 2008 | 10 | 25 | 13 | 49066.2898
2028 | 2008 | 10 | 25 | 14 | 47819.9265
2028 | 2008 | 10 | 25 | 15 | 47669.0961
2028 | 2008 | 10 | 25 | 16 | 46577.4377
2028 | 2008 | 10 | 25 | 17 | 42838.3962
2028 | 2008 | 10 | 25 | 18 | 27594.8845
2028 | 2008 | 10 | 25 | 19 | 3161.0327
2028 | 2008 | 10 | 25 | 20 | 0
2028 | 2008 | 10 | 25 | 21 | 0
2028 | 2008 | 10 | 25 | 22 | 0
2028 | 2008 | 10 | 25 | 23 | 0
2028 | 2008 | 10 | 25 | 24 | 0
2028 | 2008 | 10 | 26 | 1 | 0
2028 | 2008 | 10 | 26 | 2 | 0
2028 | 2008 | 10 | 26 | 3 | 0
2028 | 2008 | 10 | 26 | 4 | 0
2028 | 2008 | 10 | 26 | 5 | 0
2028 | 2008 | 10 | 26 | 6 | 0
2028 | 2008 | 10 | 26 | 7 | 0
2028 | 2008 | 10 | 26 | 8 | 8.289
2028 | 2008 | 10 | 26 | 9 | 11121.2513
2028 | 2008 | 10 | 26 | 10 | 35581.2367
2028 | 2008 | 10 | 26 | 11 | 40693.6271
2028 | 2008 | 10 | 26 | 12 | 40471.1797
2028 | 2008 | 10 | 26 | 13 | 41780.5325
2028 | 2008 | 10 | 26 | 14 | 43720.3278
2028 | 2008 | 10 | 26 | 15 | 41793.8443
2028 | 2008 | 10 | 26 | 16 | 38820.6079
2028 | 2008 | 10 | 26 | 17 | 38527.3431
2028 | 2008 | 10 | 26 | 18 | 29629.913
2028 | 2008 | 10 | 26 | 19 | 2962.7734
2028 | 2008 | 10 | 26 | 20 | 0
2028 | 2008 | 10 | 26 | 21 | 0
2028 | 2008 | 10 | 26 | 22 | 0
2028 | 2008 | 10 | 26 | 23 | 0
2028 | 2008 | 10 | 26 | 24 | 0
2028 | 2008 | 10 | 27 | 1 | 0
2028 | 2008 | 10 | 27 | 2 | 0
2028 | 2008 | 10 | 27 | 3 | 0
2028 | 2008 | 10 | 27 | 4 | 0
2028 | 2008 | 10 | 27 | 5 | 0
2028 | 2008 | 10 | 27 | 6 | 0
2028 | 2008 | 10 | 27 | 7 | 0
2028 | 2008 | 10 | 27 | 8 | 2.3435
2028 | 2008 | 10 | 27 | 9 | 13033.4655
2028 | 2008 | 10 | 27 | 10 | 43943.8476
2028 | 2008 | 10 | 27 | 11 | 52490.9578
2028 | 2008 | 10 | 27 | 12 | 54324.9373
2028 | 2008 | 10 | 27 | 13 | 52105.3225
2028 | 2008 | 10 | 27 | 14 | 51922.1353
2028 | 2008 | 10 | 27 | 15 | 51488.1705
2028 | 2008 | 10 | 27 | 16 | 49342.9685
2028 | 2008 | 10 | 27 | 17 | 45685.8667
2028 | 2008 | 10 | 27 | 18 | 28824.1184
2028 | 2008 | 10 | 27 | 19 | 2879.8527
2028 | 2008 | 10 | 27 | 20 | 0
2028 | 2008 | 10 | 27 | 21 | 0
2028 | 2008 | 10 | 27 | 22 | 0
2028 | 2008 | 10 | 27 | 23 | 0
2028 | 2008 | 10 | 27 | 24 | 0
2028 | 2008 | 10 | 28 | 1 | 0
2028 | 2008 | 10 | 28 | 2 | 0
2028 | 2008 | 10 | 28 | 3 | 0
2028 | 2008 | 10 | 28 | 4 | 0
2028 | 2008 | 10 | 28 | 5 | 0
2028 | 2008 | 10 | 28 | 6 | 0
2028 | 2008 | 10 | 28 | 7 | 0
2028 | 2008 | 10 | 28 | 8 | 4.1892
2028 | 2008 | 10 | 28 | 9 | 14388.6752
2028 | 2008 | 10 | 28 | 10 | 44583.7149
2028 | 2008 | 10 | 28 | 11 | 51001.944
2028 | 2008 | 10 | 28 | 12 | 51788.9667
2028 | 2008 | 10 | 28 | 13 | 50123.849
2028 | 2008 | 10 | 28 | 14 | 48730.961
2028 | 2008 | 10 | 28 | 15 | 48431.9592
2028 | 2008 | 10 | 28 | 16 | 46798.2055
2028 | 2008 | 10 | 28 | 17 | 42205.2795
2028 | 2008 | 10 | 28 | 18 | 30105.7041
2028 | 2008 | 10 | 28 | 19 | 2558.9758
2028 | 2008 | 10 | 28 | 20 | 0
2028 | 2008 | 10 | 28 | 21 | 0
2028 | 2008 | 10 | 28 | 22 | 0
2028 | 2008 | 10 | 28 | 23 | 0
2028 | 2008 | 10 | 28 | 24 | 0
2028 | 2008 | 10 | 29 | 1 | 0
2028 | 2008 | 10 | 29 | 2 | 0
2028 | 2008 | 10 | 29 | 3 | 0
2028 | 2008 | 10 | 29 | 4 | 0
2028 | 2008 | 10 | 29 | 5 | 0
2028 | 2008 | 10 | 29 | 6 | 0
2028 | 2008 | 10 | 29 | 7 | 0
2028 | 2008 | 10 | 29 | 8 | 5.4891
2028 | 2008 | 10 | 29 | 9 | 12436.7353
2028 | 2008 | 10 | 29 | 10 | 41606.3043
2028 | 2008 | 10 | 29 | 11 | 49226.1039
2028 | 2008 | 10 | 29 | 12 | 49678.2408
2028 | 2008 | 10 | 29 | 13 | 48029.2074
2028 | 2008 | 10 | 29 | 14 | 47626.8838
2028 | 2008 | 10 | 29 | 15 | 46337.8726
2028 | 2008 | 10 | 29 | 16 | 45198.2496
2028 | 2008 | 10 | 29 | 17 | 43408.734
2028 | 2008 | 10 | 29 | 18 | 27511.909
2028 | 2008 | 10 | 29 | 19 | 2294.7906
2028 | 2008 | 10 | 29 | 20 | 0
2028 | 2008 | 10 | 29 | 21 | 0
2028 | 2008 | 10 | 29 | 22 | 0
2028 | 2008 | 10 | 29 | 23 | 0
2028 | 2008 | 10 | 29 | 24 | 0
2028 | 2008 | 10 | 30 | 1 | 0
2028 | 2008 | 10 | 30 | 2 | 0
2028 | 2008 | 10 | 30 | 3 | 0
2028 | 2008 | 10 | 30 | 4 | 0
2028 | 2008 | 10 | 30 | 5 | 0
2028 | 2008 | 10 | 30 | 6 | 0
2028 | 2008 | 10 | 30 | 7 | 0
2028 | 2008 | 10 | 30 | 8 | 2.4384
2028 | 2008 | 10 | 30 | 9 | 7691.2808
2028 | 2008 | 10 | 30 | 10 | 24546.0728
2028 | 2008 | 10 | 30 | 11 | 30494.444
2028 | 2008 | 10 | 30 | 12 | 33917.0592
2028 | 2008 | 10 | 30 | 13 | 38023.5687
2028 | 2008 | 10 | 30 | 14 | 40917.1171
2028 | 2008 | 10 | 30 | 15 | 40765.3124
2028 | 2008 | 10 | 30 | 16 | 42772.4408
2028 | 2008 | 10 | 30 | 17 | 38297.0936
2028 | 2008 | 10 | 30 | 18 | 24354.3197
2028 | 2008 | 10 | 30 | 19 | 1989.4348
2028 | 2008 | 10 | 30 | 20 | 0
2028 | 2008 | 10 | 30 | 21 | 0
2028 | 2008 | 10 | 30 | 22 | 0
2028 | 2008 | 10 | 30 | 23 | 0
2028 | 2008 | 10 | 30 | 24 | 0
2028 | 2008 | 10 | 31 | 1 | 0
2028 | 2008 | 10 | 31 | 2 | 0
2028 | 2008 | 10 | 31 | 3 | 0
2028 | 2008 | 10 | 31 | 4 | 0
2028 | 2008 | 10 | 31 | 5 | 0
2028 | 2008 | 10 | 31 | 6 | 0
2028 | 2008 | 10 | 31 | 7 | 0
2028 | 2008 | 10 | 31 | 8 | 2.1371
2028 | 2008 | 10 | 31 | 9 | 6104.7056
2028 | 2008 | 10 | 31 | 10 | 21386.8118
2028 | 2008 | 10 | 31 | 11 | 27534.402
2028 | 2008 | 10 | 31 | 12 | 34267.5253
2028 | 2008 | 10 | 31 | 13 | 37407.1173
2028 | 2008 | 10 | 31 | 14 | 38962.9335
2028 | 2008 | 10 | 31 | 15 | 40688.9417
2028 | 2008 | 10 | 31 | 16 | 39389.476
2028 | 2008 | 10 | 31 | 17 | 38950.3264
2028 | 2008 | 10 | 31 | 18 | 23172.4983
2028 | 2008 | 10 | 31 | 19 | 2975.2573
2028 | 2008 | 10 | 31 | 20 | 0
2028 | 2008 | 10 | 31 | 21 | 0
2028 | 2008 | 10 | 31 | 22 | 0
2028 | 2008 | 10 | 31 | 23 | 0
2028 | 2008 | 10 | 31 | 24 | 0
2029 | 2008 | 10 | 1 | 1 | 0
2029 | 2008 | 10 | 1 | 2 | 0
2029 | 2008 | 10 | 1 | 3 | 0
2029 | 2008 | 10 | 1 | 4 | 0
2029 | 2008 | 10 | 1 | 5 | 0
2029 | 2008 | 10 | 1 | 6 | 0
2029 | 2008 | 10 | 1 | 7 | 0
2029 | 2008 | 10 | 1 | 8 | 48.6855
2029 | 2008 | 10 | 1 | 9 | 20132.441
2029 | 2008 | 10 | 1 | 10 | 50992.8964
2029 | 2008 | 10 | 1 | 11 | 56350.6373
2029 | 2008 | 10 | 1 | 12 | 56939.1687
2029 | 2008 | 10 | 1 | 13 | 55804.8781
2029 | 2008 | 10 | 1 | 14 | 55189.7023
2029 | 2008 | 10 | 1 | 15 | 54075.7603
2029 | 2008 | 10 | 1 | 16 | 54908.1598
2029 | 2008 | 10 | 1 | 17 | 53761.2875
2029 | 2008 | 10 | 1 | 18 | 42168.3701
2029 | 2008 | 10 | 1 | 19 | 14429.3839
2029 | 2008 | 10 | 1 | 20 | 0
2029 | 2008 | 10 | 1 | 21 | 0
2029 | 2008 | 10 | 1 | 22 | 0
2029 | 2008 | 10 | 1 | 23 | 0
2029 | 2008 | 10 | 1 | 24 | 0
2029 | 2008 | 10 | 2 | 1 | 0
2029 | 2008 | 10 | 2 | 2 | 0
2029 | 2008 | 10 | 2 | 3 | 0
2029 | 2008 | 10 | 2 | 4 | 0
2029 | 2008 | 10 | 2 | 5 | 0
2029 | 2008 | 10 | 2 | 6 | 0
2029 | 2008 | 10 | 2 | 7 | 0
2029 | 2008 | 10 | 2 | 8 | 60.204
2029 | 2008 | 10 | 2 | 9 | 20475.1419
2029 | 2008 | 10 | 2 | 10 | 49172.9989
2029 | 2008 | 10 | 2 | 11 | 56679.016
2029 | 2008 | 10 | 2 | 12 | 56862.5851
2029 | 2008 | 10 | 2 | 13 | 55025.9464
2029 | 2008 | 10 | 2 | 14 | 54349.6226
2029 | 2008 | 10 | 2 | 15 | 53119.1894
2029 | 2008 | 10 | 2 | 16 | 53935.5736
2029 | 2008 | 10 | 2 | 17 | 53075.356
2029 | 2008 | 10 | 2 | 18 | 41833.349
2029 | 2008 | 10 | 2 | 19 | 14178.8702
2029 | 2008 | 10 | 2 | 20 | 0
2029 | 2008 | 10 | 2 | 21 | 0
2029 | 2008 | 10 | 2 | 22 | 0
2029 | 2008 | 10 | 2 | 23 | 0
2029 | 2008 | 10 | 2 | 24 | 0
2029 | 2008 | 10 | 3 | 1 | 0
2029 | 2008 | 10 | 3 | 2 | 0
2029 | 2008 | 10 | 3 | 3 | 0
2029 | 2008 | 10 | 3 | 4 | 0
2029 | 2008 | 10 | 3 | 5 | 0
2029 | 2008 | 10 | 3 | 6 | 0
2029 | 2008 | 10 | 3 | 7 | 0
2029 | 2008 | 10 | 3 | 8 | 57.8862
2029 | 2008 | 10 | 3 | 9 | 16553.0011
2029 | 2008 | 10 | 3 | 10 | 46172.291
2029 | 2008 | 10 | 3 | 11 | 53357.4819
2029 | 2008 | 10 | 3 | 12 | 52645.2136
2029 | 2008 | 10 | 3 | 13 | 51531.0682
2029 | 2008 | 10 | 3 | 14 | 50321.8394
2029 | 2008 | 10 | 3 | 15 | 50626.2434
2029 | 2008 | 10 | 3 | 16 | 49362.7808
2029 | 2008 | 10 | 3 | 17 | 48004.238
2029 | 2008 | 10 | 3 | 18 | 39039.7617
2029 | 2008 | 10 | 3 | 19 | 13286.9436
2029 | 2008 | 10 | 3 | 20 | 0
2029 | 2008 | 10 | 3 | 21 | 0
2029 | 2008 | 10 | 3 | 22 | 0
2029 | 2008 | 10 | 3 | 23 | 0
2029 | 2008 | 10 | 3 | 24 | 0
2029 | 2008 | 10 | 4 | 1 | 0
2029 | 2008 | 10 | 4 | 2 | 0
2029 | 2008 | 10 | 4 | 3 | 0
2029 | 2008 | 10 | 4 | 4 | 0
2029 | 2008 | 10 | 4 | 5 | 0
2029 | 2008 | 10 | 4 | 6 | 0
2029 | 2008 | 10 | 4 | 7 | 0
2029 | 2008 | 10 | 4 | 8 | 37.5899
2029 | 2008 | 10 | 4 | 9 | 12485.9313
2029 | 2008 | 10 | 4 | 10 | 38964.6288
2029 | 2008 | 10 | 4 | 11 | 48774.6315
2029 | 2008 | 10 | 4 | 12 | 53103.5948
2029 | 2008 | 10 | 4 | 13 | 53074.3563
2029 | 2008 | 10 | 4 | 14 | 51660.6968
2029 | 2008 | 10 | 4 | 15 | 51041.5946
2029 | 2008 | 10 | 4 | 16 | 50757.5871
2029 | 2008 | 10 | 4 | 17 | 49538.9619
2029 | 2008 | 10 | 4 | 18 | 37850.511
2029 | 2008 | 10 | 4 | 19 | 13054.2656
2029 | 2008 | 10 | 4 | 20 | 0
2029 | 2008 | 10 | 4 | 21 | 0
2029 | 2008 | 10 | 4 | 22 | 0
2029 | 2008 | 10 | 4 | 23 | 0
2029 | 2008 | 10 | 4 | 24 | 0
2029 | 2008 | 10 | 5 | 1 | 0
2029 | 2008 | 10 | 5 | 2 | 0
2029 | 2008 | 10 | 5 | 3 | 0
2029 | 2008 | 10 | 5 | 4 | 0
2029 | 2008 | 10 | 5 | 5 | 0
2029 | 2008 | 10 | 5 | 6 | 0
2029 | 2008 | 10 | 5 | 7 | 0
2029 | 2008 | 10 | 5 | 8 | 39.1087
2029 | 2008 | 10 | 5 | 9 | 12481.7587
2029 | 2008 | 10 | 5 | 10 | 33668.0461
2029 | 2008 | 10 | 5 | 11 | 36568.6711
2029 | 2008 | 10 | 5 | 12 | 41866.8812
2029 | 2008 | 10 | 5 | 13 | 42633.5084
2029 | 2008 | 10 | 5 | 14 | 39740.8721
2029 | 2008 | 10 | 5 | 15 | 37979.784
2029 | 2008 | 10 | 5 | 16 | 38197.0241
2029 | 2008 | 10 | 5 | 17 | 36606.6823
2029 | 2008 | 10 | 5 | 18 | 30514.9654
2029 | 2008 | 10 | 5 | 19 | 10661.1093
2029 | 2008 | 10 | 5 | 20 | 0
2029 | 2008 | 10 | 5 | 21 | 0
2029 | 2008 | 10 | 5 | 22 | 0
2029 | 2008 | 10 | 5 | 23 | 0
2029 | 2008 | 10 | 5 | 24 | 0
2029 | 2008 | 10 | 6 | 1 | 0
2029 | 2008 | 10 | 6 | 2 | 0
2029 | 2008 | 10 | 6 | 3 | 0
2029 | 2008 | 10 | 6 | 4 | 0
2029 | 2008 | 10 | 6 | 5 | 0
2029 | 2008 | 10 | 6 | 6 | 0
2029 | 2008 | 10 | 6 | 7 | 0
2029 | 2008 | 10 | 6 | 8 | 18.5113
2029 | 2008 | 10 | 6 | 9 | 9610.0711
2029 | 2008 | 10 | 6 | 10 | 30467.3273
2029 | 2008 | 10 | 6 | 11 | 41514.2861
2029 | 2008 | 10 | 6 | 12 | 46176.3594
2029 | 2008 | 10 | 6 | 13 | 47164.4967
2029 | 2008 | 10 | 6 | 14 | 47325.3644
2029 | 2008 | 10 | 6 | 15 | 47348.3454
2029 | 2008 | 10 | 6 | 16 | 48974.536
2029 | 2008 | 10 | 6 | 17 | 48660.7729
2029 | 2008 | 10 | 6 | 18 | 38002.4139
2029 | 2008 | 10 | 6 | 19 | 12375.6156
2029 | 2008 | 10 | 6 | 20 | 0
2029 | 2008 | 10 | 6 | 21 | 0
2029 | 2008 | 10 | 6 | 22 | 0
2029 | 2008 | 10 | 6 | 23 | 0
2029 | 2008 | 10 | 6 | 24 | 0
2029 | 2008 | 10 | 7 | 1 | 0
2029 | 2008 | 10 | 7 | 2 | 0
2029 | 2008 | 10 | 7 | 3 | 0
2029 | 2008 | 10 | 7 | 4 | 0
2029 | 2008 | 10 | 7 | 5 | 0
2029 | 2008 | 10 | 7 | 6 | 0
2029 | 2008 | 10 | 7 | 7 | 0
2029 | 2008 | 10 | 7 | 8 | 23.6528
2029 | 2008 | 10 | 7 | 9 | 13129.6925
2029 | 2008 | 10 | 7 | 10 | 40973.4268
2029 | 2008 | 10 | 7 | 11 | 47152.1752
2029 | 2008 | 10 | 7 | 12 | 51380.5062
2029 | 2008 | 10 | 7 | 13 | 52183.8527
2029 | 2008 | 10 | 7 | 14 | 52351.4026
2029 | 2008 | 10 | 7 | 15 | 51715.2256
2029 | 2008 | 10 | 7 | 16 | 53190.8691
2029 | 2008 | 10 | 7 | 17 | 49171.6203
2029 | 2008 | 10 | 7 | 18 | 37398.6173
2029 | 2008 | 10 | 7 | 19 | 13256.747
2029 | 2008 | 10 | 7 | 20 | 0
2029 | 2008 | 10 | 7 | 21 | 0
2029 | 2008 | 10 | 7 | 22 | 0
2029 | 2008 | 10 | 7 | 23 | 0
2029 | 2008 | 10 | 7 | 24 | 0
2029 | 2008 | 10 | 8 | 1 | 0
2029 | 2008 | 10 | 8 | 2 | 0
2029 | 2008 | 10 | 8 | 3 | 0
2029 | 2008 | 10 | 8 | 4 | 0
2029 | 2008 | 10 | 8 | 5 | 0
2029 | 2008 | 10 | 8 | 6 | 0
2029 | 2008 | 10 | 8 | 7 | 0
2029 | 2008 | 10 | 8 | 8 | 32.2666
2029 | 2008 | 10 | 8 | 9 | 19337.9664
2029 | 2008 | 10 | 8 | 10 | 52459.7688
2029 | 2008 | 10 | 8 | 11 | 57559.8334
2029 | 2008 | 10 | 8 | 12 | 57038.3949
2029 | 2008 | 10 | 8 | 13 | 56294.5438
2029 | 2008 | 10 | 8 | 14 | 55277.9122
2029 | 2008 | 10 | 8 | 15 | 55516.2895
2029 | 2008 | 10 | 8 | 16 | 54432.2798
2029 | 2008 | 10 | 8 | 17 | 51211.9929
2029 | 2008 | 10 | 8 | 18 | 40392.8361
2029 | 2008 | 10 | 8 | 19 | 12676.9197
2029 | 2008 | 10 | 8 | 20 | 0
2029 | 2008 | 10 | 8 | 21 | 0
2029 | 2008 | 10 | 8 | 22 | 0
2029 | 2008 | 10 | 8 | 23 | 0
2029 | 2008 | 10 | 8 | 24 | 0
2029 | 2008 | 10 | 9 | 1 | 0
2029 | 2008 | 10 | 9 | 2 | 0
2029 | 2008 | 10 | 9 | 3 | 0
2029 | 2008 | 10 | 9 | 4 | 0
2029 | 2008 | 10 | 9 | 5 | 0
2029 | 2008 | 10 | 9 | 6 | 0
2029 | 2008 | 10 | 9 | 7 | 0
2029 | 2008 | 10 | 9 | 8 | 33.4365
2029 | 2008 | 10 | 9 | 9 | 19681.8132
2029 | 2008 | 10 | 9 | 10 | 51121.3322
2029 | 2008 | 10 | 9 | 11 | 57342.503
2029 | 2008 | 10 | 9 | 12 | 57290.4543
2029 | 2008 | 10 | 9 | 13 | 55298.7381
2029 | 2008 | 10 | 9 | 14 | 55189.8094
2029 | 2008 | 10 | 9 | 15 | 54456.6053
2029 | 2008 | 10 | 9 | 16 | 54313.0143
2029 | 2008 | 10 | 9 | 17 | 49870.0828
2029 | 2008 | 10 | 9 | 18 | 40491.6053
2029 | 2008 | 10 | 9 | 19 | 12411.5634
2029 | 2008 | 10 | 9 | 20 | 0
2029 | 2008 | 10 | 9 | 21 | 0
2029 | 2008 | 10 | 9 | 22 | 0
2029 | 2008 | 10 | 9 | 23 | 0
2029 | 2008 | 10 | 9 | 24 | 0
2029 | 2008 | 10 | 10 | 1 | 0
2029 | 2008 | 10 | 10 | 2 | 0
2029 | 2008 | 10 | 10 | 3 | 0
2029 | 2008 | 10 | 10 | 4 | 0
2029 | 2008 | 10 | 10 | 5 | 0
2029 | 2008 | 10 | 10 | 6 | 0
2029 | 2008 | 10 | 10 | 7 | 0
2029 | 2008 | 10 | 10 | 8 | 24.1782
2029 | 2008 | 10 | 10 | 9 | 14026.0555
2029 | 2008 | 10 | 10 | 10 | 38077.4568
2029 | 2008 | 10 | 10 | 11 | 50109.8943
2029 | 2008 | 10 | 10 | 12 | 51702.073
2029 | 2008 | 10 | 10 | 13 | 48592.9877
2029 | 2008 | 10 | 10 | 14 | 49824.6409
2029 | 2008 | 10 | 10 | 15 | 48535.6917
2029 | 2008 | 10 | 10 | 16 | 48730.1738
2029 | 2008 | 10 | 10 | 17 | 48937.967
2029 | 2008 | 10 | 10 | 18 | 36553.0082
2029 | 2008 | 10 | 10 | 19 | 11297.9737
2029 | 2008 | 10 | 10 | 20 | 0
2029 | 2008 | 10 | 10 | 21 | 0
2029 | 2008 | 10 | 10 | 22 | 0
2029 | 2008 | 10 | 10 | 23 | 0
2029 | 2008 | 10 | 10 | 24 | 0
2029 | 2008 | 10 | 11 | 1 | 0
2029 | 2008 | 10 | 11 | 2 | 0
2029 | 2008 | 10 | 11 | 3 | 0
2029 | 2008 | 10 | 11 | 4 | 0
2029 | 2008 | 10 | 11 | 5 | 0
2029 | 2008 | 10 | 11 | 6 | 0
2029 | 2008 | 10 | 11 | 7 | 0
2029 | 2008 | 10 | 11 | 8 | 12.945
2029 | 2008 | 10 | 11 | 9 | 6732.9311
2029 | 2008 | 10 | 11 | 10 | 18824.5711
2029 | 2008 | 10 | 11 | 11 | 25634.5113
2029 | 2008 | 10 | 11 | 12 | 30951.5132
2029 | 2008 | 10 | 11 | 13 | 33375.6568
2029 | 2008 | 10 | 11 | 14 | 38097.1407
2029 | 2008 | 10 | 11 | 15 | 41719.8007
2029 | 2008 | 10 | 11 | 16 | 44356.8835
2029 | 2008 | 10 | 11 | 17 | 42633.7774
2029 | 2008 | 10 | 11 | 18 | 33638.2683
2029 | 2008 | 10 | 11 | 19 | 9968.0589
2029 | 2008 | 10 | 11 | 20 | 0
2029 | 2008 | 10 | 11 | 21 | 0
2029 | 2008 | 10 | 11 | 22 | 0
2029 | 2008 | 10 | 11 | 23 | 0
2029 | 2008 | 10 | 11 | 24 | 0
2029 | 2008 | 10 | 12 | 1 | 0
2029 | 2008 | 10 | 12 | 2 | 0
2029 | 2008 | 10 | 12 | 3 | 0
2029 | 2008 | 10 | 12 | 4 | 0
2029 | 2008 | 10 | 12 | 5 | 0
2029 | 2008 | 10 | 12 | 6 | 0
2029 | 2008 | 10 | 12 | 7 | 0
2029 | 2008 | 10 | 12 | 8 | 16.8739
2029 | 2008 | 10 | 12 | 9 | 6412.0753
2029 | 2008 | 10 | 12 | 10 | 22587.9915
2029 | 2008 | 10 | 12 | 11 | 29495.2026
2029 | 2008 | 10 | 12 | 12 | 37110.3689
2029 | 2008 | 10 | 12 | 13 | 36968.0979
2029 | 2008 | 10 | 12 | 14 | 37204.8476
2029 | 2008 | 10 | 12 | 15 | 33702.9382
2029 | 2008 | 10 | 12 | 16 | 33322.0286
2029 | 2008 | 10 | 12 | 17 | 31872.3672
2029 | 2008 | 10 | 12 | 18 | 26248.4461
2029 | 2008 | 10 | 12 | 19 | 6837.5617
2029 | 2008 | 10 | 12 | 20 | 0
2029 | 2008 | 10 | 12 | 21 | 0
2029 | 2008 | 10 | 12 | 22 | 0
2029 | 2008 | 10 | 12 | 23 | 0
2029 | 2008 | 10 | 12 | 24 | 0
2029 | 2008 | 10 | 13 | 1 | 0
2029 | 2008 | 10 | 13 | 2 | 0
2029 | 2008 | 10 | 13 | 3 | 0
2029 | 2008 | 10 | 13 | 4 | 0
2029 | 2008 | 10 | 13 | 5 | 0
2029 | 2008 | 10 | 13 | 6 | 0
2029 | 2008 | 10 | 13 | 7 | 0
2029 | 2008 | 10 | 13 | 8 | 17.7923
2029 | 2008 | 10 | 13 | 9 | 5326.9468
2029 | 2008 | 10 | 13 | 10 | 17364.1567
2029 | 2008 | 10 | 13 | 11 | 22746.9069
2029 | 2008 | 10 | 13 | 12 | 27119.0395
2029 | 2008 | 10 | 13 | 13 | 30640.6192
2029 | 2008 | 10 | 13 | 14 | 33064.2971
2029 | 2008 | 10 | 13 | 15 | 31455.4274
2029 | 2008 | 10 | 13 | 16 | 31403.2022
2029 | 2008 | 10 | 13 | 17 | 32224.0346
2029 | 2008 | 10 | 13 | 18 | 24969.6069
2029 | 2008 | 10 | 13 | 19 | 5879.5318
2029 | 2008 | 10 | 13 | 20 | 0
2029 | 2008 | 10 | 13 | 21 | 0
2029 | 2008 | 10 | 13 | 22 | 0
2029 | 2008 | 10 | 13 | 23 | 0
2029 | 2008 | 10 | 13 | 24 | 0
2029 | 2008 | 10 | 14 | 1 | 0
2029 | 2008 | 10 | 14 | 2 | 0
2029 | 2008 | 10 | 14 | 3 | 0
2029 | 2008 | 10 | 14 | 4 | 0
2029 | 2008 | 10 | 14 | 5 | 0
2029 | 2008 | 10 | 14 | 6 | 0
2029 | 2008 | 10 | 14 | 7 | 0
2029 | 2008 | 10 | 14 | 8 | 1.4228
2029 | 2008 | 10 | 14 | 9 | 1584.779
2029 | 2008 | 10 | 14 | 10 | 7186.9784
2029 | 2008 | 10 | 14 | 11 | 13735.8173
2029 | 2008 | 10 | 14 | 12 | 21808.9201
2029 | 2008 | 10 | 14 | 13 | 27090.9816
2029 | 2008 | 10 | 14 | 14 | 28527.247
2029 | 2008 | 10 | 14 | 15 | 30770.9349
2029 | 2008 | 10 | 14 | 16 | 30719.4218
2029 | 2008 | 10 | 14 | 17 | 29930.5943
2029 | 2008 | 10 | 14 | 18 | 25135.3115
2029 | 2008 | 10 | 14 | 19 | 5739.5597
2029 | 2008 | 10 | 14 | 20 | 0
2029 | 2008 | 10 | 14 | 21 | 0
2029 | 2008 | 10 | 14 | 22 | 0
2029 | 2008 | 10 | 14 | 23 | 0
2029 | 2008 | 10 | 14 | 24 | 0
2029 | 2008 | 10 | 15 | 1 | 0
2029 | 2008 | 10 | 15 | 2 | 0
2029 | 2008 | 10 | 15 | 3 | 0
2029 | 2008 | 10 | 15 | 4 | 0
2029 | 2008 | 10 | 15 | 5 | 0
2029 | 2008 | 10 | 15 | 6 | 0
2029 | 2008 | 10 | 15 | 7 | 0
2029 | 2008 | 10 | 15 | 8 | 6.4361
2029 | 2008 | 10 | 15 | 9 | 2901.9709
2029 | 2008 | 10 | 15 | 10 | 13263.0943
2029 | 2008 | 10 | 15 | 11 | 19514.9262
2029 | 2008 | 10 | 15 | 12 | 25199.7027
2029 | 2008 | 10 | 15 | 13 | 29083.8599
2029 | 2008 | 10 | 15 | 14 | 30789.0003
2029 | 2008 | 10 | 15 | 15 | 30316.3043
2029 | 2008 | 10 | 15 | 16 | 29239.683
2029 | 2008 | 10 | 15 | 17 | 28102.926
2029 | 2008 | 10 | 15 | 18 | 25756.0305
2029 | 2008 | 10 | 15 | 19 | 6884.6655
2029 | 2008 | 10 | 15 | 20 | 0
2029 | 2008 | 10 | 15 | 21 | 0
2029 | 2008 | 10 | 15 | 22 | 0
2029 | 2008 | 10 | 15 | 23 | 0
2029 | 2008 | 10 | 15 | 24 | 0
2029 | 2008 | 10 | 16 | 1 | 0
2029 | 2008 | 10 | 16 | 2 | 0
2029 | 2008 | 10 | 16 | 3 | 0
2029 | 2008 | 10 | 16 | 4 | 0
2029 | 2008 | 10 | 16 | 5 | 0
2029 | 2008 | 10 | 16 | 6 | 0
2029 | 2008 | 10 | 16 | 7 | 0
2029 | 2008 | 10 | 16 | 8 | 0.48227
2029 | 2008 | 10 | 16 | 9 | 1508.6955
2029 | 2008 | 10 | 16 | 10 | 10958.7947
2029 | 2008 | 10 | 16 | 11 | 17991.2803
2029 | 2008 | 10 | 16 | 12 | 27487.6935
2029 | 2008 | 10 | 16 | 13 | 31013.6986
2029 | 2008 | 10 | 16 | 14 | 32500.1942
2029 | 2008 | 10 | 16 | 15 | 33035.1774
2029 | 2008 | 10 | 16 | 16 | 33629.1906
2029 | 2008 | 10 | 16 | 17 | 28590.0235
2029 | 2008 | 10 | 16 | 18 | 26799.6381
2029 | 2008 | 10 | 16 | 19 | 6381.7654
2029 | 2008 | 10 | 16 | 20 | 0
2029 | 2008 | 10 | 16 | 21 | 0
2029 | 2008 | 10 | 16 | 22 | 0
2029 | 2008 | 10 | 16 | 23 | 0
2029 | 2008 | 10 | 16 | 24 | 0
2029 | 2008 | 10 | 17 | 1 | 0
2029 | 2008 | 10 | 17 | 2 | 0
2029 | 2008 | 10 | 17 | 3 | 0
2029 | 2008 | 10 | 17 | 4 | 0
2029 | 2008 | 10 | 17 | 5 | 0
2029 | 2008 | 10 | 17 | 6 | 0
2029 | 2008 | 10 | 17 | 7 | 0
2029 | 2008 | 10 | 17 | 8 | 2.332
2029 | 2008 | 10 | 17 | 9 | 8429.9015
2029 | 2008 | 10 | 17 | 10 | 28827.9913
2029 | 2008 | 10 | 17 | 11 | 33785.1148
2029 | 2008 | 10 | 17 | 12 | 35686.4519
2029 | 2008 | 10 | 17 | 13 | 37591.0934
2029 | 2008 | 10 | 17 | 14 | 37858.8665
2029 | 2008 | 10 | 17 | 15 | 36315.199
2029 | 2008 | 10 | 17 | 16 | 35807.9401
2029 | 2008 | 10 | 17 | 17 | 34766.5825
2029 | 2008 | 10 | 17 | 18 | 27796.0868
2029 | 2008 | 10 | 17 | 19 | 6537.0057
2029 | 2008 | 10 | 17 | 20 | 0
2029 | 2008 | 10 | 17 | 21 | 0
2029 | 2008 | 10 | 17 | 22 | 0
2029 | 2008 | 10 | 17 | 23 | 0
2029 | 2008 | 10 | 17 | 24 | 0
2029 | 2008 | 10 | 18 | 1 | 0
2029 | 2008 | 10 | 18 | 2 | 0
2029 | 2008 | 10 | 18 | 3 | 0
2029 | 2008 | 10 | 18 | 4 | 0
2029 | 2008 | 10 | 18 | 5 | 0
2029 | 2008 | 10 | 18 | 6 | 0
2029 | 2008 | 10 | 18 | 7 | 0
2029 | 2008 | 10 | 18 | 8 | 20.7526
2029 | 2008 | 10 | 18 | 9 | 15733.0884
2029 | 2008 | 10 | 18 | 10 | 45028.9116
2029 | 2008 | 10 | 18 | 11 | 52709.6851
2029 | 2008 | 10 | 18 | 12 | 52993.0698
2029 | 2008 | 10 | 18 | 13 | 52522.2861
2029 | 2008 | 10 | 18 | 14 | 50738.9919
2029 | 2008 | 10 | 18 | 15 | 51312.7198
2029 | 2008 | 10 | 18 | 16 | 49961.3484
2029 | 2008 | 10 | 18 | 17 | 46727.4879
2029 | 2008 | 10 | 18 | 18 | 35633.0888
2029 | 2008 | 10 | 18 | 19 | 7451.5142
2029 | 2008 | 10 | 18 | 20 | 0
2029 | 2008 | 10 | 18 | 21 | 0
2029 | 2008 | 10 | 18 | 22 | 0
2029 | 2008 | 10 | 18 | 23 | 0
2029 | 2008 | 10 | 18 | 24 | 0
2029 | 2008 | 10 | 19 | 1 | 0
2029 | 2008 | 10 | 19 | 2 | 0
2029 | 2008 | 10 | 19 | 3 | 0
2029 | 2008 | 10 | 19 | 4 | 0
2029 | 2008 | 10 | 19 | 5 | 0
2029 | 2008 | 10 | 19 | 6 | 0
2029 | 2008 | 10 | 19 | 7 | 0
2029 | 2008 | 10 | 19 | 8 | 19.9747
2029 | 2008 | 10 | 19 | 9 | 15832.3139
2029 | 2008 | 10 | 19 | 10 | 46660.2379
2029 | 2008 | 10 | 19 | 11 | 52493.2603
2029 | 2008 | 10 | 19 | 12 | 53761.2022
2029 | 2008 | 10 | 19 | 13 | 52186.4333
2029 | 2008 | 10 | 19 | 14 | 51092.5193
2029 | 2008 | 10 | 19 | 15 | 50545.8764
2029 | 2008 | 10 | 19 | 16 | 46766.2187
2029 | 2008 | 10 | 19 | 17 | 45610.1794
2029 | 2008 | 10 | 19 | 18 | 31916.0123
2029 | 2008 | 10 | 19 | 19 | 6539.6218
2029 | 2008 | 10 | 19 | 20 | 0
2029 | 2008 | 10 | 19 | 21 | 0
2029 | 2008 | 10 | 19 | 22 | 0
2029 | 2008 | 10 | 19 | 23 | 0
2029 | 2008 | 10 | 19 | 24 | 0
2029 | 2008 | 10 | 20 | 1 | 0
2029 | 2008 | 10 | 20 | 2 | 0
2029 | 2008 | 10 | 20 | 3 | 0
2029 | 2008 | 10 | 20 | 4 | 0
2029 | 2008 | 10 | 20 | 5 | 0
2029 | 2008 | 10 | 20 | 6 | 0
2029 | 2008 | 10 | 20 | 7 | 0
2029 | 2008 | 10 | 20 | 8 | 15.5983
2029 | 2008 | 10 | 20 | 9 | 14038.7872
2029 | 2008 | 10 | 20 | 10 | 42946.5903
2029 | 2008 | 10 | 20 | 11 | 49486.2178
2029 | 2008 | 10 | 20 | 12 | 49875.3131
2029 | 2008 | 10 | 20 | 13 | 49930.7667
2029 | 2008 | 10 | 20 | 14 | 48372.9971
2029 | 2008 | 10 | 20 | 15 | 48034.5243
2029 | 2008 | 10 | 20 | 16 | 46446.6465
2029 | 2008 | 10 | 20 | 17 | 42317.2352
2029 | 2008 | 10 | 20 | 18 | 31473.5601
2029 | 2008 | 10 | 20 | 19 | 6019.1835
2029 | 2008 | 10 | 20 | 20 | 0
2029 | 2008 | 10 | 20 | 21 | 0
2029 | 2008 | 10 | 20 | 22 | 0
2029 | 2008 | 10 | 20 | 23 | 0
2029 | 2008 | 10 | 20 | 24 | 0
2029 | 2008 | 10 | 21 | 1 | 0
2029 | 2008 | 10 | 21 | 2 | 0
2029 | 2008 | 10 | 21 | 3 | 0
2029 | 2008 | 10 | 21 | 4 | 0
2029 | 2008 | 10 | 21 | 5 | 0
2029 | 2008 | 10 | 21 | 6 | 0
2029 | 2008 | 10 | 21 | 7 | 0
2029 | 2008 | 10 | 21 | 8 | 9.6645
2029 | 2008 | 10 | 21 | 9 | 7827.8433
2029 | 2008 | 10 | 21 | 10 | 24939.7591
2029 | 2008 | 10 | 21 | 11 | 32667.4376
2029 | 2008 | 10 | 21 | 12 | 36839.2736
2029 | 2008 | 10 | 21 | 13 | 39832.3945
2029 | 2008 | 10 | 21 | 14 | 41239.7463
2029 | 2008 | 10 | 21 | 15 | 40846.4319
2029 | 2008 | 10 | 21 | 16 | 40939.9159
2029 | 2008 | 10 | 21 | 17 | 38072.3921
2029 | 2008 | 10 | 21 | 18 | 28354.6991
2029 | 2008 | 10 | 21 | 19 | 5055.2864
2029 | 2008 | 10 | 21 | 20 | 0
2029 | 2008 | 10 | 21 | 21 | 0
2029 | 2008 | 10 | 21 | 22 | 0
2029 | 2008 | 10 | 21 | 23 | 0
2029 | 2008 | 10 | 21 | 24 | 0
2029 | 2008 | 10 | 22 | 1 | 0
2029 | 2008 | 10 | 22 | 2 | 0
2029 | 2008 | 10 | 22 | 3 | 0
2029 | 2008 | 10 | 22 | 4 | 0
2029 | 2008 | 10 | 22 | 5 | 0
2029 | 2008 | 10 | 22 | 6 | 0
2029 | 2008 | 10 | 22 | 7 | 0
2029 | 2008 | 10 | 22 | 8 | 8.5606
2029 | 2008 | 10 | 22 | 9 | 5573.4618
2029 | 2008 | 10 | 22 | 10 | 18777.986
2029 | 2008 | 10 | 22 | 11 | 27787.714
2029 | 2008 | 10 | 22 | 12 | 32084.5085
2029 | 2008 | 10 | 22 | 13 | 36021.5589
2029 | 2008 | 10 | 22 | 14 | 37784.5279
2029 | 2008 | 10 | 22 | 15 | 36811.755
2029 | 2008 | 10 | 22 | 16 | 39165.9831
2029 | 2008 | 10 | 22 | 17 | 32936.7229
2029 | 2008 | 10 | 22 | 18 | 25427.4945
2029 | 2008 | 10 | 22 | 19 | 4477.9861
2029 | 2008 | 10 | 22 | 20 | 0
2029 | 2008 | 10 | 22 | 21 | 0
2029 | 2008 | 10 | 22 | 22 | 0
2029 | 2008 | 10 | 22 | 23 | 0
2029 | 2008 | 10 | 22 | 24 | 0
2029 | 2008 | 10 | 23 | 1 | 0
2029 | 2008 | 10 | 23 | 2 | 0
2029 | 2008 | 10 | 23 | 3 | 0
2029 | 2008 | 10 | 23 | 4 | 0
2029 | 2008 | 10 | 23 | 5 | 0
2029 | 2008 | 10 | 23 | 6 | 0
2029 | 2008 | 10 | 23 | 7 | 0
2029 | 2008 | 10 | 23 | 8 | 7.7832
2029 | 2008 | 10 | 23 | 9 | 14654.8864
2029 | 2008 | 10 | 23 | 10 | 43882.4533
2029 | 2008 | 10 | 23 | 11 | 51839.4612
2029 | 2008 | 10 | 23 | 12 | 52639.2235
2029 | 2008 | 10 | 23 | 13 | 51857.7791
2029 | 2008 | 10 | 23 | 14 | 51637.4147
2029 | 2008 | 10 | 23 | 15 | 50821.2786
2029 | 2008 | 10 | 23 | 16 | 50232.673
2029 | 2008 | 10 | 23 | 17 | 46749.7193
2029 | 2008 | 10 | 23 | 18 | 34094.3121
2029 | 2008 | 10 | 23 | 19 | 4662.5893
2029 | 2008 | 10 | 23 | 20 | 0
2029 | 2008 | 10 | 23 | 21 | 0
2029 | 2008 | 10 | 23 | 22 | 0
2029 | 2008 | 10 | 23 | 23 | 0
2029 | 2008 | 10 | 23 | 24 | 0
2029 | 2008 | 10 | 24 | 1 | 0
2029 | 2008 | 10 | 24 | 2 | 0
2029 | 2008 | 10 | 24 | 3 | 0
2029 | 2008 | 10 | 24 | 4 | 0
2029 | 2008 | 10 | 24 | 5 | 0
2029 | 2008 | 10 | 24 | 6 | 0
2029 | 2008 | 10 | 24 | 7 | 0
2029 | 2008 | 10 | 24 | 8 | 11.3728
2029 | 2008 | 10 | 24 | 9 | 15009.8186
2029 | 2008 | 10 | 24 | 10 | 47264.463
2029 | 2008 | 10 | 24 | 11 | 54335.5057
2029 | 2008 | 10 | 24 | 12 | 55004.6734
2029 | 2008 | 10 | 24 | 13 | 52367.7045
2029 | 2008 | 10 | 24 | 14 | 51721.3271
2029 | 2008 | 10 | 24 | 15 | 51253.1802
2029 | 2008 | 10 | 24 | 16 | 48233.6384
2029 | 2008 | 10 | 24 | 17 | 46394.6703
2029 | 2008 | 10 | 24 | 18 | 29624.7758
2029 | 2008 | 10 | 24 | 19 | 3792.7884
2029 | 2008 | 10 | 24 | 20 | 0
2029 | 2008 | 10 | 24 | 21 | 0
2029 | 2008 | 10 | 24 | 22 | 0
2029 | 2008 | 10 | 24 | 23 | 0
2029 | 2008 | 10 | 24 | 24 | 0
2029 | 2008 | 10 | 25 | 1 | 0
2029 | 2008 | 10 | 25 | 2 | 0
2029 | 2008 | 10 | 25 | 3 | 0
2029 | 2008 | 10 | 25 | 4 | 0
2029 | 2008 | 10 | 25 | 5 | 0
2029 | 2008 | 10 | 25 | 6 | 0
2029 | 2008 | 10 | 25 | 7 | 0
2029 | 2008 | 10 | 25 | 8 | 10.3332
2029 | 2008 | 10 | 25 | 9 | 13605.5758
2029 | 2008 | 10 | 25 | 10 | 43655.369
2029 | 2008 | 10 | 25 | 11 | 50549.876
2029 | 2008 | 10 | 25 | 12 | 51303.2613
2029 | 2008 | 10 | 25 | 13 | 49932.5311
2029 | 2008 | 10 | 25 | 14 | 48612.0072
2029 | 2008 | 10 | 25 | 15 | 48490.8857
2029 | 2008 | 10 | 25 | 16 | 47354.2886
2029 | 2008 | 10 | 25 | 17 | 43575.8505
2029 | 2008 | 10 | 25 | 18 | 28062.3196
2029 | 2008 | 10 | 25 | 19 | 3216.1809
2029 | 2008 | 10 | 25 | 20 | 0
2029 | 2008 | 10 | 25 | 21 | 0
2029 | 2008 | 10 | 25 | 22 | 0
2029 | 2008 | 10 | 25 | 23 | 0
2029 | 2008 | 10 | 25 | 24 | 0
2029 | 2008 | 10 | 26 | 1 | 0
2029 | 2008 | 10 | 26 | 2 | 0
2029 | 2008 | 10 | 26 | 3 | 0
2029 | 2008 | 10 | 26 | 4 | 0
2029 | 2008 | 10 | 26 | 5 | 0
2029 | 2008 | 10 | 26 | 6 | 0
2029 | 2008 | 10 | 26 | 7 | 0
2029 | 2008 | 10 | 26 | 8 | 8.289
2029 | 2008 | 10 | 26 | 9 | 11315.5244
2029 | 2008 | 10 | 26 | 10 | 36265.8609
2029 | 2008 | 10 | 26 | 11 | 41442.3273
2029 | 2008 | 10 | 26 | 12 | 41210.2376
2029 | 2008 | 10 | 26 | 13 | 42540.9148
2029 | 2008 | 10 | 26 | 14 | 44390.7172
2029 | 2008 | 10 | 26 | 15 | 42493.1744
2029 | 2008 | 10 | 26 | 16 | 39478.5348
2029 | 2008 | 10 | 26 | 17 | 39178.188
2029 | 2008 | 10 | 26 | 18 | 30114.6078
2029 | 2008 | 10 | 26 | 19 | 3016.9245
2029 | 2008 | 10 | 26 | 20 | 0
2029 | 2008 | 10 | 26 | 21 | 0
2029 | 2008 | 10 | 26 | 22 | 0
2029 | 2008 | 10 | 26 | 23 | 0
2029 | 2008 | 10 | 26 | 24 | 0
2029 | 2008 | 10 | 27 | 1 | 0
2029 | 2008 | 10 | 27 | 2 | 0
2029 | 2008 | 10 | 27 | 3 | 0
2029 | 2008 | 10 | 27 | 4 | 0
2029 | 2008 | 10 | 27 | 5 | 0
2029 | 2008 | 10 | 27 | 6 | 0
2029 | 2008 | 10 | 27 | 7 | 0
2029 | 2008 | 10 | 27 | 8 | 2.3435
2029 | 2008 | 10 | 27 | 9 | 13234.4485
2029 | 2008 | 10 | 27 | 10 | 44658.3912
2029 | 2008 | 10 | 27 | 11 | 53367.1927
2029 | 2008 | 10 | 27 | 12 | 55228.7508
2029 | 2008 | 10 | 27 | 13 | 52974.7499
2029 | 2008 | 10 | 27 | 14 | 52763.1211
2029 | 2008 | 10 | 27 | 15 | 52308.3565
2029 | 2008 | 10 | 27 | 16 | 50116.8488
2029 | 2008 | 10 | 27 | 17 | 46434.6729
2029 | 2008 | 10 | 27 | 18 | 29282.6043
2029 | 2008 | 10 | 27 | 19 | 2905.4713
2029 | 2008 | 10 | 27 | 20 | 0
2029 | 2008 | 10 | 27 | 21 | 0
2029 | 2008 | 10 | 27 | 22 | 0
2029 | 2008 | 10 | 27 | 23 | 0
2029 | 2008 | 10 | 27 | 24 | 0
2029 | 2008 | 10 | 28 | 1 | 0
2029 | 2008 | 10 | 28 | 2 | 0
2029 | 2008 | 10 | 28 | 3 | 0
2029 | 2008 | 10 | 28 | 4 | 0
2029 | 2008 | 10 | 28 | 5 | 0
2029 | 2008 | 10 | 28 | 6 | 0
2029 | 2008 | 10 | 28 | 7 | 0
2029 | 2008 | 10 | 28 | 8 | 4.1892
2029 | 2008 | 10 | 28 | 9 | 14573.8166
2029 | 2008 | 10 | 28 | 10 | 45247.7761
2029 | 2008 | 10 | 28 | 11 | 51757.7331
2029 | 2008 | 10 | 28 | 12 | 52601.8118
2029 | 2008 | 10 | 28 | 13 | 50857.9849
2029 | 2008 | 10 | 28 | 14 | 49470.4902
2029 | 2008 | 10 | 28 | 15 | 49137.7869
2029 | 2008 | 10 | 28 | 16 | 47506.4592
2029 | 2008 | 10 | 28 | 17 | 42853.0669
2029 | 2008 | 10 | 28 | 18 | 30582.224
2029 | 2008 | 10 | 28 | 19 | 2580.4289
2029 | 2008 | 10 | 28 | 20 | 0
2029 | 2008 | 10 | 28 | 21 | 0
2029 | 2008 | 10 | 28 | 22 | 0
2029 | 2008 | 10 | 28 | 23 | 0
2029 | 2008 | 10 | 28 | 24 | 0
2029 | 2008 | 10 | 29 | 1 | 0
2029 | 2008 | 10 | 29 | 2 | 0
2029 | 2008 | 10 | 29 | 3 | 0
2029 | 2008 | 10 | 29 | 4 | 0
2029 | 2008 | 10 | 29 | 5 | 0
2029 | 2008 | 10 | 29 | 6 | 0
2029 | 2008 | 10 | 29 | 7 | 0
2029 | 2008 | 10 | 29 | 8 | 5.4891
2029 | 2008 | 10 | 29 | 9 | 12605.4915
2029 | 2008 | 10 | 29 | 10 | 42238.1559
2029 | 2008 | 10 | 29 | 11 | 49956.9234
2029 | 2008 | 10 | 29 | 12 | 50413.6598
2029 | 2008 | 10 | 29 | 13 | 48712.5097
2029 | 2008 | 10 | 29 | 14 | 48308.0888
2029 | 2008 | 10 | 29 | 15 | 47023.9743
2029 | 2008 | 10 | 29 | 16 | 45860.2718
2029 | 2008 | 10 | 29 | 17 | 44099.7731
2029 | 2008 | 10 | 29 | 18 | 27963.672
2029 | 2008 | 10 | 29 | 19 | 2313.5803
2029 | 2008 | 10 | 29 | 20 | 0
2029 | 2008 | 10 | 29 | 21 | 0
2029 | 2008 | 10 | 29 | 22 | 0
2029 | 2008 | 10 | 29 | 23 | 0
2029 | 2008 | 10 | 29 | 24 | 0
2029 | 2008 | 10 | 30 | 1 | 0
2029 | 2008 | 10 | 30 | 2 | 0
2029 | 2008 | 10 | 30 | 3 | 0
2029 | 2008 | 10 | 30 | 4 | 0
2029 | 2008 | 10 | 30 | 5 | 0
2029 | 2008 | 10 | 30 | 6 | 0
2029 | 2008 | 10 | 30 | 7 | 0
2029 | 2008 | 10 | 30 | 8 | 2.4384
2029 | 2008 | 10 | 30 | 9 | 7856.8527
2029 | 2008 | 10 | 30 | 10 | 25181.0522
2029 | 2008 | 10 | 30 | 11 | 31248.5591
2029 | 2008 | 10 | 30 | 12 | 34678.8429
2029 | 2008 | 10 | 30 | 13 | 38818.3051
2029 | 2008 | 10 | 30 | 14 | 41636.9296
2029 | 2008 | 10 | 30 | 15 | 41414.0941
2029 | 2008 | 10 | 30 | 16 | 43480.6095
2029 | 2008 | 10 | 30 | 17 | 38931.6929
2029 | 2008 | 10 | 30 | 18 | 24752.245
2029 | 2008 | 10 | 30 | 19 | 2006.8197
2029 | 2008 | 10 | 30 | 20 | 0
2029 | 2008 | 10 | 30 | 21 | 0
2029 | 2008 | 10 | 30 | 22 | 0
2029 | 2008 | 10 | 30 | 23 | 0
2029 | 2008 | 10 | 30 | 24 | 0
2029 | 2008 | 10 | 31 | 1 | 0
2029 | 2008 | 10 | 31 | 2 | 0
2029 | 2008 | 10 | 31 | 3 | 0
2029 | 2008 | 10 | 31 | 4 | 0
2029 | 2008 | 10 | 31 | 5 | 0
2029 | 2008 | 10 | 31 | 6 | 0
2029 | 2008 | 10 | 31 | 7 | 0
2029 | 2008 | 10 | 31 | 8 | 2.1371
2029 | 2008 | 10 | 31 | 9 | 6241.0239
2029 | 2008 | 10 | 31 | 10 | 21812.7837
2029 | 2008 | 10 | 31 | 11 | 27950.0855
2029 | 2008 | 10 | 31 | 12 | 34702.8136
2029 | 2008 | 10 | 31 | 13 | 38119.4037
2029 | 2008 | 10 | 31 | 14 | 39663.0515
2029 | 2008 | 10 | 31 | 15 | 41345.3846
2029 | 2008 | 10 | 31 | 16 | 40024.983
2029 | 2008 | 10 | 31 | 17 | 39585.4277
2029 | 2008 | 10 | 31 | 18 | 23551.1733
2029 | 2008 | 10 | 31 | 19 | 3001.9802
2029 | 2008 | 10 | 31 | 20 | 0
2029 | 2008 | 10 | 31 | 21 | 0
2029 | 2008 | 10 | 31 | 22 | 0
2029 | 2008 | 10 | 31 | 23 | 0
2029 | 2008 | 10 | 31 | 24 | 0
2030 | 2008 | 10 | 1 | 1 | 0
2030 | 2008 | 10 | 1 | 2 | 0
2030 | 2008 | 10 | 1 | 3 | 0
2030 | 2008 | 10 | 1 | 4 | 0
2030 | 2008 | 10 | 1 | 5 | 0
2030 | 2008 | 10 | 1 | 6 | 0
2030 | 2008 | 10 | 1 | 7 | 0
2030 | 2008 | 10 | 1 | 8 | 48.6855
2030 | 2008 | 10 | 1 | 9 | 20132.441
2030 | 2008 | 10 | 1 | 10 | 50992.8964
2030 | 2008 | 10 | 1 | 11 | 56350.6373
2030 | 2008 | 10 | 1 | 12 | 56939.1687
2030 | 2008 | 10 | 1 | 13 | 55804.8781
2030 | 2008 | 10 | 1 | 14 | 55189.7023
2030 | 2008 | 10 | 1 | 15 | 54075.7603
2030 | 2008 | 10 | 1 | 16 | 54908.1598
2030 | 2008 | 10 | 1 | 17 | 53761.2875
2030 | 2008 | 10 | 1 | 18 | 42168.3701
2030 | 2008 | 10 | 1 | 19 | 14429.3839
2030 | 2008 | 10 | 1 | 20 | 0
2030 | 2008 | 10 | 1 | 21 | 0
2030 | 2008 | 10 | 1 | 22 | 0
2030 | 2008 | 10 | 1 | 23 | 0
2030 | 2008 | 10 | 1 | 24 | 0
2030 | 2008 | 10 | 2 | 1 | 0
2030 | 2008 | 10 | 2 | 2 | 0
2030 | 2008 | 10 | 2 | 3 | 0
2030 | 2008 | 10 | 2 | 4 | 0
2030 | 2008 | 10 | 2 | 5 | 0
2030 | 2008 | 10 | 2 | 6 | 0
2030 | 2008 | 10 | 2 | 7 | 0
2030 | 2008 | 10 | 2 | 8 | 60.204
2030 | 2008 | 10 | 2 | 9 | 20475.1419
2030 | 2008 | 10 | 2 | 10 | 49172.9989
2030 | 2008 | 10 | 2 | 11 | 56679.016
2030 | 2008 | 10 | 2 | 12 | 56862.5851
2030 | 2008 | 10 | 2 | 13 | 55025.9464
2030 | 2008 | 10 | 2 | 14 | 54349.6226
2030 | 2008 | 10 | 2 | 15 | 53119.1894
2030 | 2008 | 10 | 2 | 16 | 53935.5736
2030 | 2008 | 10 | 2 | 17 | 53075.356
2030 | 2008 | 10 | 2 | 18 | 41833.349
2030 | 2008 | 10 | 2 | 19 | 14178.8702
2030 | 2008 | 10 | 2 | 20 | 0
2030 | 2008 | 10 | 2 | 21 | 0
2030 | 2008 | 10 | 2 | 22 | 0
2030 | 2008 | 10 | 2 | 23 | 0
2030 | 2008 | 10 | 2 | 24 | 0
2030 | 2008 | 10 | 3 | 1 | 0
2030 | 2008 | 10 | 3 | 2 | 0
2030 | 2008 | 10 | 3 | 3 | 0
2030 | 2008 | 10 | 3 | 4 | 0
2030 | 2008 | 10 | 3 | 5 | 0
2030 | 2008 | 10 | 3 | 6 | 0
2030 | 2008 | 10 | 3 | 7 | 0
2030 | 2008 | 10 | 3 | 8 | 57.8862
2030 | 2008 | 10 | 3 | 9 | 16553.0011
2030 | 2008 | 10 | 3 | 10 | 46172.291
2030 | 2008 | 10 | 3 | 11 | 53357.4819
2030 | 2008 | 10 | 3 | 12 | 52645.2136
2030 | 2008 | 10 | 3 | 13 | 51531.0682
2030 | 2008 | 10 | 3 | 14 | 50321.8394
2030 | 2008 | 10 | 3 | 15 | 50626.2434
2030 | 2008 | 10 | 3 | 16 | 49362.7808
2030 | 2008 | 10 | 3 | 17 | 48004.238
2030 | 2008 | 10 | 3 | 18 | 39039.7617
2030 | 2008 | 10 | 3 | 19 | 13286.9436
2030 | 2008 | 10 | 3 | 20 | 0
2030 | 2008 | 10 | 3 | 21 | 0
2030 | 2008 | 10 | 3 | 22 | 0
2030 | 2008 | 10 | 3 | 23 | 0
2030 | 2008 | 10 | 3 | 24 | 0
2030 | 2008 | 10 | 4 | 1 | 0
2030 | 2008 | 10 | 4 | 2 | 0
2030 | 2008 | 10 | 4 | 3 | 0
2030 | 2008 | 10 | 4 | 4 | 0
2030 | 2008 | 10 | 4 | 5 | 0
2030 | 2008 | 10 | 4 | 6 | 0
2030 | 2008 | 10 | 4 | 7 | 0
2030 | 2008 | 10 | 4 | 8 | 37.5899
2030 | 2008 | 10 | 4 | 9 | 12485.9313
2030 | 2008 | 10 | 4 | 10 | 38964.6288
2030 | 2008 | 10 | 4 | 11 | 48774.6315
2030 | 2008 | 10 | 4 | 12 | 53103.5948
2030 | 2008 | 10 | 4 | 13 | 53074.3563
2030 | 2008 | 10 | 4 | 14 | 51660.6968
2030 | 2008 | 10 | 4 | 15 | 51041.5946
2030 | 2008 | 10 | 4 | 16 | 50757.5871
2030 | 2008 | 10 | 4 | 17 | 49538.9619
2030 | 2008 | 10 | 4 | 18 | 37850.511
2030 | 2008 | 10 | 4 | 19 | 13054.2656
2030 | 2008 | 10 | 4 | 20 | 0
2030 | 2008 | 10 | 4 | 21 | 0
2030 | 2008 | 10 | 4 | 22 | 0
2030 | 2008 | 10 | 4 | 23 | 0
2030 | 2008 | 10 | 4 | 24 | 0
2030 | 2008 | 10 | 5 | 1 | 0
2030 | 2008 | 10 | 5 | 2 | 0
2030 | 2008 | 10 | 5 | 3 | 0
2030 | 2008 | 10 | 5 | 4 | 0
2030 | 2008 | 10 | 5 | 5 | 0
2030 | 2008 | 10 | 5 | 6 | 0
2030 | 2008 | 10 | 5 | 7 | 0
2030 | 2008 | 10 | 5 | 8 | 39.1087
2030 | 2008 | 10 | 5 | 9 | 12481.7587
2030 | 2008 | 10 | 5 | 10 | 33668.0461
2030 | 2008 | 10 | 5 | 11 | 36568.6711
2030 | 2008 | 10 | 5 | 12 | 41866.8812
2030 | 2008 | 10 | 5 | 13 | 42633.5084
2030 | 2008 | 10 | 5 | 14 | 39740.8721
2030 | 2008 | 10 | 5 | 15 | 37979.784
2030 | 2008 | 10 | 5 | 16 | 38197.0241
2030 | 2008 | 10 | 5 | 17 | 36606.6823
2030 | 2008 | 10 | 5 | 18 | 30514.9654
2030 | 2008 | 10 | 5 | 19 | 10661.1093
2030 | 2008 | 10 | 5 | 20 | 0
2030 | 2008 | 10 | 5 | 21 | 0
2030 | 2008 | 10 | 5 | 22 | 0
2030 | 2008 | 10 | 5 | 23 | 0
2030 | 2008 | 10 | 5 | 24 | 0
2030 | 2008 | 10 | 6 | 1 | 0
2030 | 2008 | 10 | 6 | 2 | 0
2030 | 2008 | 10 | 6 | 3 | 0
2030 | 2008 | 10 | 6 | 4 | 0
2030 | 2008 | 10 | 6 | 5 | 0
2030 | 2008 | 10 | 6 | 6 | 0
2030 | 2008 | 10 | 6 | 7 | 0
2030 | 2008 | 10 | 6 | 8 | 18.5113
2030 | 2008 | 10 | 6 | 9 | 9610.0711
2030 | 2008 | 10 | 6 | 10 | 30467.3273
2030 | 2008 | 10 | 6 | 11 | 41514.2861
2030 | 2008 | 10 | 6 | 12 | 46176.3594
2030 | 2008 | 10 | 6 | 13 | 47164.4967
2030 | 2008 | 10 | 6 | 14 | 47325.3644
2030 | 2008 | 10 | 6 | 15 | 47348.3454
2030 | 2008 | 10 | 6 | 16 | 48974.536
2030 | 2008 | 10 | 6 | 17 | 48660.7729
2030 | 2008 | 10 | 6 | 18 | 38002.4139
2030 | 2008 | 10 | 6 | 19 | 12375.6156
2030 | 2008 | 10 | 6 | 20 | 0
2030 | 2008 | 10 | 6 | 21 | 0
2030 | 2008 | 10 | 6 | 22 | 0
2030 | 2008 | 10 | 6 | 23 | 0
2030 | 2008 | 10 | 6 | 24 | 0
2030 | 2008 | 10 | 7 | 1 | 0
2030 | 2008 | 10 | 7 | 2 | 0
2030 | 2008 | 10 | 7 | 3 | 0
2030 | 2008 | 10 | 7 | 4 | 0
2030 | 2008 | 10 | 7 | 5 | 0
2030 | 2008 | 10 | 7 | 6 | 0
2030 | 2008 | 10 | 7 | 7 | 0
2030 | 2008 | 10 | 7 | 8 | 23.6528
2030 | 2008 | 10 | 7 | 9 | 13129.6925
2030 | 2008 | 10 | 7 | 10 | 40973.4268
2030 | 2008 | 10 | 7 | 11 | 47152.1752
2030 | 2008 | 10 | 7 | 12 | 51380.5062
2030 | 2008 | 10 | 7 | 13 | 52183.8527
2030 | 2008 | 10 | 7 | 14 | 52351.4026
2030 | 2008 | 10 | 7 | 15 | 51715.2256
2030 | 2008 | 10 | 7 | 16 | 53190.8691
2030 | 2008 | 10 | 7 | 17 | 49171.6203
2030 | 2008 | 10 | 7 | 18 | 37398.6173
2030 | 2008 | 10 | 7 | 19 | 13256.747
2030 | 2008 | 10 | 7 | 20 | 0
2030 | 2008 | 10 | 7 | 21 | 0
2030 | 2008 | 10 | 7 | 22 | 0
2030 | 2008 | 10 | 7 | 23 | 0
2030 | 2008 | 10 | 7 | 24 | 0
2030 | 2008 | 10 | 8 | 1 | 0
2030 | 2008 | 10 | 8 | 2 | 0
2030 | 2008 | 10 | 8 | 3 | 0
2030 | 2008 | 10 | 8 | 4 | 0
2030 | 2008 | 10 | 8 | 5 | 0
2030 | 2008 | 10 | 8 | 6 | 0
2030 | 2008 | 10 | 8 | 7 | 0
2030 | 2008 | 10 | 8 | 8 | 32.2666
2030 | 2008 | 10 | 8 | 9 | 19337.9664
2030 | 2008 | 10 | 8 | 10 | 52459.7688
2030 | 2008 | 10 | 8 | 11 | 57559.8334
2030 | 2008 | 10 | 8 | 12 | 57038.3949
2030 | 2008 | 10 | 8 | 13 | 56294.5438
2030 | 2008 | 10 | 8 | 14 | 55277.9122
2030 | 2008 | 10 | 8 | 15 | 55516.2895
2030 | 2008 | 10 | 8 | 16 | 54432.2798
2030 | 2008 | 10 | 8 | 17 | 51211.9929
2030 | 2008 | 10 | 8 | 18 | 40392.8361
2030 | 2008 | 10 | 8 | 19 | 12676.9197
2030 | 2008 | 10 | 8 | 20 | 0
2030 | 2008 | 10 | 8 | 21 | 0
2030 | 2008 | 10 | 8 | 22 | 0
2030 | 2008 | 10 | 8 | 23 | 0
2030 | 2008 | 10 | 8 | 24 | 0
2030 | 2008 | 10 | 9 | 1 | 0
2030 | 2008 | 10 | 9 | 2 | 0
2030 | 2008 | 10 | 9 | 3 | 0
2030 | 2008 | 10 | 9 | 4 | 0
2030 | 2008 | 10 | 9 | 5 | 0
2030 | 2008 | 10 | 9 | 6 | 0
2030 | 2008 | 10 | 9 | 7 | 0
2030 | 2008 | 10 | 9 | 8 | 33.4365
2030 | 2008 | 10 | 9 | 9 | 19681.8132
2030 | 2008 | 10 | 9 | 10 | 51121.3322
2030 | 2008 | 10 | 9 | 11 | 57342.503
2030 | 2008 | 10 | 9 | 12 | 57290.4543
2030 | 2008 | 10 | 9 | 13 | 55298.7381
2030 | 2008 | 10 | 9 | 14 | 55189.8094
2030 | 2008 | 10 | 9 | 15 | 54456.6053
2030 | 2008 | 10 | 9 | 16 | 54313.0143
2030 | 2008 | 10 | 9 | 17 | 49870.0828
2030 | 2008 | 10 | 9 | 18 | 40491.6053
2030 | 2008 | 10 | 9 | 19 | 12411.5634
2030 | 2008 | 10 | 9 | 20 | 0
2030 | 2008 | 10 | 9 | 21 | 0
2030 | 2008 | 10 | 9 | 22 | 0
2030 | 2008 | 10 | 9 | 23 | 0
2030 | 2008 | 10 | 9 | 24 | 0
2030 | 2008 | 10 | 10 | 1 | 0
2030 | 2008 | 10 | 10 | 2 | 0
2030 | 2008 | 10 | 10 | 3 | 0
2030 | 2008 | 10 | 10 | 4 | 0
2030 | 2008 | 10 | 10 | 5 | 0
2030 | 2008 | 10 | 10 | 6 | 0
2030 | 2008 | 10 | 10 | 7 | 0
2030 | 2008 | 10 | 10 | 8 | 24.1782
2030 | 2008 | 10 | 10 | 9 | 14026.0555
2030 | 2008 | 10 | 10 | 10 | 38077.4568
2030 | 2008 | 10 | 10 | 11 | 50109.8943
2030 | 2008 | 10 | 10 | 12 | 51702.073
2030 | 2008 | 10 | 10 | 13 | 48592.9877
2030 | 2008 | 10 | 10 | 14 | 49824.6409
2030 | 2008 | 10 | 10 | 15 | 48535.6917
2030 | 2008 | 10 | 10 | 16 | 48730.1738
2030 | 2008 | 10 | 10 | 17 | 48937.967
2030 | 2008 | 10 | 10 | 18 | 36553.0082
2030 | 2008 | 10 | 10 | 19 | 11297.9737
2030 | 2008 | 10 | 10 | 20 | 0
2030 | 2008 | 10 | 10 | 21 | 0
2030 | 2008 | 10 | 10 | 22 | 0
2030 | 2008 | 10 | 10 | 23 | 0
2030 | 2008 | 10 | 10 | 24 | 0
2030 | 2008 | 10 | 11 | 1 | 0
2030 | 2008 | 10 | 11 | 2 | 0
2030 | 2008 | 10 | 11 | 3 | 0
2030 | 2008 | 10 | 11 | 4 | 0
2030 | 2008 | 10 | 11 | 5 | 0
2030 | 2008 | 10 | 11 | 6 | 0
2030 | 2008 | 10 | 11 | 7 | 0
2030 | 2008 | 10 | 11 | 8 | 12.945
2030 | 2008 | 10 | 11 | 9 | 6732.9311
2030 | 2008 | 10 | 11 | 10 | 18824.5711
2030 | 2008 | 10 | 11 | 11 | 25634.5113
2030 | 2008 | 10 | 11 | 12 | 30951.5132
2030 | 2008 | 10 | 11 | 13 | 33375.6568
2030 | 2008 | 10 | 11 | 14 | 38097.1407
2030 | 2008 | 10 | 11 | 15 | 41719.8007
2030 | 2008 | 10 | 11 | 16 | 44356.8835
2030 | 2008 | 10 | 11 | 17 | 42633.7774
2030 | 2008 | 10 | 11 | 18 | 33638.2683
2030 | 2008 | 10 | 11 | 19 | 9968.0589
2030 | 2008 | 10 | 11 | 20 | 0
2030 | 2008 | 10 | 11 | 21 | 0
2030 | 2008 | 10 | 11 | 22 | 0
2030 | 2008 | 10 | 11 | 23 | 0
2030 | 2008 | 10 | 11 | 24 | 0
2030 | 2008 | 10 | 12 | 1 | 0
2030 | 2008 | 10 | 12 | 2 | 0
2030 | 2008 | 10 | 12 | 3 | 0
2030 | 2008 | 10 | 12 | 4 | 0
2030 | 2008 | 10 | 12 | 5 | 0
2030 | 2008 | 10 | 12 | 6 | 0
2030 | 2008 | 10 | 12 | 7 | 0
2030 | 2008 | 10 | 12 | 8 | 16.8739
2030 | 2008 | 10 | 12 | 9 | 6412.0753
2030 | 2008 | 10 | 12 | 10 | 22587.9915
2030 | 2008 | 10 | 12 | 11 | 29495.2026
2030 | 2008 | 10 | 12 | 12 | 37110.3689
2030 | 2008 | 10 | 12 | 13 | 36968.0979
2030 | 2008 | 10 | 12 | 14 | 37204.8476
2030 | 2008 | 10 | 12 | 15 | 33702.9382
2030 | 2008 | 10 | 12 | 16 | 33322.0286
2030 | 2008 | 10 | 12 | 17 | 31872.3672
2030 | 2008 | 10 | 12 | 18 | 26248.4461
2030 | 2008 | 10 | 12 | 19 | 6837.5617
2030 | 2008 | 10 | 12 | 20 | 0
2030 | 2008 | 10 | 12 | 21 | 0
2030 | 2008 | 10 | 12 | 22 | 0
2030 | 2008 | 10 | 12 | 23 | 0
2030 | 2008 | 10 | 12 | 24 | 0
2030 | 2008 | 10 | 13 | 1 | 0
2030 | 2008 | 10 | 13 | 2 | 0
2030 | 2008 | 10 | 13 | 3 | 0
2030 | 2008 | 10 | 13 | 4 | 0
2030 | 2008 | 10 | 13 | 5 | 0
2030 | 2008 | 10 | 13 | 6 | 0
2030 | 2008 | 10 | 13 | 7 | 0
2030 | 2008 | 10 | 13 | 8 | 17.7923
2030 | 2008 | 10 | 13 | 9 | 5326.9468
2030 | 2008 | 10 | 13 | 10 | 17364.1567
2030 | 2008 | 10 | 13 | 11 | 22746.9069
2030 | 2008 | 10 | 13 | 12 | 27119.0395
2030 | 2008 | 10 | 13 | 13 | 30640.6192
2030 | 2008 | 10 | 13 | 14 | 33064.2971
2030 | 2008 | 10 | 13 | 15 | 31455.4274
2030 | 2008 | 10 | 13 | 16 | 31403.2022
2030 | 2008 | 10 | 13 | 17 | 32224.0346
2030 | 2008 | 10 | 13 | 18 | 24969.6069
2030 | 2008 | 10 | 13 | 19 | 5879.5318
2030 | 2008 | 10 | 13 | 20 | 0
2030 | 2008 | 10 | 13 | 21 | 0
2030 | 2008 | 10 | 13 | 22 | 0
2030 | 2008 | 10 | 13 | 23 | 0
2030 | 2008 | 10 | 13 | 24 | 0
2030 | 2008 | 10 | 14 | 1 | 0
2030 | 2008 | 10 | 14 | 2 | 0
2030 | 2008 | 10 | 14 | 3 | 0
2030 | 2008 | 10 | 14 | 4 | 0
2030 | 2008 | 10 | 14 | 5 | 0
2030 | 2008 | 10 | 14 | 6 | 0
2030 | 2008 | 10 | 14 | 7 | 0
2030 | 2008 | 10 | 14 | 8 | 1.4228
2030 | 2008 | 10 | 14 | 9 | 1584.779
2030 | 2008 | 10 | 14 | 10 | 7186.9784
2030 | 2008 | 10 | 14 | 11 | 13735.8173
2030 | 2008 | 10 | 14 | 12 | 21808.9201
2030 | 2008 | 10 | 14 | 13 | 27090.9816
2030 | 2008 | 10 | 14 | 14 | 28527.247
2030 | 2008 | 10 | 14 | 15 | 30770.9349
2030 | 2008 | 10 | 14 | 16 | 30719.4218
2030 | 2008 | 10 | 14 | 17 | 29930.5943
2030 | 2008 | 10 | 14 | 18 | 25135.3115
2030 | 2008 | 10 | 14 | 19 | 5739.5597
2030 | 2008 | 10 | 14 | 20 | 0
2030 | 2008 | 10 | 14 | 21 | 0
2030 | 2008 | 10 | 14 | 22 | 0
2030 | 2008 | 10 | 14 | 23 | 0
2030 | 2008 | 10 | 14 | 24 | 0
2030 | 2008 | 10 | 15 | 1 | 0
2030 | 2008 | 10 | 15 | 2 | 0
2030 | 2008 | 10 | 15 | 3 | 0
2030 | 2008 | 10 | 15 | 4 | 0
2030 | 2008 | 10 | 15 | 5 | 0
2030 | 2008 | 10 | 15 | 6 | 0
2030 | 2008 | 10 | 15 | 7 | 0
2030 | 2008 | 10 | 15 | 8 | 6.4361
2030 | 2008 | 10 | 15 | 9 | 2901.9709
2030 | 2008 | 10 | 15 | 10 | 13263.0943
2030 | 2008 | 10 | 15 | 11 | 19514.9262
2030 | 2008 | 10 | 15 | 12 | 25199.7027
2030 | 2008 | 10 | 15 | 13 | 29083.8599
2030 | 2008 | 10 | 15 | 14 | 30789.0003
2030 | 2008 | 10 | 15 | 15 | 30316.3043
2030 | 2008 | 10 | 15 | 16 | 29239.683
2030 | 2008 | 10 | 15 | 17 | 28102.926
2030 | 2008 | 10 | 15 | 18 | 25756.0305
2030 | 2008 | 10 | 15 | 19 | 6884.6655
2030 | 2008 | 10 | 15 | 20 | 0
2030 | 2008 | 10 | 15 | 21 | 0
2030 | 2008 | 10 | 15 | 22 | 0
2030 | 2008 | 10 | 15 | 23 | 0
2030 | 2008 | 10 | 15 | 24 | 0
2030 | 2008 | 10 | 16 | 1 | 0
2030 | 2008 | 10 | 16 | 2 | 0
2030 | 2008 | 10 | 16 | 3 | 0
2030 | 2008 | 10 | 16 | 4 | 0
2030 | 2008 | 10 | 16 | 5 | 0
2030 | 2008 | 10 | 16 | 6 | 0
2030 | 2008 | 10 | 16 | 7 | 0
2030 | 2008 | 10 | 16 | 8 | 0.48227
2030 | 2008 | 10 | 16 | 9 | 1508.6955
2030 | 2008 | 10 | 16 | 10 | 10958.7947
2030 | 2008 | 10 | 16 | 11 | 17991.2803
2030 | 2008 | 10 | 16 | 12 | 27487.6935
2030 | 2008 | 10 | 16 | 13 | 31013.6986
2030 | 2008 | 10 | 16 | 14 | 32500.1942
2030 | 2008 | 10 | 16 | 15 | 33035.1774
2030 | 2008 | 10 | 16 | 16 | 33629.1906
2030 | 2008 | 10 | 16 | 17 | 28590.0235
2030 | 2008 | 10 | 16 | 18 | 26799.6381
2030 | 2008 | 10 | 16 | 19 | 6381.7654
2030 | 2008 | 10 | 16 | 20 | 0
2030 | 2008 | 10 | 16 | 21 | 0
2030 | 2008 | 10 | 16 | 22 | 0
2030 | 2008 | 10 | 16 | 23 | 0
2030 | 2008 | 10 | 16 | 24 | 0
2030 | 2008 | 10 | 17 | 1 | 0
2030 | 2008 | 10 | 17 | 2 | 0
2030 | 2008 | 10 | 17 | 3 | 0
2030 | 2008 | 10 | 17 | 4 | 0
2030 | 2008 | 10 | 17 | 5 | 0
2030 | 2008 | 10 | 17 | 6 | 0
2030 | 2008 | 10 | 17 | 7 | 0
2030 | 2008 | 10 | 17 | 8 | 2.332
2030 | 2008 | 10 | 17 | 9 | 8429.9015
2030 | 2008 | 10 | 17 | 10 | 28827.9913
2030 | 2008 | 10 | 17 | 11 | 33785.1148
2030 | 2008 | 10 | 17 | 12 | 35686.4519
2030 | 2008 | 10 | 17 | 13 | 37591.0934
2030 | 2008 | 10 | 17 | 14 | 37858.8665
2030 | 2008 | 10 | 17 | 15 | 36315.199
2030 | 2008 | 10 | 17 | 16 | 35807.9401
2030 | 2008 | 10 | 17 | 17 | 34766.5825
2030 | 2008 | 10 | 17 | 18 | 27796.0868
2030 | 2008 | 10 | 17 | 19 | 6537.0057
2030 | 2008 | 10 | 17 | 20 | 0
2030 | 2008 | 10 | 17 | 21 | 0
2030 | 2008 | 10 | 17 | 22 | 0
2030 | 2008 | 10 | 17 | 23 | 0
2030 | 2008 | 10 | 17 | 24 | 0
2030 | 2008 | 10 | 18 | 1 | 0
2030 | 2008 | 10 | 18 | 2 | 0
2030 | 2008 | 10 | 18 | 3 | 0
2030 | 2008 | 10 | 18 | 4 | 0
2030 | 2008 | 10 | 18 | 5 | 0
2030 | 2008 | 10 | 18 | 6 | 0
2030 | 2008 | 10 | 18 | 7 | 0
2030 | 2008 | 10 | 18 | 8 | 20.7526
2030 | 2008 | 10 | 18 | 9 | 15733.0884
2030 | 2008 | 10 | 18 | 10 | 45028.9116
2030 | 2008 | 10 | 18 | 11 | 52709.6851
2030 | 2008 | 10 | 18 | 12 | 52993.0698
2030 | 2008 | 10 | 18 | 13 | 52522.2861
2030 | 2008 | 10 | 18 | 14 | 50738.9919
2030 | 2008 | 10 | 18 | 15 | 51312.7198
2030 | 2008 | 10 | 18 | 16 | 49961.3484
2030 | 2008 | 10 | 18 | 17 | 46727.4879
2030 | 2008 | 10 | 18 | 18 | 35633.0888
2030 | 2008 | 10 | 18 | 19 | 7451.5142
2030 | 2008 | 10 | 18 | 20 | 0
2030 | 2008 | 10 | 18 | 21 | 0
2030 | 2008 | 10 | 18 | 22 | 0
2030 | 2008 | 10 | 18 | 23 | 0
2030 | 2008 | 10 | 18 | 24 | 0
2030 | 2008 | 10 | 19 | 1 | 0
2030 | 2008 | 10 | 19 | 2 | 0
2030 | 2008 | 10 | 19 | 3 | 0
2030 | 2008 | 10 | 19 | 4 | 0
2030 | 2008 | 10 | 19 | 5 | 0
2030 | 2008 | 10 | 19 | 6 | 0
2030 | 2008 | 10 | 19 | 7 | 0
2030 | 2008 | 10 | 19 | 8 | 19.9747
2030 | 2008 | 10 | 19 | 9 | 15832.3139
2030 | 2008 | 10 | 19 | 10 | 46660.2379
2030 | 2008 | 10 | 19 | 11 | 52493.2603
2030 | 2008 | 10 | 19 | 12 | 53761.2022
2030 | 2008 | 10 | 19 | 13 | 52186.4333
2030 | 2008 | 10 | 19 | 14 | 51092.5193
2030 | 2008 | 10 | 19 | 15 | 50545.8764
2030 | 2008 | 10 | 19 | 16 | 46766.2187
2030 | 2008 | 10 | 19 | 17 | 45610.1794
2030 | 2008 | 10 | 19 | 18 | 31916.0123
2030 | 2008 | 10 | 19 | 19 | 6539.6218
2030 | 2008 | 10 | 19 | 20 | 0
2030 | 2008 | 10 | 19 | 21 | 0
2030 | 2008 | 10 | 19 | 22 | 0
2030 | 2008 | 10 | 19 | 23 | 0
2030 | 2008 | 10 | 19 | 24 | 0
2030 | 2008 | 10 | 20 | 1 | 0
2030 | 2008 | 10 | 20 | 2 | 0
2030 | 2008 | 10 | 20 | 3 | 0
2030 | 2008 | 10 | 20 | 4 | 0
2030 | 2008 | 10 | 20 | 5 | 0
2030 | 2008 | 10 | 20 | 6 | 0
2030 | 2008 | 10 | 20 | 7 | 0
2030 | 2008 | 10 | 20 | 8 | 15.5983
2030 | 2008 | 10 | 20 | 9 | 14038.7872
2030 | 2008 | 10 | 20 | 10 | 42946.5903
2030 | 2008 | 10 | 20 | 11 | 49486.2178
2030 | 2008 | 10 | 20 | 12 | 49875.3131
2030 | 2008 | 10 | 20 | 13 | 49930.7667
2030 | 2008 | 10 | 20 | 14 | 48372.9971
2030 | 2008 | 10 | 20 | 15 | 48034.5243
2030 | 2008 | 10 | 20 | 16 | 46446.6465
2030 | 2008 | 10 | 20 | 17 | 42317.2352
2030 | 2008 | 10 | 20 | 18 | 31473.5601
2030 | 2008 | 10 | 20 | 19 | 6019.1835
2030 | 2008 | 10 | 20 | 20 | 0
2030 | 2008 | 10 | 20 | 21 | 0
2030 | 2008 | 10 | 20 | 22 | 0
2030 | 2008 | 10 | 20 | 23 | 0
2030 | 2008 | 10 | 20 | 24 | 0
2030 | 2008 | 10 | 21 | 1 | 0
2030 | 2008 | 10 | 21 | 2 | 0
2030 | 2008 | 10 | 21 | 3 | 0
2030 | 2008 | 10 | 21 | 4 | 0
2030 | 2008 | 10 | 21 | 5 | 0
2030 | 2008 | 10 | 21 | 6 | 0
2030 | 2008 | 10 | 21 | 7 | 0
2030 | 2008 | 10 | 21 | 8 | 9.6645
2030 | 2008 | 10 | 21 | 9 | 7827.8433
2030 | 2008 | 10 | 21 | 10 | 24939.7591
2030 | 2008 | 10 | 21 | 11 | 32667.4376
2030 | 2008 | 10 | 21 | 12 | 36839.2736
2030 | 2008 | 10 | 21 | 13 | 39832.3945
2030 | 2008 | 10 | 21 | 14 | 41239.7463
2030 | 2008 | 10 | 21 | 15 | 40846.4319
2030 | 2008 | 10 | 21 | 16 | 40939.9159
2030 | 2008 | 10 | 21 | 17 | 38072.3921
2030 | 2008 | 10 | 21 | 18 | 28354.6991
2030 | 2008 | 10 | 21 | 19 | 5055.2864
2030 | 2008 | 10 | 21 | 20 | 0
2030 | 2008 | 10 | 21 | 21 | 0
2030 | 2008 | 10 | 21 | 22 | 0
2030 | 2008 | 10 | 21 | 23 | 0
2030 | 2008 | 10 | 21 | 24 | 0
2030 | 2008 | 10 | 22 | 1 | 0
2030 | 2008 | 10 | 22 | 2 | 0
2030 | 2008 | 10 | 22 | 3 | 0
2030 | 2008 | 10 | 22 | 4 | 0
2030 | 2008 | 10 | 22 | 5 | 0
2030 | 2008 | 10 | 22 | 6 | 0
2030 | 2008 | 10 | 22 | 7 | 0
2030 | 2008 | 10 | 22 | 8 | 8.5606
2030 | 2008 | 10 | 22 | 9 | 5573.4618
2030 | 2008 | 10 | 22 | 10 | 18777.986
2030 | 2008 | 10 | 22 | 11 | 27787.714
2030 | 2008 | 10 | 22 | 12 | 32084.5085
2030 | 2008 | 10 | 22 | 13 | 36021.5589
2030 | 2008 | 10 | 22 | 14 | 37784.5279
2030 | 2008 | 10 | 22 | 15 | 36811.755
2030 | 2008 | 10 | 22 | 16 | 39165.9831
2030 | 2008 | 10 | 22 | 17 | 32936.7229
2030 | 2008 | 10 | 22 | 18 | 25427.4945
2030 | 2008 | 10 | 22 | 19 | 4477.9861
2030 | 2008 | 10 | 22 | 20 | 0
2030 | 2008 | 10 | 22 | 21 | 0
2030 | 2008 | 10 | 22 | 22 | 0
2030 | 2008 | 10 | 22 | 23 | 0
2030 | 2008 | 10 | 22 | 24 | 0
2030 | 2008 | 10 | 23 | 1 | 0
2030 | 2008 | 10 | 23 | 2 | 0
2030 | 2008 | 10 | 23 | 3 | 0
2030 | 2008 | 10 | 23 | 4 | 0
2030 | 2008 | 10 | 23 | 5 | 0
2030 | 2008 | 10 | 23 | 6 | 0
2030 | 2008 | 10 | 23 | 7 | 0
2030 | 2008 | 10 | 23 | 8 | 7.7832
2030 | 2008 | 10 | 23 | 9 | 14654.8864
2030 | 2008 | 10 | 23 | 10 | 43882.4533
2030 | 2008 | 10 | 23 | 11 | 51839.4612
2030 | 2008 | 10 | 23 | 12 | 52639.2235
2030 | 2008 | 10 | 23 | 13 | 51857.7791
2030 | 2008 | 10 | 23 | 14 | 51637.4147
2030 | 2008 | 10 | 23 | 15 | 50821.2786
2030 | 2008 | 10 | 23 | 16 | 50232.673
2030 | 2008 | 10 | 23 | 17 | 46749.7193
2030 | 2008 | 10 | 23 | 18 | 34094.3121
2030 | 2008 | 10 | 23 | 19 | 4662.5893
2030 | 2008 | 10 | 23 | 20 | 0
2030 | 2008 | 10 | 23 | 21 | 0
2030 | 2008 | 10 | 23 | 22 | 0
2030 | 2008 | 10 | 23 | 23 | 0
2030 | 2008 | 10 | 23 | 24 | 0
2030 | 2008 | 10 | 24 | 1 | 0
2030 | 2008 | 10 | 24 | 2 | 0
2030 | 2008 | 10 | 24 | 3 | 0
2030 | 2008 | 10 | 24 | 4 | 0
2030 | 2008 | 10 | 24 | 5 | 0
2030 | 2008 | 10 | 24 | 6 | 0
2030 | 2008 | 10 | 24 | 7 | 0
2030 | 2008 | 10 | 24 | 8 | 11.3728
2030 | 2008 | 10 | 24 | 9 | 15009.8186
2030 | 2008 | 10 | 24 | 10 | 47264.463
2030 | 2008 | 10 | 24 | 11 | 54335.5057
2030 | 2008 | 10 | 24 | 12 | 55004.6734
2030 | 2008 | 10 | 24 | 13 | 52367.7045
2030 | 2008 | 10 | 24 | 14 | 51721.3271
2030 | 2008 | 10 | 24 | 15 | 51253.1802
2030 | 2008 | 10 | 24 | 16 | 48233.6384
2030 | 2008 | 10 | 24 | 17 | 46394.6703
2030 | 2008 | 10 | 24 | 18 | 29624.7758
2030 | 2008 | 10 | 24 | 19 | 3792.7884
2030 | 2008 | 10 | 24 | 20 | 0
2030 | 2008 | 10 | 24 | 21 | 0
2030 | 2008 | 10 | 24 | 22 | 0
2030 | 2008 | 10 | 24 | 23 | 0
2030 | 2008 | 10 | 24 | 24 | 0
2030 | 2008 | 10 | 25 | 1 | 0
2030 | 2008 | 10 | 25 | 2 | 0
2030 | 2008 | 10 | 25 | 3 | 0
2030 | 2008 | 10 | 25 | 4 | 0
2030 | 2008 | 10 | 25 | 5 | 0
2030 | 2008 | 10 | 25 | 6 | 0
2030 | 2008 | 10 | 25 | 7 | 0
2030 | 2008 | 10 | 25 | 8 | 10.3332
2030 | 2008 | 10 | 25 | 9 | 13605.5758
2030 | 2008 | 10 | 25 | 10 | 43655.369
2030 | 2008 | 10 | 25 | 11 | 50549.876
2030 | 2008 | 10 | 25 | 12 | 51303.2613
2030 | 2008 | 10 | 25 | 13 | 49932.5311
2030 | 2008 | 10 | 25 | 14 | 48612.0072
2030 | 2008 | 10 | 25 | 15 | 48490.8857
2030 | 2008 | 10 | 25 | 16 | 47354.2886
2030 | 2008 | 10 | 25 | 17 | 43575.8505
2030 | 2008 | 10 | 25 | 18 | 28062.3196
2030 | 2008 | 10 | 25 | 19 | 3216.1809
2030 | 2008 | 10 | 25 | 20 | 0
2030 | 2008 | 10 | 25 | 21 | 0
2030 | 2008 | 10 | 25 | 22 | 0
2030 | 2008 | 10 | 25 | 23 | 0
2030 | 2008 | 10 | 25 | 24 | 0
2030 | 2008 | 10 | 26 | 1 | 0
2030 | 2008 | 10 | 26 | 2 | 0
2030 | 2008 | 10 | 26 | 3 | 0
2030 | 2008 | 10 | 26 | 4 | 0
2030 | 2008 | 10 | 26 | 5 | 0
2030 | 2008 | 10 | 26 | 6 | 0
2030 | 2008 | 10 | 26 | 7 | 0
2030 | 2008 | 10 | 26 | 8 | 8.289
2030 | 2008 | 10 | 26 | 9 | 11315.5244
2030 | 2008 | 10 | 26 | 10 | 36265.8609
2030 | 2008 | 10 | 26 | 11 | 41442.3273
2030 | 2008 | 10 | 26 | 12 | 41210.2376
2030 | 2008 | 10 | 26 | 13 | 42540.9148
2030 | 2008 | 10 | 26 | 14 | 44390.7172
2030 | 2008 | 10 | 26 | 15 | 42493.1744
2030 | 2008 | 10 | 26 | 16 | 39478.5348
2030 | 2008 | 10 | 26 | 17 | 39178.188
2030 | 2008 | 10 | 26 | 18 | 30114.6078
2030 | 2008 | 10 | 26 | 19 | 3016.9245
2030 | 2008 | 10 | 26 | 20 | 0
2030 | 2008 | 10 | 26 | 21 | 0
2030 | 2008 | 10 | 26 | 22 | 0
2030 | 2008 | 10 | 26 | 23 | 0
2030 | 2008 | 10 | 26 | 24 | 0
2030 | 2008 | 10 | 27 | 1 | 0
2030 | 2008 | 10 | 27 | 2 | 0
2030 | 2008 | 10 | 27 | 3 | 0
2030 | 2008 | 10 | 27 | 4 | 0
2030 | 2008 | 10 | 27 | 5 | 0
2030 | 2008 | 10 | 27 | 6 | 0
2030 | 2008 | 10 | 27 | 7 | 0
2030 | 2008 | 10 | 27 | 8 | 2.3435
2030 | 2008 | 10 | 27 | 9 | 13234.4485
2030 | 2008 | 10 | 27 | 10 | 44658.3912
2030 | 2008 | 10 | 27 | 11 | 53367.1927
2030 | 2008 | 10 | 27 | 12 | 55228.7508
2030 | 2008 | 10 | 27 | 13 | 52974.7499
2030 | 2008 | 10 | 27 | 14 | 52763.1211
2030 | 2008 | 10 | 27 | 15 | 52308.3565
2030 | 2008 | 10 | 27 | 16 | 50116.8488
2030 | 2008 | 10 | 27 | 17 | 46434.6729
2030 | 2008 | 10 | 27 | 18 | 29282.6043
2030 | 2008 | 10 | 27 | 19 | 2905.4713
2030 | 2008 | 10 | 27 | 20 | 0
2030 | 2008 | 10 | 27 | 21 | 0
2030 | 2008 | 10 | 27 | 22 | 0
2030 | 2008 | 10 | 27 | 23 | 0
2030 | 2008 | 10 | 27 | 24 | 0
2030 | 2008 | 10 | 28 | 1 | 0
2030 | 2008 | 10 | 28 | 2 | 0
2030 | 2008 | 10 | 28 | 3 | 0
2030 | 2008 | 10 | 28 | 4 | 0
2030 | 2008 | 10 | 28 | 5 | 0
2030 | 2008 | 10 | 28 | 6 | 0
2030 | 2008 | 10 | 28 | 7 | 0
2030 | 2008 | 10 | 28 | 8 | 4.1892
2030 | 2008 | 10 | 28 | 9 | 14573.8166
2030 | 2008 | 10 | 28 | 10 | 45247.7761
2030 | 2008 | 10 | 28 | 11 | 51757.7331
2030 | 2008 | 10 | 28 | 12 | 52601.8118
2030 | 2008 | 10 | 28 | 13 | 50857.9849
2030 | 2008 | 10 | 28 | 14 | 49470.4902
2030 | 2008 | 10 | 28 | 15 | 49137.7869
2030 | 2008 | 10 | 28 | 16 | 47506.4592
2030 | 2008 | 10 | 28 | 17 | 42853.0669
2030 | 2008 | 10 | 28 | 18 | 30582.224
2030 | 2008 | 10 | 28 | 19 | 2580.4289
2030 | 2008 | 10 | 28 | 20 | 0
2030 | 2008 | 10 | 28 | 21 | 0
2030 | 2008 | 10 | 28 | 22 | 0
2030 | 2008 | 10 | 28 | 23 | 0
2030 | 2008 | 10 | 28 | 24 | 0
2030 | 2008 | 10 | 29 | 1 | 0
2030 | 2008 | 10 | 29 | 2 | 0
2030 | 2008 | 10 | 29 | 3 | 0
2030 | 2008 | 10 | 29 | 4 | 0
2030 | 2008 | 10 | 29 | 5 | 0
2030 | 2008 | 10 | 29 | 6 | 0
2030 | 2008 | 10 | 29 | 7 | 0
2030 | 2008 | 10 | 29 | 8 | 5.4891
2030 | 2008 | 10 | 29 | 9 | 12605.4915
2030 | 2008 | 10 | 29 | 10 | 42238.1559
2030 | 2008 | 10 | 29 | 11 | 49956.9234
2030 | 2008 | 10 | 29 | 12 | 50413.6598
2030 | 2008 | 10 | 29 | 13 | 48712.5097
2030 | 2008 | 10 | 29 | 14 | 48308.0888
2030 | 2008 | 10 | 29 | 15 | 47023.9743
2030 | 2008 | 10 | 29 | 16 | 45860.2718
2030 | 2008 | 10 | 29 | 17 | 44099.7731
2030 | 2008 | 10 | 29 | 18 | 27963.672
2030 | 2008 | 10 | 29 | 19 | 2313.5803
2030 | 2008 | 10 | 29 | 20 | 0
2030 | 2008 | 10 | 29 | 21 | 0
2030 | 2008 | 10 | 29 | 22 | 0
2030 | 2008 | 10 | 29 | 23 | 0
2030 | 2008 | 10 | 29 | 24 | 0
2030 | 2008 | 10 | 30 | 1 | 0
2030 | 2008 | 10 | 30 | 2 | 0
2030 | 2008 | 10 | 30 | 3 | 0
2030 | 2008 | 10 | 30 | 4 | 0
2030 | 2008 | 10 | 30 | 5 | 0
2030 | 2008 | 10 | 30 | 6 | 0
2030 | 2008 | 10 | 30 | 7 | 0
2030 | 2008 | 10 | 30 | 8 | 2.4384
2030 | 2008 | 10 | 30 | 9 | 7856.8527
2030 | 2008 | 10 | 30 | 10 | 25181.0522
2030 | 2008 | 10 | 30 | 11 | 31248.5591
2030 | 2008 | 10 | 30 | 12 | 34678.8429
2030 | 2008 | 10 | 30 | 13 | 38818.3051
2030 | 2008 | 10 | 30 | 14 | 41636.9296
2030 | 2008 | 10 | 30 | 15 | 41414.0941
2030 | 2008 | 10 | 30 | 16 | 43480.6095
2030 | 2008 | 10 | 30 | 17 | 38931.6929
2030 | 2008 | 10 | 30 | 18 | 24752.245
2030 | 2008 | 10 | 30 | 19 | 2006.8197
2030 | 2008 | 10 | 30 | 20 | 0
2030 | 2008 | 10 | 30 | 21 | 0
2030 | 2008 | 10 | 30 | 22 | 0
2030 | 2008 | 10 | 30 | 23 | 0
2030 | 2008 | 10 | 30 | 24 | 0
2030 | 2008 | 10 | 31 | 1 | 0
2030 | 2008 | 10 | 31 | 2 | 0
2030 | 2008 | 10 | 31 | 3 | 0
2030 | 2008 | 10 | 31 | 4 | 0
2030 | 2008 | 10 | 31 | 5 | 0
2030 | 2008 | 10 | 31 | 6 | 0
2030 | 2008 | 10 | 31 | 7 | 0
2030 | 2008 | 10 | 31 | 8 | 2.1371
2030 | 2008 | 10 | 31 | 9 | 6241.0239
2030 | 2008 | 10 | 31 | 10 | 21812.7837
2030 | 2008 | 10 | 31 | 11 | 27950.0855
2030 | 2008 | 10 | 31 | 12 | 34702.8136
2030 | 2008 | 10 | 31 | 13 | 38119.4037
2030 | 2008 | 10 | 31 | 14 | 39663.0515
2030 | 2008 | 10 | 31 | 15 | 41345.3846
2030 | 2008 | 10 | 31 | 16 | 40024.983
2030 | 2008 | 10 | 31 | 17 | 39585.4277
2030 | 2008 | 10 | 31 | 18 | 23551.1733
2030 | 2008 | 10 | 31 | 19 | 3001.9802
2030 | 2008 | 10 | 31 | 20 | 0
2030 | 2008 | 10 | 31 | 21 | 0
2030 | 2008 | 10 | 31 | 22 | 0
2030 | 2008 | 10 | 31 | 23 | 0
2030 | 2008 | 10 | 31 | 24 | 0

## Seasons
Summer | Summer | Summer | Summer | Summer | Winter | Winter | Winter | Winter | Winter | Spring | Spring | Spring | Spring | Spring | Fall | Fall | Fall | Fall | Fall
2026 | 2027 | 2028 | 2029 | 2030 | 2026/2027 | 2027/2028 | 2028/2029 | 2029/2030 | 2030/2031 | 2026 | 2027 | 2028 | 2029 | 2030 | 2026 | 2027 | 2028 | 2029 | 2030
Input cells (non-formulas)

## Acronyms
Acronyms
General
GIM = Generator Interconnection or Modification request
CDR = Capacity, Demand and Reserves Report
COD = Commercial Operations Date
ELCC = Effective Load Carrying Capability
HE = Hour Ending
INR = Interconnection Request Number
RIOO-IS = "Resource Integration and Ongoing Operations - Integration Services" system
RIOO-RS = "Resource Integration and Ongoing Operations - Registration Services" system
RTP = Regional Transmission Plan
TSP = Transmission Service Provider
Technology Types (For Unit Details table)
BA = Battery Energy Storage
CC = Combined-Cycle
CE = Compressed Air Energy Storage
CP = Concentrated Solar Power
EN = Energy Storage
FC = Fuel Cell
GT = Combustion (gas) Turbine, but not part of a Combined-Cycle
HY = Hydroelectric Turbine
IC = Internal Combustion Engine, e.g. Reciprocating
MWH = Direct Current Asynchronous Tie
OT = Other
PV = Photovoltaic Solar
ST = Steam Turbine other than Combined-Cycle
WT = Wind Turbine
Fuel Types (For Unit Details Table)
BIOMASS = Biomass
COAL = Coal (bituminous, subbituminous, lignite)
DIESEL = Diesel/Fuel Oil
GAS = Natural Gas
GEO = Geothermal
HYD = Hydrogen
HYDRO = Water
MWH = Direct Current Asynchronous Tie
NUCLEAR = Nuclear
OTH = Other
PET = Petroleum Coke
SOLAR-FW = Solar from the Far West CDR solar region
SOLAR-O = Solar from the Other CDR solar region
SOLAR-W = Solar from the West CDR solar region
STORAGE = Storage
WIND-C = Wind from the Coastal wind region
WIND-O = Wind from the Other wind region
WIND-P = Wind from the Panhandle wind region
CDR Status (For Unit Details table)
OPER = Operational
OPER-UNFC = Unconfirmed Fuel Conversion
OPER-UNR = Unconfirmed Planned Retirement
EXT-OUT = Extended outage
MOTH-SEA = Seasonal mothballed (Unit operating under a seasonal availability schedule)
MOTH-IND = Indefinitely mothballed
OPER-SYN = Operational, synchronized only
OPER-SLF = Operational Self-Limiting Facility (See the Definitions tab for the SLF definition)
PLAN = Planned
PLAN-SLF = Planned Self-Limiting Facility (See the Definitions tab for the SLF definition)
PLAN-RPR = An existing unit being repowered and required to submit an interconnection request (See the Definitions tab for the CDR repower definition)
RMR = Reliability Must-Run, A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
CDR Resource Attributes (For Unit Details table)
CONV = Conventional Generation Resource (Unit that does not fall under the other CDR Attribute categories)
CONV-DGR = Conventional, Distributed Generation Resource
CONV-SLF = Conventional Generation Resource, Self-Limiting Facility (See the Definitions tab for the SLF definition)
CONV-SODG = Conventional, Settlement Only Distribution Generator
CONV-TGR = Conventional, Transmission Generation Resource unit
DC-TIE = Direct Current Asynchronous Tie
SWGR-AVA = Switchable Generation Resource, Available
SWGR-UNA = Switchable Generation Resource, Unavailable

## Definitions
Definitions
Available Mothballed Capacity based on Owner's Return Probability
Mothballed capacity with a return-to-service probability of 50% or greater for a given season of the year, as provided by its owner, constitutes available mothballed generation. Return probabilities for individual units are considered protected information under the ERCOT Protocols and therefore are not included in this report.
Capacity Pending Retirement
Announced retired capacity that is undergoing ERCOT grid reliability reviews pursuant to Nodal Protocol Section 3.14.1.2.
Contracted / Non-Contracted TSP Loads
Contracted Large Load: A Large Load, as defined in ERCOT's Planning Guide, reported to ERCOT for which an interconnection agreements and/or Facility Extension Agreements (FEA) has been signed by the customer and Transmission Service Provider, and the customer share of costs for the extension of TSP facilities has been paid to the TSP. A contracted Load typically falls into the following general categories: crypto-mining, data centers, hydrogen/ammonia production, oil and gas production, and industrial/manufacturing. Officer letter Large Load: A Load (or Loads) for which an officer of a TSP has documented in a letter sent to ERCOT attesting that there is a high likelihood that the Load(s) will materialize. These prospective Loads are not associated with a signed interconnection agreement or FEA, and are therefore considered more speculative than Loads with a signed interconnection agreement or FEA.
Decommissioned Generation Resource
A Generation Resource for which a Resource Entity has submitted a Notification of Suspension of Operations (NSO) or a Notification of Change of Generation Resource Designation (NCGRD), for which ERCOT has declined to execute a Reliability Must-Run (RMR) Agreement, and which has been decommissioned and permanently retired.
Distribution Resource Types:
Settlement Only Distribution Generator (SODG)
A generator that is connected to the Distribution System with a rating of: (1) One MW or less that chooses to register as an SODG; or (2) Greater than one and up to ten MW that is capable of providing a net export to the ERCOT System and does not register as a Distribution Generation Resource (DGR). SODGs are settled for exported energy only, but may not participate in the Ancillary Services market, Reliability Unit Commitment (RUC), Security-Constrained Economic Dispatch (SCED), or make energy offers. SODGs are listed in the SummerCapacities and WinterCapacities with a DG_ prefix in the UNIT CODE column
Distribution Generation Resource (DGR)
A Generation Resource connected to the Distribution System that is either: (1) Greater than ten MW and not registered with the Public Utility Commission of Texas (PUCT) as a self-generator; or (2) Ten MW or less that chooses to register as a Generation Resource to participate in the ERCOT markets. DGRs must be registered with ERCOT in accordance with Planning Guide Section 6.8.2, Resource Registration Process, and will be modeled in ERCOT systems in accordance with Section 3.10.7.2, Modeling of Resources and Transmission Loads. DGRs are listed in the SummerCapacities and WinterCapacities tabs with a (DGR) suffix in the UNIT NAME column
Effective Load Carrying Capability (ELCC)
Represents the aggregate average Megawatt (MW) contribution of a resource class in maintaining a target level of resource reliability for a given resource portfolio and forecast period. ELCCs are developed using Monte Carlo system simulation techniques to capture a wide range of system reliability outcomes. ELCC derivation starts with a base portfolio constructed to achieve the target reliability level. The resource class (e.g., wind) is removed and substituted with capacity that has perfect availability until the target reliability level is again reached. The ELCC is the amount of perfect capacity added divided by the amount of the resource class capacity removed, expressed as a percentage.
Emergency Response Service
ERCOT uses the methodology specified in Protocol Section 3.2.6.2.1, Peak Load Estimate, to derive the ERS capacity forecast for future years. The Current Year for the calculations is defined as the latest year for which ERS has been procured. The ERS capacity amounts are grossed up by 2% to reflect avoided transmission line losses.
Energy Efficiency Program Savings Forecast
ERCOT's energy efficiency forecast uses the PUCT's annual verified energy efficiency program savings estimates as the starting point. (See the definition for verified energy efficiency program savings below.) Savings from TDSP standard offer load management programs are not included in the ERCOT energy efficiency forecast. ERCOT calculates the historical average annual verified savings while excluding 2017 from the computation due to the load impacts caused by Hurricane Harvey. (For prior forecasts, ERCOT used a formula based on the State energy efficiency goals in Utilities Code Section 39.905. Since the impacts of the goals were assumed to accumulate for just seven years from the time that the goals must be first met (2013), ERCOT no longer uses the goal-based forecasting approach.) Finally, ERCOT incorporates annual energy efficiency estimates from municipal utilities and electric cooperatives provided to the State Energy Conservation Office (SECO). Annual SECO report submission by these entities is required under S.B. No. 924. If annual reports for the previous calendar year are not available at the time the CDR is prepared, ERCOT incorporates report data for the most recently available reporting year. The energy efficiency capacity amounts are grossed up by a factor representing avoided transmission and distribution line losses. The factor is currently 1.076, reflecting 2% for avoided transmission losses and 5.6% for avoided distribution losses. The loss percentages are based on transmission and distribution loss factors posted to ERCOT's MIS website.
Energy Emergency Alert (EEA)
An ERCOT EEA declaration is made when operating reserves and system frequency drop below established severity levels (Levels 1, 2 and 3) and reserves are not projected to recover within 30 minutes unless certain actions are taken. An EEA declaration initiates an orderly, predetermined procedure for maximizing the use of available Resources, including the use of voluntary load reduction programs that are only available under EEA operations. Only under the most severe EEA level, would ERCOT direct Transmission and Distribution Service Providers to start shedding Load on a rotating basis in order to maintain system reliability and integrity. See Nodal Protocol Section 6.5.9.4, Energy Emergency Alert, for more details.
ERCOT Contingency Reserve Service (ECRS)
An Ancillary Service that provides operating reserves that is intended to: (a) Restore Responsive Reserve (RRS) within ten minutes of a frequency deviation that results in significant depletion of RRS by restoring frequency to its scheduled value to return the system to normal; (b) Provide energy or continued Load interruption to avoid or during the implementation of an Energy Emergency Alert (EEA); (c) Provide backup regulation; and (d) Be sustained at a specified level for two consecutive hours. ECRS was developed to address net load ramps and take advantage of Energy Storage Resources with maximum durations of at least two hours.
Forecast Zone
The CDR report uses Forecast Zones to identify the geographical location of generation resources. Forecast Zones generally have the same boundaries as the 2003 Congestion Management Zones with the following exceptions: A) Panhandle Zone for resources in the Texas Panhandle counties and outside the 2003 Congestion Management Zones, and B) Coastal Zone for resources in 11 counties along the Texas Gulf Coast and formerly in the South Zone of the 2003 Congestion Management Zones. There are six Forecast Zones: Coastal, Houston, North, Panhandle, South, and West. Note that the CDR Forecast Zones are only used for resource adequacy reporting and are distinct from other ERCOT geographical reporting schemes used for planning, operational, or data reporting purposes.
Full Interconnection Study (FIS)
The set of studies conducted by a Transmission Service Provider (TSP) for the purpose of identifying any electric system improvements or enhancements required to reliably interconnect a new All-Inclusive Generation Resource consistent with the provisions of Planning Guide Section 5, Generation Resource Interconnection or Change Request. These studies may include steady-state studies, system protection (short-circuit) studies, dynamic and transient stability studies, facility studies, and sub-synchronous oscillation studies.
Hydroelectric, Peak Average Capacity Contribution
Hydroelectric, Peak Average Capacity Contribution listed in the Seasonal Summary tab is based on average of the power that can be provided by hydroelectric generators during the during the highest 20 peak Load hours for each preceding three-year period for each Reserve Risk Period.
Inactive Projects
Per Planning Guide Section 5.7.6, a proposed Resource shall be given the status of “Inactive” if the Resource has not met the conditions for inclusion in the ERCOT planning models, as specified in Section 6.9, Addition of Proposed Generation to the Planning Models, within two years of the date on which ERCOT posts the final FIS studies for the Resource to the MIS Secure Area. A developer may also elect Inactive status and stop any interconnection studies in process at its own discretion. When an Inactive Resource subsequently meets the requirements of Section 6.9, it shall be added to the planning models and the status changed back to Planned. If a Resource has been Inactive for five years, ERCOT may cancel the project pursuant to Planning Guide Section 5.7.7, Cancellation of a Project Due to Failure to Comply with Requirements. Inactive planned projects are excluded from the CDR's reserve margin calculations.
Installed Capacity Rating
The installed capacity rating is the maximum power that a generating unit can produce during normal sustained operating conditions as specified by the equipment manufacturer. ERCOT uses Real Power Ratings that reflect the continuous flow of power to loads (as opposed to reactive power, which is the power that flows back and forth between the power source and loads, and doesn't perform useful work.)
Large Flexible Load (LFL)
A Large Load (as defined below) that can come online quickly and is very responsive to real time prices. An LFL is typically a crypto-currency mining site.
Large Load
One or more Facilities at a single site with an aggregate peak Demand greater than or equal to 75 MW behind one or more common Points of Interconnection (POIs) or Service Delivery Points.
LRs (Load Resources)
Load capable of reducing or increasing the need for electrical energy or providing Ancillary Services to the ERCOT System, as described in the ERCOT Protocols, Section 6, Ancillary Services. These Resources may provide the following Ancillary Services: Responsive Reserve Service, Non-Spinning Reserve Service, Replacement Reserve Service, and Regulation Service. The Resources must be registered and qualified by ERCOT and will be scheduled by a Qualified Scheduling Entity (QSE). LR capacity has been grossed up by 2% to reflect avoided transmission line losses.
Mothballed Unit
A generation resource for which a generation entity has submitted a Notification of Suspension of Operations, for which ERCOT has declined to execute an RMR agreement, and for which the generation entity has not announced retirement of the generation resource. A seasonal mothballed unit is one in which the generation entity requests a seasonal operation period that must include the summer Peak Load Season, June 1 through September 30.
Mothballed Capacity
Capacity that is designated as mothballed by a generating unit's owner as described above, and which is not available for operations during the summer Peak Load Season (June, July, August and September) or winter Peak Load Season (December, January and February).
Seasons
Summer months are June, July, August, and September; winter months are December, January, and February.
Net Load / Peak Net Load
The Load for a given period minus generation from PhotoVoltaic Generation Resources (PVGRs) and Wind Generation Resources (WGRs) for the same period. The peak Net Load is the highest value for the given period.
Private Use Networks (PUNs)
An electric network connected to the ERCOT transmission grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation). The Capacity from Private Use Networks forecast estimate in the Seasonal Summary tab is based on the average available power during the seasonal peak days over the past three years, and it is adjusted for any reported changes in capacity at the start of the forecast season.
Non-Synchronous Tie
Any non-synchronous transmission interconnection between ERCOT and non-ERCOT electric power systems.
Reliability Must-Run (RMR) Unit
A generation resource unit operated under the terms of an agreement with ERCOT that would not otherwise be operated except that they are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria.
Repower
For CDR reporting purposes, a repower is an operational resource for which the owner plans to modify it where one of the two following conditions apply: ● The Resource Entity is changing the inverter, turbine, generator, or power converter associated with a facility with an aggregate real power rating of ten MW or greater, unless the replacement is in-kind; See Planning Guide Section 5.2.1(1)(c)(ii). ● Increasing the aggregate nameplate capacity of a generator less than ten MW to ten MW or greater. See Planning Guide Section 5.2.1(1)(c)(v).
Self-Limiting Facility (SLF)
A modeled generation station that includes one or more Generation Resources, Energy Storage Resources (ESRs), and/or Settlement Only Generators (SOGs) with an established limit on the total MW Injection that is less than the total nameplate capacity of all registered generators or Energy Storage Systems (ESSs) within the Facility. A Facility with one or more ESRs may also have an established limit on the MW Withdrawal that is less than the total nameplate MW Withdrawal rating of all ESRs within the facility. (MW Withdrawal is defined as the instantaneous Megawatt (MW) energy withdrawn from the ERCOT System as measured at the Point of Interconnection (POI) or Point of Common Coupling (POCC).
Signed SGIA (Standard Generation Interconnection Agreement)
An agreement that sets forth requirements for physical connection between an eligible transmission service customer and a transmission or distribution service provider.
Switchable Generation Resource (SWGR)
A generation resource that can be connected to either the ERCOT transmission grid or a grid outside the ERCOT Region.
Synchronized but not Approved for Commercial Operations Capacity
These units have met requirements to Energize Equipment (Part 1 of Generator Commissioning Checklist): provided latest model data, verified Voltage Ride-Through capability and communication capabilities specified by ERCOT Operating Guides are in place. Output for these resources is not limited once they have passed a curtailment test and the project developer has submitted an attestation for the following plant controls: Automatic Voltage Regulator (AVR), Primary Frequency Response (PFR), Voltage Support Service (VSS), and Power System Stabilizer (PSS). A Synchronized unit get approved for Commercial Operations after the plant controls have been verified by ERCOT. More information on Synchronized units can be found in the Resource Interconnection Handbook pages 24 – 33. http://www.ercot.com/content/wcm/lists/168284/Resource_Interconnection_Handbook_v1.91_01082021.docx
TDSP Standard Offer Load Management Programs
For the May releases of the CDR report, ERCOT uses the megawatt amount of verified peak load capacity reductions, adjusted for avoided transmission losses, due to TDSP Standard Officer load management programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. The reported amounts are for the most current reporting year, which is the calendar year prior to the year during which the May CDR is prepared. (For example, the May 2019 CDR report used verified program savings for the 2018 reporting year.) For the December CDR releases, ERCOT uses TDSP data received for the current load management program year, which is more timely than the verified savings estimates provided to the PUCT. The data obtained from the TDSPs reflect verified program performance for the summer based on testing, and is adjusted for avoided transmission losses.
Unconfirmed Retirement
The capacity of Generation Resources for which a public announcement of the intent to permanently shut the unit down has been released, but a Notice of Suspension of Operations for the unit has not been received by ERCOT. To be considered an Unconfirmed Planned Retirement, the Generation Resource must meet the following criteria: (1) a specific retirement date is cited in the announcement, or other timing information is provided that indicates the unit will be unavailable for a given season and year, and (2) the announcement, with follow-up inquiry by ERCOT, does not indicate that retirement timing is highly speculative.
Verified Energy Efficiency Program Savings
The total megawatt (MW) amount of verified peak load capacity reductions due to residential and commercial sector energy efficiency incentive programs that are reported by electric utilities in the ERCOT Region to the Public Utility Commission of Texas. See Utilities Code Section 39.905. Note that savings from TDSP standard offer load management programs are not included in the ERCOT energy efficiency forecast, but rather handled as a separate reporting line item.
Wind and Solar Regions
See the "Wind-Solar Region Mapping" tab to see which counties are assigned to each region. The assigned Wind Region for each wind generation resource is indicated as "WIND-C," "WIND-P," or "WIND-O" in the Fuel columns of the summer/winter Capacities tabs. The assigned Solar Region assigned to each solar generation resources is indicated as "SOLAR-W," SOLAR-FW," and SOLAR-O."

## Wind-Solar Region Mapping
The tables below show what counties in the ERCOT region are mapped to the CDR Wind and Solar Regions.
Note: The CDR Wind and Solar Regions are intended to facilitate calculation of geographic-based Effective Load Carrying Capabilities (ELCCs) that represent wind and solar availabilities for Planning Reserve Margin calculation purposes. These are distinct from ERCOT zone definitions defined for other uses, such as the zones used for wind and solar production forecasting and reporting. These regions are reflected in the FUEL column for wind and solar units found in the Unit Details tab.
County | CDR Wind Region | County | CDR Solar Region
Aransas | Coastal | Andrews | Far West
Brazoria | Coastal | Brewster | Far West
Calhoun | Coastal | Crane | Far West
Cameron | Coastal | Culberson | Far West
Chambers | Coastal | Ector | Far West
Galveston | Coastal | El Paso | Far West
Jefferson | Coastal | Gaines | Far West
Kenedy | Coastal | Hudspeth | Far West
Kleberg | Coastal | Jeff Davis | Far West
Matagorda | Coastal | Loving | Far West
Nueces | Coastal | Midland | Far West
Orange | Coastal | Pecos | Far West
Refugio | Coastal | Presidio | Far West
San Patricio | Coastal | Reeves | Far West
Willacy | Coastal | Terrell | Far West
Anderson | Other | Upton | Far West
Angelina | Other | Ward | Far West
Bell | Other | Winkler | Far West
Bosque | Other | Yoakum | Far West
Bowie | Other | Bandera | Other
Brazos | Other | Bell | Other
Brown | Other | Blanco | Other
Camp | Other | Bosque | Other
Cass | Other | Brown | Other
Cherokee | Other | Burnet | Other
Collin | Other | Collin | Other
Comanche | Other | Comal | Other
Cooke | Other | Comanche | Other
Coryell | Other | Cooke | Other
Dallas | Other | Coryell | Other
Delta | Other | Dallas | Other
Denton | Other | Denton | Other
Eastland | Other | Eastland | Other
Ellis | Other | Edwards | Other
Erath | Other | Ellis | Other
Falls | Other | Erath | Other
Fannin | Other | Gillespie | Other
Franklin | Other | Grayson | Other
Freestone | Other | Hamilton | Other
Grayson | Other | Hays | Other
Gregg | Other | Hill | Other
Grimes | Other | Hood | Other
Hamilton | Other | Jack | Other
Harrison | Other | Johnson | Other
Henderson | Other | Kendall | Other
Hill | Other | Kerr | Other
Hood | Other | Kimble | Other
Hopkins | Other | Lampasas | Other
Houston | Other | Llano | Other
Hunt | Other | Mason | Other
Jack | Other | McCulloch | Other
Jasper | Other | McLennan | Other
Johnson | Other | Mills | Other
Kaufman | Other | Montague | Other
Lamar | Other | Palo Pinto | Other
Lampasas | Other | Parker | Other
Leon | Other | Real | Other
Limestone | Other | San Saba | Other
Madison | Other | Somervell | Other
Marion | Other | Stephens | Other
McLennan | Other | Tarrant | Other
Mills | Other | Travis | Other
Montague | Other | Williamson | Other
Morris | Other | Wise | Other
Nacogdoches | Other | Young | Other
Navarro | Other | Anderson | Other
Newton | Other | Angelina | Other
Palo Pinto | Other | Austin | Other
Panola | Other | Bastrop | Other
Parker | Other | Bowie | Other
Polk | Other | Brazoria | Other
Rains | Other | Brazos | Other
Red River | Other | Burleson | Other
Robertson | Other | Caldwell | Other
Rockwall | Other | Camp | Other
Rusk | Other | Cass | Other
Sabine | Other | Chambers | Other
San Augustine | Other | Cherokee | Other
San Jacinto | Other | Colorado | Other
San Saba | Other | Delta | Other
Shelby | Other | Falls | Other
Smith | Other | Fannin | Other
Somervell | Other | Fayette | Other
Stephens | Other | Fort Bend | Other
Tarrant | Other | Franklin | Other
Titus | Other | Freestone | Other
Trinity | Other | Galveston | Other
Tyler | Other | Gregg | Other
Upshur | Other | Grimes | Other
Van Zandt | Other | Hardin | Other
Walker | Other | Harris | Other
Wise | Other | Harrison | Other
Wood | Other | Henderson | Other
Atascosa | Other | Hopkins | Other
Austin | Other | Houston | Other
Bandera | Other | Hunt | Other
Bastrop | Other | Jackson | Other
Bee | Other | Jasper | Other
Bexar | Other | Jefferson | Other
Blanco | Other | Kaufman | Other
Brooks | Other | Lamar | Other
Burleson | Other | Lavaca | Other
Burnet | Other | Lee | Other
Caldwell | Other | Leon | Other
Colorado | Other | Liberty | Other
Comal | Other | Limestone | Other
DeWitt | Other | Madison | Other
Dimmit | Other | Marion | Other
Duval | Other | Matagorda | Other
Edwards | Other | Milam | Other
Fayette | Other | Montgomery | Other
Fort Bend | Other | Morris | Other
Frio | Other | Nacogdoches | Other
Gillespie | Other | Navarro | Other
Goliad | Other | Newton | Other
Gonzales | Other | Orange | Other
Guadalupe | Other | Panola | Other
Hardin | Other | Polk | Other
Harris | Other | Rains | Other
Hays | Other | Red River | Other
Hidalgo | Other | Robertson | Other
Jackson | Other | Rockwall | Other
Jim Hogg | Other | Rusk | Other
Jim Wells | Other | Sabine | Other
Karnes | Other | San Augustine | Other
Kendall | Other | San Jacinto | Other
Kerr | Other | Shelby | Other
Kimble | Other | Smith | Other
Kinney | Other | Titus | Other
La Salle | Other | Trinity | Other
Lavaca | Other | Tyler | Other
Lee | Other | Upshur | Other
Liberty | Other | Van Zandt | Other
Live Oak | Other | Walker | Other
Llano | Other | Waller | Other
Mason | Other | Washington | Other
Maverick | Other | Wharton | Other
McCulloch | Other | Wood | Other
McMullen | Other | Aransas | Other
Medina | Other | Atascosa | Other
Milam | Other | Bee | Other
Montgomery | Other | Bexar | Other
Real | Other | Brooks | Other
Starr | Other | Calhoun | Other
Travis | Other | Cameron | Other
Uvalde | Other | DeWitt | Other
Victoria | Other | Dimmit | Other
Waller | Other | Duval | Other
Washington | Other | Frio | Other
Webb | Other | Goliad | Other
Wharton | Other | Gonzales | Other
Williamson | Other | Guadalupe | Other
Wilson | Other | Hidalgo | Other
Zapata | Other | Jim Hogg | Other
Zavala | Other | Jim Wells | Other
Andrews | Other | Karnes | Other
Archer | Other | Kenedy | Other
Baylor | Other | Kinney | Other
Borden | Other | Kleberg | Other
Brewster | Other | La Salle | Other
Callahan | Other | Live Oak | Other
Clay | Other | Maverick | Other
Coke | Other | McMullen | Other
Coleman | Other | Medina | Other
Concho | Other | Nueces | Other
Cottle | Other | Refugio | Other
Crane | Other | San Patricio | Other
Crockett | Other | Starr | Other
Culberson | Other | Uvalde | Other
Dawson | Other | Victoria | Other
Ector | Other | Webb | Other
El Paso | Other | Willacy | Other
Fisher | Other | Wilson | Other
Foard | Other | Zapata | Other
Gaines | Other | Zavala | Other
Garza | Other | Archer | West
Glasscock | Other | Baylor | West
Hardeman | Other | Borden | West
Haskell | Other | Callahan | West
Howard | Other | Clay | West
Hudspeth | Other | Coke | West
Irion | Other | Coleman | West
Jeff Davis | Other | Concho | West
Jones | Other | Crockett | West
Kent | Other | Fisher | West
King | Other | Glasscock | West
Knox | Other | Haskell | West
Loving | Other | Howard | West
Lynn | Other | Irion | West
Martin | Other | Jones | West
Menard | Other | Knox | West
Midland | Other | Martin | West
Mitchell | Other | Menard | West
Nolan | Other | Mitchell | West
Pecos | Other | Nolan | West
Presidio | Other | Reagan | West
Reagan | Other | Runnels | West
Reeves | Other | Schleicher | West
Runnels | Other | Scurry | West
Schleicher | Other | Shackelford | West
Scurry | Other | Sterling | West
Shackelford | Other | Stonewall | West
Sterling | Other | Sutton | West
Stonewall | Other | Taylor | West
Sutton | Other | Throckmorton | West
Taylor | Other | Tom Green | West
Terrell | Other | Val Verde | West
Terry | Other | Wichita | West
Throckmorton | Other | Wilbarger | West
Tom Green | Other | Armstrong | West
Upton | Other | Bailey | West
Val Verde | Other | Briscoe | West
Ward | Other | Carson | West
Wichita | Other | Castro | West
Wilbarger | Other | Childress | West
Winkler | Other | Cochran | West
Yoakum | Other | Collingsworth | West
Young | Other | Cottle | West
Armstrong | Panhandle | Crosby | West
Bailey | Panhandle | Dallam | West
Briscoe | Panhandle | Dawson | West
Carson | Panhandle | Deaf Smith | West
Castro | Panhandle | Dickens | West
Childress | Panhandle | Donley | West
Cochran | Panhandle | Floyd | West
Collingsworth | Panhandle | Foard | West
Crosby | Panhandle | Garza | West
Dallam | Panhandle | Gray | West
Deaf Smith | Panhandle | Hale | West
Dickens | Panhandle | Hall | West
Donley | Panhandle | Hansford | West
Floyd | Panhandle | Hardeman | West
Gray | Panhandle | Hartley | West
Hale | Panhandle | Hemphill | West
Hall | Panhandle | Hockley | West
Hansford | Panhandle | Hutchinson | West
Hartley | Panhandle | Kent | West
Hemphill | Panhandle | King | West
Hockley | Panhandle | Lamb | West
Hutchinson | Panhandle | Lipscomb | West
Lamb | Panhandle | Lubbock | West
Lipscomb | Panhandle | Lynn | West
Lubbock | Panhandle | Moore | West
Moore | Panhandle | Motley | West
Motley | Panhandle | Ochiltree | West
Ochiltree | Panhandle | Oldham | West
Oldham | Panhandle | Parmer | West
Parmer | Panhandle | Potter | West
Potter | Panhandle | Randall | West
Randall | Panhandle | Roberts | West
Roberts | Panhandle | Sherman | West
Sherman | Panhandle | Swisher | West
Swisher | Panhandle | Terry | West
Wheeler | Panhandle | Wheeler | West

## Background
CDR Report Background
The main purpose of the CDR is to provide forecasted Planning Reserve Margins by season and year. The Planning Reserve Margin represents the percentage of resource capacity, in excess of firm electricity demand, available to cover uncertainty in future demand, generator availability and new resource supply. Firm demand accounts for load reductions available through interruptible load programs controlled by ERCOT as well as incremental load reductions from rooftop solar systems. The methodologies used to develop Planning Reserve Margins and other elements of the CDR are outlined in the ERCOT Nodal Protocols, Section 3.2.6 (See https://www.ercot.com/mktrules/nprotocols/current). ERCOT's load forecasts are based on normal weather conditions and determined by the methodologies described in the methodology documents posted to the Load Forecast webpage, https://www.ercot.com/gridinfo/load/forecast. The CDR also conforms to requirements for resource adequacy reporting specified by the Public Utility Commission of Texas in their Substantive Rules, §25.505(b).
Resource data comes from generation capacity developers (Interconnecting Entities, IEs) and owners as reported in ERCOT's Resource Integration and Ongoing Operations (RIOO) system, as well as other data collection mechanisms described in the ERCOT Nodal Protocols.
Note that the CDR is not intended for characterizing the risk of capacity scarcity conditions from a real-time operations perspective.
ELCC Background
What is an Effective Load Carrying Capability?
- ELCC measures the effectiveness of a resource type—wind, solar and battery energy storage—in maintaining a resource portfolio’s reliability level over a given period. Reliability is measured as the expected frequency of loss-of-load (LOL) events, where an event represents an hourly period when rotating load shed is necessary to maintain overall grid reliability. The availability of the resource type when LOL events are more likely to occur determines the ELCC. ELCC is not a direct measure of generation output available for a given period, but rather an indicator of the expected reliability benefit of the capacity for the given period.
- ELCCs estimated for the CDR reflect the resource reliability benefit for a given multi-hour "risk period" rather than an individual hour. The reason is that loss-of-load events can span multiple hours, which makes it impractical to calculate ELCCs for just a given hour.
Why has ERCOT changed its method for calculating the capacity contribution of wind and solar resources?
- ELCCs estimated for wind, solar and battery energy storage—Inverter Based Resources, or IBRs—are now being used for ERCOT’s CDR. ELCCs replace a methodology whereby average historical wind and solar capacity availability is estimated for a sample of the highest peak load hours during past seasons. This prior approach fails to account for the expected reliability impacts of increasing wind and solar penetration, resulting in reserve margins that belie the increased reliability risk for these intermittent resources. Importantly, the ELCC method aligns the CDR with how IBRs are represented in the probabilistic simulation model to be used to support analysis for the Texas Public Utility Commission’s new Reliability Standard.
How are ELCCs Estimated?
- A resource type’s ELCC is gauged against so-called “perfect capacity,” which is hypothetical generation capacity that is available 100% of the time when the capacity is needed. For example, a wind ELCC of 25% means that the resource portfolio’s wind capacity is only 25% as effective as perfect capacity in maintaining the portfolio’s reliability level for the given period. The associated ELCC capacity is the ELCC percentage multiplied by the resource type’s aggregate installed capacity in megawatts (MW). - ELCCs are determined by running a probabilistic reliability model for a future year. The model produces many reliability outcomes for the forecast year based on simulating grid conditions with variations in load and resource availabilities. ELCCs account for a resource type’s average reliability contribution across all the simulation outcomes. The basic process for estimating ELCCs is as follows: 1. The future-year resource portfolio is first modified to meet a reliability level based on the reliability criteria established for a prevailing reliability standard. 2. All the capacity for the resource type is then removed and replaced with perfect capacity until the reliability level is again reached based on simulation results. (The perfect capacity is a gas turbine plant with a zero-percent outage rate). 3. The final step is to divide the perfect capacity added by the capacity of the resource type removed. The result is the ELCC percentage. ELCCs will aways be less than 100%.
- ELCC study reports are available in the "Wind, Solar and Energy Storage Resources" | ERCOT's Resource Adequacy webpage
Key Attributes of ELCCs:
- Annual ELCCs can be decomposed into values for shorter periods. ERCOT’s ELCCs are estimated by year, season, and daily risk period (afternoon and evening for non-winter months; morning, afternoon, and evening for winter months.)
- ELCCs decline as more of the resource type is added to the resource portfolio. When there is not much of the resource type installed on the grid, its capacity yields a high ELCC. However, adding more capacity dilutes the reliability benefit of the existing and new capacity, thereby lowering the ELCC. This effect is most dramatic for solar capacity. At low penetration levels, solar has a large reliability benefit in the afternoon when solar output is at its highest. As more solar is added, the risk of reliability issues is then pushed into the evening hours when solar generation drops and becomes much less effective at maintaining reliability. Solar ELCCs decrease sharply for the evening risk period, but also decrease for the afternoon.
- ELCCs for a resource type account for the joint reliability impacts of other portfolio resources and the grid conditions modeled. Resource diversity can have benefits for maintaining a given portfolio reliability level. For example, the combination of solar and battery energy storage can provide a combined ELCC greater than adding the ELCCs estimated separately for these resource types. This synergistic reliability effect is captured by running simulations designed to isolate the incremental ELCC increase of the combined solar/battery resource portfolio. ELCCs also reflect all modeled grid conditions that impact the timing, length and magnitude of LOL events.
- ELCCs are unique for a given set of portfolio resources, load forecasts, and other modeling assumptions. ELCCs typically need to be re-estimated as resource portfolios and other grid attributes affecting reliability change. To minimize the frequency of needed updates, a library of ELCCs has been developed based on a range of future resource-type combinations and load levels. This library development approach supports ELCCs calculated for the range of planning reserve margin periods reported in the CDRs.
- ELCCs for battery energy storage systems (BESSs) are estimated for a range of design durations. BESS ELCCs are impacted by system duration; the longer the duration, the higher the ELCC, not accounting for the “diminishing returns” effect of adding more BESS capacity to the resource portfolio. Estimating BESS-duration ELCCs is more complicated than estimating them for wind and solar capacity, requiring both probabilistic modeling and a separate model to estimate all the reliability impacts of these systems.
ELCCs Values used in this CDR
- The ELCC tab in the CDR report contains the wind, solar and battery energy storage Effective Load Carrying Capability (ELCC) values used for Planning Reserve Margin calculations. ELCC values are disaggregated by time periods: forecast year, season and applicable reserve risk period. Unlike the summer and winter seasons, there currently isn't sufficient LOL events surfaced by the probabilistic reliability simulation model for the spring and fall seasons to provide meaningfully distinct ELCCs. Therefore, ELCCs for the winter evenings are used as proxies for the spring season, and summer afternoon ELCCs are used as proxies for the fall.
ELCC tab