## Slide 1
STEC Ammonia Plant Load Regional Planning Group Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
January 21, 2026

## Slide 2: Overview
STEC submitted the Ammonia Plant Load Project for Regional Planning Group (RPG) review in May 2025
    This Tier 2 STEC proposed project submission was estimated to cost $65.47 million and will require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues due to proposed load additions in Victoria County in the Coast Zone

## Slide 3: Project Need
ERCOT’s independent review verified reliability planning criteria violations in Victoria County in the Coast Weather Zone
System improvement is needed to meet reliability planning criteria
Contingency Category | Voltage Violations | Thermal Violations | Unsolved Power Flow
N-0 (P0) | None | None | None
N-1 (P1, P2-1, P7) | None | None | None
G-1+N-1 (P3)* | 24 | 8 | None
X-1+N-1 (P6-2)** | None | None | None
*G-1 Generator tested: Victoria Port Units, Formosa Units
**X-1 Transformers tested: Coleto Creek – Ckt 1

## Slide 4: Comparison of Project Options
ERCOT analyzed eight options and short-listed four options
Among the four short-listed options, Option 1 addresses the reliability violations, is the least expensive option, improves long-term load-serving capability, and requires the least amount of CCN miles
ERCOT recommends Option 1 as the preferred option and reclassified the project as a Tier 1 Project
STEC’s initial cost estimate did not include AEP’s increased capability requirement for the 138-kV transmission rebuild and the increased cost associated with recent tariff changes
*Cost estimates were provided by the TSPs
 | Option 1 | Option 2 | Option 2A | Option 5
Addresses the Project Needs | Yes | Yes | Yes | Yes
Meets ERCOT and NERC Reliability Criteria | Yes | Yes | Yes | Yes
Improves Long-Term Load-Serving Capability | Yes (Best) | Yes | Yes | Yes
CCN Required (~miles) | Yes (11.1) | Yes (23.0) | Yes (22.6) | Yes (11.4)
Construction Feasibility (Based on TSP assessment) | Yes | Yes | Yes | Yes
Capital Cost Estimates* (~$M) | 117.38 | 117.52 | 132.38 | 154.54

## Slide 5: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 1 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 1 did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 1 to address reliability issues in Victoria County in the Coast Weather Zone
TSPs expect to implement the upgrades by June 2028
Estimated Capital Cost: $117.38 million
  CCN filling will be required to:
    Construct the new 138-kV single-circuit line from Dupont Switching station to the new large load and the removal of the double-circuit section of the Victoria Plant to Shepley and Victoria Plant to Dupont 138-kV circuits

## Slide 9: ERCOT Recommendation
Connect the new large load confirmed by Transmission Service Provider (TSP) Attestation Letter to AEP’s 138-kV Dupont Switching station via a 138-kV transmission line, with normal and emergency ratings of at least 427 MVA and 478 MVA, respectively, which will require a new ROW, approximately 3.4-mile;
Rebuild the existing Victoria Plant to Shepley to Dupont 138-kV transmission line with normal and emergency ratings of at least 485 MVA, approximately 7.66-mile;
Rebuild the existing Victoria Plant to Dupont 138-kV transmission line ckt2 with normal and emergency ratings of at least 485 MVA, approximately 7.66-mile;
Remove the double-circuit section of the Victoria Plant to Shepley and Victoria Plant to Dupont circuits (by rebuilding the two circuits on separate structures) to eliminate the NERC P7/ERCOT_1 (common tower outage) events. This would require a new ROW;

## Slide 10: ERCOT Recommendation
Rebuild the existing Formosa to Joslin 138-kV transmission line with normal and emergency ratings of at least 485 MVA, approximately 2.41-mile; and
Rebuild the existing Tungsten to Vistron to Black Bayou to Big Three to Dupont 138-kV transmission line with normal and emergency ratings of at least 485 MVA, approximately 21.11-mile.

## Slide 11: ERCOT Recommendation