## Slide 1: Large Load Interconnection Batch Study Workshop Draft Framework
February 3, 2026

## Slide 2: Disclaimer
All information included in this presentation is preliminary and subject to change
The PGRR115 process is still in effect and the timing of the transition to a Batch Study process is to be determined
This presentation is conceptual in nature and many of the details will be further refined and specified in revision requests

## Slide 3: Agenda
Process flow overview
Introduction and context for LLI process redesign
Overview of end-state batch process (batches 1+)
Overview of Batch Zero (Zero A and Zero B)
Batch timing and sequencing
Other core considerations arising from interviews and LLWG discussions
2
Next steps
Key upcoming process dates
3
1
Key insights emerging from stakeholder interviews
Review of stakeholder interviews process
High-level areas of broad agreement and divergence based on stakeholder input
Open Q&A
4

## Slide 4: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
Next steps

## Slide 5: Batch Study Process Background
Currently, the transmission adequacy studies for new Large Load Interconnection (LLI) requests are conducted individually by Transmission Service Providers (TSPs)
This approach has resulted in the need to restudy some LLI requests one or more times due to outdated study assumptions as other requests in the area meet milestones to be considered “must study” loads. Restudies have created uncertainty and risk for developers and have slowed the process to interconnect
ERCOT is engaging with stakeholders on the development of a new ERCOT-led Batch Study process before presenting the framework to the PUCT at its February 20, 2026, Open Meeting

## Slide 6: Integration of stakeholder insights into process redesign
How each takeaway is reflected
Stakeholder interview takeaways
Focus page(s)
Shift from sequential LLIs to ERCOT-led batch studies
Redesigned process to revolve around batch study principle
1
5, 8
Coupling between load studies and transmission planning
Developed a seamless integration plan for new process within existing RTP/RPG procedures
2
9, 44-45
Transparency and status visibility across the process
Predictable timelines matter more than favorable outcomes
Laid out an explicit steady state timeline, by study step, from early 2027 through mid 2029
Integrated stakeholder input throughout redesign
Dashboard to provide regular communications and status updates to ILLEs/TSPs
3
26-27
Acceptance of partial, ramped, or conditional load
High appetite for BYOG and CLR if treated appropriately
Developing new rules to specifically address the unique needs and system-impacts of CLR and BYOG loads in batches 1+
4
38-41
Screening and commitment to filter speculative load
5
15-24
Fragmented ownership before ERCOT involvement
Defined a clear end-to-end flow with named responsibilities and time horizons for ILLEs, TSPs, and ERCOT
6
30-33
Relied on guidance provided in proposed PUCT rules in Projects 58480 and 58481, where possible

## Slide 7: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
Next steps

## Slide 8: Preliminary batch study process overview
Developer / TSP action
ERCOT batch process
Other ERCOT action
RPG
Deposit required (SB61)
Approval to energize
Box widths roughly correlate with relative duration of each step
Planning forecast
Dev. input and initial screening
ERCOT case building
Allocate & commit
Batch study
RPG
A
QSA
Committed load added to baseline for next batch
B
C
D
E
F
G
A
Developer input and initial screening studies
Developers submit interconnection requests and required information to relevant T(D)SPs, which in turn perform preliminary analysis before submitting all information to ERCOT to include in batch studies; developers meet SB6 entry requirements1
B
ERCOT annual planning forecast
ERCOT builds full forward-looking model of system through next 6+ years, including both large (>75 MW) and small loads
Planning forecast + new large load requests form baseline for each batch’s case building
C
ERCOT case building
ERCOT defines set of variables and parameters to run batch studies (Steady State and Stability) based on latest planning forecast and loads that have successfully entered the batch
D
Batch study
ERCOT performs a Steady State study and Stability screening2 using parameters defined in case building to assess how much load the system can reliably serve and where; each study considers 3 scenarios across 5 study years for 15 total “cases”
Pre-study inputs
Study / modeling
E
Allocate and commit
ERCOT notifies T(D)SPs and developers of load allocation and expected Tx upgrades, ramping over following 5 years; developers have limited timeframe to decline or meet SB6 commitment requirements1 to accept
F
RPG (Regional Planning Group)
Stakeholders comment on Tx upgrades and align on actual transmission build plan
Post-study outputs
G
QSA (Quarterly Stability Assessment)
ERCOT studies stability and reliability of full grid at regular intervals; loads must meet requirements ~5-8 months before actual energization
To be laid out in PUCT rule 58481
Steady State and Stability Studies are focused on transmission adequacy, i.e., this is not intended to be an assessment of resource adequacy

## Slide 9: ERCOT / TSP / Developer actions throughout batch study process
ERCOT
TSP
Developer (Interconnecting Large Load Entity – ILLE)
Start of batch process
First possible energization date
Developer notified if in batch
Developer notified of load allocation
Case building
Study
Already completed for Batch Zero
Illustrative
QSA
RPG
Initial studies for screening (optional)
Gather materials, submit to TSP
Pre-study inputs
Study / modeling
Post-study outputs
Respond to allocation
Submit upgrades to RPG
Provide additional input when / if requested
RPG
Build planning forecast (for batches starting in Q1)
Active role
Passive / waiting role
Develop project
Develop project1
1. Actual development timeline will vary by project; developers with higher risk tolerance may begin sooner if desired
Deposit required
ERCOT and TSPs both take part in RPG
Construct transmission
RTP

## Slide 10: Ongoing Batch Study Scope and Process
Key Design Considerations
Study should ensure loads can be reliably connected
Study should provide clear expectations for ILLEs regarding allocated load levels by year
Scope
Year 1-Year 5 Summer Peak and Year 1-Year 5 Summer Net Peak
  N-1, select G-1+N-1, select X-1+N-1, select N-1-1
Year 1-Year 5 Fall Peak
  Maintenance outage (N-1-1)
Process
Condition cases
  Update transmission and generation
  Add LLI requests
Perform contingency analysis and decrease consumption for LLI requests for constraints for which they have a >=X% harming shift factor until the constraints are resolved
Perform stability screening analysis and decrease consumption for LLI requests until constraints are resolved
Communicate results to impacted TSPs
In coordination with impacted TSPs, identify transmission upgrade projects
Communicate:
  To each ILLE to communicate allocated load limits by year through Year 6
  Confidential report for TSPs listing identified transmission upgrade projects and associated LLI requests

## Slide 11: Year 6 Considerations
In ERCOT, transmission projects are typically completed in six years or less
Larger, long-lead time transmission projects, like new Right of Way transmission lines, require more analysis that is better suited for the Regional Transmission Plan and/or a Regional Planning Group review
Therefore, for Batch Studies, ERCOT will:
  Not identify new Right of Way or long-lead time transmission upgrade projects;
  Assume that all Large Load requested consumption can be served by Year 6; and
  Allocate the full requested consumption for the Large Load request for Year 6

## Slide 12: Ongoing Batch Study Timeline Considerations
Key Design Considerations
In interviews, most stakeholders expressed a preference for multiple Batch Studies to be run in a year. A six-month cadence was often mentioned
Tradeoffs
To complete a Batch Study process in six months, several tradeoffs need to be made
Commitment Time
For the next Batch (Batch N+1), ERCOT needs to know the commitment (via “interconnection agreement”) of LLI requests from the current Batch (Batch N) so that transmission capacity is not reallocated
To allow for case building and study time, a one-month commitment time is necessary
An alternative would be to allow for a longer commitment time, extending the Batch Study process in proportion
Stability Studies
Full stability analysis would take ~5 months to complete. Since stability analysis cannot begin until initial steady state analysis has been completed, full stability analysis does not fit into a six-month Batch Study process
ERCOT will perform a stability screening analysis to identify potential stability limitations. This necessarily means using conservative assumptions, which may yield false positive stability limitations
ERCOT will perform full stability analysis to meet NERC FAC-002 compliance after the Batch Study has been completed but before the QSA
An alternative would be to perform full stability analysis in the Batch Study process, but this would lengthen the study time to ~9 months
Transmission Upgrade Project Identification
Identification of upgrade projects to resolve found transmission constraints is limited by the study timeline. It is possible that with a longer study time, more transmission upgrade solutions could be identified

## Slide 13: Ongoing Batch Study Timeline
Activity | Timeline 1 | Timeline 2
Case Conditioning | January 1 – April 1 | July 1 – October 1
Deadline for LLI request to meet entry requirements | January 15 | July 15
Study and Load Allocation | April 1 – July 15 | October 1 – January 15
Communicate Results | July 31 | January 31
Deadline for ILLE to meet 58481 interconnection agreement requirements for load allocation to be firm in the next Batch | August 31 | February 28
ILLE has one month from when the report is issued to meet commitment requirements

## Slide 14: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
Next steps

## Slide 15: Batch Zero is a bridge between existing and new processes
Current process
Batch 1+
Batch Zero
Existing LLI process
  Singular case-by-case study process
  Frequent restudies due to lack of capacity “reservation” capability
  Created a 250+ GW backlog that now must be addressed
Transitional process
  Only for loads already in the interconnection process: some loads to be considered firm, some to require restudies
  2-phase Batch Study approach based on energization date
Fully redesigned batch study process
  Batch studies every 6 months
  All loads must meet 58481 criteria to qualify for studying
  Outcome of study is reserved capacity and allocated ramping schedule for loads and transmission upgrades
Deep dive follows

## Slide 16: Batch Zero A and Zero B qualification and anticipated capacity studied
Chart: 
 | 36.063 | 36.063
 | 8.2 | 8.2
 | 30.6 | 30.6
 | 8.2 | 8.2
 | 38.2
 | 59.6
94
Zero A
94
Zero B1
141 (47 new)
239 (98 new)
Batch Zero max capacity by sub-batch, GW
Maximum load scenario; assumes all ~39 GW of firm load from Zero A passes 58481 criteria and all ~8 GW of assessed load from Zero A gets allocated
Loads that have not been assessed by Batch Zero B must manually reapply for Batch 1
SS = Steady State
Loads that meet only “intermediate requirements” of 58481 are not considered firm and will be restudied
Load allocation assessment criteria
  Has approved SS3 study as of 1/28/26…
  AND is expected to energize on or before 6/30/27
  Has SS3 and/or stability study submitted to ERCOT by 1/28/26…
  AND meets 58481 "intermediate agreement" requirements prior to start of Batch Zero B
2026 Baseline
Other firm load
Allocation Assessed
Firm load qualification criteria
  2026 planning forecast plus…
  Is operational or approved to energize
  Has already moved through the LLI study process in the past, i.e.,:
  2026 planning forecast plus…
  Firm load from Batch Zero A that meets 58481 interconnection agreement criteria
  Approved allocation of loads from Batch Zero A that meet 58481 interconnection agreement criteria
  Loads exempted from the interim LLI process and included in an RPG or RTP study and did not meet criteria for inclusion in Batch Zero A4
1
2
3
4
2
4
1
3
Study outcomes
  Load allocation for 2027 only
  No transmission upgrades identified
  Allocation dependent on loads meeting 58481 interconnection agreement criteria
  Load allocation for 2027-2032
  Identified transmission upgrades to be reviewed by RPG, if needed
  Loads that have not been assessed by Batch Zero B must reapply for Batch 1
    Exempt from the interim LLI process and included in an RPG or RTP study
    OR met interim LLI process criteria (approved SS3 study and IA) for not needing restudy by 12/15/25
    OR met PGRR115 process criteria (PG 9.4 and 9.5) for not needing restudy by 1/28/26
Some load may not be allocated
5
5

## Slide 17: Batch Zero Timing Considerations
QSA timings and regulatory guidance impact energization timing for Batch Zero and beyond
QSA start date
Feb 1, 2026
May 1, 2026
Aug 1, 2026
Nov 1, 2026
Feb 1, 2027
Initial energization
Q3 2026
Q4 2026
Q1 2027
Q2 2027
Q3 2027
Impact on interconnection timing
For requests with an initial energization date in 2026, studies and agreements must have been completed through the existing PGRR115 process
Requests with an initial energization date in Q2 2027 or earlier that have not completed all studies and agreements will go through Batch Zero A study process, to be completed in Q2 2026
Requests with an initial energization date in Q3 2027 or later or requests with a prior initial energization date that have not completed agreements will go through Batch Zero B study process, to be completed by Q1 2027
Regulatory guidance
Final release date of PUCT implementation guidance for SB6 (rule 58481) is yet to be announced
Proposed Batch Zero B is linked to 58481, so timing is difficult to establish in the interim
May 1, 2027
Q4 2027

## Slide 18: Inclusion Criteria for Batch Zero A
If your Large Load project | Treatment of your project in Batch Zero A | Approximate MWs in this category*
Is Operational or Approved to Energize | Included and not subject to assessment of load allocation, i.e. load is firm | 8,223 MW
Was exempt from the interim LLI process and was included in an RPG or RTP study with a requested an energization date before October 1, 2027 | Included and not subject to assessment of load allocation, i.e. load is firm | 17,437 MW
Met the criteria (approved steady state study and signed interconnection agreement) to be designated "must study" under the interim LLI process before December 15, 2025 | Included and not subject to assessment of load allocation, i.e. load is firm | 4,666 MW
Fulfilled the requirements in Planning Guide 9.4 (all LLIS studies complete) and PG 9.5 (agreements, financial security, notice to proceed) before January 28, 2026 | Included and not subject to assessment of load allocation, i.e. load is firm | 8,471 MW
Has requested an energization date on or before June 30, 2027 and has a steady state study approved before January 28, 2026 | Included and subject to assessment of load allocation | 8,224 MW
Started the LLI study process but does not meet the above criteria | Not included | 59,411 MW
Was exempt from the interim LLI process and was included in an RPG or RTP study with a requested an energization date on after October 1, 2027 | Not included | 38,211 MW
Has a LLI number but has not started the study process | Not included | 139,252 MW
* Based on information submitted to ERCOT as of January 29, 2026

## Slide 19: Inclusion Criteria for Batch Zero B
If your Large Load project | Treatment of your project in Batch Zero B | Approximate MWs in this category*
Is Operational or Approved to Energize | Included and not subject to assessment of load allocation, i.e. load is firm | 8,223 MW
Was included in Batch Zero A regardless of whether the project was subject to reallocation | Included and not subject to assessment of load allocation (firm) if project meets 58481 “interconnection agreement” requirements before the start of Batch Zero B Included and subject to assessment of load allocation if project meets 58481 “intermediate agreements” requirements before the start of Batch Zero B Not included if project does not meet either above requirement | Up to** 38,798 MW
Was exempt from the interim LLI process and was included in an RPG or RTP study and did not meet criteria for inclusion in Batch Zero A | Included and not subject to assessment of load allocation (firm) if project meets 58481 “interconnection agreement” requirements before the start of Batch Zero B Included and subject to assessment of load allocation if project meets 58481 “intermediate agreements” requirements before the start of Batch Zero B Not included if project does not meet either above requirement | Up to** 38,211 MW
Was not included in Batch Zero A and has a TSP steady state or stability study submitted to ERCOT by January 28, 2026 and meets the 58481 “intermediate agreement” requirements before start of Batch Zero B | Included and subject to assessment of load allocation | Up to** 59,579 MW
Does not meet the above requirements | Not included | 139,252 MW
* Based on information submitted to ERCOT as of January 29, 2026
** ERCOT is unable to predict the number of projects that will meet the indicated milestones by the start of Batch Zero B

## Slide 20: Inclusion Criteria for Batch Zero B – Additional Notes
Inclusion of LLI requests for Batch Zero B will depend on meeting the criteria set out in PUCT rule 58481 (currently in draft)
As a result, inclusion in Batch Zero A will not guarantee inclusion in Batch Zero B if there is no commitment from the ILLE
Further, loads that were not subject to reassessment of load allocation in Zero A may be subject to reassessment of load allocation in Zero B if they do not meet the necessary requirements set out in 58481

## Slide 21: Batch Zero A Study Scope and Process
Key Design Considerations
Study should ensure “subject to load allocation” loads can be reliably connected
Study should be completed in an expeditious manner due to requested energization dates
Timeline does not allow for study of later years or identification of potential transmission upgrade projects
Scope
2027 Summer Peak and 2027 Summer Net Peak
  N-1, select G-1+N-1, select X-1+N-1, select N-1-1
2027 Fall Peak Maintenance outage (N-1-1)
Process
Condition cases
  Update transmission and generation
  Identify and add Large Loads that meet “firm” or “subject to load allocation” criteria
  Identify and remove Large Loads that do not meet “firm” or “subject to load allocation” criteria
Perform steady state contingency analysis and decrease consumption for “subject to load allocation” Large Loads for constraints for which they have a >=X% harming shift factor until the constraints are resolved
Communicate the 2027 allocated load limits to each ILLE
  Load limits for later years will be communicated as part of Batch Zero B but will not decrease from 2027 limits

## Slide 22: Batch Zero A Timeline
Activity | Timeline
Case Conditioning | February – March 31
Study and Load Allocation | April 1 – May 29
Communicate Results | June 15
Deadline for ILLE to meet 58481 interconnection agreement requirements for load allocation to be firm in Batch Zero B | August 1
Note: Because ERCOT is not performing stability analysis for Batch Zero A, TSPs will need to complete the LLIS stability study before a LLI request in Batch Zero A would be allowed to enter a QSA

## Slide 23: Batch Zero B Study Scope and Process
Key Design Considerations
Study should ensure “subject to load allocation” loads can be reliably connected
Study should provide clear expectations for ILLEs regarding allocated load levels by year
Scope
2027-31 Summer Peak and 2027-31 Summer Net Peak
  N-1, select G-1+N-1, select X-1+N-1, select N-1-1
2027-31 Fall Peak
  Maintenance outage (N-1-1)
Process
Condition cases
  Update transmission and generation
  Identify and add Large Loads that meet “firm” or “subject to load allocation” criteria
  Identify and remove Large Loads that do not meet “firm” or “subject to load allocation” criteria
Perform contingency analysis and decrease consumption for “subject to load allocation” Large Loads for constraints for which they have a >=X% harming shift factor until the constraints are resolved
Perform stability screening analysis and decrease consumption for “subject to load allocation” Large Loads until constraints are resolved
Communicate results to impacted TSPs
In coordination with impacted TSPs, identify transmission upgrade projects
Communicate:
  ILLE allocated load limits by year through 2032
  Confidential report for TSPs listing identified transmission upgrade projects and associated LLI requests

## Slide 24: Batch Zero B Timeline
Activity | Timeline
Case Conditioning | June 1 – September 1
Deadline for LLI request to meet 58481 intermediate agreement requirements | August 1
Study and Load Allocation | September 1 – December 31
Communicate Results | January 15
Deadline for ILLE to meet 58481 interconnection agreement requirements for load allocation to be firm in Batch 1 | February 28

## Slide 25: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
Next steps

## Slide 26: Design, Approval, and Implementation Timeline for Batches Zero A and Zero B
1/22 LLWG
2/3 Workshop
2/12 Workshop
2/20 PUCT Open Meeting
PUCT
Approval

## Slide 27: Detailed Batches 1-3 Study Timeline

## Slide 28: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
  LLI request considerations
  Study methodology detail
  Modifications to other processes
Next steps

## Slide 29: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
  LLI request considerations
  Study methodology detail
  Modifications to other processes
Next steps

## Slide 30: LLI Request Information
Key Design Considerations
ERCOT needs certain information from the interconnecting TSP and from ILLE in order to perform a Batch Study
Some ILLEs may choose to not move forward with a LLI request if the load allocation is below a certain threshold
Some LLI requests may be developed in discrete blocks, while others may not
Information ERCOT needs from TSP
Point of Interconnection
POI model information (.idv’s and associated contingencies)
LLI request “intermediate agreement” and “interconnection agreement” (see PUCT 58481 rulemaking) status
Information ERCOT needs from ILLE
Peak load
Dynamic model data and associated information
Ramp schedule
Minimum load allocation for a viable project
Load block size(s), if applicable
CLR information, if applicable
Co-located generation information, if applicable

## Slide 31: Information Flow (Option 1: TSP is liaison to ERCOT for ILLE)
Request Interconnection
Provide LLI Information
Process Request
Identify POI
Provide LLI Information
Request LLI Number Assignment
Perform Batch Study
Assess “Intermediate Agreement” Status
Allocate Load
Communicate Load Allocation to ILLE
Interconnection Agreement
Assess “Interconnection Agreement” Status
Update Planning Forecast
Assign LLI Number
Intermediate Agreement
TSP
ILLE
ERCOT

## Slide 32: Information Flow (Option 2: ILLE has direct relationship with ERCOT)
Identify POI
Assess “Interconnection Agreement” Status
Assess “Intermediate Agreement” Status
TSP
Interconnection Agreement
Request Interconnection
Provide LLI Information
Intermediate Agreement
ILLE
Allocate Load
Communicate Load Allocation to ILLE
Update Planning Forecast
Process Request
Assign LLI Number
Perform Batch Study
ERCOT

## Slide 33: Other TSP Requirements
Before interconnection agreement
Within Batch Study
Screening study (optional?)
Subsynchronous Oscillation (SSO) screening study
Short circuit study
Facilities study
Transmission upgrade project ideation and feasibility
Any other studies TSPs deem necessary for their own purposes

## Slide 34: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
  LLI request considerations
  Study methodology detail
  Modifications to other processes
Next steps

## Slide 35: Methodology for Addition of Generation to Study Cases
Key Design Considerations
Most planning cases do not have sufficient generation meeting Planning Guide Section 6.9(1) criteria for addition to the cases
ERCOT will need to add generation to the Batch Study cases to balance the load additions
The Batch Study process is focused on transmission system security and is not a resource adequacy assessment
Methodology
ERCOT plans to use the PGRR127, Addition of Proposed Generation to the Planning Models, methodology for adding generation to the study cases
PGRR127 is expected to be approved by the ERCOT Board in February and the PUCT in March
The relevant language in PGRR127 states (Section 6.9(5)):
ERCOT may include large generator projects that have not met all of the requirements of paragraph (1) above in the base cases created and maintained by SSWG to ensure that sufficient generation is available to meet the demand in the base cases. These large generator projects may be added to the base cases in the following order until the demand is met:
(a) Large generator projects with “Planned” status that meet the conditions of paragraph (1) of Section 5.2.1 and have a signed SGIA submitted by the TSP via the online RIOO system;
(b) Large generator projects with “Planned” status that meet the conditions of paragraph (1) of Section 5.2.1 and have completed the FIS;
(c) Large generator projects with “Planned” status that meet the conditions of paragraph (1) of Section 5.2.1, have not completed the FIS, and:
  (i) Have completed the steady-state and stability studies of the FIS;
  (ii) Have completed the steady-state study of the FIS;
  (iii) Have started the FIS;
(d) Large generator projects with “Inactive” status that meet the conditions of paragraphs (a), (b), or (c) above that have completed FIS stability studies, with the most recently inactivated projects to be included first; and
(e) Additional generation outside of the interconnection queue based on ERCOT’s discretion.

## Slide 36: Methodology for Allocating Load
Key Design Considerations
When projected transmission system constraints prevent all the load requests in an area from being reliably served, ERCOT needs a methodology to “allocate” the load
Powerflow software tools can automate allocation using a load maximization approach based on the physical constraints of the transmission system. This is also an equitable solution
Other, non-physics-based approaches may require manual work that could make a six-month Batch Study process unachievable
Some loads have minimum allocation amounts or discrete block sizes
Methodology
Make all Large Load requests “dispatchable” in the case
Assign a dispatch cost to the loads such that generation is first dispatched to resolve the constraint and loads are not dispatched for constraints for which they have less than X% shift factor
  All loads in a Batch will receive the same dispatch cost
Run Security Constrained Optimal Power Flow (SCOPF) to minimize cost; i.e. dispatch (allocate) loads
Iteratively identify transmission upgrade projects to increase load allocation
Remove any loads dispatched below their minimum allocation level and round down to the next lowest block size for loads with discrete blocks
Run final SCOPF and assign load allocation
Example
LLI A
100 MW
5% sf
Trans Constraint
50 MW Overloaded
LLI B
500 MW
25% sf
To relieve the 50 MW overload, SCOPF will dispatch LLI B to 300 MW:
50 MW /0.25 = 200 MW
500-200 = 300 MW
Load allocation:
LLI A = 100 MW
LLI B = 300 MW

## Slide 37: Load Allocation – Additional Notes
Load allocation will be by year
  If a subsequent study year has a lower load allocation for a LLI request, the previous years’ allocation will be reduced. For example, if the results show 200 MW in 2028, 200 MW in 2029, and 150 MW in 2030, 2028 and 2029 allocations will be set to 150 MW
  As noted earlier, Year 6 load allocation will be for the full requested amount
Load allocation cannot be reduced in subsequent Batches if the LLI request meets the interconnection agreement requirements prior to the start of the next Batch
  However, if the LLI request does not meet the interconnection agreement requirements, the load allocation is forfeited
Load allocation is not a guarantee that the load will be served in real-time. Emergencies and other situations may arise that require the load to be shed, the same as for any other load on the system
Load above the allocated amount may be resubmitted for study in subsequent Batch studies and may receive additional allocations if neighboring loads drop out of the process

## Slide 38: CLR and Co-Located Generation Considerations
The following rules needed for CLRs and LLI requests co-located with new generators need to be in place at the start of a Batch Study. It is unlikely that these rules will be in place for Batch Zero since they need to be codified in the Batch Study revision requests

## Slide 39: Controllable Load Resource Rules
Key Design Considerations
CLR is an existing resource type in ERCOT Protocols
Similar to generators, CLRs can be dispatched down in real-time by ERCOT’s Security Constrained Economic Dispatch tool
Some CLRs can be dispatched to zero load while others have a higher minimum load values
ILLEs registering loads as CLRs still want the transmission system to be planned to serve the full load
ERCOT and CLR entities need clearly defined rules to govern expectations
NPRR1188 (expected late 2026 implementation) provides some but not all rules necessary for allowing specific consideration of CLRs in the Batch Study process
Additional CLR Rules Needed
Offer mitigation or similar concept to ensure high CLR offers don’t result in constraint violations in SCED optimization
Binding agreement and exit conditions so CLRs remain as CLRs until necessary transmission upgrades are complete
CLR Treatment in Batch Studies
LLI request selection of CLR/ not CLR will be binding for the Batch Study
A CLR will be allocated their full load request but may be required to have a minimum load amount assigned in the Batch process
CLR Treatment in Other Studies
CLRs will be modeled at their full requested load in transmission planning studies and the FAC-002 stability study
All TSP studies must consider the full load

## Slide 40: Co-Location with New Generation Rules
Key Design Considerations
New co-located generators can reduce the need for the transmission system to support a new Large Load
There are multiple scenarios regarding how the co-located generation and Large Load interact with the transmission system, each requiring different rules
In some scenarios, new rules are needed to link generation interconnection requests to LLI requests
Scenario 1: Large Load does not consume from the grid – only from the co-located generation
The co-located Large Load will be allocated their full load request
Rules needed to ensure Large Load will never consume from the grid, even momentarily
Rules needed to ensure LLI request and GINR are linked
Scenario 2: Scenario 1 temporarily until transmission upgrades are complete
All Scenario 1 rules apply
A separate study is needed to determine the required transmission upgrades and rules needed to exit no-transmission-system-load status
Scenario 3: Large Load has co-located dispatchable generation and may sometimes consume from the grid
The co-located Large Load will be allocated their full load request except in the G-1+N-1 analysis
Rules needed to ensure LLI request and GINR are linked
Scenario 4: Large Load has co-located intermittent generation and/or energy storage and may sometimes consume from the grid
No specific rules

## Slide 41: Co-Location with Existing Generation Rules
Key Design Considerations
Senate Bill 6 rules may apply for generators existing before September 1, 2025
The transmission system has been planned assuming the existing generation supports the system
Co-Location with existing generation
No specific rules aside from existing requirements in the Protocols (such as an updated Reactive Power study)

## Slide 42: Loads Less Than 75 MW
Loads less than 75 MW will be included in the Batch Studies to the extent they are included in the forecasts. It is important for the planning forecasts to include this load growth.

## Slide 43: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
  LLI request considerations
  Study methodology detail
  Modifications to other processes
Next steps

## Slide 44: Regional Planning Group Process Alignment
Key Design Considerations
A consistent theme in stakeholder interviews was a noted pain point with the existing process regarding the tie between a LLI request Load Commissioning Plan and proposed transmission projects that may change during the RPG review process
The RPG comment process is valuable for gathering stakeholder feedback on proposed transmission upgrade projects
To the extent Batch Study assumptions change, the RPG process can be used to refine transmission upgrade project proposals
Transmission Upgrade Project Process
At the conclusion of a Batch Study, ERCOT will send a confidential report to TSPs listing proposed transmission upgrade projects and associated LLI requests
If all LLI requests associated with a proposed transmission upgrade project meet the interconnection agreement requirements, the TSP will be required to submit the project for RPG review (if required) within X days. ERCOT’s Batch Study may be used as establishing the need for the project for RPG submittal purposes and may also be used as ERCOT’s Independent Review, subject to ERCOT’s concurrence
If a subset of LLI requests associated with a proposed transmission upgrade project meet the interconnection agreement requirements, the TSP will be required to assess the need for the project and, if still needed, submit the project for RPG review (if required) within Y days
Proposed transmission upgrade projects will not be assumed in subsequent Batch Study or RTP base cases until they have received RPG approval, but may be added as proposed upgrade projects
Load Commissioning Plans will no longer be tied to specific transmission upgrade projects due to the changing nature of planning assumptions and upgrade projects

## Slide 45: Regional Transmission Plan Process Alignment
Key Design Considerations
The RTP uses an annual process to satisfy NERC TPL-001-5 requirements
The Batch Study is envisioned to be a six-month process to study the addition of new Large Loads
Upon adoption, for a Large Load to be included in the Planning Forecast, it must meet the interconnection agreement requirements from PUCT rule 58481, meaning the RTP will not include Large Loads that have not gone through a Batch Study (except for those deemed firm in Batch Zero)
Both the RTP and Batch Study will identify transmission upgrade projects
RTP-Batch Study Alignment
ERCOT does not envision requirements to ensure transmission upgrade projects proposed in the RTP or Batch Study will be consistent, but would implement processes to align outcomes as a matter of practice

## Slide 46: Contents
Introduction and context
Future batch process flow
Transitional process (Batch Zero)
Anticipated timeline
Other key considerations
Next steps

## Slide 47: Next Steps – Impacts on current Large Load process
As the dates and details of the Batch Study process presented at today’s workshop are preliminary, the current Large Load interconnection process remains in effect
Requests to interconnect new Large Loads to the ERCOT system should still follow the process described in Section 9 of the ERCOT Planning Guide
ERCOT will provide additional details at a later date about when the transition away from this process will begin

## Slide 48: Next steps
Date
Event
Notes
February 6
PUCT Open Meeting
Update
February 9-10
Board of Directors
Overview
February 12
Workshop
Final draft framework
February 20
PUCT Open Meeting
Proposed batch study framework
February 5 (end of day)
Online survey responses due;
Comments due to LLWG_Feedback@ercot.com
February 3
Survey released (Market Notice)
One response per organization

## Slide 49: Questions?