## Slide 1: Large Load Interconnection Batch Study Workshop Feedback Review and Next Steps
February 12th, 2026

## Slide 2: Agenda
4
Next steps
  Expectations for Revision Request development
2
Review of stakeholder feedback received
  Stakeholder survey results​
  Stakeholder feedback received through open comments window​
1
Update on 2/6 PUCT Open Meeting
  Update on PUCT's guidance given during the 2/6 Open Meeting
  Review of new timeline and approach
3
ERCOT feedback on key market topics
  Review of ERCOT's proposed approach on a subset of key feedback topics
Addressed in a separate presentation

## Slide 3: Contents
Update on 2/6 PUCT Open Meeting
ERCOT feedback on key market topics
Next steps
Appendix: Feb 3, 2026 Workshop proposal of LLI Batch Study process
(noting concepts such as Batch 0a / Batch 0b are no longer valid)
3

## Slide 4: Guidance from 2/6/2026 PUC Open Meeting*
PUCT provided guidance to develop the transitional Batch Zero process within the current ERCOT Stakeholder process rather than through a Good Cause Exception
  This decision effectively removes the Batch Zero A/Zero B option from consideration
ERCOT stakeholders were strongly encouraged to have Revision Request(s) developed for Batch Zero for June 2026 ERCOT Board consideration
  BYOG details can be considered in parallel Revision Request(s) (if developed in time)
  CLR details can be considered in parallel Revision Request(s) (if developed in time)
PGRR115 process remains in effect (where some Large Load customers will continue forward and be approved, while others continue with the risk of re-study delays)
* Link to PUCT broadcast: https://www.adminmonitor.com/tx/puct/open_meeting/20260206/
4

## Slide 5: The critical path to a successful Batch Zero NPRR relies on a series of successive May 2026 votes
Forums
Workshops and working groups
PRS (Protocols Review Subcommittee)
ROS1 (Reliability and Operations Subcommittee)
TAC
ERCOT Board
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 2/12
Workshop #4 Mar TBD
Workshop #5 Mar TBD
Workshop #6 Apr TBD
Workshop #8 May TBD
PRS Update 3/11
PRS Vote 5/13
ROS Update 3/5
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
8/1 Target effective date of protocols
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
Preview structure/governing concepts of Batch Zero NPRR before filing
Confirm proposed protocol changes are ready for governance review
Endorse NPRR for advancement to TAC (contingent on technical valid.)
If accompanying PGRR filed, then ROS will be involved in review
ROS approval will be required for any PGRR(s).
Review/endorse combined NPRR/PGRR package for Board approval
Authorize implementation of Batch Zero by approval of NPRR/PGRRs
LLWG 2/19
Workshop #3 Late Feb
TAC Vote 5/20
1. May be unneccessary if the Revision Request ends up utilizing only a NPRR and not an additional PGRR
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Target Board approval date
Board Meeting 4/20
PRS Update 4/15
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr TBD
Note that TAC leadership is also considering options to ensure successful review and approval.

## Slide 6: Contents
Update on 2/6 PUCT Open Meeting
ERCOT feedback on key market topics
Next steps
Appendix: Feb 3, 2026 Workshop proposal of LLI Batch Study process
6

## Slide 7
ERCOT feedback on key feedback received from Feb 3 Workshop
7
15
TSP study sequencing and responsibilities
8
16
Deposits, cost allocation, and dropouts
9
17
Submitted vs. approved dates/TSP-driven delays
10
18
Transparency and publishing
11
19
Load allocation methodology
12
20
Good-cause exception
1
Batch Zero cutoff dates
8
2
Energization timeline assumptions
9
3
CLR1/BYOG2/co-located generation rules
10-11
4
RTP/RPG alignment and firm energization
12
5
Eligibility for Batch Zero, IA3, and financial gates
13
6
Stability model quality and screening
14
Batch Zero
Process
Technical
Classification
Page
Page
Source: Batch Study Process for Large Load Interconnections Workshop, Feb 3rd 2026
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework
1 Controllable Load Resource | 2 Bring Your Own Generation | 3. Interconnection Agreement

## Slide 8: Batch Zero cutoff snapshot dates
ERCOT feedback
Key stakeholder input
1
Batch Zero A and Zero B dates are no longer in play. Going forward, ERCOT will carefully consider stakeholder feedback shared during and after the Feb 3 workshop and how they align with:
PUCT Project Nos. 58480 and 58481​
Senate Bill 6 ​
Stakeholders questioned whether retroactive snapshot dates unfairly invalidate completed work and create winners and losers based on timing rather than project readiness
Batch Zero
Process
Technical
Classification
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 9: Energization timeline assumptions
ERCOT feedback
2
With the pivot away from Batch Zero A and Batch Zero B to a single Batch Zero, the energization date cut-off shared in the Feb 3 workshop is no longer valid and ERCOT will run studies for all energization dates.
June-2027 energization cutoff may not align with realistic 18–24-month construction timelines following Batch Zero A results, potentially disadvantaging projects that submitted credible in-service dates relative to those with more aggressive schedules
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 10: CLR1/BYOG2/co-located generation rules (1/2)
ERCOT feedback
3
ERCOT views the treatment of Controllable Load Resources (CLRs) and the proper handling of Large Loads proposed concurrently with generation interconnection requests as two separate issues
​
For CLRs, ERCOT intends to file Revision Requests to:
Allow a Large Load to declare its intent to register as a CLR and be treated accordingly in the Batch process
Create a binding framework that would require the Large Load to register as a CLR once operational and remain a CLR until defined exit conditions are met
Include updated SCED methodology to ensure the CLR is dispatched to resolve constraints in real-time operations
Define how CLRs are reflected in other planning assessments to ensure transmission is ultimately built to serve these Large Loads
Stakeholders noted that CLR/BYOG rules are not fully finalized and asked how such loads will be treated, modeled, or voluntarily committed during the interim period
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework
1 Controllable Load Resource | 2 Bring Your Own Generation

## Slide 11: CLR1/BYOG2/co-located generation rules (2/2)
ERCOT feedback
3
For Loads proposing to concurrently build new generation to serve some or all the requested demand (BYOG), ERCOT intends to file separate Revision Requests to:
Create a definition that captures the technical requirements needed for some or all of a Large Load to “never” be seen or served by the grid
Define the scenarios that still must be assessed in the Batch and other planning studies (would depend on the type and amount of generation)
Define the allowed modes of participation in the market for the generation with the potential for defined exit criteria
Establish rules preventing the energization of a Large Load studied with new co-located generation until that generation is operational, with the potential for energization of equal amounts of Load as the generation is commissioned
Note: ERCOT plans to develop CLR and BYOG concepts in 2 separate Revision Requests that will align with the main Batch Zero Revision Requests. The intent is to move all Revision Requests forward on the same timeline if possible
Stakeholders noted that CLR/BYOG rules are not fully finalized and asked how such loads will be treated, modeled, or voluntarily committed during the interim period
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework
1 Controllable Load Resource | 2 Bring Your Own Generation

## Slide 12: RTP/RPG alignment and firm energization
ERCOT feedback
4
ERCOT understands this concern and is still considering options
Certainty is a common goal
Stakeholders sought clarity on how batch MW allocations translate into firm energization when required upgrades remain subject to RTP/RPG review and sequencing
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 13: Eligibility for Batch Zero, IA, and financial gates
ERCOT feedback
5
Although Batch Zero A and Zero B concept and dates are no longer in play, ERCOT will carefully consider criteria shared in the Feb 3 workshop and how they align with:
PUCT Project Nos. 58480 and 58481​
Senate Bill 6 ​
Other factors already shared​
Stakeholders requested clearer, batch-specific criteria for inclusion and firmness, including what qualifies as an Interconnection Agreement and when financial security is required
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 14: Stability model quality and screening
ERCOT feedback
6
Stability models for Large Loads are required for it to be included in the Batch
Dynamic model and DWG large load data survey (for LEL) are required
A PGRR will be submitted soon to update requirements for providing dynamic data and model quality tests. Model quality tests must demonstrate their capability to meet performance requirements
​
Stability Screening
  The key stability concern for Large Load additions is voltage stability
  The stability screening will assess the impact of added Large Loads during the Batch process using P-V analysis to ensure sufficient voltage stability margin
  Subsequent stability analysis results will not reduce the MW allocation
Stakeholders questioned whether stability screening could later reduce MW allocations after projects plan around initial results, and asked for clarity on model quality and validation
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 15: TSP study sequencing and responsibilities
ERCOT feedback
7
ERCOT is working closely with TSPs to consider future division of responsibilities, timing, and feasibility of this approach
Stakeholders asked where TSP-led screening, short-circuit, stability, and facility studies fit in the six-month batch timeline and who is accountable for each step
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 16: Deposits, cost allocation, and dropouts
ERCOT feedback
8
Who pays for transmission upgrades?​
Senate Bill 6 directs the PUCT to evaluate transmission cost allocation methods and to establish large load interconnections standards that include financial commitments for the development of transmission infrastructure needed to serve a large load customer
The PUCT is addressing the transmission cost allocation directive in Project No. 58484 and the large load interconnection standards directive in Project No. 58481
How are deposits for transmission upgrades addressed in the process?​
In the Project No. 58481 second Discussion Draft, the PUCT has explored the refundability of financial commitments, such as a dollar per MW security posting and security for significant equipment or services, and contribution in aid of construction
What happens to MW allocations if a project drops out?​
ERCOT is considering whether, when, and how to reallocate MW if a large load customer withdraws or is otherwise canceled
Stakeholders raised questions about who pays for transmission upgrades, how deposits are treated, and what happens to MW allocations if projects drop out
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 17: Submitted vs. approved dates/TSP-driven delays
ERCOT feedback
9
ERCOT considered approval dates as an objective metric that was representative of progress through the current process.
ERCOT will carefully consider feedback on the criteria shared in the Feb 3 workshop and how they align with:
PUCT Project Nos. 58480 and 58481​
Senate Bill 6 ​
Other factors already shared​
Stakeholders asked why approval dates are used as eligibility gates when timing often reflects ERCOT or TSP processing backlogs rather than developer readiness
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 18: Transparency and publishing
ERCOT feedback
10
ERCOT agrees there needs to be a single source of information available to the involved parties ranging from date-certain activities in the batch process to status of individual projects
As an interim solution, ERCOT is considering how to share periodic status reports with TSPs that can then be shared with Large Load customers
As a long-term solution, ERCOT has initiated development of a self-serve portal for submitting required information and observing the status of projects in ERCOT’s Large Load interconnection process
Stakeholders asked for greater visibility into batch participation, study status, decision timing, and milestones, while recognizing confidentiality constraints
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 19: Load allocation methodology
ERCOT feedback
11
Generally, ERCOT believes load allocation within a batch when constraints exist will be based on the impact that each Large Load customer has on the constraints
Stakeholders requested a clearer explanation of how ERCOT allocates MW under thermal, voltage, and stability constraints, and the role of engineering judgment versus rules
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 20: Good-cause exception
ERCOT feedback
12
As discussed earlier, PUCT guidance is to pursue a Batch Study approach through Revision Request instead of a Good Cause Exception
Stakeholders asked for examples and guardrails around the use of a good-cause exception, including who decides, how it is applied, and how stakeholders can engage
Batch Zero
Process
Technical
Classification
Key stakeholder input
Note: This section summarizes key feedback themes raised during the initial workshop and outlines ERCOT’s preliminary considerations in response. It does not represent a final determination or an endorsed decision framework

## Slide 21: Contents
Update on 2/6 PUCT Open Meeting
ERCOT feedback on key market topics
Next steps
Appendix: Feb 3, 2026 Workshop proposal of LLI Batch Study process
21

## Slide 22: The critical path to a successful Batch Zero NPRR relies on a series of successive May 2026 votes
Forums
Workshops and working groups
PRS (Protocols Review Subcommittee)
ROS1 (Reliability and Operations Subcommittee)
TAC
ERCOT Board
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 2/12
Workshop #4 Mar TBD
Workshop #5 Mar TBD
Workshop #6 Apr TBD
Workshop #8 May TBD
PRS Update 3/11
PRS Vote 5/13
ROS Update 3/5
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
8/1 Target effective date of protocols
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
Preview structure/governing concepts of Batch Zero NPRR before filing
Confirm proposed protocol changes are ready for governance review
Endorse NPRR for advancement to TAC (contingent on technical valid.)
If accompanying PGRR filed, then ROS will be involved in review
ROS approval will be required for any PGRR(s).
Review/endorse combined NPRR/PGRR package for Board approval
Authorize implementation of Batch Zero by approval of NPRR/PGRRs
LLWG 2/19
Workshop #3 Late Feb
TAC Vote 5/20
1. May be unneccessary if the Revision Request ends up utilizing only a NPRR and not an additional PGRR
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Target Board approval date
Board Meeting 4/20
PRS Update 4/15
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr TBD
Note that TAC leadership is also considering options to ensure successful review and approval.

## Slide 23: Contents
Update on 2/6 PUCT Open Meeting
ERCOT feedback on key market topics
Next steps
Appendix: Feb 3, 2026 Workshop proposal of LLI Batch Study process
23

## Slide 24: Appendix
Appendix: Feb 3, 2026 Workshop proposal of LLI Batch Study process
(noting concepts such as Batch 0a / Batch 0b are no longer valid)
24

## Slide 25: Regional Transmission Plan Process Alignment
Key Design Considerations
The RTP uses an annual process to satisfy NERC TPL-001-5 requirements
The Batch Study is envisioned to be a six-month process to study the addition of new Large Loads
Upon adoption, for a Large Load to be included in the Planning Forecast, it must meet the interconnection agreement requirements from PUCT rule 58481, meaning the RTP will not include Large Loads that have not gone through a Batch Study (except for those deemed firm in Batch Zero)
Both the RTP and Batch Study will identify transmission upgrade projects
RTP-Batch Study Alignment
ERCOT does not envision requirements to ensure transmission upgrade projects proposed in the RTP or Batch Study will be consistent, but would implement processes to align outcomes as a matter of practice

## Slide 26: Batch Study Process Background
Currently, the transmission adequacy studies for new Large Load Interconnection (LLI) requests are conducted individually by Transmission Service Providers (TSPs)
This approach has resulted in the need to restudy some LLI requests one or more times due to outdated study assumptions as other requests in the area meet milestones to be considered “must study” loads. Restudies have created uncertainty and risk for developers and have slowed the process to interconnect
ERCOT is engaging with stakeholders on the development of a new ERCOT-led Batch Study process before presenting the framework to the PUCT at its February 20, 2026, Open Meeting

## Slide 27: Integration of stakeholder insights into process redesign
How each takeaway is reflected
Stakeholder interview takeaways
Focus page(s)1
Shift from sequential LLIs to ERCOT-led batch studies
Redesigned process to revolve around batch study principle
1
5, 8
Coupling between load studies and transmission planning
Developed a seamless integration plan for new process within existing RTP/RPG procedures
2
9, 44-45
Transparency and status visibility across the process
Predictable timelines matter more than favorable outcomes
Laid out an explicit steady state timeline, by study step, from early 2027 through mid 2029
Integrated stakeholder input throughout redesign
Dashboard to provide regular communications and status updates to ILLEs/TSPs
3
26-27
Acceptance of partial, ramped, or conditional load
High appetite for BYOG and CLR if treated appropriately
Developing new rules to specifically address the unique needs and system-impacts of CLR and BYOG loads in batches 1+
4
38-41
Screening and commitment to filter speculative load
5
15-24
Fragmented ownership before ERCOT involvement
Defined a clear end-to-end flow with named responsibilities and time horizons for ILLEs, TSPs, and ERCOT
6
30-33
Relied on guidance provided in proposed PUCT rules in Projects 58480 and 58481, where possible
1. From original document, which can be found on the ERCOT website at https://www.ercot.com/calendar/02032026-Batch-Study-Process-for

## Slide 28: ERCOT / TSP / Developer actions throughout batch study process
ERCOT
TSP
Developer (Interconnecting Large Load Entity – ILLE)
Start of batch process
First possible energization date
Developer notified if in batch
Developer notified of load allocation
Case building
Study
Already completed for Batch Zero
Illustrative
QSA
RPG
Initial studies for screening (optional)
Gather materials, submit to TSP
Pre-study inputs
Study / modeling
Post-study outputs
Respond to allocation
Submit upgrades to RPG
Provide additional input when / if requested
RPG
Build planning forecast (for batches starting in Q1)
Active role
Passive / waiting role
Develop project
Develop project1
1. Actual development timeline will vary by project; developers with higher risk tolerance may begin sooner if desired
Deposit required
ERCOT and TSPs both take part in RPG
Construct transmission
RTP

## Slide 29: Ongoing Batch Study Scope and Process
Key Design Considerations
Study should ensure loads can be reliably connected
Study should provide clear expectations for ILLEs regarding allocated load levels by year
Scope
Year 1-Year 5 Summer Peak and Year 1-Year 5 Summer Net Peak
  N-1, select G-1+N-1, select X-1+N-1, select N-1-1
Year 1-Year 5 Fall Peak
  Maintenance outage (N-1-1)
Process
Condition cases
  Update transmission and generation
  Add LLI requests
Perform contingency analysis and decrease consumption for LLI requests for constraints for which they have a >=X% harming shift factor until the constraints are resolved
Perform stability screening analysis and decrease consumption for LLI requests until constraints are resolved
Communicate results to impacted TSPs
In coordination with impacted TSPs, identify transmission upgrade projects
Communicate:
  To each ILLE to communicate allocated load limits by year through Year 6
  Confidential report for TSPs listing identified transmission upgrade projects and associated LLI requests

## Slide 30: Year 6 Considerations
In ERCOT, transmission projects are typically completed in six years or less
Larger, long-lead time transmission projects, like new Right of Way transmission lines, require more analysis that is better suited for the Regional Transmission Plan and/or a Regional Planning Group review
Therefore, for Batch Studies, ERCOT will:
  Not identify new Right of Way or long-lead time transmission upgrade projects;
  Assume that all Large Load requested consumption can be served by Year 6; and
  Allocate the full requested consumption for the Large Load request for Year 6

## Slide 31: Ongoing Batch Study Timeline Considerations
Key Design Considerations
In interviews, most stakeholders expressed a preference for multiple Batch Studies to be run in a year. A six-month cadence was often mentioned
Tradeoffs
To complete a Batch Study process in six months, several tradeoffs need to be made
Commitment Time
For the next Batch (Batch N+1), ERCOT needs to know the commitment (via “interconnection agreement”) of LLI requests from the current Batch (Batch N) so that transmission capacity is not reallocated
To allow for case building and study time, a one-month commitment time is necessary
An alternative would be to allow for a longer commitment time, extending the Batch Study process in proportion
Stability Studies
Full stability analysis would take ~5 months to complete. Since stability analysis cannot begin until initial steady state analysis has been completed, full stability analysis does not fit into a six-month Batch Study process
ERCOT will perform a stability screening analysis to identify potential stability limitations. This necessarily means using conservative assumptions, which may yield false positive stability limitations
ERCOT will perform full stability analysis to meet NERC FAC-002 compliance after the Batch Study has been completed but before the QSA
An alternative would be to perform full stability analysis in the Batch Study process, but this would lengthen the study time to ~9 months
Transmission Upgrade Project Identification
Identification of upgrade projects to resolve found transmission constraints is limited by the study timeline. It is possible that with a longer study time, more transmission upgrade solutions could be identified

## Slide 32: Ongoing Batch Study Timeline
Activity | Timeline 1 | Timeline 2
Case Conditioning | January 1 – April 1 | July 1 – October 1
Deadline for LLI request to meet entry requirements | January 15 | July 15
Study and Load Allocation | April 1 – July 15 | October 1 – January 15
Communicate Results | July 31 | January 31
Deadline for ILLE to meet 58481 interconnection agreement requirements for load allocation to be firm in the next Batch | August 31 | February 28
ILLE has one month from when the report is issued to meet commitment requirements

## Slide 33: Batch Zero is a bridge between existing and new processes
Current process
Batch 1+
Batch Zero
Existing LLI process
  Singular case-by-case study process
  Frequent restudies due to lack of capacity “reservation” capability
  Created a 250+ GW backlog that now must be addressed
Transitional process
  Only for loads already in the interconnection process: some loads to be considered firm, some to require restudies
  2-phase Batch Study approach based on energization date
Fully redesigned batch study process
  Batch studies every 6 months
  All loads must meet 58481 criteria to qualify for studying
  Outcome of study is reserved capacity and allocated ramping schedule for loads and transmission upgrades
Deep dive follows

## Slide 34: Batch Zero A and Zero B qualification and anticipated capacity studied
Chart: 
 | 36.063 | 36.063
 | 8.2 | 8.2
 | 30.6 | 30.6
 | 8.2 | 8.2
 | 38.2
 | 59.6
94
Zero A
94
Zero B1
141 (47 new)
239 (98 new)
Batch Zero max capacity by sub-batch, GW
Maximum load scenario; assumes all ~39 GW of firm load from Zero A passes 58481 criteria and all ~8 GW of assessed load from Zero A gets allocated
Loads that have not been assessed by Batch Zero B must manually reapply for Batch 1
SS = Steady State
Loads that meet only “intermediate requirements” of 58481 are not considered firm and will be restudied
Load allocation assessment criteria
  Has approved SS3 study as of 1/28/26…
  AND is expected to energize on or before 6/30/27
  Has SS3 and/or stability study submitted to ERCOT by 1/28/26…
  AND meets 58481 "intermediate agreement" requirements prior to start of Batch Zero B
2026 Baseline
Other firm load
Allocation Assessed
Firm load qualification criteria
  2026 planning forecast plus…
  Is operational or approved to energize
  Has already moved through the LLI study process in the past, i.e.,:
  2026 planning forecast plus…
  Firm load from Batch Zero A that meets 58481 interconnection agreement criteria
  Approved allocation of loads from Batch Zero A that meet 58481 interconnection agreement criteria
  Loads exempted from the interim LLI process and included in an RPG or RTP study and did not meet criteria for inclusion in Batch Zero A4
1
2
3
4
2
4
1
3
Study outcomes
  Load allocation for 2027 only
  No transmission upgrades identified
  Allocation dependent on loads meeting 58481 interconnection agreement criteria
  Load allocation for 2027-2032
  Identified transmission upgrades to be reviewed by RPG, if needed
  Loads that have not been assessed by Batch Zero B must reapply for Batch 1
    Exempt from the interim LLI process and included in an RPG or RTP study
    OR met interim LLI process criteria (approved SS3 study and IA) for not needing restudy by 12/15/25
    OR met PGRR115 process criteria (PG 9.4 and 9.5) for not needing restudy by 1/28/26
Some load may not be allocated
5
5

## Slide 35: Batch Zero Timing Considerations
QSA timings and regulatory guidance impact energization timing for Batch Zero and beyond
QSA start date
Feb 1, 2026
May 1, 2026
Aug 1, 2026
Nov 1, 2026
Feb 1, 2027
Initial energization
Q3 2026
Q4 2026
Q1 2027
Q2 2027
Q3 2027
Impact on interconnection timing
For requests with an initial energization date in 2026, studies and agreements must have been completed through the existing PGRR115 process
Requests with an initial energization date in Q2 2027 or earlier that have not completed all studies and agreements will go through Batch Zero A study process, to be completed in Q2 2026
Requests with an initial energization date in Q3 2027 or later or requests with a prior initial energization date that have not completed agreements will go through Batch Zero B study process, to be completed by Q1 2027
Regulatory guidance
Final release date of PUCT implementation guidance for SB6 (rule 58481) is yet to be announced
Proposed Batch Zero B is linked to 58481, so timing is difficult to establish in the interim
May 1, 2027
Q4 2027

## Slide 36: Inclusion Criteria for Batch Zero A
If your Large Load project | Treatment of your project in Batch Zero A | Approximate MWs in this category*
Is Operational or Approved to Energize | Included and not subject to assessment of load allocation, i.e. load is firm | 8,223 MW
Was exempt from the interim LLI process and was included in an RPG or RTP study with a requested an energization date before October 1, 2027 | Included and not subject to assessment of load allocation, i.e. load is firm | 17,437 MW
Met the criteria (approved steady state study and signed interconnection agreement) to be designated "must study" under the interim LLI process before December 15, 2025 | Included and not subject to assessment of load allocation, i.e. load is firm | 4,666 MW
Fulfilled the requirements in Planning Guide 9.4 (all LLIS studies complete) and PG 9.5 (agreements, financial security, notice to proceed) before January 28, 2026 | Included and not subject to assessment of load allocation, i.e. load is firm | 8,471 MW
Has requested an energization date on or before June 30, 2027 and has a steady state study approved before January 28, 2026 | Included and subject to assessment of load allocation | 8,224 MW
Started the LLI study process but does not meet the above criteria | Not included | 59,411 MW
Was exempt from the interim LLI process and was included in an RPG or RTP study with a requested an energization date on after October 1, 2027 | Not included | 38,211 MW
Has a LLI number but has not started the study process | Not included | 139,252 MW
* Based on information submitted to ERCOT as of January 29, 2026

## Slide 37: Inclusion Criteria for Batch Zero B
If your Large Load project | Treatment of your project in Batch Zero B | Approximate MWs in this category*
Is Operational or Approved to Energize | Included and not subject to assessment of load allocation, i.e. load is firm | 8,223 MW
Was included in Batch Zero A regardless of whether the project was subject to reallocation | Included and not subject to assessment of load allocation (firm) if project meets 58481 “interconnection agreement” requirements before the start of Batch Zero B Included and subject to assessment of load allocation if project meets 58481 “intermediate agreements” requirements before the start of Batch Zero B Not included if project does not meet either above requirement | Up to** 38,798 MW
Was exempt from the interim LLI process and was included in an RPG or RTP study and did not meet criteria for inclusion in Batch Zero A | Included and not subject to assessment of load allocation (firm) if project meets 58481 “interconnection agreement” requirements before the start of Batch Zero B Included and subject to assessment of load allocation if project meets 58481 “intermediate agreements” requirements before the start of Batch Zero B Not included if project does not meet either above requirement | Up to** 38,211 MW
Was not included in Batch Zero A and has a TSP steady state or stability study submitted to ERCOT by January 28, 2026 and meets the 58481 “intermediate agreement” requirements before start of Batch Zero B | Included and subject to assessment of load allocation | Up to** 59,579 MW
Does not meet the above requirements | Not included | 139,252 MW
* Based on information submitted to ERCOT as of January 29, 2026
** ERCOT is unable to predict the number of projects that will meet the indicated milestones by the start of Batch Zero B

## Slide 38: Inclusion Criteria for Batch Zero B – Additional Notes
Inclusion of LLI requests for Batch Zero B will depend on meeting the criteria set out in PUCT rule 58481 (currently in draft)
As a result, inclusion in Batch Zero A will not guarantee inclusion in Batch Zero B if there is no commitment from the ILLE
Further, loads that were not subject to reassessment of load allocation in Zero A may be subject to reassessment of load allocation in Zero B if they do not meet the necessary requirements set out in 58481

## Slide 39: Batch Zero A Study Scope and Process
Key Design Considerations
Study should ensure “subject to load allocation” loads can be reliably connected
Study should be completed in an expeditious manner due to requested energization dates
Timeline does not allow for study of later years or identification of potential transmission upgrade projects
Scope
2027 Summer Peak and 2027 Summer Net Peak
  N-1, select G-1+N-1, select X-1+N-1, select N-1-1
2027 Fall Peak Maintenance outage (N-1-1)
Process
Condition cases
  Update transmission and generation
  Identify and add Large Loads that meet “firm” or “subject to load allocation” criteria
  Identify and remove Large Loads that do not meet “firm” or “subject to load allocation” criteria
Perform steady state contingency analysis and decrease consumption for “subject to load allocation” Large Loads for constraints for which they have a >=X% harming shift factor until the constraints are resolved
Communicate the 2027 allocated load limits to each ILLE
  Load limits for later years will be communicated as part of Batch Zero B but will not decrease from 2027 limits

## Slide 40: Batch Zero A Timeline
Activity | Timeline
Case Conditioning | February – March 31
Study and Load Allocation | April 1 – May 29
Communicate Results | June 15
Deadline for ILLE to meet 58481 interconnection agreement requirements for load allocation to be firm in Batch Zero B | August 1
Note: Because ERCOT is not performing stability analysis for Batch Zero A, TSPs will need to complete the LLIS stability study before a LLI request in Batch Zero A would be allowed to enter a QSA

## Slide 41: Batch Zero B Study Scope and Process
Key Design Considerations
Study should ensure “subject to load allocation” loads can be reliably connected
Study should provide clear expectations for ILLEs regarding allocated load levels by year
Scope
2027-31 Summer Peak and 2027-31 Summer Net Peak
  N-1, select G-1+N-1, select X-1+N-1, select N-1-1
2027-31 Fall Peak
  Maintenance outage (N-1-1)
Process
Condition cases
  Update transmission and generation
  Identify and add Large Loads that meet “firm” or “subject to load allocation” criteria
  Identify and remove Large Loads that do not meet “firm” or “subject to load allocation” criteria
Perform contingency analysis and decrease consumption for “subject to load allocation” Large Loads for constraints for which they have a >=X% harming shift factor until the constraints are resolved
Perform stability screening analysis and decrease consumption for “subject to load allocation” Large Loads until constraints are resolved
Communicate results to impacted TSPs
In coordination with impacted TSPs, identify transmission upgrade projects
Communicate:
  ILLE allocated load limits by year through 2032
  Confidential report for TSPs listing identified transmission upgrade projects and associated LLI requests

## Slide 42: Batch Zero B Timeline
Activity | Timeline
Case Conditioning | June 1 – September 1
Deadline for LLI request to meet 58481 intermediate agreement requirements | August 1
Study and Load Allocation | September 1 – December 31
Communicate Results | January 15
Deadline for ILLE to meet 58481 interconnection agreement requirements for load allocation to be firm in Batch 1 | February 28

## Slide 43: Design, Approval, and Implementation Timeline for Batches Zero A and Zero B
1/22 LLWG
2/3 Workshop
2/12 Workshop
2/20 PUCT Open Meeting
PUCT
Approval

## Slide 44: Detailed Batches 1-3 Study Timeline

## Slide 45: LLI Request Information
Key Design Considerations
ERCOT needs certain information from the interconnecting TSP and from ILLE in order to perform a Batch Study
Some ILLEs may choose to not move forward with a LLI request if the load allocation is below a certain threshold
Some LLI requests may be developed in discrete blocks, while others may not
Information ERCOT needs from TSP
Point of Interconnection
POI model information (.idv’s and associated contingencies)
LLI request “intermediate agreement” and “interconnection agreement” (see PUCT 58481 rulemaking) status
Information ERCOT needs from ILLE
Peak load
Dynamic model data and associated information
Ramp schedule
Minimum load allocation for a viable project
Load block size(s), if applicable
CLR information, if applicable
Co-located generation information, if applicable

## Slide 46: Information Flow (Option 1: TSP is liaison to ERCOT for ILLE)
Request Interconnection
Provide LLI Information
Process Request
Identify POI
Provide LLI Information
Request LLI Number Assignment
Perform Batch Study
Assess “Intermediate Agreement” Status
Allocate Load
Communicate Load Allocation to ILLE
Interconnection Agreement
Assess “Interconnection Agreement” Status
Update Planning Forecast
Assign LLI Number
Intermediate Agreement
TSP
ILLE
ERCOT

## Slide 47: Information Flow (Option 2: ILLE has direct relationship with ERCOT)
Identify POI
Assess “Interconnection Agreement” Status
Assess “Intermediate Agreement” Status
TSP
Interconnection Agreement
Request Interconnection
Provide LLI Information
Intermediate Agreement
ILLE
Allocate Load
Communicate Load Allocation to ILLE
Update Planning Forecast
Process Request
Assign LLI Number
Perform Batch Study
ERCOT

## Slide 48: Other TSP Requirements
Before interconnection agreement
Within Batch Study
Screening study (optional?)
Subsynchronous Oscillation (SSO) screening study
Short circuit study
Facilities study
Transmission upgrade project ideation and feasibility
Any other studies TSPs deem necessary for their own purposes

## Slide 49: Methodology for Addition of Generation to Study Cases
Key Design Considerations
Most planning cases do not have sufficient generation meeting Planning Guide Section 6.9(1) criteria for addition to the cases
ERCOT will need to add generation to the Batch Study cases to balance the load additions
The Batch Study process is focused on transmission system security and is not a resource adequacy assessment
Methodology
ERCOT plans to use the PGRR127, Addition of Proposed Generation to the Planning Models, methodology for adding generation to the study cases
PGRR127 is expected to be approved by the ERCOT Board in February and the PUCT in March
The relevant language in PGRR127 states (Section 6.9(5)):
ERCOT may include large generator projects that have not met all of the requirements of paragraph (1) above in the base cases created and maintained by SSWG to ensure that sufficient generation is available to meet the demand in the base cases. These large generator projects may be added to the base cases in the following order until the demand is met:
(a) Large generator projects with “Planned” status that meet the conditions of paragraph (1) of Section 5.2.1 and have a signed SGIA submitted by the TSP via the online RIOO system;
(b) Large generator projects with “Planned” status that meet the conditions of paragraph (1) of Section 5.2.1 and have completed the FIS;
(c) Large generator projects with “Planned” status that meet the conditions of paragraph (1) of Section 5.2.1, have not completed the FIS, and:
  (i) Have completed the steady-state and stability studies of the FIS;
  (ii) Have completed the steady-state study of the FIS;
  (iii) Have started the FIS;
(d) Large generator projects with “Inactive” status that meet the conditions of paragraphs (a), (b), or (c) above that have completed FIS stability studies, with the most recently inactivated projects to be included first; and
(e) Additional generation outside of the interconnection queue based on ERCOT’s discretion.

## Slide 50: Methodology for Allocating Load
Key Design Considerations
When projected transmission system constraints prevent all the load requests in an area from being reliably served, ERCOT needs a methodology to “allocate” the load
Powerflow software tools can automate allocation using a load maximization approach based on the physical constraints of the transmission system. This is also an equitable solution
Other, non-physics-based approaches may require manual work that could make a six-month Batch Study process unachievable
Some loads have minimum allocation amounts or discrete block sizes
Methodology
Make all Large Load requests “dispatchable” in the case
Assign a dispatch cost to the loads such that generation is first dispatched to resolve the constraint and loads are not dispatched for constraints for which they have less than X% shift factor
  All loads in a Batch will receive the same dispatch cost
Run Security Constrained Optimal Power Flow (SCOPF) to minimize cost; i.e. dispatch (allocate) loads
Iteratively identify transmission upgrade projects to increase load allocation
Remove any loads dispatched below their minimum allocation level and round down to the next lowest block size for loads with discrete blocks
Run final SCOPF and assign load allocation
Example
LLI A
100 MW
5% sf
Trans Constraint
50 MW Overloaded
LLI B
500 MW
25% sf
To relieve the 50 MW overload, SCOPF will dispatch LLI B to 300 MW:
50 MW /0.25 = 200 MW
500-200 = 300 MW
Load allocation:
LLI A = 100 MW
LLI B = 300 MW

## Slide 51: Load Allocation – Additional Notes
Load allocation will be by year
  If a subsequent study year has a lower load allocation for a LLI request, the previous years’ allocation will be reduced. For example, if the results show 200 MW in 2028, 200 MW in 2029, and 150 MW in 2030, 2028 and 2029 allocations will be set to 150 MW
  As noted earlier, Year 6 load allocation will be for the full requested amount
Load allocation cannot be reduced in subsequent Batches if the LLI request meets the interconnection agreement requirements prior to the start of the next Batch
  However, if the LLI request does not meet the interconnection agreement requirements, the load allocation is forfeited
Load allocation is not a guarantee that the load will be served in real-time. Emergencies and other situations may arise that require the load to be shed, the same as for any other load on the system
Load above the allocated amount may be resubmitted for study in subsequent Batch studies and may receive additional allocations if neighboring loads drop out of the process

## Slide 52: CLR and Co-Located Generation Considerations
The following rules needed for CLRs and LLI requests co-located with new generators need to be in place at the start of a Batch Study. It is unlikely that these rules will be in place for Batch Zero since they need to be codified in the Batch Study revision requests

## Slide 53: Controllable Load Resource Rules
Key Design Considerations
CLR is an existing resource type in ERCOT Protocols
Similar to generators, CLRs can be dispatched down in real-time by ERCOT’s Security Constrained Economic Dispatch tool
Some CLRs can be dispatched to zero load while others have a higher minimum load values
ILLEs registering loads as CLRs still want the transmission system to be planned to serve the full load
ERCOT and CLR entities need clearly defined rules to govern expectations
NPRR1188 (expected late 2026 implementation) provides some but not all rules necessary for allowing specific consideration of CLRs in the Batch Study process
Additional CLR Rules Needed
Offer mitigation or similar concept to ensure high CLR offers don’t result in constraint violations in SCED optimization
Binding agreement and exit conditions so CLRs remain as CLRs until necessary transmission upgrades are complete
CLR Treatment in Batch Studies
LLI request selection of CLR/ not CLR will be binding for the Batch Study
A CLR will be allocated their full load request but may be required to have a minimum load amount assigned in the Batch process
CLR Treatment in Other Studies
CLRs will be modeled at their full requested load in transmission planning studies and the FAC-002 stability study
All TSP studies must consider the full load

## Slide 54: Co-Location with New Generation Rules
Key Design Considerations
New co-located generators can reduce the need for the transmission system to support a new Large Load
There are multiple scenarios regarding how the co-located generation and Large Load interact with the transmission system, each requiring different rules
In some scenarios, new rules are needed to link generation interconnection requests to LLI requests
Scenario 1: Large Load does not consume from the grid – only from the co-located generation
The co-located Large Load will be allocated their full load request
Rules needed to ensure Large Load will never consume from the grid, even momentarily
Rules needed to ensure LLI request and GINR are linked
Scenario 2: Scenario 1 temporarily until transmission upgrades are complete
All Scenario 1 rules apply
A separate study is needed to determine the required transmission upgrades and rules needed to exit no-transmission-system-load status
Scenario 3: Large Load has co-located dispatchable generation and may sometimes consume from the grid
The co-located Large Load will be allocated their full load request except in the G-1+N-1 analysis
Rules needed to ensure LLI request and GINR are linked
Scenario 4: Large Load has co-located intermittent generation and/or energy storage and may sometimes consume from the grid
No specific rules

## Slide 55: Co-Location with Existing Generation Rules
Key Design Considerations
Senate Bill 6 rules may apply for generators existing before September 1, 2025
The transmission system has been planned assuming the existing generation supports the system
Co-Location with existing generation
No specific rules aside from existing requirements in the Protocols (such as an updated Reactive Power study)

## Slide 56: Loads Less Than 75 MW
Loads less than 75 MW will be included in the Batch Studies to the extent they are included in the forecasts. It is important for the planning forecasts to include this load growth.

## Slide 57: Regional Planning Group Process Alignment
Key Design Considerations
A consistent theme in stakeholder interviews was a noted pain point with the existing process regarding the tie between a LLI request Load Commissioning Plan and proposed transmission projects that may change during the RPG review process
The RPG comment process is valuable for gathering stakeholder feedback on proposed transmission upgrade projects
To the extent Batch Study assumptions change, the RPG process can be used to refine transmission upgrade project proposals
Transmission Upgrade Project Process
At the conclusion of a Batch Study, ERCOT will send a confidential report to TSPs listing proposed transmission upgrade projects and associated LLI requests
If all LLI requests associated with a proposed transmission upgrade project meet the interconnection agreement requirements, the TSP will be required to submit the project for RPG review (if required) within X days. ERCOT’s Batch Study may be used as establishing the need for the project for RPG submittal purposes and may also be used as ERCOT’s Independent Review, subject to ERCOT’s concurrence
If a subset of LLI requests associated with a proposed transmission upgrade project meet the interconnection agreement requirements, the TSP will be required to assess the need for the project and, if still needed, submit the project for RPG review (if required) within Y days
Proposed transmission upgrade projects will not be assumed in subsequent Batch Study or RTP base cases until they have received RPG approval, but may be added as proposed upgrade projects
Load Commissioning Plans will no longer be tied to specific transmission upgrade projects due to the changing nature of planning assumptions and upgrade projects