## Slide 1
Read-Only EMS in Cloud
Sreenivas Badri
February 19, 2026

## Slide 2: Background – Extended Loss of EMS
As part of enterprise risk assessment, ERCOT identified “extended loss of EMS” as one of key Tier 1 risk. The Texas grid today is vastly different than the grid in 2016, and the complexity to operate the grid is increasing. At the same time, the cyber threat landscape is also increasing. As a result “extended loss of EMS” is being elevated as Tier 1 risk under evolving ERCOT Enterprise Risk Management (ERM) framework.
EMS at ERCOT is designed to have local redundancy at each site. Hardware issues or application issues are often resolved by the automatic redundancy solution in place. In case of a loss of EMS, due to a variety of possible reasons (software, infrastructure or data etc.), ERCOT IT evaluates the fastest recourse to restore EMS. If restoring at the active site is not an option, ERCOT IT will fail over to the redundant site. If the backup site is not available (example Site is being patched) or if the problem extends to the backup site, then IT communicates estimated restoration time to the control room for mitigation actions.
We have defined procedures in place to mitigate loss of EMS at both active and passive sites. ERCOT control room may transfer Frequency control of the grid to a QSE providing regulation and operate in Constant Frequency Control (CFC) mode. In this mode other QSEs hold their generation unless instructed by ERCOT. During this period, no single entity has full visibility of the grid. The process is defined in Nodal Operating Guide 2.2.4.3 – ERCOT loss of AGC.
While we have a lot of redundancy, “extended loss of EMS” is an “unlikely” event, but it is an impactful risk within our Risk Framework. Last time ERCOT went into a Constant Frequency Control (CFC) mode was on 7/7/2016. Frequency Control was given to a QSE.

## Slide 3: Read-Only EMS in Cloud - Objectives and Scope
A small scale “Read-Only EMS” will be deployed in cloud utilizing our cloud infrastructure and make it available to Control Room and Grid Operations. It provides ERCOT control room visibility into grid while a QSE is controlling the frequency when ERCOT enters CFC mode due to EMS being unavailable for extended time.
“Read-Only EMS” will have ICCP, SCADA, state estimator (SE), real-time contingency analysis (RTCA), AGC and study network applications (STNET) etc. EMS applications setup and running.
Read-Only EMS does not provide control capability to control room and EMS applications output, and control signals are not sent to QSEs.
“Read-Only EMS” on cloud includes small scale TSP/QSE ICCP servers, real-time and study EMS servers. Telemetry data feed to Read-Only EMS on Cloud will be set up from on-prem EMS for testing purposes. Periodic software deployments and tests will be performed to ensure that “Read-Only EMS” on cloud is fully operational with the latest production code set.
Control Room and Operations Support staff also can run studies to have visibility into voltage/thermal violations and can work with TOs and QSEs to ensure Grid reliability during extended loss of EMS.
ERCOT Board of Directors approved to build Read-Only EMS solution on Cloud to mitigate this Tier 1 risk.

## Slide 4: Scenarios
This effort shall test the following scenarios to ensure on-prem EMS and Read-Only EMS in Cloud are functional in respective scenarios.
Scenario 1 – ERCOT WAN is up but EMS is down
  In this scenario, Control Room uses “Read-Only EMS in Cloud” and we will Utilize Cloud foundation private network to reroute the WAN traffic to “EMS in Cloud” over dedicated secure connections.
  This scenario does not have hard dependency on market participants system changes.
Scenario 2 – ERCOT WAN is down but EMS is up
  In this scenario, Control Room continue to use on-prem EMS but Bypass WAN by switching to Internet (or any other secure communication methods) for ICCP Telemetry – Nodal Operating Guides section 7.1.(5).
  ERCOT may approve conditional use of other forms of data exchange or communications for exchange of the types of data listed in paragraph (4) above when a WAN Participant loses their connection to the ERCOT WAN. A WAN Participant may use the Internet as a tertiary communication path if the ERCOT WAN and backup communication paths are both unavailable.
  This scenario requires market participants (QSEs/TSPs) ICCP changes and potentially require hardware changes.
Scenario 3 – WAN and EMS are both down
  Control Room uses “Read-Only EMS in Cloud” and we switch to Internet IPs (or any other secure communication methods) for ICCP Telemetry and have QSEs/TSPs to communicate to ICCP/EMS in Cloud over internet using Nodal Operating Guides section 7.1.(5).
  This scenario requires market participants (QSEs/TSPs) ICCP changes and potentially require hardware changes.
ERCOT will have discussions with QSEs/TSPs on alternative communication methods in the event WAN services are not available (for scenario 2 and 3) before developing the solution.

## Slide 5: Implementation Timelines
Currently this effort in Concept phase
Plan to have meetings with QSEs and TSPs and collect their feedback by end of Q1 this year.
  We sent out emails to few QSEs/TSPs this week requesting feedback, plan to setup the meetings starting from next week
Incorporate QSEs/TSPs feedback in project requirements, solution design and complete impact analysis by early Q2 this year.
Initiate the project for implementation – Q2 this year.
Implement Scenario 1 – end of this year
Determine implementation timelines for Scenario 2 and 3 working with QSEs/TSPs – Q3 this year
*** Above timelines are tentative, subject to change based on impact analysis timelines ***

## Slide 6: Questions
Questions / Comments / Feedback