## Slide 1: Large Load Interconnection Batch Study Workshop
February 26th, 2026
Workshop #3
Version 2- Added slides 9 and 38 and minor edits

## Slide 2: Agenda
Update on timeline and key workshop dates
Outline PRS/ROS/TAC pathways to June Board with key submission dates
1
Timeline and governance recap
2
Batch Zero study scope and process overview
Align on core structural elements of the proposed Batch Zero revision request
Batch process overview and final transmission plan
3
Deep-dive on key design elements
Batch Study process overview and final transmission plan
Criteria for Batch Zero
4
Initial discussion on BYOG and CLR
Review propose approaches for BYOG/co-located generation and CLR loads
Discuss timeline for filing NPRR for each
5
Post-meeting survey questions
Identify key questions to be answered for each design element of the revision request (potentially to be addressed through ad-hoc feedback surveys)
6
Q&A
Open forum for Batch Zero concerns, comments, and suggestions
Note: The concepts presented during the February 26, 2026 Workshop are subject to change and further development

## Slide 3: Agenda
Timeline and governance recap
  Batch Zero study scope and process overview
  Deep-dive on key design elements
    Batch Study process overview and final transmission plan
    Criteria for Batch Zero
  Initial discussion on BYOG and CLR (1:30pm-2:30pm)
  Post-meeting survey questions
  Appendix
- Brief walkthrough of ERCOT’s 3 slides - 15-minute Presentation from Sam Brandin (posted powerpoint file) - 15-minute Walkthrough of PUC filing on topic from Arushi Sharma Frank

## Slide 4: The critical path to a successful Batch Zero revision request relies on a series of successive May 2026 votes
Forums
Workshops and working groups
PRS (Protocols Review Subcommittee)
ROS1 (Reliability and Operations Subcommittee)
TAC
ERCOT Board
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Update 3/5
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
8/1 Target effective date of protocols
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
Preview structure/governing concepts of Batch Zero NPRR before filing
Confirm proposed protocol changes are ready for governance review
Endorse NPRR for advancement to TAC (contingent on technical valid.)
If accompanying PGRR filed, then ROS will be involved in review
ROS approval will be required for any PGRR(s).
Review/endorse combined NPRR/PGRR package for Board approval
Authorize implementation of Batch Zero by approval of NPRR/PGRRs
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
1. May be unnecessary if the Revision Request ends up utilizing only a NPRR and not an additional PGRR
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Target Board approval date
Board Meeting 4/20
Regular PRS 4/15
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Note that TAC leadership is involved in considering options to ensure successful review and approval
Special PRS 4/22
Regular TAC 4/29
Special TAC 5/13
PRS Vote 5/6
4
Monthly LLWG updates

## Slide 5: Related PUCT Activities
PUC Project 58480, 16 TAC § 25.370, Large Load Forecasting Rule (Adopted & Effective March 1, 2026)
After 2026, only Large Loads that have executed an interconnection agreement that satisfies the requirements in PUC Project 58481 will be included in the Large Load forecast. These requirements will be reflected in future revision requests.
Establishes alternative gating criteria for Large Loads to be included in the 2026 Large Load Forecast, which is used in planning assessments until new cases are constructed in 2027 using new rule criteria.
PUC Project 58481, proposed to be 16 TAC § 25.194, Large Load Interconnection Standards (Staff filed a draft Proposal for Publication on February 13, 2026)
Intermediate Agreement Requirements:
  Site control
  Financial Security, $100,000/MW
  Disclosures
  Option to pay for significant equipment or services
Interconnection Agreement Requirements:
  Financial security
  CIAC
Other Provisions
  Reallocation
  Withdrawal Consequences
  Refund Eligibility and Timing

## Slide 6: Reminder of Scope and Priorities for Workshops
Issue #1: ERCOT is committed to developing Batch Zero Process (first priority NPRR and/or PGRR) with target release March 4 for June 1 Board approval
Issues #2 and #3: ERCOT is committed to working on options/RRs for inclusion of both items below, but if not resolved prior to June 1 Board, will be out of Scope for Batch Zero
  CLR revisions
  BYOG revisions
Issue #4: Long-term Batch Process revisions. Out of scope for now and ERCOT will be taking lessons learned from Batch Zero into future revision request
At the end of today’s workshop we will be asking for real-time input to survey questions to solicit common-ground issues and priorities from stakeholders after the workshop
  Example, which BYOG scenarios most interested in? Load+DispatchableGen, Load+IRR, etc

## Slide 7: How stakeholder feedback and collaboration shaped the proposed Batch Zero framework
ERCOT refined the proposed Batch Zero and future batch framework based on multi-channel stakeholder feedback, incorporating several of the suggestions collected:
  6-month frequency of Batch process
  Defined commitment window to meet Batch Zero inclusion criteria and 30-day commitment window following study results
  Clear, readiness-based eligibility criteria for Batch Zero inclusion, with explicit evaluation of development activity and feasibility for energization targets
  Centralized ERCOT-led Batch Study, with ERCOT and TSPs working iteratively to identify, evaluate, and refine transmission upgrades
  Application of PGRR127 methodology for generation shortfalls
  Actionable transmission plan as an outcome
Note: Appendix includes survey highlights for reference
ERCOT looks forward to continued partnership with stakeholders as we transition to a durable, transparent batch study framework

## Slide 8: Agenda
Timeline and governance recap
  Batch Zero study scope and process overview
  Deep-dive on key design elements
    Batch Study process overview and final transmission plan
    Criteria for Batch Zero
  Initial discussion on BYOG and CLR
  Post-meeting survey questions
  Appendix

## Slide 9: Batch Zero Overview – Two Phases
Batch Zero Study
Batch Zero Refinement
ILLE Commitment Period
Study Inputs
Steady state study and dynamic stability screening
Identify planning criteria violations
Work iteratively with TSPs to determine amount of load that can be reliably served in each year and, where feasible, upgrades needed to serve full load request
Work iteratively with TSPs to
  Determine which upgrades are still needed based on ILLE commitments
  Review cost estimates and alternative upgrade options
  Develop a transmission plan to serve committed loads
Transmission Plan to RPG
6 months
3 months

## Slide 10: Batch Zero Study Scope Overview
Key Design Considerations
One consistent, system-wide reliability study: ERCOT evaluates all Batch Zero-eligible Large Loads using a common set of assumptions, criteria, and cases to identify system limitations and needed upgrades
Clear, year-by-year outcomes: for each assessed Large Load, the study determines the maximum peak MW that can be reliably served each year (2028–2033) and the transmission upgrades needed to increase service toward the requested level
Scope details
Study horizon: 2028–2032 (Years 1–5)
What ERCOT studies (per year): ERCOT builds cases from SSWG base cases and runs reliability assessment across:
  Summer peak load (high load system stress)
  Summer peak net load
  Fall peak (used to assess maintenance outage conditions consistent with ERCOT Planning Guide criteria)
Reliability assessment coverage:
  Evaluate planning criteria violations triggered by adding the Batch Zero loads (across scenarios/contingencies ERCOT selects)
  Determine “reliably served MW” per load, per year (i.e., deliverable load that can be served without violating planning criteria)
  Load that cannot reliably be served in years 1-5 will be allocated in year 6.
Generation assumptions: if additional generation is needed to serve the modeled load, ERCOT adds it consistent with PGRR127 methodology
Transparency: ERCOT posts the study cases used for Batch Zero on the MIS Certified Area once available

## Slide 11: Batch Zero Study Methodology and Study Elements
Key Design Considerations
Study must be repeatable and explainable: ERCOT uses transparent study inputs (posted cases), consistent criteria, and a clear link from violations to upgrades to year-by-year reliably served MW
Actionable coordination: the process enables rapid, iterative ERCOT–TSP alignment on transmission improvements while the study is underway
Study elements and methodology
Prepare system-wide study cases (ERCOT)
  Develop annual cases for 2028–2032 from SSWG base cases
  Add Batch Zero-eligible Large Loads per the inclusion criteria and model treatment rules
  Post cases to MIS Certified once available
System-wide reliability assessment (ERCOT)
  Study scenarios and contingencies ERCOT determines are needed to evaluate reliability impacts
  For each assessed LL, identify planning criteria violations associated with the proposed addition
  Determine the amount of peak load that can be reliably served each year
Stability screening assessment (ERCOT)
  Perform the stability component of the Batch Zero study
  Document identified stability issues and reflect any resulting limitations in year-by-year reliably served MW
Identify transmission improvements (ERCOT and impacted TSPs)
  Once violations are identified, ERCOT initiates communication with relevant TSPs
  TSPs provide upgrade recommendations; ERCOT and TSPs iterate through the study period until needed upgrades are identified
  Results translate into upgrades resolving violations/enabling higher reliably served MW over time
Supporting prerequisites (TDSPs/TSPs, as applicable)
  Short-circuit and other relevant studies are completed by the interconnecting TDSP/TSP at least 30 days before ERCOT issues Batch Zero awards/results
  TDSPs/TSPs provide necessary model information prior to start of Batch Zero

## Slide 12: Outputs, Deliverables, and Timeline
Key Design Considerations
Actionable outcomes: each Large Load receives a year-by-year Load Commissioning Plan (LCP) and estimated security requirements to support commitment decisions. TSPs receive
Clear commitment gate to planning certainty: only Large Loads that meet commitment milestones move into the Refinement Study and transmission plan delivered to RPG
Process and outputs
Core timeline
  By TBD: required project info submitted for inclusion
  TBD: ERCOT commences Batch Zero study
  By TBD + 19 weeks: ERCOT issues the Batch Zero Study Report, provides Load Commissioning Plans (LCPs) and notifies TSPs of Batch Zero results
  By TBD + 24 weeks: TDSPs notify ERCOT which Large Loads have met commitment requirements
  By TBD + 37 weeks: ERCOT completes the Batch Zero Refinement Study and delivers the Batch Zero Transmission Plan to RPG
Primary outputs
  Batch Zero Study Report (summary of reliability impacts, identified planning criteria violations, and proposed transmission upgrades)
  Load Commissioning Plan (LCP) per Large Load
    Maximum reliably served peak MW for each year (2028–2033)
      Loads receive full requested allocation for year 2033
  Estimated security requirements (upgrade-related) to inform ILLE commitment decisions
  Confidential TSP package: detailed upgrade list and associated Large Loads (as applicable)
Refinement and RPG handoff
  Only Large Loads that meet commitment milestones remain in scope
  ERCOT re-evaluates whether previously identified upgrades are still needed/modified/no longer required
  Final Batch Zero Transmission Plan is delivered into the RPG process

## Slide 13: Agenda
Timeline and governance recap
  Batch Zero study scope and process overview
  Deep-dive on key design elements
    Batch Study process overview and final transmission plan
    Criteria for Batch Zero
  Initial discussion on BYOG and CLR
  Post-meeting survey questions
  Appendix

## Slide 14: Potential Batch Zero Timeline
2026
2027
Jul
Aug
Sep
Oct
Nov
Dec
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
RPG Comment Period (3 weeks)
RPG Study Mode (4-weeks, if required)
TAC (August 2027)
Board (September 2027)
2026 RTP
Final Report (2 weeks)
2027 RTP
Batch 0 (Study years 2028-2032)
Stability Screening Study (14 weeks)
Steady State Analysis (15 weeks)
Case Build (13 weeks)
Developer Commitment Deadline
FAC-002 Stability
Batch Refinement Study (13 weeks)
1
2
3
4
5
6
7
8
9
9
Batch Refinement Study:
ERCOT: determine which transmission improvements identified in the Batch study are still required based on which loads met the commitment requirements
TSPs: provide cost estimates and refinement of transmission improvement projects and alternatives
ERCOT: final analysis of alternatives and determinization of final set of transmission improvement projects
ERCOT: prepare final report and submit to RPG
Steady State and Stability Analyses:
ERCOT: identification of criteria violations
ERCOT and TSPs: identification of transmission improvement projects and alternatives to resolve violations
TSPs: determination of transmission improvement feasibility and schedule
TSPs: provide transmission improvement cost estimates
ERCOT: final determination of transmission improvement projects that are feasible
ERCOT: allocate MWs to loads
ERCOT: create load request to transmission improvement mapping

## Slide 15: Case Build
Key Design Considerations
Standardized ERCOT intake and deadline
Clear eligibility and inclusion rules for Batch Zero
Defined modeling treatment at entry
Transparent study case development
Details
For Batch Zero, the interconnecting TDSP submits required information and a written attestation that the ILLE has met the applicable eligibility requirements
ERCOT applies the Batch Zero eligibility criteria to determine which Large Loads are included and whether they are treated as base load not subject to further evaluation or load subject to reliability assessment and allocation
Projects that do not meet the criteria or fail to submit required information by the deadline are not included
ERCOT develops the 2028–2032 study cases using SSWG-based summer peak, summer peak net load, and fall peak cases, and posts those cases to the MIS Certified area to provide transparency into study assumptions
1

## Slide 16: Steady State Analysis
Key Design Considerations
Single, system-wide ERCOT study
Reliability-based contingency analysis
Identification of planning criteria violations
Determination of reliably served MW by year
Details
ERCOT performs a singular, system-wide steady-state study for all Large Loads included in Batch Zero using SSWG derived base cases appropriate for the study horizon
ERCOT studies all scenarios and contingencies necessary to assess reliability with applicable NERC Reliability Standards, ERCOT Protocols, the Planning Guide, and Operating Guides
As soon as violations are identified, ERCOT begins collaborative, iterative process working with TSPs to identify feasible transmission upgrades to serve the Large Loads
For each Large Load subject to assessment, ERCOT documents planning criteria violations and determines the amount of peak Demand that may be reliably served for each year of the 2028–2032 study period. Load amounts that cannot be reliably served in in this period receive automatic allocation in 2033.
2

## Slide 17: Stability Screening Study
Key Design Considerations
Maintain sufficient stability margin
Mitigation of identified instability
Coordination with TSPs
Details
If stability screening criteria violation is identified, ERCOT and the applicable TSP(s) investigates mitigation measures, including transmission improvements, and identifies any required modifications to load levels or timing reflected in the Load Commissioning Plan
3

## Slide 18: Final Report
Key Design Considerations
Actionable study outcome
Clear MW allocations by year
Identification of required upgrades
Security visibility
Details
ERCOT produces the Batch Zero Report summarizing study results and proposed transmission upgrades
For each assessed Large Load, ERCOT updates the originally provided Load Commissioning Plan reflecting the amount of peak Demand that can be reliably served each year and the upgrades required to support each level of Demand
TSP uses the Batch Zero Report and other study results to determine a ILLE’s financial security and CIAC consistent with interconnection agreement requirements in Project No. 58481 rule (to be 16 TAC § 25.194)
4

## Slide 19: Developer Commitment Deadline
Key Design Considerations
Clear commitment gate
TDSP attestation as trigger
Removal of non-committed projects
Planning certainty before refinement
Details
To accept the allocated MW and schedule documented in the LCP, the ILLE must execute an interconnection agreement that meets the requirements of a rule adopted in Project No. 58481 (to be 16 TAC § 25.194)
The interconnecting TDSP must notify ERCOT of Large Loads that execute an interconnection agreement that meets the requirements of a final rule in Project No. 58481 (to be 16 TAC § 25.194) by the deadline
Large Loads that do not meet the requirements by the deadline are considered withdrawn from Batch Zero and are not included in the refinement study
5

## Slide 20: Batch Refinement Study
Key Design Considerations
Removal of non-committed loads
Re-evaluation of identified upgrades
Right-sizing of transmission scope
Preparation of Transmission Plan for RPG
Details
Immediately following the commitment deadline, ERCOT updates the Batch Zero study to include only those Large Loads that met commitment requirements
ERCOT evaluates whether the remaining loads continue to result in planning criteria violations and whether previously identified transmission upgrades are still needed, need modification, or are no longer required
ERCOT works iteratively with relevant TSPs during this period and develops the final Transmission Plan to be delivered to RPG
6

## Slide 21: RPG Comment Period
Key Design Considerations
Stakeholder review and transparency
Time-bound comment process
Preservation of governance pathway
Details
The Batch Refinement Study is submitted to the Regional Planning Group for review
Stakeholders are provided an opportunity to submit comments within a defined review period
7

## Slide 22: RPG Study Mode
Key Design Considerations
Targeted additional evaluation if necessary
Focused response to material concerns
Details
If needed, ERCOT conducts limited additional study to address specific issues raised during RPG review
This step is intended to provide focused technical clarification rather than a full annual RTP-level re-evaluation
8

## Slide 23: TAC and Board
Key Design Considerations
Formal governance review
Recommendation pathway
Final approval authority
ERCOT endorsement of recommended projects
Details
Following completion of RPG review and any additional study, the Batch Transmission Plan proceeds to TAC for consideration and recommendation in accordance with ERCOT governance procedures
The ERCOT Board considers and acts on the recommended Transmission Plan resulting from the Batch Zero process
Approval reflects ERCOT’s independent technical review, TSP coordination, and stakeholder input through the RPG process
9

## Slide 24: Steady-State Batch Study process: 6-month study cadence with continuous planning integration
Year 1
Year 2
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Batch refinement and transmission plan finalization​
Batch refinement and transmission plan finalization​
6-month study
6-month study
6-month study
Activity
Batch 2
Batch 1
Batch 0
Batch Study process going live
Following completion of the batch study and confirmation of commitments, ERCOT advances the resulting transmission plan through the RPG process for stakeholder review and governance approval
ILLUSTRATIVE
A new batch begins every six months, ensuring predictable decision cycles without processing gaps and building on upgrades approved in prior cycles

## Slide 25: Agenda
Timeline and governance recap
  Batch Zero study scope and process overview
  Deep-dive on key design elements
    Batch Study process overview and final transmission plan
    Criteria for Batch Zero
  Initial discussion on BYOG and CLR
  Post-meeting survey questions
  Appendix

## Slide 26: Fundamental Principles for ERCOT's Proposed Batch Zero Criteria
ERCOT’s Reliability Responsibility: Ensure all Large Loads confirmed to be firm in Batch Zero have been studied to show that the load can be served reliably
Senate Bill 6 and PUC Gating Rules: Utilize the gating criteria reflected in Project No. 58481 rulemaking to determine which large loads should be confirmed firm and which should be included to be studied in Batch Zero
Pre-Transition Processes: Respect to the extent feasible already granted approvals, including approval to energize and approved studies
Large Load Near-Term Energizations: Assess development activity for large loads that declare 2026 or 2027 energization to evaluate schedule feasibility
Reallocate Non-utilized Capacity: Release non-utilized large load capacity for use by other loads in accordance with Project No. 58481, new 16 TAC § 25.194

## Slide 27: Eligibility flowchart: how to assess if a load is eligible for Batch Zero?
X
Reference tracker
Is the load operational or Approved to Energize?
Start
Yes
Included in Batch Zero as base load
Does the load meet intermediate criteria?
Are interconnection studies complete and valid?
No
Does the load meet full commitment criteria?
Yes
No
Yes
No
Studied in Batch Zero and will receive load allocation amounts
Are interconnection studies partially complete?
Not included in Batch Zero
1
5
Will the load be operational by end of year 2027?
Yes
Studies are no longer valid
Set initial energization date to 1/1/2028 or later
No
Has the load demonstrated development activity?
Yes
No
No
Yes
Yes
2
No
3
5
6
4
4

## Slide 28: Deep-dive: “Included as base load” (1/2)
If your Large Load by June 1, 2026 | Treatment in Transitional Process | MW Allocation
Is Operational or Approved to Energize | Included as base load | Loads operational before ERCOT’s interim LLI process will be allocated the MWs modeled in the 2025 RTP Loads operational after ERCOT’s interim LLI process will be allocated the lesser of: MWs modeled in the 2025 RTP less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs included in their Load Commissioning Plan, if applicable, less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs in an updated ramp schedule as provided to the DSP by June 1, 2026 Loads not yet operational will be allocated the lesser of: MWs that can be reliably served as indicated in their interconnection studies MWs included in their interconnection agreement and reflected in their financial security
1
If your Large Load by TBD
MW Allocation
Treatment in Transitional Process
Is Operational or Approved to Energize
Loads operational before ERCOT’s interim LLIS process will be allocated the MWs modeled in the 2025 RTP
Loads operational after ERCOT’s interim LLIS process will be allocated the lesser of:
  MWs modeled in the 2025 RTP less the difference between:
    The planned MWs by December 1, 2025, and the maximum MWs consumed by June 1, 2026
  MWs included in their Load Commissioning Plan, if applicable, less the difference between:
    The planned MWs by December 1, 2025, and the maximum consumed by June 1, 2026
  MWs in an updated ramp schedule as provided to the DSP by TBD
Loads not yet operational will be allocated the lesser of:
  MWs that can be reliably served as indicated in their interconnection studies
  MWs included in their interconnection agreement and reflected in their financial security
Included as base load

## Slide 29: Deep-dive: “Included as base load” (2/2)
1
If your Large Load by TBD
MW Allocation
Loads not yet operational will be allocated the lesser of:
  MWs that can be reliably served as indicated in their interconnection studies
  MWs included in their interconnection agreement and financial security
Treatment in Transitional Process
Included as base load
Has complete and valid interconnection studies + meets 58481 interconnection agreement requirements* + requested energization date on or before 12/31/2027 + demonstrated development activity
Has complete and valid interconnection studies + meets 58481 interconnection agreement requirements* + will be operational after 12/31/2027

## Slide 30: Deep-dive: “Studied in Batch Zero”
2
If your Large Load by TBD
MW Allocation
To be determined during Batch Zero study
Treatment in Transitional Process
Studied in Batch Zero
Has complete and valid interconnection studies + does not meet 58481 interconnection agreement requirements* + meets 58481 intermediate agreement requirements*
Has complete and valid interconnection studies + meets 58481 interconnection agreement requirements* + requested energization date on or before 12/31/2027 + cannot demonstrate development activity
Has partially complete or valid interconnection studies + meets 58481 intermediate agreement requirements*

## Slide 31: Deep-dive: “Not included in Batch Zero”
3
If your Large Load by TBD
MW Allocation
To be determined in Batch One if Large Load meets Batch One criteria
Treatment in Transitional Process
Not included in Batch Zero
Has complete and valid interconnection studies + does not meet 58481 interconnection agreement requirements* + does not meet 58481 intermediate agreement requirements*
Has partially complete or valid interconnection studies + does not meet 58481 intermediate agreement requirements*

## Slide 32: Interconnection Studies
4
A Large Load has complete and valid interconnection studies, if it has:
Provided dynamic data to the interconnecting TSP and the TSP provided the dynamic data to ERCOT by TBD. Dynamic data includes a model and any supporting documentation, such as a completed ERCOT Dynamic Working Group Large Load Survey document that accurately represents the characteristics of the Large Load
Steady state and stability studies that demonstrate the load can be reliably served considering any changes in assumptions since the study was completed. LLIS, RTP, and RPG studies may be considered. ERCOT is still drafting the methodology for making this determination
A Large Load has partially complete studies if the TSP submitted and ERCOT approved a steady-state or stability study by TBD

## Slide 33: Harmonizing Batch Zero process with Project 58481
5
Incorporating PUC Project 58481 into Batch Zero: two implementation pathways
Project 58481 will define readiness and financial commitment standards for Large Loads. ERCOT must determine how to align Batch Zero timing with this rulemaking
Option 1: Replicate the Draft 58481 PFP in the PGRR (proceed in parallel)
  Description: embed the February 13, 2026 draft Proposal for Publication (PFP) concepts directly into the PGRR language and update the PGRR with the published PFP once available
  Implications
    Enables earlier Batch Zero launch
    Uses proposed draft for intermediate agreement and interconnection agreement criteria
    Risk of misalignment if final rule differs from draft
Option 2: Tie PGRR to Final Adopted 58481 Rule (sequential alignment)
  Description: draft PGRR to reference the final adopted 16 TAC §25.194 and begin Batch Zero a defined period (e.g., X days) after the rule becomes effective
  Implications
    Batch Zero will be aligned with final PUC rule
    May delay Batch Zero start depending on rule adoption timeline

## Slide 34: Demonstrated Development Activity
6
To demonstrate development activity, a Large Load must meet 1 or 2:
It was included in a Quarterly Stability Assessment by May 1, 2026, or
The DSP or interconnecting TSP has attested to ERCOT by TBD, that the Large Load met all the following:
  Begun site preparation and construction; and
  Purchased all necessary customer-owned high-voltage transformers and circuit breakers

## Slide 35: Agenda
Timeline and governance recap
  Batch Zero study scope and process overview
  Deep-dive on key design elements
    Batch Study process overview and final transmission plan
    Criteria for Batch Zero
  Initial discussion on BYOG and CLR
  Post-meeting survey questions
  Appendix
- Brief walkthrough of ERCOT’s 3 slides - 15-minute Presentation from Sam Brandin (posted Agentic presentation) - 15-minute Walkthrough of PUC filing on topic from Arushi Sharma Frank

## Slide 36: Controllable Load Resource Rules
Key Design Considerations
CLR is an existing resource type in ERCOT Protocols
Similar to generators, CLRs can be dispatched down in real-time by ERCOT’s Security Constrained Economic Dispatch tool
Some CLRs can be dispatched to zero load while others have a higher minimum load values
ILLEs registering loads as CLRs still want the transmission system to be planned to serve the full load
ERCOT and CLR entities need clearly defined rules to govern expectations
NPRR1188 (expected late 2026 implementation) provides some but not all rules necessary for allowing specific consideration of CLRs in the Batch Study process
Additional CLR Rules Needed
Offer mitigation or similar concept to ensure high CLR offers don’t result in constraint violations in SCED optimization (SCED Step2)
Binding commitment and exit conditions so CLRs remain as CLRs until necessary transmission upgrades are complete
NPRR1188 does not support CLR composed of Load+Gen/Battery
CLR Treatment in Batch Studies
An ILLE’s designation of intent to register as CLR will be binding for the Batch Study
A CLR will be allocated its full load request but may be required to have a minimum load amount assigned in the Batch Study process
CLR Treatment in Other Studies
CLRs will be modeled at their full requested load in transmission planning studies and the FAC-002 stability study
All TSP studies must consider the full load

## Slide 37
Co-Location with New Generation Rules
37
Key Design Considerations
New co-located generators can reduce the need for the transmission system to support a new Large Load
There are multiple scenarios regarding how the co-located generation resource and Large Load interact with the transmission system, each requiring different rules
In some scenarios, new rules are needed to link generation interconnection requests to LLI requests
Examples:
Scenario 1: Large Load does not consume from the grid – only from the co-located generation
The co-located Large Load will be allocated its full load request
Rules needed to ensure Large Load will never consume from the grid, even momentarily
Rules needed to ensure LLI request and GINR are linked
Scenario 2: Scenario 1 temporarily until transmission upgrades are complete
All Scenario 1 rules apply
A separate study is needed to determine the required transmission upgrades and rules needed to exit no-transmission-system-load status
Scenario 3: Large Load has co-located dispatchable generation and may sometimes consume from the grid
The co-located Large Load will be allocated their full load request except in the G-1+N-1 analysis
Rules needed to ensure LLI request and GINR are linked
Scenario 4: Large Load has co-located intermittent generation and/or energy storage and may sometimes consume from the grid
No specific rules
Not enough time in Batch Zero development for numerous scenarios; looking for feedback on priority and feasibility of scenario options (will also discuss as part of post-meeting survey).

## Slide 38: Co-Location with Existing Generation Rules
Key Design Considerations
Senate Bill 6 rules may apply for generators existing before September 1, 2025
The transmission system has been planned assuming the existing generation supports the system
Co-Location with existing generation
No specific rules aside from existing requirements in the Protocols (such as an updated Reactive Power study)

## Slide 39: Agenda
Timeline and governance recap
  Batch Zero study scope and process overview
  Deep-dive on key design elements
    Batch Study process overview and final transmission plan
    Criteria for Batch Zero
  Initial discussion on BYOG and CLR
  Post-meeting survey questions
  Appendix

## Slide 40: Proposed survey questions to be addressed post-workshop
What should be the latest in-service date for projects that will be required to demonstrate development activity?
What information should be required for projects to demonstrate development activity?
What date should ERCOT set for projects to meet the intermediate agreement or interconnection agreement criteria to be included in Batch Zero?
Do you agree with ERCOT’s fundamental principles for Batch Zero? If no, why not?
Do you agree with the proposed Batch Zero refinement study approach? If no, why not?
What should remain confidential (e.g., exact customer identity, POI, requested MW, awarded MW by year, associated transmission upgrade list)?
Which co-location configurations (e.g., load plus battery, load plus solar) should ERCOT prioritize when defining BYOG rules?
[Any other questions to be added to survey – to be discussed]

## Slide 41: Q&A session

## Slide 42: Agenda
Timeline and governance recap
  Batch Zero study scope and process overview
  Deep-dive on key design elements
    Batch Study process overview and final transmission plan
    Criteria for Batch Zero
  Initial discussion on BYOG and CLR
  Post-meeting survey questions
  Appendix – Support material from Stakeholder Survey
  Appendix

## Slide 43: Initial Screening Study/Early Input: Consistency across T(D)SPs
“How should ERCOT ensure consistency in initial study quality across T(D)SPs?” (% of overall respondents)
Commentary
A clear majority of respondents (66%) prefer ERCOT to change processes to standardize initial screening study quality across T(D)SPs; substantially fewer favor a joint T(D)SP-designed approach (20%), and limited support exists for retaining individual T(D)SP processes (14%)
High stakeholder alignment:
  “T(D)SPs” predominantly support ERCOT-led standardization of initial screening processes
  “Large Load customers” and “Other” stakeholders strongly favor ERCOT-driven standardization, with limited support for T(D)SP-joint approaches
Chart: 
 | 18 | 4 | 7.0588
 | 34 | 15 | 7.0588
 | 14.1176 | 1.1765 | 0
14%
34%
18%
ERCOT to change processes to standardize
1%
15%
4%
TSPs collaborate to design joint approach
7%
7%
TSPs to retain individual processes
66%
20%
14%
T(D)SPs
LL customers
Other
N=85 (19 T(D)SPs, 48 LLC, 18 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey

## Slide 44: Initial Screening Study/Early Input: ERCOT and T(D)SP delay handling
“Regarding feedback on T(D)SP and ERCOT delayed responses, what are appropriate next steps to consider?” (% of overall respondents)
Commentary
Majority of respondents (94%) favor standardizing end-to-end processes and timeline expectations across the Large Load Interconnection process to address delayed responses by T(D)SPs and ERCOT; few respondents believe that transparency improvements alone are sufficient (7%)
High stakeholder alignment:
  “T(D)SPs”, “Large Load customers”, and “Other” stakeholders each show strong support for standardized processes with enforceable timelines
Chart: 
 | 21 | 5.7471
 | 52 | 1.1494
 | 20.6897 | 0
21%
52%
21%
Standardize end-to-end processes and timelines
1%
6%
Improve transparency within the existing process
94%
7%
T(D)SPs
LL customers
Other
N=87 (19 T(D)SPs, 50 LLC, 18 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey

## Slide 45: Eligibility criteria: Batch Zero criteria
“Based on ERCOT’s proposal laid out in the ERCOT Large Load Batch Study Workshop, are there any additional factors that should be considered to prioritize interconnection requests for inclusion in Batch Zero?” (% of overall respondents that selected a specific option)
Chart: 
 | 12.987 | 9.0909 | 11.6883 | 16.8831 | 25.974 | 3.8961 | 3.8961 | 11.6883
 | 37.6623 | 40.2597 | 36.3636 | 22.0779 | 14.2857 | 22.0779 | 14.2857 | 10.3896
 | 16.8831 | 14.2857 | 14.2857 | 6.4935 | 0 | 10.3896 | 9.0909 | 2.5974
40%
9%
Date request submitted to TSP
10%
22%
4%
Date request submitted to ERCOT
14%
36%
12%
Operational readiness criteria
6%
22%
17%
BYOG (Bring Your Own Generation) status
3%
10%
12%
CLR
status
14%
14%
4%
Required energization date
14%
26%
Current status of application through existing study process
17%
38%
13%
Financial security
64%
36%
62%
45%
25%
27%
40%
68%
9%
T(D)SPs
LL customers
Other
N=77; note that respondents could multi-select responses so total % > 100
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey
Commentary
Majority of respondents favor financial security (68%), date of request submission to T(D)SP (64%), and operational readiness criteria (62%) as Batch Zero entry criteria; other popular options included BYOG status (45%) and current application status (40%), while date of submission to ERCOT (36%), required energization date (27%), and CLR status (25%) were less frequent selections
Stakeholders differ on which criteria they prefer:
  “T(D)SPs” and “Large Load customers” tended toward financial security, operational readiness, and date of submission to T(D)SP
  “Other” stakeholders agreed with the above most popular criteria, but most strongly preferred financial security and BYOG status

## Slide 46: Eligibility criteria: Batch Zero inclusion criteria
Commentary
Majority of respondents favor allowing some form of grace period for Batch Zero eligibility, with a preference for a short administrative grace period to cure documentation or administrative gaps (53%); a smaller but meaningful share support an extended grace period for substantive changes (38%), while limited support exists for a strict cutoff with no grace period (8%)
Overall stakeholder alignment:
  “T(D)SPs” show greater support for an extended grace period for allowing substantive changes
  “Large Load customers” support both administrative and extended grace periods
  “Other” stakeholders also favor a short administrative grace period over an extended one, with no support for a strict cutoff with no grace period at all
Chart: 
 | 4 | 12 | 5
 | 4.1667 | 33 | 22.2222
 | 0 | 8.3333 | 11.1111
4%
4%
No grace period (strict cutoff)
8%
33%
12%
Short administrative grace period
11%
22%
5%
Extended grace period for substantive changes
8%
53%
38%
T(D)SPs
LL customers
Other
N=72 (17 T(D)SPs, 43 LLC, 13 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey
“Should ERCOT allow a grace period for projects to meet Batch Zero eligibility criteria?” (% of overall respondents)

## Slide 47: Batch study: Batch study responsibility centralization
Commentary
Majority of respondents (75%) favor centralizing batch study responsibility with ERCOT while partnering with T(D)SPs to identify transmission upgrades, reflecting a preference for ERCOT-led coordination with T(D)SP technical input; comparatively fewer respondents support fully ERCOT-led upgrade identification (12%) or leaving studies primarily with T(D)SPs (14%)
Overall stakeholder alignment:
  “T(D)SPs”, “Large Load customers”, and “Other” stakeholders each show strong preference for an ERCOT-led, centrally managed study framework supported by T(D)SP expertise
Chart: 
 | 6.8493 | 14 | 12.3288
 | 5.4795 | 40 | 1.3699
 | 0 | 20.5479 | 0
5%
7%
ERCOT-led studies and upgrade identification
21%
40%
14%
ERCOT-led studies with TSP-supported upgrade identification
1%
12%
TSP-led studies with ERCOT coordination only
12%
75%
14%
T(D)SPs
LL customers
Other
N=73 (16 T(D)SPs, 42 LLC, 15 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey
“Should ERCOT centralize responsibility for large load interconnection batch studies?” (% of overall respondents)

## Slide 48: Batch study: Batch frequency
Commentary
Overwhelming majority of respondents (89%) favor running batch studies on a semi-annual cadence (every 6 months) following Batch Zero; comparatively few support a nine-month cadence (8%) or an annual cadence (3%)
Overall stakeholder alignment:
  “T(D)SPs”, “Large Load customers”, and “Other” stakeholders each show strong support for a semi-annual batch cadence
Chart: 
 | 14 | 5.5556 | 1.3889
 | 56 | 1.3889 | 1.3889
 | 19.4444 | 1.3889 | 0
19%
56%
14%
Semi-annual batch cadence (every 6 months)
1%
1%
6%
Nine-month batch cadence
1%
1%
Annual batch cadence (every 12 months)
89%
8%
3%
T(D)SPs
LL customers
Other
N=72 (16 T(D)SPs, 42 LLC, 14 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey
“How frequently should batch studies be run (after Batch Zero)?” (% of overall respondents)

## Slide 49: Batch study: Generation methodology
“Do you agree with ERCOT’s proposal laid out in the ERCOT Large Load Batch Study Workshop to use the “PGRR127” methodology if there is not sufficient generation in the cases to serve the modeled load level?” (% of overall respondents)
Commentary
Strong majority of respondents (89%) agree with ERCOT’s proposal to apply the PGRR127 methodology when available generation is insufficient to serve the modeled load level; a small minority favor applying an alternative methodology (11%)
Overall stakeholder alignment:
  “T(D)SPs”, “Large Load customers”, and “Other” stakeholders each show strong support for using the PGRR127 methodology
Supporters of alternative methodology express caution about relying solely on PGRR127 assumptions for generation shortfalls, emphasizing the need to:
  Better reflect committed and co-located generation
  Phase or allocate load based on demonstrated readiness
  Avoid masking real system constraints while allowing market-driven generation to respond over time
Chart: 
 | 19 | 6.25
 | 50 | 4.6875
 | 20.3125 | 0
20%
50%
19%
Yes - apply the PGRR127 methodology
5%
6%
No - apply an alternative methodology
89%
11%
T(D)SPs
LL customers
Other
N=64 (16 T(D)SPs, 36 LLC, 12 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey

## Slide 50: Allocate and commit: Decision window
“Assuming the decision window is part of the batch study duration, how long should applicants have to accept or decline their capacity allocation (decision window)?” (% of overall respondents that selected a specific option)
Chart: 
 | 1.3889 | 9.7222 | 2.7778 | 4.1667 | 2.7778 | 0
 | 2.7778 | 41.6667 | 9.7222 | 5.5556 | 4.1667 | 0
 | 1.3889 | 12.5 | 2.7778 | 4.1667 | 2.7778 | 0
1%
3%
1%
14 days (resulting in a 6-month Batch Study process)
13%
42%
10%
30 days (resulting in a 6-month Batch Study process)
3%
10%
3%
45 days (resulting in a 7-month Batch Study process)
4%
6%
4%
60 days (resulting in a 7-month Batch Study process)
3%
4%
3%
90 days (resulting in an 8-month Batch Study process)
More than 90 days (resulting in an 8-month+ Batch Study process)
6%
64%
15%
14%
10%
0%
N=72; note that respondents could multi-select responses so total % > 100
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey
Commentary
Strong majority of respondents favor a 30-day window resulting in a 6-month process (64%); 15% prefer a 45-day option, 14% prefer a 60-day option, 10% prefer the 90-day option, and 6% prefer a 2-week window
General stakeholder alignment:
  “T(D)SPs,” “Large Load customers,” and “Other” stakeholders tended to overwhelmingly prefer a 30-day decision window as their top response
  No stakeholder from any group selected the option which would allow a decision window longer than 90 days
T(D)SPs
LL customers
Other

## Slide 51: Allocate and commit: Milestone enforcement
Commentary
Majority of respondents (38%) favor reducing or reallocating capacity after a defined grace period when milestones are missed, signaling a preference for consequences that recycle capacity without immediately removing projects from the process; smaller shares support removal and reapplication (24%), financial penalties while retaining allocation (21%) or other (18%)
Some divergence across stakeholders:
  “T(D)SPs” are ambivalent between reduction/ reallocation of capacity and removing the project from the process
  “Large Load customers”, and “Other” stakeholders show support for capacity reduction or reallocation following a grace period
Other alternatives suggested:
  Use escalating consequences, starting with financial penalties, then capacity reduction, and ultimately removal if milestones remain unmet
  Allow limited flexibility for non-developer delays, (excl. when issues are outside ILLE’s control)
  Set clear milestones/cure periods, with penalties meaningful enough to deter speculation
Chart: 
 | 8.8235 | 7.3529 | 2.9412 | 1.4706
 | 22.0588 | 8.8235 | 16.1765 | 11.7647
 | 7.3529 | 7.3529 | 1.4706 | 4.4118
7%
22%
9%
Reduce or reallocate capacity after a grace period
7%
9%
7%
Remove project from the process (reapplication required)
1%
16%
3%
Apply financial penalties while retaining allocation
4%
12%
1%
Other
38%
24%
21%
18%
T(D)SPs
LL customers
Other
N=56 (11 T(D)SPs, 32 LLC, 13 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey
D5
“If milestones are missed, which consequence should apply?” (% of overall respondents)

## Slide 52: RPG: Transmission upgrade linkage
Commentary
Chart: 
 | 9.0909 | 12.1212
 | 27.2727 | 28.7879
 | 22.7273 | 0
23%
27%
9%
LLI request load commissioning plans should be linked to transmission upgrade projects
29%
12%
LLI request load commissioning plans should NOT be linked to transmission upgrade projects
59%
41%
T(D)SPs
LL customers
Other
N=66 (15 T(D)SPs, 37 LLC, 14 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey
“How should LLI request load commissioning plans be linked to transmission upgrade projects?” (% of overall respondents)
Majority of respondents (59%) favor a link between LLI request load commissioning plans and transmission upgrade projects such that the loads are not allowed to energize or increase consumption if the transmission upgrade project is delayed; fewer respondents advocated that LLI request load commissioning plans should not be linked to transmission upgrade projects because ERCOT and T(D)SPs should account for potential transmission project delays in the Batch Study load allocation (41%)
Mixed stakeholder alignment:
  “T(D)SPs” show complete support for the link
  “Large Load Customers” and “Other” stakeholders conversely show stronger support for not having the two plans be linked

## Slide 53: End to end: Restudies
Commentary
N=66 (14 T(D)SPs, 39 LLC, 13 Other)
Source: ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey
“Should restudies ever be permitted?” (% of overall respondents)
Chart: 
 | 15.1515 | 4.5455
 | 43.9394 | 15.1515
 | 15.1515 | 6.0606
15%
44%
15%
Yes, if necessary
6%
15%
5%
Never
74%
26%
T(D)SPs
LL customers
Other
Strong majority of respondents (74%) disagree with ERCOT’s proposed complete elimination of restudies, while a smaller share agree that restudies should never be permitted (26%)
Overall stakeholder alignment:
  “T(D)SPs”, “Large Load customers”, and “Other” stakeholders each show majority support for restudies being permitted if necessary
Supporters of restudies urge clear justifications and restudy thresholds:
  Limiting restudies to a single, well-justified instance to limit risk of current ‘restudy loop’
  Desire for queue position to be upheld during restudies/use of discipling sequencing
  Certain respondents requested more transparent access to modeling results to reduce restudy disputes via independent analysis