## Slide 1: DWG Report to ROS
Aditi Upadhyay – DWG Chair
March 5th, 2026

## Slide 2: DWG Update
DWG Webex meeting held on 2/12/2026
NOGRR282 Discussion and Comments
  AEP FRT Curve Revisions: ERCOT and DWG supports increasing the high-frequency threshold from 61.8 Hz to 63 Hz, with consensus to maintain the 57 Hz low-frequency threshold pending any data center concerns.
  Post- Disturbance voltage Recovery Requirement: ERCOT and DWG supports AEP’s proposed revision “If voltage at the SDP/POIB exceeds ride-through limits (>1.2 pu or beyond minimum duration) and the LEL does not trip or transfer to backup, it must restore at least 90% of pre-disturbance grid consumption within 2 seconds after voltage returns to the continuous range (0.90–1.10 pu)”
Frequency (Hz) | Minimum Ride-Through Time (seconds)
f > 63.0 | May ride-through or trip
61.2 < f ≤ 63.0 | 299
58.8 < f ≤ 61.2 | Continuous
57.0 < f ≤ 58.8 | 299
f ≤ 57.0 | May ride-through or trip

## Slide 3: DWG Update, continued
  Post-Fault Active Power Recovery: ERCOT revised the post fault active power recovery from 1 sec to 2 sec; acceptable to DWG.
  Transient Overcurrent Tolerance: Discussed possibility of increasing threshold from 125% to 150% to enhance ride-through, with duration limited to <0.5 sec; decision pending SPWG input and formal data center feedback.
  Exemption/Grandfathering: Loads >75 MW that modify dynamic characteristics may lose ride-through exemptions
2025/2026 DWG Flat Start Updates
  Pass 4 submitted for review. DWG members to review and help reduce the size of the initial condition suspect list through case tuning measures.
  UFLS/UVLS dynamic load model updates, contingency data due by March 20th
  ERCOT to use PSS®E 36 for next case build

## Slide 4: DWG Update, continued
Draft PGRR for LL Model Submission and Review Requirements
  New Draft PGRR is submitted for formal discussion on Model Submission and Review requirements.
  New paragraph in PG (Section 6.2) defines required data for load model submission; large electronic load must provide validated PSSE, TSAT, and PSCAD models.
  Model must accurately represent load behavior using platforms like PSSE, TSAT and PSCAD models required for large electronic loads.
  Introduces model quality tests for large loads with the focus on demonstrating ride-through capabilities and model performance.
  DWG concerns: non-utility customers may face challenges and will require guidance and educational support.
  Action items: ERCOT to present interim modeling approach and LL modeling requirement to LLWG for transparency and feedback
  R1 of Pending NERC MOD-026-2
  ERCOT believes that many requirements are already covered in the current DWG procedure manual.
  ERCOT to draft initial edits, share with DWG for feedback and discuss in the future meetings or form a small group within DWG to develop and review edits (email poll to determine preference)
  Timeline aims for draft updates by June, compliance review by September, and final approval/posting by December.

## Slide 5: Questions or Feedback?