## Slide 1: Large Load Interconnection Batch Study Workshop
March 10th, 2026
Workshop #4

## Slide 2: Agenda
1
Timeline and governance recap
Update on timeline and key workshop dates
Outline PRS/ROS/TAC pathways to June Board with key submission dates
2
Stakeholder Survey Feedback and FAQ
Review FAQs and common stakeholder questions, including ERCOT responses
Review results from the stakeholder feedback survey and key themes emerging
3
Batch Zero PGRR/NPRR Walk-though
Review February 26 slides and highlight key updates since the last version
Walk through proposed PGRR language and relevant sections for alignment
4
Market Comments filed on NPRR/PGRR (if any)
Open discussion: stakeholder comments, initial requests, and areas requiring refinement after filing
5
Discussion of CLR and BYOG concepts
Resume discussion on treatment of CLR and BYOG (note that LLWG on Mar 13th will focus on these topics)
6
Q&A
Open forum for Batch Zero concerns, comments, and suggestions

## Slide 3: Agenda
Timeline and governance recap
Feb 26 Workshop Feedback
  FAQs and common stakeholder questions
  Results from stakeholder feedback survey
Batch Zero PGRR Deep Dive
PGRR stakeholder feedback
Follow-on Discussion: CLR and BYOG
Q&A
Appendix

## Slide 4: Batch Zero revision request timeline
Forums
Workshops and working groups
PRS (Protocols Review Subcommittee)
ROS (Reliability and Operations Subcommittee)
TAC
ERCOT Board
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Update 3/5
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
8/1 Target effective date of protocols
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
Preview structure/governing concepts of Batch Zero NPRR before filing
Confirm proposed protocol changes are ready for governance review
Endorse NPRR 1325 for advancement to TAC
File PGRR145 for Workshops and ROS review
Endorse PGRR145 for advancement to TAC
Review/endorse combined NPRR/PGRR package for Board approval
Consideration Batch Zero NPRR/PGRR
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Target Board approval date
Board Meeting 4/20
Regular PRS 4/15
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Note that TAC leadership is involved in considering options to ensure successful review and approval
Special PRS 4/22
Regular TAC 4/29
Special TAC 5/13
PRS Vote 5/6
Monthly LLWG updates
Apr (TBD) ERCOT files CLR/BYOG Revision Request(s)

## Slide 5: Revision Request Process Flow
Comments may be filed between each step of the process.
Comments for NPRR1325 may be submitted using the Comments Form found here.
Comments for PGRR145 may be submitted using the Comments Form found here.
NPRR Comments
PGRR Comments
Large Load Interconnection Workshops
NPRR/PGRR
Review
BOARD
PUCT
TAC
ROS
PGRR Language/IA Review
PRS
NPRR Language/IA Review

## Slide 6: Related PUCT Activities
PUC Project 58480, 16 TAC § 25.370, Large Load Forecasting Rule (Adopted & Effective March 1, 2026)
  After 2026, only Large Loads that have executed an interconnection agreement that satisfies the requirements in PUC Project 58481 will be included in the Large Load forecast. These requirements will be reflected in future revision requests.
  Establishes alternative gating criteria for Large Loads to be included in the 2026 Large Load Forecast, which is used in planning assessments until new cases are constructed in 2027 using new rule criteria.
PUC Project 58481, proposed to be 16 TAC § 25.194, Large Load Interconnection Standards (Staff filed a draft Proposal for Publication on February 13, 2026)
  Intermediate Agreement Requirements:
    Site control
    Financial Security, $100,000/MW
    Disclosures
    Option to pay for significant equipment or services
  Interconnection Agreement Requirements:
    Financial security
    CIAC
  Other Provisions
    Reallocation
    Withdrawal Consequences
    Refund Eligibility and Timing

## Slide 7: Reminder of Scope and Priorities for Workshops
March 4 filings completed for Batch Zero: ERCOT filed the Batch Zero PGRR145 and related NPRR1325 on March 4, initiating the formal governance process and aligning with the May PRS/ROS/TAC sequence and June 1 Board target reflected in the critical path timeline
Additional filings on target (CLR and BYOG): ERCOT is advancing targeted revision requests to clarify CLR and BYOG treatment and is currently targeting an April filing (TBD)
Continuous feedback collection: ERCOT follow-up stakeholder survey to gather additional input (e.g., eligibility criteria, development activity standards) for Batch Zero, CLR, and BYOG. Responses are being evaluated and incorporated, where appropriate, to further refine the proposal
Long-term Batch Process revisions: development of the enduring batch framework is out of scope for the current filing. ERCOT will incorporate lessons learned from Batch Zero to inform future revision requests and the design of a durable, repeatable batch study process

## Slide 8: Agenda
Timeline and governance recap
Feb 26 Workshop Feedback
  FAQs and common stakeholder questions
  Results from stakeholder feedback survey
Batch Zero PGRR Deep Dive
PGRR stakeholder feedback
Follow-on Discussion: CLR and BYOG
Q&A
Appendix

## Slide 9: Frequently Asked Questions (1/3)
Source: ERCOT discussions, Feb 26th LLI Batch Study Workshop
Batch Zero process timeline and decision points
Batch Zero and planning integration
“When will the Batch Zero Study allocation be finalized and communicated?”
Allocation timing is tied to completion of the Batch Zero study phase. Under the draft PGRR145 timeline, allocation results would be issued in January 2027; final dates will be confirmed following finalization of PGRR145
“Can the 30-day commitment window be extended?”
ERCOT intends to maintain a 30-day commitment window consistent with the draft PFP in PUCT Project No. 58481. The full Batch Zero schedule, including the commitment deadline, will be published in advance
“How can Batch 1 proceed before Batch Zero Year-6 transmission solutions are fully identified and vetted?”
Under a 6-month cadence, each batch produces actionable results for Years 1–5, while Year-6 transmission solutions may continue through the RTP/RPG process. This reflects a tradeoff between speed and full transmission vetting
“What is the date for meeting commitment criteria?”
The date for meeting commitment criteria is proposed as March 1, 2027 in PGRR145 (9.3.1)
“Is it possible to include a second, post-refinement decision point for participant opt-out?”
ERCOT is designing Batch Zero with one binding commitment point. Refinement does not change the committed ramp and is not intended to increase costs; it only finalizes the transmission solution. A second opt-out would reintroduce restudy loop risk
Topic
Representative question
ERCOT answer

## Slide 10: Frequently Asked Questions (2/3)
Source: ERCOT discussions, Feb 26th LLI Batch Study Workshop
Topic
Representative question
ERCOT answer
“How are in-flight RPG projects incorporated into Batch Zero?”
Projects that have progressed through RPG and received endorsement at the start of Batch Zero will be treated consistent with established planning practices and be incorporated into Batch Zero study
“How does Batch Zero interact with the 2026 and 2027 RTP?”
Based on the current sequencing, Batch Zero will not affect the 2026 RTP because commitment occurs after the 2026 RTP modeling cycle is complete. Loads that meet commitment milestones in March 2027 may be incorporated into the 2027 RTP. Final timing alignment depends on finalization of PGRR145 and publication of the Batch Zero schedule
Batch Zero and planning integration
Transmission upgrades
“How are multi-year (Year-6) upgrades and base cases handled?”
ERCOT recognizes that Year-6 solutions may involve complex, multi-year transmission upgrades. Batch Zero establishes a committed load baseline and provides earlier clarity on required improvements. Long-duration upgrades will continue to proceed through established transmission planning processes, including RTP and RPG pathways
“If no reliable transmission solution exists within the study horizon, how will allocated MW be handled?”
Within Years 1–5, ERCOT will allocate the MW that can be reliably served based on existing system capability. Projects may receive partial allocations during this period if constraints exist. By Year 6, assumption is that RTP process will identify the transmission upgrades necessary to serve the full committed load. Accordingly, Year 6 reflects full service (100%) of the committed MW

## Slide 11: Frequently Asked Questions (3/3)
Source: ERCOT discussions, Feb 26th LLI Batch Study Workshop
Topic
Representative question
ERCOT answer
Allocation outcomes and ramp schedules
“If a project drops out, are MWs reallocated within the same batch?”
No. ERCOT is not planning to reallocate MWs within Batch Zero after commitment because it creates complexity and reopens restudy cycles. Additional MWs would generally be addressed in subsequent batches, maintaining process stability and schedule certainty
“Can ERCOT change the MW allocations after commitment?”
No. For Batch Zero after the commitment point, the MW allocation by year is locked. The refinement phase is intended to finalize only the transmission plan, not reduce MW or delay delivery years for committed MW
Financial security and cost responsibility
“Are financial obligations (including CIAC and security) locked at commitment?”
Based on the draft PFP for PUCT Project No. 58481, ERCOT is proposing that financial obligations are established and locked at the commitment point. The refinement phase may adjust transmission solution details, but it is not intended to re-price commitments or introduce post-commitment true-ups. The process is designed to provide cost certainty and avoid reopening financial obligations in subsequent planning steps
Study modeling
“How will additional generation be modeled in Batch Zero?”
ERCOT will apply the methodology established in PGRR127 when modeling additional generation in Batch Zero Study cases. The modeling approach and associated assumptions will be documented in the published case assumptions to ensure transparency and consistency
“Does Batch Zero include a low-solar scenario?”
The Batch Zero Study includes a no-solar scenario intended to reflect stressed conditions

## Slide 12: Agenda
Timeline and governance recap
Feb 26 Workshop Feedback
  FAQs and common stakeholder questions
  Results from stakeholder feedback survey
Batch Zero PGRR Deep Dive
PGRR stakeholder feedback
Follow-on Discussion: CLR and BYOG
Q&A
Appendix

## Slide 13: Survey responses overview and organization demographics dashboard
87
Individual organizations surveyed
64
Average responses per multiple choice question
Chart: 
 | 68 | 32
Yes
No
68%
32%
Respondents previously interviewed by ERCOT in LLI stakeholder process (% of overall respondents)
Organizational distribution (% of respondents)
Chart: 
 | 5.7471 | 6.8966 | 6.8966 | 11.4943 | 5.7471 | 0 | 1.1494 | 39.0805 | 13.7931 | 2.2989 | 1.1494 | 0 | 5.7471
Investor-Owned Utilities (IOUs)
Municipals
Cooperatives (Co-ops)
Hyperscalers
Co-locators
Consumers (Residential/Commercial)
Industrial/Large Load Consumers
Developers
Independent Generators
Independent Power Marketers
Independent Retail Electric Provider (REPs)
Research Organizations
Other (please specify)
6%
7%
7%
11%
6%
0%
1%
39%
14%
2%
1%
0%
6%
T(D)SPs
Other
LL Customers
Generators
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 14: The survey covered six areas and contained 20 questions
Survey section
Questions
Topics covered
A
2 Multiple choices
3 Free response
Screener
Respondent identification and stakeholder segmentation, including organization type and prior engagement with ERCOT on the Batch Study process
B
2 Multiple choices
3 Free response
Eligibility and screening
Batch Zero entry criteria, including development activity milestones, study completion cut-off dates, interconnection agreement timing, and evidence of project readiness
C
3 Multiple choices
Design of Batch Zero
Stakeholder alignment on Batch Zero principles, refinement study methodology, and preferred study cadence and transmission upgrade identification approach
D
1 Multiple choice
Commitment and risk allocation
Treatment of financial commitments and load ramp adjustments during refinement studies, including whether commitments should be fixed, adjustable, or re-opened
E
1 Multiple choice
Confidentiality and transparency
Determination of which Batch Study data elements should remain confidential versus publicly disclosed
F
5 Multiple choice
CLR and BYOG
Preferred co-location configurations and BYOG policy design
20 questions (14 multiple choice, 6 free response)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
Not covered in following pages

## Slide 15: Process redesign survey insights summary
Eligibility and screening
Partially complete studies cutoff
B2
Stakeholders show a clear preference for a June 2026 cutoff date to determine Batch Zero eligibility for partially complete studies
Development activity cutoff
B1
Stakeholders show a preference for a December 2027 latest in-service date to demonstrate development activity
Key insights
Key questions
Module
Interm./interconnection agreement criteria cutoff
B3
Stakeholders show the strongest preference for a July 2026 deadline to meet agreement criteria for Batch Zero inclusion
Development activity
B4
Stakeholders strongly favor site preparation and construction as proof of development activity, with additional emphasis on capital commitment, site control, and interconnection readiness
Site preparation and construction
B5
Stakeholders strongly favor defining “site preparation and construction” through site control and posted financial security, also supporting staged engineering, permitting, and equipment-deposit
Design of Batch Zero
Fundamental principles
C1
Stakeholders show support for ERCOT’s Batch Zero principles, though the relatively close split indicates meaningful stakeholder sensitivity to how the framework is implemented
Refinement study approach
C2
Stakeholders broadly support the proposed refinement study approach, though a minority signals sensitivity to implementation details
Transmission upgrade process and design
C3
Stakeholders overwhelmingly favor a shorter 6-month Batch Study timeline, signaling a strong preference for speed and process efficiency over a longer study duration
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
Commitment and risk allocation
Final commitment period
D1
Stakeholders broadly favor preserving flexibility in load ramp and financial commitments as cost estimates evolve, with limited support for rigid or fully re-opened allocation approaches
Confidentiality and transparency
Publicly disclosed information
E1
Stakeholders strongly support protecting customer identity and commercially sensitive project data, signaling a preference for transparency at the system level

## Slide 16: Eligibility and screening: Development activity cutoff date
B1
“What should be the latest in-service date for projects that will be required to demonstrate development activity?” (% of overall respondents)
Commentary
Majority of respondents (24%) support a December 2027 latest in-service date requirement for demonstrating development activity, with more limited support for alternative dates (e.g., 9% for Jun/Dec 2026 and Jun 2027)
Chart: 
 | 3.0303 | 3.0303 | 3.0303 | 3.0303 | 3.0303 | 3.0303 | 3.0303 | 3.0303 | 21.2121 | 6.0606 | 3.0303 | 3.0303 | 3.0303 | 3.0303 | 3.0303 | 3.0303
 | 6.0606 | 3.0303 | 6.0606 | 3.0303 | 3.0303 | 3.0303 | 3.0303
 | 3.0303
Feb-26
Mar-26
Apr-26
May-26
6%
3%
Jun-26
Jul-26
Aug-26
Sep-26
Oct-26
Nov-26
3%
3%
3%
Dec-26
3%
Jan-27
3%
Feb-27
3%
Mar-27
3%
Apr-27
May-27
6%
3%
Jun-27
Jul-27
3%
Aug-27
Sep-27
Oct-27
Nov-27
3%
21%
Dec-27
6%
Jan-28
Feb-28
3%
Mar-28
Apr-28
3%
3%
May-28
Jun-28
Jul-28
Aug-28
Sep-28
Oct-28
Nov-28
3%
3%
Dec-28
3%
Jan-29
Feb-29
Mar-29
Apr-29
May-29
Jun-29
3%
Jul-29
Aug-29
Jan-26
Oct-29
Nov-29
3%
Dec-29
9%
9%
3%
3%
3%
3%
Sep-29
3%
24%
6%
3%
6%
6%
3%
3%
6%
3%
9%
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
T(D)SPs
LL Customers
Generators
N=33 (6 T(D)SPs, 21 LLC, 6 Generators)

## Slide 17: Eligibility and screening: Partially complete studies cutoff date
B2
“What date should ERCOT use to determine whether partially complete studies are eligible for inclusion in Batch Zero?” (% of overall respondents)
Commentary
Majority of respondents (42%) support using June 2026 as the cutoff date to determine eligibility of partially complete studies for Batch Zero inclusion, with more limited support for alternative dates (e.g., 17% for Jul 2026, 14% for May 2026)
Chart: 
 | 2.7778 | 2.7778 | 2.7778 | 5.5556 | 5.5556 | 2.7778 | 5.5556 | 2.7778 | 2.7778
 | 2.7778 | 2.7778 | 5.5556 | 27.7778 | 5.5556
 | 2.7778 | 2.7778 | 8.3333 | 8.3333
Feb-26
Mar-26
Apr-26
May-26
28%
Jun-26
Jul-26
Aug-26
Sep-26
Oct-26
Nov-26
Dec-26
Jan-27
Feb-27
Mar-27
Apr-27
May-27
Jun-27
Jul-27
Aug-27
Sep-27
Oct-27
Nov-27
Dec-27
Jan-28
Feb-28
Mar-28
Apr-28
May-28
Jun-28
Jul-28
Aug-28
Sep-28
Oct-28
Nov-28
Dec-28
Jan-29
Feb-29
Mar-29
Apr-29
May-29
Jun-29
Jul-29
Aug-29
Sep-29
Oct-29
Nov-29
Dec-29
42%
3%
14%
6%
Jan-26
17%
6%
8%
6%
8%
3%
3%
3%
8%
3%
3%
6%
6%
3%
3%
3%
3%
6%
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
T(D)SPs
LL Customers
Generators
Other
N=36 (10 T(D)SPs, 19 LLC, 6 Generators, 1 Other)

## Slide 18: Eligibility and screening: Intermediate or interconnection agreement criteria cutoff date
B3
“What date should ERCOT set for projects to meet the intermediate agreement or interconnection agreement criteria to be included in Batch Zero?” (% of overall respondents)
Commentary
Majority of respondents (26%) support setting July 2026 as the deadline for meeting intermediate or interconnection agreement criteria for Batch Zero inclusion, with June 2026 (24%) and May/Sep 2026 (12%) also receiving notable support
Chart: 
 | 2.9412 | 8.8235 | 11.7647 | 5.8824 | 2.9412 | 5.8824 | 2.9412 | 2.9412 | 2.9412 | 2.9412
 | 14.7059 | 2.9412 | 8.8235
 | 2.9412 | 11.7647
 | 8.8235
Feb-26
Mar-26
Apr-26
May-26
3%
15%
6%
Jun-26
9%
12%
Jul-26
Aug-26
Sep-26
Oct-26
Nov-26
Dec-26
Jan-27
Feb-27
Mar-27
Apr-27
May-27
Jun-27
Jul-27
Aug-27
Sep-27
Oct-27
Nov-27
Dec-27
Jan-28
Feb-28
Mar-28
Apr-28
May-28
Jun-28
Jul-28
Aug-28
Sep-28
Oct-28
Nov-28
Dec-28
Jan-29
Feb-29
Mar-29
Apr-29
May-29
Jun-29
Jul-29
Aug-29
Sep-29
Oct-29
Jan-26
Dec-29
3%
9%
12%
24%
26%
6%
Nov-29
3%
12%
3%
9%
3%
3%
3%
3%
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
T(D)SPs
LL Customers
Generators
Other
N=34 (9 T(D)SPs, 19 LLC, 5 Generators, 1 Other)

## Slide 19: Eligibility and screening: Development activity
“What information should be required for projects to demonstrate development activity?” (% of overall respondents that selected a specific option)
Commentary
Majority of respondents favor requiring site preparation and construction as proof of development activity (65%), with the next tier of support clustered around capital-equipment milestones (47%) and other proposed criteria (49%)
General stakeholder alignment:
  “Large Load customers”, “Generators,” and “Other” stakeholders are most aligned around site preparation and construction
  “T(D)SPs” show comparatively stronger emphasis on the purchase of customer-owned high-voltage transformers and circuit breakers
Other criteria suggested:
  Evidence of financial commitment (e.g., deposits posted, equipment orders placed, security provided) vs. full equipment purchase
  Demonstrated site control, zoning approvals, and permitting progress
  Engineering and interconnection readiness milestones (e.g., executed agreements, modeling data submitted, EPC contracts)
  Commercial firmness indicators (e.g., PPAs)
Chart: 
 | 4.4118 | 7.3529 | 5.8824 | 7.3529
 | 1.4706 | 5.8824 | 2.9412 | 2.9412
 | 13.2353 | 41.1765 | 25 | 26.4706
 | 7.3529 | 10.2941 | 13.2353 | 11.7647
7%
13%
1%
4%
Inclusion in a Quarterly Stability Assessment
10%
41%
6%
7%
Site preparation and construction
13%
25%
3%
6%
Purchase of all necessary customer-owned high-voltage transformers and circuit breakers with delivery by project in-service date
12%
26%
3%
7%
Other
26%
65%
47%
49%
T(D)SPs
LL Customers
Other
Generators
B4
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
N=68 (14 T(D)SPs, 40 LLC, 5 Other, 9 Generators). Note: respondents could multi-select responses so total % > 100

## Slide 20: Eligibility and screening: Site preparation and construction
“How should ERCOT define ‘site preparation and construction’ for Batch Zero eligibility” (% of overall respondents that selected a specific option)
Commentary
Chart: 
 | 2.9412 | 10.2941 | 10.2941 | 4.4118 | 7.3529 | 7.3529 | 7.3529 | 4.4118 | 5.8824
 | 5.8824 | 7.3529 | 5.8824 | 4.4118 | 2.9412 | 4.4118 | 2.9412 | 2.9412 | 2.9412
 | 39.7059 | 51.4706 | 51.4706 | 30.8824 | 32.3529 | 33.8235 | 16.1765 | 13.2353 | 16.1765
 | 8.8235 | 14.7059 | 17.6471 | 5.8824 | 11.7647 | 14.7059 | 7.3529 | 7.3529 | 10.2941
40%
6%
3%
Executed interconnection agreement
15%
51%
7%
10%
Posted financial security / deposits
18%
51%
6%
10%
Site control (owned or long-term leased land)
6%
31%
4%
4%
Engineering design completed
12%
32%
3%
7%
High-voltage (HV) transformer deposits placed
15%
34%
4%
7%
Breaker or major electrical equipment deposits placed
7%
16%
3%
7%
Civil construction commenced
7%
13%
3%
4%
Purchase of all necessary customer-owned high-voltage transformers and circuit breakers
10%
16%
9%
6%
Other
57%
84%
85%
3%
54%
60%
34%
28%
35%
46%
T(D)SPs
LL Customers
Other
Generators
B5
Strong majority of respondents favor defining site preparation and construction to include posted financial security/deposits (84%) and demonstrated site control (85%), with support for breaker or major electrical equipment deposits (60%), executed interconnection agreements (57%), and HV transformer deposits (54%)
General stakeholder alignment: “T(D)SPs,” “Large Load customers,” “Generators,” and “Other” stakeholders are broadly aligned around site control and posted financial security as the primary components of defining site preparation and construction eligibility
Other suggestions:
  Clarify key definitions (e.g., financial security, purchase vs. deposit, intermediate/ interconnection agreements) and avoid subjective eligibility standards
  Recognize staged development milestones, including engineering progress, civil construction commencement, and permitting approvals
  Allow flexibility in equipment procurement and sequencing (e.g., deposits, ramp-aligned purchases, portfolio-based procurement)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
N=68 (14 T(D)SPs, 40 LLC, 5 Other, 9 Generators). Note: respondents could multi-select responses so total % > 100

## Slide 21: Design of Batch Zero: Fundamental principles
Commentary
Majority of respondents (55%) agree with ERCOT’s fundamental principles for Batch Zero, while a sizable minority (45%) do not
Mixed stakeholder alignment: “T(D)SPs,” and “Generators” stakeholders show clear majority support for proposed fundamental principles, “Large Load customers” are ambivalent while and “Other” stakeholders are opposed
Reasons of opposition:
  Concern over retroactive application of proposed PUCT 58481 rules and potential invalidation of previously approved studies or allocated MW
  Objection to reallocation of non-utilized capacity and the $100k/MW financial security requirement, viewed as economically harmful and premature
  Risk of inequitable treatment due to TSP-driven delays, potentially disadvantaging projects through no fault of developers
  Need for clearer alignment with SB6 and final PUCT gating rules before implementing Batch Zero criteria
Chart: 
 | 10.6061 | 4.5455
 | 3.0303 | 6.0606
 | 28.7879 | 28.7879
 | 12.1212 | 6.0606
Yes
No
55%
45%
12%
29%
3%
11%
6%
29%
6%
5%
T(D)SPs
LL Customers
Other
Generators
N=66 (12 T(D)SPs, 38 LLC, 6 Other, 10 Generators)
C1
“Do you agree with ERCOT’s fundamental principles for Batch Zero?” (% of overall respondents)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 22: Design of Batch Zero: Refinement study approach
Commentary
Strong majority of respondents (70%) agree with the proposed Batch Zero refinement study approach, while a smaller share (30%) do not
Overall stakeholder alignment: “T(D)SPs,” “Large Load customers,” “Generators,” and “Other” stakeholders each show majority support for the refinement study approach
Reasons of opposition:
  Concern that the refinement study could delay projects or overlap with subsequent batches, creating inefficiencies, restudies, or uncertainty
  Need for clearer criteria, sequencing, and operational transparency
  Risk that the process could reopen or effectively restudy previously approved projects, penalizing investments made under earlier assumptions
  Requirement to ensure alignment with statutory timelines (e.g., PURA 120-day requirement) and avoid conflict with SB6/net-metering review processes
  Objections to certain implementation elements, including the $100k/MW security requirement and extended governance approval timelines
Chart: 
 | 8.9552 | 5.9701
 | 5.9701 | 2.9851
 | 40.2985 | 17.9104
 | 14.9254 | 2.9851
Yes
No
70%
30%
3%
15%
40%
6%
9%
18%
3%
6%
T(D)SPs
LL Customers
Other
Generators
N=67 (12 T(D)SPs, 39 LLC, 6 Other, 10 Generators)
C2
“Do you agree with the proposed Batch Zero refinement study approach?” (% of overall respondents)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 23: Design of Batch Zero: Transmission upgrade process and design
“Which transmission upgrade-Batch Study process would you prefer?” (% of overall respondents)
Commentary
Chart: 
 | 13.4328 | 1.4925
 | 4.4776 | 0
 | 58.209 | 2.9851
 | 13.4328 | 5.9701
13%
58%
13%
6-month Batch Study option
6%
3%
12-month Batch Study option
90%
10%
4%
1%
T(D)SPs
LL Customers
Generators
Other
N=67 (13 T(D)SPs, 41 LLC, 3 Other, 10 Generators)
C3
Strong majority of respondents (90%) prefer the 6-month Batch Study option, while a small minority (10%) favor the 12-month option
Overall stakeholder alignment: “T(D)SPs,” “Large Load customers,” “Generators,” and “Other” stakeholders each show strong majority preference for the 6-month Batch Study option
12-month Batch support: the data within the data indicates most large T(D)SPs favor the 12-month Batch
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 24: Commitment and allocation: Final commitment period
“[…], some participants were considering a final commitment period after refinement period. In this case, how should cost and load ramp differences during subsequent study refinements?” (% of overall respondents)
D1
Chart: 
 | 1.4706 | 5.8824 | 17.6471 | 4.4118 | 2.9412
 | 4.4118 | 1.4706 | 4.4118 | 0 | 1.4706
 | 16.1765 | 7.3529 | 0 | 4.4118 | 11.7647
 | 7.3529 | 4.4118 | 0 | 0 | 4.4118
7%
16%
4%
1%
Adjust load ramp and financial security upward or downward based on updated cost estimates
4%
7%
1%
6%
Lock original load ramp and financial commitment regardless of later cost adjustments
4%
18%
Allow limited adjustment within a defined tolerance band (e.g., ±10%)
4%
4%
Re-open allocation decision if cost materially changes
4%
12%
1%
3%
Other
29%
19%
22%
9%
21%
N=68 (14 T(D)SPs, 39 LLC, 5 Other, 10 Generators)
Commentary
Majority of respondents favor adjusting the load ramp and financial security upward or downward based on updated cost estimates (29%) followed by allowing limited adjustment within a defined tolerance band (22%) and other alternative approaches (21%)
Mixed stakeholder alignment: “T(D)SPs,” “Large Load customers,” and “Other” stakeholders are aligned around allowing flexibility to adjust commitments, while “Generators” show comparatively stronger support for locking the original load ramp and financial commitment
Other suggestions:
  Preference for allowing downward or capped adjustments
  Emphasis on avoiding additional restudies or extended commitment windows
  Requests for caps and refundability of financial security, especially if costs decline or projects cannot proceed due to study outcomes
  View that cost and collateral adjustments should align with final PUCT 58481 rules, with TSPs managing security true-ups
T(D)SPs
LL Customers
Other
Generators
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 25: Confidentiality and transparency: Publicly disclosed information
Commentary
E1
“What should remain confidential? Select all information elements that you believe should not be publicly disclosed” (% of overall respondents that selected a specific option)
Chart: 
 | 1.4925 | 8.9552 | 5.9701 | 1.4925 | 1.4925 | 1.4925 | 1.4925 | 2.9851 | 2.9851 | 4.4776 | 5.9701 | 5.9701
 | 0 | 2.9851 | 1.4925 | 1.4925 | 1.4925 | 0 | 0 | 1.4925 | 1.4925 | 1.4925 | 2.9851 | 2.9851
 | 8.9552 | 52.2388 | 22.3881 | 14.9254 | 14.9254 | 8.9552 | 16.4179 | 29.8507 | 28.3582 | 22.3881 | 28.3582 | 16.4179
 | 2.9851 | 14.9254 | 4.4776 | 2.9851 | 4.4776 | 2.9851 | 2.9851 | 10.4478 | 2.9851 | 4.4776 | 10.4478 | 10.4478
9%
1%
LLIS and status (no customer identity)
15%
52%
3%
9%
Customer identity
4%
22%
1%
6%
POI
3%
15%
1%
1%
Requested MW
4%
15%
1%
1%
Awarded MW (by year)
3%
9%
1%
Transmission upgrade list
3%
16%
1%
Upgrade cost estimates
10%
30%
1%
3%
Financial commitment amounts
3%
28%
1%
3%
Ramp schedule
4%
22%
1%
4%
Study results
10%
28%
3%
6%
Development milestones
10%
3%
3%
6%
Other
13%
79%
34%
21%
16%
13%
21%
45%
36%
33%
48%
36%
22%
T(D)SPs
LL Customers
Other
Generators
Strong majority of respondents favor keeping customer identity (79%) confidential, followed by development milestones (48%) and financial commitment amounts (45%)
Broad stakeholder alignment: “T(D)SPs,” “Large Load customers,” “Generators,” and “Other” stakeholders are aligned in prioritizing protection of customer identity and commercially sensitive information
Other suggestions:
  Maintain strict protection of CEII and legally protected customer data, consistent with ERCOT protocols and PURA requirements
  Provide aggregated and anonymized disclosures (e.g., county-level or weather zone level) to preserve market transparency without revealing project-specific identities
  Improve direct transparency between ERCOT, TSPs, and individual customers (e.g., secure portals), rather than broad public dashboards
  Align disclosure standards with generator interconnection processes and final PUCT 58481 rules
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
N=67 (13 T(D)SPs, 41 LLC, 5 Other, 8 Generators). Note: respondents could multi-select responses so total % > 100

## Slide 26: Agenda
Timeline and governance recap
Feb 26 Workshop Feedback
  FAQs and common stakeholder questions
  Results from stakeholder feedback survey
Batch Zero PGRR Deep Dive
PGRR stakeholder feedback
Follow-on Discussion: CLR and BYOG
Q&A
Appendix

## Slide 27: Batch Zero Overview – Two Phases
Study Inputs
Batch Zero Study
Batch Zero Refinement
ILLE Commitment Period
Transmission Plan to RPG
6 months
3 months
  Steady state study and dynamic stability screening
  Identify planning criteria violations
  Work iteratively with TSPs to determine amount of load that can be reliably served in each year and, where feasible, upgrades needed to serve full load request
Work iteratively with TSPs to
  Determine which upgrades are still needed based on ILLE commitments
  Review cost estimates and alternative upgrade options
  Develop a transmission plan to serve committed loads
Reference: Batch Zero PGRR, Sections 9.3–9.5 (Study Phase, Commitment Gate, and Refinement Phase)

## Slide 28: Batch Zero Study Scope Overview
  Study horizon: 2028–2032 (Years 1–5), load amounts not reliably served within 2028-2032, will receive full allocation in 2033 (Year 6)
  What ERCOT studies (per year): ERCOT builds cases from SSWG base cases and runs reliability assessment across:
    Summer peak load (high load system stress)
    Summer, no solar (sunset, net peak load)
    Fall peak (used to assess maintenance outage conditions consistent with ERCOT Planning Guide criteria)
  Reliability assessment coverage:
    Evaluate planning criteria violations triggered by adding the Batch Zero loads (across scenarios/contingencies ERCOT selects)
    Determine “reliably served MW” per load, per year (i.e., deliverable load that can be served without violating planning criteria)
    Load that cannot reliably be served in years 1-5 will be allocated in year 6 (2033).
  Generation assumptions: if additional generation is needed to serve the modeled load, ERCOT models generation additions consistent with applicable planning methodologies
  Transparency: ERCOT posts the study cases used for Batch Zero on the MIS Certified Area once available
Scope details
Key Design Considerations
  One consistent, system-wide reliability study: ERCOT evaluates all Batch Zero-eligible Large Loads using a common set of assumptions, criteria, and cases to identify system limitations and needed upgrades
  Clear, year-by-year outcomes: for each assessed Large Load, the study determines the maximum peak MW that can be reliably served each year (2028–2033) and the transmission upgrades needed to increase service toward the requested level
XXX Changes/ Clarification vs. Feb 26th Workshop
Reference: Batch Zero PGRR, Sections 9.3.1–9.3.2 (Batch Zero Study and Methodology)

## Slide 29: Batch Zero Study Methodology and Study Elements
Study elements and methodology
Key Design Considerations
  Study must be repeatable and explainable: ERCOT uses transparent study inputs (posted cases), consistent criteria, and a clear link from violations to upgrades to year-by-year reliably served MW
  Actionable coordination: the process enables rapid, iterative ERCOT–TSP alignment on transmission improvements while the study is underway
  Prepare system-wide study cases (ERCOT)
    Develop annual cases for 2028–2032 from SSWG base cases
    Add Batch Zero-eligible Large Loads per the inclusion criteria and model treatment rules
    Post cases to MIS Certified once available
  System-wide reliability assessment (ERCOT)
    Study scenarios and contingencies ERCOT determines are needed to evaluate reliability impacts
    For each assessed LL, identify planning criteria violations associated with the proposed addition
    Determine the amount of peak load that can be reliably served each year
  Stability screening assessment (ERCOT)
    Perform the stability component of the Batch Zero study
    Document identified stability issues and reflect any resulting limitations in year-by-year reliably served MW
  Identify transmission improvements (ERCOT and impacted TSPs)
    Once violations are identified, ERCOT initiates communication with relevant TSPs
    TSPs provide upgrade recommendations; ERCOT and TSPs iterate through the study period until needed upgrades are identified
    Results translate into upgrades resolving violations/enabling higher reliably served MW over time
  Supporting prerequisites (TDSPs/TSPs, as applicable)
    Short-circuit and other relevant studies are completed by the interconnecting TDSP/TSP at least 30 days before ERCOT issues Batch Zero awards/results
    TDSPs/TSPs provide necessary model information prior to start of Batch Zero
Reference: Batch Zero PGRR, Sections 9.3.1–9.3.2 (Batch Zero Study Scope, Methodology, and Coordination)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 30: Outputs, Deliverables, and Timeline
Process and outputs
  Core timeline
    By July 15, 2026: required project info submitted for inclusion
    January 29, 2027: ERCOT issues the Batch Zero Study Report, provides Load Commissioning Plans (LCPs) and notifies TSPs of Batch Zero results
    March 1, 2027: TDSPs notify ERCOT which Large Loads have met commitment requirements
    June 1, 2027: ERCOT completes the Batch Zero Refinement Study and delivers the Batch Zero Transmission Plan to RPG
  Primary outputs
    Batch Zero Study Report (summary of reliability impacts, identified planning criteria violations, and proposed transmission upgrades)
    Load Commissioning Plan (LCP) per Large Load
      Maximum reliably served peak MW for each year (2028–2033)
        Loads not reliably served receive full requested allocation for year 2033
    Estimated security requirements and CIAC obligations required to inform ILLE commitment decisions
    Confidential TSP package: detailed upgrade list and associated Large Loads (as applicable)
  Refinement and RPG handoff
    Only Large Loads that meet commitment milestones remain in scope
    MW allocations for Large Loads that meet commitment criteria by the deadline are not adjusted during the Refinement Study
    ERCOT re-evaluates whether previously identified upgrades are still needed/modified/no longer required
    Final Batch Zero Transmission Plan is delivered into the RPG process
  Actionable outcomes: each Large Load receives a year-by-year Load Commissioning Plan (LCP) and estimated security requirements to support commitment decisions. TSPs receive
  Clear commitment gate to planning certainty: only Large Loads that meet commitment milestones move into the Refinement Study and transmission plan delivered to RPG
Key Design Considerations
Reference: Batch Zero PGRR, Sections 9.3.1, 9.4, and 9.5 (Timeline, Outputs, and Refinement Process)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 31: Batch Zero process flow chart for studied load
Submit intermediate agreement requirements
Sign intermediate agreement & Send Batch Info to ERCOT
Build Cases & Post on MIS Certified
Perform Batch Steady State Study
Perform transmission improvement analysis
Perform Short Circuit, SSR Screening, and Facilities Studies
Communicate Results
Submit interconnection agreement requirements
Sign interconnection agreement
Perform Refinement Transmission Plan Study
Provide Cost Estimates and Final Review
Submit Refinement Transmission Plan Study for RPG Review
Resolve RPG Comments and Seek BOD endorsement, when necessary
ERCOT
T(D)SP
Developer (Interconnecting Large Load Entity – ILLE)
Perform Batch Stability Screening Study

## Slide 32: Proposed Batch Zero Timeline
1
2
3
4
5
6
7
8
9
9
Batch Refinement Study:
ERCOT: determine which transmission improvements identified in the Batch study are still required based on which loads met the commitment requirements
TSPs: provide cost estimates and refinement of transmission improvement projects and alternatives
ERCOT: final analysis of alternatives and determinization of final set of transmission improvement projects
ERCOT: prepare final report and submit to RPG
2026
2027
Aug
Sep
Oct
Nov
Jul
Dec
Feb
Mar
Apr
May
Jun
Jul
Aug
Jan
Sep
RPG Comment Period (3 weeks)
RPG Study Mode (4-weeks, if required)
TAC (August 2027)
Board (September 2027)
2026 RTP
Final Report (2 weeks)
2027 RTP
Batch Zero (Study years 2028-2032)
Stability Screening Study (14 weeks)
Steady State Analysis (15 weeks)
Developer Commitment Deadline
FAC-002 Stability
Batch Refinement Study (13 weeks)
Case Build (13 weeks)
Steady State and Stability Analyses:
ERCOT: identification of criteria violations
ERCOT and TSPs: identification of transmission improvement projects and alternatives to resolve violations
TSPs: determination of transmission improvement feasibility and schedule
TSPs: provide transmission improvement cost estimates
ERCOT: final determination of transmission improvement projects that are feasible
ERCOT: allocate MWs to loads
ERCOT: create load request to transmission improvement mapping
Reference: Batch Zero PGRR, Sections 9.3–9.5 (Study Timeline, Commitment Gate, Refinement, and RPG Delivery)

## Slide 33: Case Build
Details
Key Design Considerations
1
  Standardized ERCOT intake and deadline
  Clear eligibility and inclusion rules for Batch Zero
  Defined modeling treatment at entry
  Transparent study case development
  For Batch Zero, the interconnecting TDSP submits required project information and any required attestations related to executed agreements or equipment procurement by the applicable deadlines
  ERCOT applies the Batch Zero eligibility criteria to determine which Large Loads are included and whether they are treated as base load not subject to further evaluation or load subject to reliability assessment and allocation including ERCOTs determination of whether existing interconnection studies are complete and valid for eligibility treatment
  Projects that do not meet the criteria or fail to submit required information by the deadline are not included
  ERCOT develops the 2028–2032 study cases using SSWG-based summer peak, summer peak net load, and fall peak cases, and posts those cases to the MIS Certified area to provide transparency into study assumptions
Reference: Batch Zero PGRR, Sections 9.2.1–9.2.2 and 9.3.2 (Eligibility Determination and Study Case Development)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 34: Steady State Analysis
Details
Key Design Considerations
2
  ERCOT performs a singular, system-wide steady-state study for all Large Loads included in Batch Zero using SSWG derived base cases appropriate for the study horizon
  ERCOT studies all scenarios and contingencies necessary to assess reliability with applicable NERC Reliability Standards, ERCOT Protocols, the Planning Guide, and Operating Guides
  As soon as violations are identified, ERCOT begins collaborative, iterative process working with TSPs to identify feasible transmission upgrades to serve the Large Loads
  For each Large Load subject to assessment, ERCOT documents planning criteria violations and determines the amount of peak Demand that may be reliably served for each year of the 2028–2032 study period. The amount of load that may be reliably served for 2033 will be set to the requested amount
  Single, system-wide ERCOT study
  Reliability-based contingency analysis
  Identification of planning criteria violations
  Determination of reliably served MW by year
Reference: Batch Zero PGRR, Sections 9.3.1(1)–(2) (Batch Zero Overview) and 9.3.2(1), (3) (Batch Zero Study Methodology)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 35: Stability Screening Study
3
Details
Key Design Considerations
  Maintain sufficient stability margin
  Mitigation of identified instability
  Coordination with TSPs
  If stability screening criteria violation is identified, ERCOT and the applicable TSP(s) investigates mitigation measures, including transmission improvements, and identifies any required modifications to load levels or timing reflected in the Load Commissioning Plan and determines the amount of peak Demand that can be reliably served in each study year consistent with applicable planning criteria and identified violations, including stability constraints
Reference: Batch Zero PGRR, Sections 9.3.1(1), 9.3.2(3), and 9.3.4.3 (Batch Zero Study – Stability Screening and Mitigation)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 36: Final Report
4
Details
Key Design Considerations
  Actionable study outcome
  Clear MW allocations by year
  Identification of required upgrades
  Security visibility
  ERCOT produces the Batch Zero Report summarizing study results and proposed transmission upgrades
  For each assessed Large Load, ERCOT updates the originally provided Load Commissioning Plan reflecting the amount of peak Demand that can be reliably served each year and the upgrades required to support each level of Demand. The amount of load that may be reliably served for 2033 will be set to the requested amount
  TSP uses the Batch Zero Report and related study results to determine applicable financial security and CIAC obligations under the Interconnection Agreement
  Execution of the Interconnection Agreement reflecting required financial security and cost obligations is required for the ILLE to accept allocated MW amounts and schedule
Reference: Batch Zero PGRR, Sections 9.4(1)–(2), 9.5(1)–(5), and 9.7.2 (Batch Zero Report, Commitment, and Transmission Plan Delivery)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 37: Developer Commitment Deadline
5
Details
Key Design Considerations
  Clear commitment gate
  TDSP attestation as trigger
  Removal of non-committed projects
  Planning certainty before refinement
  To accept the allocated MW and schedule documented in the LCP, the ILLE must execute a binding Interconnection Agreement by the commitment deadline. The agreement must satisfy the requirements adopted in a final rule in Project No. 58481
  The interconnecting TDSP must submit formal attestation to ERCOT confirming that the ILLE has executed the Interconnection Agreement by the deadline. This attestation serves as verification that the load has satisfied the commitment requirement for inclusion in the Batch Zero Refinement Study
  Large Loads that do not satisfy the commitment requirement by the deadline are deemed withdrawn from the Batch Zero process and are excluded from the Refinement Study and resulting Transmission Plan
  MW allocations for Large Loads that meet the commitment requirement by the deadline are preserved and are not adjusted during the Refinement Study. The Refinement Study may modify recommended transmission facility improvements but does not revisit committed MW amounts
Reference: Batch Zero PGRR, Sections 9.4(2)–(3) and 9.5(5) (ILLE Commitment, Withdrawal, and MW Protection in Refinement)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 38: Batch Refinement Study
6
Details
Key Design Considerations
  Removal of non-committed loads
  Re-evaluation of identified upgrades
  Right-sizing of transmission scope
  Preparation of Transmission Plan for RPG
  Immediately following the commitment deadline, ERCOT updates the Batch Zero study to include only those Large Loads that met commitment requirements
  ERCOT evaluates whether the remaining loads continue to result in planning criteria violations and whether previously identified transmission upgrades are still needed, need modification, or are no longer required
  ERCOT works iteratively with relevant TSPs during this period and develops the final Transmission Plan to be delivered to RPG
  The Refinement Study may modify recommended transmission improvements but does not adjust MW allocations for Large Loads that met commitment criteria
  The Refinement Study results in a final report and recommended Transmission Facility improvements submitted for RPG Project Review
Reference: Batch Zero PGRR, Section 9.5(1)–(5) (Batch Zero Refinement Study and Transmission Plan Delivery)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 39: RPG Comment Period
7
update (highlight changes)
Details
Key Design Considerations
  Stakeholder review and transparency
  Time-bound comment process
  Preservation of governance pathway
  The Batch Refinement Study is submitted to the Regional Planning Group for review including recommended Transmission Facility improvements resulting from the Refinement Study
  Stakeholders are provided an opportunity to submit comments within a defined review period. RPG review focuses on the recommended Transmission Facility improvements identified in the Refinement Study and the associated technical assumptions
  RPG review does not reopen MW allocations for committed Large Loads
  RPG Project classification is based on the sum total of all transmission projects in the Refinement Study
Reference: Batch Zero PGRR, Sections 9.5(1)–(5) (Refinement Study and RPG Project Review)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 40: RPG Study Mode
8
Details
Key Design Considerations
  Targeted additional evaluation if necessary
  Focused response to material concerns
  If needed, ERCOT conducts limited additional study to address specific issues raised during RPG review, any additional study is limited to recommended Transmission Facility improvements and does not reopen MW allocations for committed Large Loads
  This step is intended to provide focused technical clarification rather than a full annual RTP-level re-evaluation
  The scope of RPG Study Mode is limited to evaluation of recommended Transmission Facility improvements identified in the Refinement Study
Reference: Batch Zero PGRR, Sections 9.5(1)–(5) (Refinement Study and RPG Project Review)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 41: TAC and Board
9
Details
Key Design Considerations
  Formal governance review
  Recommendation pathway
  Final approval authority
  ERCOT endorsement of recommended projects
  Following completion of RPG review and any additional study, the Batch Transmission Plan proceeds to TAC for consideration and recommendation in accordance with ERCOT governance procedures
  The ERCOT Board considers and acts on the recommended Transmission Plan resulting from the Batch Zero process. Board action applies to recommended Transmission Facility improvements identified in the Refinement Study
  MW allocations for Large Loads that meet commitment criteria are not adjusted during the Refinement Study and are not part of the Transmission Plan approval considered by TAC or the ERCOT Board
  Approval reflects ERCOT’s independent technical review, TSP coordination, and stakeholder input through the RPG process
Reference: Batch Zero PGRR, Section 9.5 (Batch Zero Refinement and Delivery of Transmission Plan) and Nodal Protocol Section 3.11.4
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 42: Steady-State Batch Study process: 6-month study cadence with continuous planning integration
Year 1
Year 2
Year 3
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Jan
Batch refinement and transmission plan finalization​
Batch refinement and transmission plan finalization​
6-month study
6-month study
6-month study
Batch Study process going live
Batch 0
Activity
Batch 1
Batch 2
Following completion of the batch study and confirmation of commitments, ERCOT advances the resulting transmission plan through the RPG process for stakeholder review and governance approval
A new batch begins every six months, ensuring predictable decision cycles without processing gaps and building on upgrades approved in prior cycles
ILLUSTRATIVE

## Slide 43: Fundamental Principles for ERCOT's Proposed Batch Zero Criteria
Senate Bill 6 and PUC Gating Rules: Utilize the gating criteria reflected in Project No. 58481 rulemaking to determine which large loads should be confirmed firm and which should be included to be studied in Batch Zero
Pre-Transition Processes: Respect to the extent feasible already granted approvals, including approval to energize and approved studies
Large Load Near-Term Energizations: Assess development activity for large loads that declare 2026 or 2027 energization to evaluate schedule feasibility
Reallocate Non-utilized Capacity: Release non-utilized large load capacity for use by other loads in accordance with Project No. 58481, new 16 TAC § 25.194
ERCOT’s Reliability Responsibility: Ensure all Large Loads confirmed to be firm in Batch Zero have been studied to show that the load can be served reliably

## Slide 44: Eligibility flowchart: how to assess if a load is included for Batch Zero?
1. See Batch Zero PGRR, Section 9.2.1.1(1)(a)–(b) (Eligibility Criteria for Inclusion as Base Load — Energized Loads) | 2. See Batch Zero PGRR, Section 9.2.1.1(1)(d)–(e) (Eligibility Criteria for Inclusion as Base Load — Requested Initial Energization Date Thresholds) | 3. See Batch Zero PGRR, Section 9.2.1.1(1)(d) (Eligibility Criteria for Inclusion as Base Load — Pre-2028 Loads) and Batch Zero PGRR, Section 9.2.1.1(1)(c)(i)–(ii) (Development activity attestation; QSA/interim VRT inclusion) | 4. See Batch Zero PGRR, Sections 9.2.1.4 and 9.2.1.1–9.2.1.2 (Evaluation of Existing Studies and Eligibility Treatment) | 5. See Batch Zero PGRR, Section 9.2.1.2(1) (Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero) | 6. See Batch Zero PGRR, Section 9.2.1.1(1)(a)–(b) and 9.2.1.1(2)(a)–(c) (Eligibility and Modeling for Base Load) | 7. See Batch Zero PGRR, Sections 9.2.1.2(1)(a)–(b) and 9.7.1 (Eligibility for Inclusion as Load to be Studied) | 8. See Batch Zero PGRR, Sections 9.2.1.3 and 9.2.2 (Load Not Included in Batch Zero)
Source: PGRR Batch Zero, March 4 2026
Has the load achieved Initial Energization?1
Large Load request
Included in Batch Zero as a base load6
Not included in Batch Zero8
Studied in Batch Zero and will receive load allocation amounts7
Yes
Is the requested Initial Energization date on or before December 31, 2027?2
No
Does the load, by the required deadline, either: (i) qualify via QSA / interim VRT inclusion and required attestations; OR (ii) have complete and valid studies, an executed Interconnection Agreement, and required development activity?3
Yes
Has the load executed an Intermediate Agreement and met the applicable eligibility criteria for inclusion as load to be studied?5
Does the load meet the eligibility criteria for inclusion as base load (including execution of an Interconnection Agreement)?4
Yes
Yes
No
Yes
No
1
2
3
4
4
5
X
Reference tracker
No
No

## Slide 45: Deep-dive: “Included as base load” (1/2)
If your Large Load by June 1, 2026 | Treatment in Transitional Process | MW Allocation
Is Operational or Approved to Energize | Included as base load | Loads operational before ERCOT’s interim LLI process will be allocated the MWs modeled in the 2025 RTP Loads operational after ERCOT’s interim LLI process will be allocated the lesser of: MWs modeled in the 2025 RTP less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs included in their Load Commissioning Plan, if applicable, less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs in an updated ramp schedule as provided to the DSP by June 1, 2026 Loads not yet operational will be allocated the lesser of: MWs that can be reliably served as indicated in their interconnection studies MWs included in their interconnection agreement and reflected in their financial security
MW Allocation
If your Large Load
  Achieved Initial Energization before March 25, 2022; or
  Achieved Initial Energization between March 25, 2022 and July 15, 2026
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
  Large Loads that achieved Initial Energization before March 25, 2022 shall be modeled at the level of peak Demand reported to ERCOT as part of development of the 2026 RTP
  Large Loads that achieved Initial Energization between March 25, 2022 and July 15, 2026 shall be modeled at the lesser of:
    The level of peak Demand reported to ERCOT as part of development of the 2026 RTP; or
    The level of peak Demand indicated in the most recent Load Commissioning Plan (if applicable) provided to ERCOT on or before July 15, 2026
  Loads not yet operational will be allocated the lesser of:
    The level of peak Demand that can be served reliably as indicated in the Large Load’s complete and valid existing studies
    The level of peak Demand specified in the executed Interconnection Agreement meeting Section 9.7.2
1
Reference: Batch Zero PGRR, Section 9.2.1.1(1)(a)–(b) and 9.2.1.1(2)(a)–(c) (Eligibility and Modeling for Base Load)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 46: Deep-dive: “Included as base load” (2/2)
If your Large Load
  Has a requested Initial Energization date on or before December 31, 2027, has complete and valid interconnection studies, has executed an Interconnection Agreement by the required deadline, and has satisfied required equipment procurement and development attestations
  Has a requested Initial Energization date on or after January 1, 2028, and either (i) has complete and valid interconnection studies and (ii) executed an Interconnection Agreement by the required deadline
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
MW Allocation
  Loads not yet operational will be allocated the lesser of:
    The level of peak Demand that can be served reliably as indicated in complete and valid existing studies; or
    The level of peak Demand specified in the executed Interconnection Agreement meeting Section 9.7.2.
1
Reference: Batch Zero PGRR, Section 9.2.1.1(1)(d)–(e) and 9.2.1.1(2)(c) (Eligibility and Modeling for Non-Energized Base Load)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 47: Deep-dive: “Studied in Batch Zero”
If your Large Load
Treatment in Transitional Process
MW Allocation
  Has a requested Initial Energization date on or before December 31, 2027, does not meet the Base Load requirements under Section 9.2.1.1(d)(iii)–(v), and has executed an Intermediate Agreement meeting Section 9.7.1; or
  Has a requested Initial Energization date on or after January 1, 2028, has studies sufficient for inclusion under Section 9.2.1.4, and has executed an Intermediate Agreement meeting Section 9.7.1 by the required eligibility deadline (July 15, 2026)
  Studied in Batch Zero
  To be determined during Batch Zero study and reflected in the Load Commissioning Plan (LCP)
2
Reference: Batch Zero PGRR, Sections 9.2.1.2(1)(a)–(b) and 9.7.1 (Eligibility for Inclusion as Load to be Studied)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 48: Deep-dive: “Not included in Batch Zero”
If your Large Load
Treatment in Transitional Process
MW Allocation
  Does not meet all applicable eligibility criteria in Sections 9.2.1.1 or 9.2.1.2; or
  Has studies that are sufficient for inclusion under Section 9.2.1.4 but does not meet the eligibility criteria in Section 9.2.1.2; or
  Not included in Batch Zero
  No MW allocation in Batch Zero
  May seek inclusion in a future batch process if eligibility criteria are met
3
  Fails to provide all required project information under Section 9.2.2 on or before the required submission deadline (July 15, 2026)
Reference: Batch Zero PGRR, Sections 9.2.1.3 and 9.2.2 (Load Not Included in Batch Zero)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 49: Interconnection Studies
  ERCOT has determined that the Large Load has a complete and valid set of interconnection studies that accurately reflect current system conditions and are suitable for eligibility treatment
  ERCOT has determined that existing studies are sufficient to support inclusion as load to be studied under Section 9.2.1.2.
Complete and valid existing studies
4
Reference: Batch Zero PGRR, Sections 9.2.1.4 and 9.2.1.1–9.2.1.2 (Evaluation of Existing Studies and Eligibility Treatment)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 50: Demonstrated Development Activity
Large Loads with requested Initial Energization dates on or before December 31, 2027 have two paths to demonstrate development progress:
The Large Load was included in a Quarterly Stability Assessment or was included in an interim voltage-ride-through assessment on or before May 1, 2026 and the TSP/DSP has provided both of the following to ERCOT by July 15, 2026;
    Confirmation the ILLE has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence supporting the attestation; and
    An attestation the TSP/DSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance of the requested Initial Energization date so equipment can be installed by December 31, 2026
OR
The Large Load has been found to have valid studies by ERCOT according to PG 9.2.1.4 and the TSP/DSP provides all of the following on or before July 15, 2026:
    A notarized attestation that the ILLE has executed an interconnection agreement that meets the requirements defined in Section 9.7.2;
    An attestation the TSP/DSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance of the requested Initial Energization date the equipment can be installed by the ILLE’s requested Initial Energization date;
    Confirmation the ILLE has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence supporting the attestation; and
    Confirmation the ILLE has purchased all necessary ILLE-owned high-voltage transformers and circuit breakers and will take delivery sufficiently in advance so the equipment can be installed by the ILLE’s requested Initial Energization date
5
Reference: Batch Zero PGRR, Section 9.2.1.1(1)(c)(i)–(ii) (Development activity attestation; QSA/interim VRT inclusion)
XXX Changes/ Clarification vs. Feb 26th Workshop

## Slide 51: Incorporating PUC Project 58481 into Batch Zero: two implementation pathways
2026
2027
Q2
Q3
Q4
Q1
Case building
  Batch Zero Study
  Illustrative publication date of Project No. 58481
Deferred launch of Batch Zero
No need for re-alignment if final 58481 publication is different from draft
Case building
Batch Zero Study
Potential re-alignment needed if final 58481 publication is different from draft
Early launch of Batch Zero
Project 58481 will define readiness and financial commitment standards for Large Loads. ERCOT must determine how to align Batch Zero timing with this rulemaking
Context
  Description: embed the February 13, 2026 draft Proposal for Publication (PFP) concepts directly into the PGRR language and update the PGRR with the published PFP once available
  Implications
  Enables earlier Batch Zero launch
  Uses proposed draft for intermediate agreement and interconnection agreement criteria
  Risk of misalignment if final rule differs from draft
  Description: draft PGRR to reference the final adopted 16 TAC §25.194 and begin Batch Zero a defined period (e.g., X days) after the rule becomes effective
  Implications
  Batch Zero will be aligned with final PUC rule
  May delay Batch Zero start depending on rule adoption timeline
Illustrative timeline
Option 1: Replicate the Draft 58481 PFP in the PGRR (proceed in parallel)
Option 2: Tie PGRR to Final Adopted 58481 Rule (sequential alignment)
Option
Description and implications

## Slide 52: Agenda
Timeline and governance recap
Feb 26 Workshop Feedback
  FAQs and common stakeholder questions
  Results from stakeholder feedback survey
Batch Zero PGRR Deep Dive
PGRR stakeholder feedback
Follow-on Discussion: CLR and BYOG
Q&A
Appendix

## Slide 53: Agenda
Timeline and governance recap
Feb 26 Workshop Feedback
  FAQs and common stakeholder questions
  Results from stakeholder feedback survey
Batch Zero PGRR Deep Dive
PGRR stakeholder feedback
Follow-on Discussion: CLR and BYOG
Q&A
Appendix

## Slide 54: Process redesign survey insights summary
CLR and BYOG
BYOG Self-Limiting Facility
F2
Stakeholders broadly support the BYOG self-limiting facility framework as a workable interim solution until transmission upgrades are completed
BYOG Configurations
F1
Stakeholders strongly prefer co-location models anchored by dispatchable thermal generation, particularly when paired with storage
Key insights
Key questions
Module
CLR as a bridge solution
F3
Stakeholders broadly support leveraging CLR as a bridge solution to access additional capacity while transmission upgrades are under development
CLR concept expansion
F4
Stakeholders broadly favor formalizing CLR within the BYOG framework, signaling strong interest in maintaining operational flexibility within co-location models
Pre-registration of non-firm MW as CLR
F5
Stakeholders broadly favor enabling pre-registration of non-firm MW as CLR, reinforcing strong interest in flexible pathways to utilize capacity ahead of full firm availability
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 55: CLR and BYOG: Configurations
Commentary
Strong majority of respondents favor prioritizing Load + dispatchable thermal generation (71%), followed by Load + thermal + storage hybrid (52%) and other hybrid configurations (40%)
Overall stakeholder alignment: “T(D)SPs,” “Large Load customers,” and “Generators” are aligned in prioritizing configurations that include dispatchable thermal resources
Other suggestions:
  Preference for a technology-agnostic, non-discriminatory framework focused on reliability attributes rather than fuel type
  Support for broader hybrid “energy campus” models, incl. combinations of renewables + storage + thermal, nuclear + storage, geothermal, and fast-deploying resources
  Strong emphasis on integrated energy storage to enhance operational flexibility, manage ramping, and reduce grid withdrawals
  Consideration of non-co-located resource arrangements and simplified CLR structures
Chart: 
 | 16.129 | 6.4516 | 8.0645 | 6.4516 | 12.9032 | 8.0645 | 4.8387 | 9.6774
 | 1.6129 | 0 | 1.6129 | 0 | 0 | 1.6129 | 1.6129 | 6.4516
 | 38.7097 | 14.5161 | 20.9677 | 16.129 | 29.0323 | 16.129 | 8.0645 | 20.9677
 | 14.5161 | 1.6129 | 3.2258 | 1.6129 | 9.6774 | 6.4516 | 0 | 3.2258
Load + renewable generation
Load + storage
Load + renewable + storage hybrid
Load + thermal + storage hybrid
Generation capacity is greater than the load
Load is greater than the generation capacity
Other
71%
23%
34%
24%
52%
32%
15%
40%
2%
3%
2%
2%
2%
3%
15%
39%
2%
16%
15%
6%
21%
2%
8%
16%
6%
10%
Load + dispatchable thermal generation
13%
6%
16%
8%
29%
5%
21%
6%
10%
8%
T(D)SPs
LL Customers
Other
Generators
F1
“Which co-location configurations (e.g., load plus battery, load plus solar) should ERCOT prioritize when defining BYOG rules?” (% of overall respondents that selected a specific option)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results
N=62 (11 T(D)SPs, 35 LLC, 5 Other, 11 Generators). Note: respondents could multi-select responses so total % > 100

## Slide 56: CLR and BYOG: BYOG Self-Limiting Facility
Commentary
Strong majority of respondents (80%) agree that the BYOG self-limiting facility concept is adequate, while a minority (20%) do not
Overall stakeholder alignment: “T(D)SPs,” “Large Load customers,” “Generators,” and “Other” stakeholders each show majority support for the self-limiting facility concept
Reasons of opposition:
  Operational and reliability concerns, including need for real-time controls, enforceability, and clear compliance mechanisms
  Preference for dynamic (rather than fixed) injection/withdrawal limits, potentially reflecting seasonal or system conditions
  Need for greater flexibility, including ramping as transmission is built or site-specific agreements among ERCOT, TSP, and the customer
  Concerns that SLF may be impractical or misaligned with certain configurations (e.g., fully dispatchable co-located generation, G-1 events, maintenance scenarios)
  Requests for clearer BYOG/SLF definitions and implementation details before full endorsement
Chart: 
 | 11.8644 | 6.7797
 | 3.3898 | 3.3898
 | 47.4576 | 5.0847
 | 16.9492 | 5.0847
Yes
No
80%
20%
3%
17%
47%
3%
12%
5%
5%
7%
T(D)SPs
LL Customers
Other
Generators
N=59 (13 T(D)SPs, 31 LLC, 4 Other, 11 Generators)
F2
“For BYOG, is the self-limiting facility concept adequate? In other words, BYOG site agrees to fixed injections/withdrawal limitation until transmission is built?” (% of overall respondents)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 57: CLR and BYOG: CLR as a bridge solution
Commentary
Strong majority of respondents (79%) would consider using CLR status to consume power above their firm allocation while upgrades are being built, while a smaller share (21%) would not
Overall stakeholder alignment: “T(D)SPs,” “Large Load customers,” “Generators,” and “Other” stakeholders each show majority support for using CLR status as a transitional mechanism
Additional comments:
  Need for clearer definition and consistent understanding of what constitutes CLR participation and its reliability expectations
  Some stakeholders prefer BYOG or alternative mechanisms over CLR, particularly where operational dispatchability is constrained
  Concerns about real-time dispatch feasibility, monitoring requirements, and cost implications for certain large loads
  Broad interest in using CLR (or expanded definitions that include BYOG) to maximize early energization, provided it does not delay the batch process
Chart: 
 | 15.7895 | 3.5088
 | 5.2632 | 1.7544
 | 47.3684 | 14.0351
 | 10.5263 | 1.7544
Yes
No
79%
21%
2%
2%
4%
11%
47%
5%
16%
14%
T(D)SPs
LL Customers
Other
Generators
N=57 (7 T(D)SPs, 35 LLC, 4 Other, 11 Generators)
F3
“If Batch Zero provides less firm capacity than your requested ramp, would you consider using CLR status to consume power above your firm allocation while upgrades are being built?” (% of overall respondents)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 58: CLR and BYOG: CLR concept expansion
Commentary
Strong majority of respondents (74%) support expanding the Controllable Load Resource (CLR) concept to be explicitly included as a co-location configuration option under BYOG rules, while 26% do not
Overall stakeholder alignment: “T(D)SPs,” “Large Load customers,” “Generators,” and “Other” stakeholders each show majority support for explicitly incorporating CLR into BYOG
Additional comments:
  Broad support for CLR inclusion, but strong caution against adding complexity or delaying BYOG implementation
  Preference by several stakeholders to treat CLR and BYOG separately, at least initially
  Recognition that CLR could provide valuable operational flexibility, particularly for storage-integrated or “powered campus” configurations
  Concerns about market design, metering, and implementation readiness
  Emphasis that participation in CLR should remain optional and flexible, not mandatory for BYOG configurations
Chart: 
 | 14.0351 | 5.2632
 | 3.5088 | 1.7544
 | 45.614 | 12.2807
 | 10.5263 | 7.0175
Yes
No
74%
26%
2%
11%
46%
4%
14%
7%
12%
5%
T(D)SPs
LL Customers
Other
Generators
N=57 (10 T(D)SPs, 33 LLC, 3 Other, 11 Generators)
F4
“When defining BYOG rules, should Controllable Load Resources (CLRs) concept be expanded to be explicitly included as a co-location configuration option?” (% of overall respondents)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 59: CLR and BYOG: Pre-registration of non-firm MW as CLR
Commentary
Strong majority of respondents (82%) support allowing Large Load customers in Batch Zero to pre-register non-firm allocated MWs as a CLR after study results are released, while 18% do not
Overall stakeholder alignment: “T(D)SPs,” “Large Load customers,” “Generators,” and “Other” stakeholders each show strong majority support for providing this pre-registration option
Additional comments:
  Support for pre-registration as a flexible, optional bridge mechanism, but not as a condition tied to Batch Zero approval
  Operational and reliability concerns, including dispatch authority, emergency procedures, and system risk management
  Need for clear definitions and implementation details, incl. timing of registration/revocation risk
  Preference to keep CLR participation voluntary/ separate from traditional interconnection rights
  Strong interest from large loads in using CLR to energize non-firm MW early, often paired with private mitigation or on-site resources
Chart: 
 | 15 | 3.3333
 | 5 | 1.6667
 | 50 | 6.6667
 | 11.6667 | 6.6667
Yes
No
82%
18%
2%
3%
12%
50%
5%
15%
7%
7%
T(D)SPs
LL customers
Other
Generators
N=60 (11 T(D)SPs, 34 LLC, 4 Other, 11 Generators)
F5
“Should Large Load customers included in Batch Zero have the option to pre-register non-firm allocated MWs as a CLR after study results are released, to operate those MWs as controllable load until full firm capacity is available?” (% of overall respondents)
Source: Feb 26, 2026 ERCOT Large Load Interconnection (LLI) Batch Study Process Stakeholder Survey results

## Slide 60: Four different constructs were identified by ERCOT to integrate CLR and BYOG concepts into Batch Zero
Construct
Description
Feasibility
1A
Load-Only CLR (No Generation/No Batteries Behind the POI)
Large Load registers entirely as a CLR at the POI. No generation or storage is electrically connected in a way that can synchronize with, parallel, or export to the ERCOT grid
Potentially feasible
1B
CLR with Non-Synchronous Backup Generation
Large Load registers as a CLR and utilizes behind-the-meter backup generation that is not synchronized with the ERCOT grid
Potentially feasible
2
BYOG Self-Limiting Facility (SLF)
Colocated Large Load and Generation operate behind a single POI under a defined net injection/withdrawal limit enforced at the POI
Potentially feasible
3
Netted Network
Colocated Large Load and Generation operate behind a single POI (physically similar to SLF), but are permitted to participate simultaneously on both the supply and demand sides of the ERCOT market, subject to the POI interconnection limit
Not feasible

## Slide 61: Load-Only CLR (No Generation or Batteries)
Source: ERCOT discussions
Point of interconnection
Large Load registers entirely as a CLR, with no associated generation or storage behind the POI
Load-Only CLR leverages the existing CLR framework as the simplest near-term option1, subject to required market/system implementation items (e.g., SCED/mitigation enhancements) before energization
Participates as dispatchable demand and must follow SCED basepoints within its registered operating range (PC/LPC/MPC)
No assurance of service above awarded firm MW; real-time consumption may be reduced below PC based on system conditions and SCED mitigation
ERCOT observes and verifies performance based on net MW at the POI and adherence to SCED dispatch instructions
Must meet existing CLR telemetry and dispatch performance requirements (subject to SCED instructions and registered operating limits)
Load may register operational capability above awarded firm MW, subject to real-time dispatch and congestion mitigation2
Illustrative example
  150 MW requested in Year 1
  ERCOT performs steady-state and stability studies and allocate phased MW (e.g., 100 MW in Years 1–4 until transmission upgrade in Year 5)
  Operational parameters:
    PC = 0–100 MW (firm)
    LPC = 0–100 MW
    MPC = 150 MW (upper operational capability; not a planning guarantee)
    CLR quantity may be modified in later years as transmission capability increases
1. NPRR1188 later in 2026: Nodal pricing align local congestion prices. NPRR1255 mitigation methods needed (small project) | 2. Potentially subject to additional limits identified in dynamic studies
Description
Details
Load
Illustrative scheme
Chart: 
 | 100 | 100 | 100 | 100 | 1000
 | 50 | 200 | 400 | 600
50
Year 1
Year 2
Year 3
Year 4
Year 5
150
300
500
700
CLR Load
Firm Load
POTENTIALLY FEASIBLE CONFIGURATION
1A
ERCOT grid

## Slide 62: CLR with Non-Synchronous Backup Generation
Source: ERCOT discussions
Point of interconnection
Large Load registers as a CLR and utilizes behind-the-meter backup generation that is not synchronized1 with the ERCOT grid
This construct allows internal self-supply during curtailment without parallel operation or export to the ERCOT system
To qualify under this construct, backup generation must not be synchronized with or operate in parallel with the ERCOT grid and must be incapable of exporting power at the POI
ERCOT models the facility as load only at the POI for steady-state and stability studies and observes only net load at the POI
Transmission study limits remain binding on the net load at POI
Load must follow SCED basepoints within its LPC–MPC range
Large Load may need to segment internal load into controllable tranches (e.g., 10 MW blocks) to comply with SCED
Any internal switching to backup generation is behind-the-fence and not visible to ERCOT
If backup generation fails, the load remains responsible for meeting SCED dispatch instructions
No export or generation market participation is permitted under this construct2
Description
Illustrative scheme
POTENTIALLY FEASIBLE CONFIGURATION
1B
1. Any behind-the-meter generator or storage that can operate in parallel with the ERCOT grid (i.e., can be synchronized/connected while the POI remains energized) must be registered as a GR/ESR and is not compatible with a Load-Only CLR construct | 2. No energy or ancillary service participation from the backup resource is permitted
Load
ERCOT grid
Backup Gen
Backup Gen
Details
Load
ERCOT grid
Backup Generation
Backup Generation
No AC path to ERCOT grid

## Slide 63: BYOG Self-Limiting Facility (SLF)
Source: ERCOT discussions
Point of interconnection
Colocated Large Load and Generation operate behind a single POI under a defined net injection/ withdrawal limit enforced at the POI
Facility is structured as a PUN with a Self-Limiting Feature (SLF) (consistent with NPRR1026 framework)
The SLF ensures that net real power at the POI never exceeds the approved interconnection limit, regardless of internal load or generation configuration
Load and Generation are both registered with ERCOT
Interconnection limit applies to net MW at the POI
Requires operational coordination agreement between Load and Generator
ERCOT models the facility as a net resource at the POI, subject to the self-limiting cap
Facility must ensure net injection/withdrawal does not exceed POI cap at any time (may require breaker logic and/or reverse power relay to enforce the limit)
Transmission planning does not assume simultaneous full load and full generation at the POI:
  Either supply-side (GR/ESR) or demand-side (CLR) may participate at a given time
  Simultaneous full participation on both sides is not permitted unless structured as a Netted Network (separate construct)
The largest modeled contingency depends on internal configuration (e.g., if generators share a common step-up transformer, transformer loss may be most limiting event; if generators are electrically independent, individual G-1 may apply)
Description
Illustrative scheme
Load = 1,000 MW
Gen = 5 x 250 MW
G-1 compliant (serve 1,000 MW load) or most limiting contingency
POTENTIALLY FEASIBLE CONFIGURATION
2
Load
ERCOT grid
Gen 1
Gen 2
Gen 3
Gen 4
Gen 5
Load = 1,000 MW
Gen = 2 x 500 MW
G-1 compliant (only serve 500 MW load)
Load
ERCOT grid
Gen 1
Gen 2
Details

## Slide 64: Netted Network
Source: ERCOT discussions
Point of interconnection
Colocated Large Load and Generation operate behind a single POI (physically similar to SLF), but are permitted to participate simultaneously on both the supply and demand sides of the ERCOT market, subject to the POI interconnection limit
Same physical configuration as SLF (Load and GR/ESR behind one POI)
Net injection/withdrawal at the POI remains capped by the interconnection agreement
Unlike SLF:
  Supply and demand may participate simultaneously in Energy and AS1 markets
  Enables concurrent market activity from load and generation behind the same POI
Description
UNFEASIBLE CONFIGURATION
3
Illustrative scheme
Load = 1,000 MW
Gen = 5 x 250 MW
G-1 compliant (serve 1,000 MW load) or most limiting contingency
Load
ERCOT grid
Gen 1
Gen 2
Gen 3
Gen 4
Gen 5
Load = 1,000 MW
Gen = 2 x 500 MW
G-1 compliant (only serve 500 MW load)
Load
ERCOT grid
Gen 1
Gen 2
1. Ancillary services
Details

## Slide 65: Agenda
Timeline and governance recap
Feb 26 Workshop Feedback
  FAQs and common stakeholder questions
  Results from stakeholder feedback survey
Batch Zero PGRR Deep Dive
PGRR stakeholder feedback
Follow-on Discussion: CLR and BYOG
Q&A
Appendix

## Slide 66: Q&A session
66

## Slide 67: Agenda
Timeline and governance recap
Feb 26 Workshop Feedback
  FAQs and common stakeholder questions
  Results from stakeholder feedback survey
Batch Zero PGRR Deep Dive
PGRR stakeholder feedback
Follow-on Discussion: CLR and BYOG
Q&A
Appendix

## Slide 68: Controllable Load Resource Rules
Key Design Considerations
  CLR is an existing resource type in ERCOT Protocols
  Similar to generators, CLRs can be dispatched down in real-time by ERCOT’s Security Constrained Economic Dispatch tool
  Some CLRs can be dispatched to zero load while others have a higher minimum load values
  ILLEs registering loads as CLRs still want the transmission system to be planned to serve the full load
  ERCOT and CLR entities need clearly defined rules to govern expectations
  NPRR1188 (expected late 2026 implementation) provides some but not all rules necessary for allowing specific consideration of CLRs in the Batch Study process
  Additional CLR Rules Needed
    Offer mitigation or similar concept to ensure high CLR offers don’t result in constraint violations in SCED optimization (SCED Step2)
    Binding commitment and exit conditions so CLRs remain as CLRs until necessary transmission upgrades are complete
    NPRR1188 does not support CLR composed of Load+Gen/Battery
  CLR Treatment in Batch Studies
    An ILLE’s designation of intent to register as CLR will be binding for the Batch Study
    A CLR will be allocated its full load request but may be required to have a minimum load amount assigned in the Batch Study process
  CLR Treatment in Other Studies
    CLRs will be modeled at their full requested load in transmission planning studies and the FAC-002 stability study
    All TSP studies must consider the full load

## Slide 69: Co-Location with Existing Generation Rules
Co-Location with existing generation
Key Design Considerations
  Senate Bill 6 rules may apply for generators existing before September 1, 2025
  The transmission system has been planned assuming the existing generation supports the system
  No specific rules aside from existing requirements in the Protocols (such as an updated Reactive Power study)

## Slide 70: Co-Location with New Generation Rules
Examples
Key Design Considerations
  New co-located generators can reduce the need for the transmission system to support a new Large Load
  There are multiple scenarios regarding how the co-located generation resource and Large Load interact with the transmission system, each requiring different rules
  In some scenarios, new rules are needed to link generation interconnection requests to LLI requests
  Scenario 1: Large Load does not consume from the grid – only from the co-located generation
    The co-located Large Load will be allocated its full load request
    Rules needed to ensure Large Load will never consume from the grid, even momentarily
    Rules needed to ensure LLI request and GINR are linked
  Scenario 2: Scenario 1 temporarily until transmission upgrades are complete
    All Scenario 1 rules apply
    A separate study is needed to determine the required transmission upgrades and rules needed to exit no-transmission-system-load status
  Scenario 3: Large Load has co-located dispatchable generation and may sometimes consume from the grid
    The co-located Large Load will be allocated their full load request except in the G-1+N-1 analysis
    Rules needed to ensure LLI request and GINR are linked
  Scenario 4: Large Load has co-located intermittent generation and/or energy storage and may sometimes consume from the grid
    No specific rules
  Not enough time in Batch Zero development for numerous scenarios; looking for feedback on priority and feasibility of scenario options (will also discuss as part of post-meeting survey).