## Slide 1
25RPG004 Oncor Southern DFW Load Interconnection and General Grid Strengthening Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
March 25, 2026

## Slide 2: Overview
Oncor Electric Delivery Company LLC (Oncor) submitted the Southern Dallas Forth Worth (DFW) Load Interconnection and General Grid Strengthening Project for Regional Planning Group (RPG) review in February 2025
    This Tier 1 STEC proposed project submission was estimated to cost $1.219 billion and will require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues due to proposed load additions in the Southern DFW in the North Central and East Weather Zones

## Slide 3: Study Assumptions
Final 2024 Regional Transmission Planning (RTP) 2029 summer peak load case was used as the start case
Modified RTP Large Loads including Officer Letter Loads (OLLs) relevant to the project, provided by Oncor, to address approximately 4 GW of load in the study area
Additional load updates (approximately 50 MW) in the study area were applied based on feedback from Brazos Electric Cooperative (BEC)
Generation in East and North Central Weather Zones that did not meet Planning Guide Section 6.9(1) were opened (turned off) to balance power

## Slide 4: Project Need
ERCOT’s independent review verified reliability planning criteria violations in the Southern DFW in the North Central and East Weather Zones
System improvement is needed to meet reliability planning criteria
Contingency Category | Voltage Violations | Thermal Violations | Unsolved Power Flow
P0: N-0 | None | 1 | None
P1, P2-1, P7: N-1 | 6 | 14 | None
P3: (G-1+N-1)* | 8 | 10 | None
P6-2: (X-1+N-1)* | 30 | 23 | 3
*See Appendix A for list of G-1 generators and X-1 transformers tested

## Slide 5: Project Options
ERCOT’s modified option (Option 3) addresses all NERC Reliability Standard TPL-001-5.1 and ERCOT Planning Guide reliability criteria
Option 3 consists of:
  Oncor’s proposed option
  All the upgrades identified in Oncor and Lone Star Navarro and Ellis Area upgrade project (25RPG038)
  A subset of upgrades identified in Oncor Set 1 and Set 2 North and Central Texas Reliability Projects (25RPG040 and 25RPG042)

## Slide 6: Comparison of Project Options
ERCOT analyzed three options
Among the three options, Option 3 addresses the reliability violations, is the cost-effective option, improves long-term load-serving capability, and improves operational flexibility
*Cost estimates were provided by the TSPs
** Cost estimate is different from initial project submittal
 | Option 1 | Option 2 | Option 3
Meets ERCOT and NERC Reliability Criteria | No | No | Yes
Improves Long-Term Load-Serving Capability (~MW) | 2305 | 2335 | 2904
Requires CCN (~miles) | Yes (2.0) | Yes (2.0) | Yes (111.0)
Cost Estimate* (~$B) | $1.248** | $1.266 | $2.886
Feasible | Yes | Yes | Yes
Expected ISD | May 2026 to April 2033 | May 2026 to April 2033 | May 2026 to April 2033

## Slide 7: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 8: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 3 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 9: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 3 did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 10: Dynamic Stability Analysis
ERCOT performed a dynamic stability analysis for the ERCOT’s preferred option. The study utilized the 2024 DWG 2026 Summer Peak dynamic case provided by Oncor, and the following were incorporated and evaluated in the analysis:
  Large loads included in Oncor’s RPG proposal within the study area
  Critical contingencies provided by Oncor and additional contingencies near Large Load locations in the study area
  Option 3 (ERCOT’s preferred option)
ERCOT observed no adverse dynamic stability impacts resulting from the implementation of Option 3 (ERCOT’s preferred option)

## Slide 11: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 3 to address reliability issues in the Southern DFW in the North Central and East Weather Zones
TSPs expect to implement the upgrades May 2026 to April 2033
Estimated Capital Cost: $2.886 billion
  CCN filling will be required for the new transmission lines
    From the existing Desoto Switch to the existing Sam Switch
    From the existing Wilmer Switch to the existing Navarro Switch
    From the existing Midlothian Tap to the new Ironwood Switch
  The upgrades identified in Oncor and Lone Star Navarro and Ellis Area upgrade project (25RPG038) were included in its entirety as part of this project (approximately $856.28 million)
  A subset of upgrades identified in Oncor Set 1 and Set 2 North and Central Texas Reliability Projects (25RPG040 and 25RPG042) were included as part of this project (approximately $763.58 million)

## Slide 12: ERCOT Recommendation Summary
Construct six new substations
  Two new 345/138-kV switches
  Two new 345-kV switches
  Two new 138-kV substations
Rebuild six existing substations
  Five 345-kV switches
  One 345/138-kV switches
Construct twelve new 345-kV and 138-kV lines
  Approximately 218.0 circuit miles of new 345-kV lines
  Approximately 8.0 circuit miles of new 138-kV lines
Upgrade of existing 345-kV and 138-kV lines
  Approximately 394.8 circuit miles of existing 345-kV lines
  Approximately 73.8 circuit miles of existing 138-kV lines
Full project details in Appendix B
Install nine reactive devices
  Three ±250 MVA 345-kV STATCOMs
  Three 345-kV capacitor banks
  Three 138-kV capacitor banks

## Slide 13: ERCOT Recommendation

## Slide 14: Appendix A – G-1 Generators and X-1 Transformers
G-1 Generators | X-1 Transformers
Comanche Peak | Desoto Switch 345/138-kV
Forney Combine Cycle Train | Monticello SES 345/138-kV
Martain Lake | Sargent Road Switch 345/138-kV
Mt. Creek SES | Seagoville Switch 345/138-kV
Midlothian | Trinidad SES Switch 345/138-kV
 | Venus Kemp Ranch Switch 345/138-kV
 | Watermill Switch 345/138-kV
 | West Levee Switch 345/138-kV
 | Wilmer Switch 345/138-kV

## Slide 15: Appendix B – ERCOT Recommendation
Construct a new Greene Road 345/138-kV Switch (SW) by installing fourteen 345-kV, 5,000 A and ten 138-kV, 3,200 A breakers in a breaker-and-a-half bus arrangement:
  Install two new 345/138-kV autotransformers with a normal rating of 700 MVA and an emergency rating of 750 MVA;
  Re-terminate the existing Watermill SW to Sargent Road SW/West Levee SW 345-kV double-circuit transmission line into the new Greene Road 345-kV SW, which creates the new Watermill SW to Greene Road SW and the new Greene Road SW to Sargent Road SW/West Levee SW 345-kV double-circuit transmission lines;
  Re-terminate the existing Wilson SW to Cedar Hill SW/Cedar Crest SW 138-kV double-circuit transmission line into the new Greene Road 138-kV SW, which creates the new Wilson SW to Greene Road SW and the new Greene Road SW to Cedar Hill SW/Cedar Crest SW 138-kV double-circuit transmission line;
Rebuild the new Greene Road SW to Watermill SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 2,987 MVA, approximately 3.6 miles;
Rebuild the new Wilson SW to Greene Road SW 138-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 764 MVA, approximately 2.0 miles;
Rebuild the new Greene Road SW to Cedar Crest 138-kV single-circuit transmission line on double-circuit structures with one circuit in place, with normal and emergency ratings of at least 764 MVA, approximately 10.9 miles;

## Slide 16: Appendix B – ERCOT Recommendation (cont.)
Construct a new Alba Road 345-kV SW by installing eleven 345-kV, 5,000 breakers in a breaker-and-a-half bus arrangement:
  Re-terminate the new Watermill SW to Greene Road SW 345-kV double-circuit transmission line into the new Alba Road 345-kV SW, which creates the new Watermill SW to Alba Road SW and the new Alba Road SW to Greene Road SW 345-kV double-circuit transmission lines;
Construct a new Stainback 345-kV SW by installing fourteen 345-kV, 5,000 breakers in a breaker-and-a-half bus arrangement:
  Re-terminate the existing Watermill SW to Elrod SW/Big Onion SW 345-kV double-circuit transmission line into the new Stainback 345-kV SW, which creates the new Watermill SW to Stainback SW and the new Stainback SW to Elrod SW/Big Onion SW 345-kV double-circuit transmission lines;
Rebuild the new Watermill SW to Stainback SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 2,987 MVA, approximately 3.0 miles;
Rebuild the existing Watermill SW to Wilson SW 138-kV double-circuit transmission line on double-circuit structures with both circuit in place, with normal and emergency ratings of at least 764 MVA, approximately 0.8 miles;

## Slide 17: Appendix B – ERCOT Recommendation (cont.)
Construct a new Ironwood 345/138-kV SW by installing seventeen 345-kV, 5,000 A and ten 138-kV, 3,200 A breakers in a breaker-and-a-half bus arrangement:
  Install two 345/138-kV autotransformers with normal and emergency ratings of 700 MVA and 750 MVA, respectively;
  Re-terminate the existing Liggett SW to Endeavor SW 345-kV Line at the new Ironwood 345-kV SW, which creates the new Liggett SW to Venus SW (north bus)/Ironwood SW 345-kV double-circuit transmission line;
  Disconnect the existing Endeavor SW to Venus SW (south bus) and Midlothian ANP #2 to Venus SW (south bus) 345-kV Lines from Venus SW (south bus) and connect the Midlothian ANP to Endeavor 345-kV SW. This will create Midlothian ANP #1 to Venus SW (north bus) and Midlothian ANP #2 to Endeavor SW 345-kV double-circuit transmission line;
  Re-terminate the existing Timberview SW to Venus SW (south bus) at the new Ironwood 345-kV SW, which creates the new Everman SW to Venus SW (north bus) and the new Timberview SW to Ironwood SW 345-kV double-circuit transmission line;
  Re-terminate the existing Cedar Hill SW to Venus SW (south bus) at the new Ironwood 345-kV SW, which creates the new Sherry SW to Venus SW (north bus) and the new Cedar Hill SW to Ironwood SW 345-kV double-circuit transmission line;
  Re-terminate the existing Sam SW to Venus SW (south bus) at the new Ironwood 345-kV SW, which creates the new Fort Smith SW to Venus SW (north bus) and the new Sam SW to Ironwood SW 345-kV double-circuit transmission line;
  Re-terminate the existing Navarro SW to Venus SW (south bus) at the new Ironwood 345-kV SW, which creates the new Navarro SW to Venus SW (north bus)/Ironwood SW 345-kV double-circuit transmission line;
  Re-terminate the existing Cottonwood Creek 345/138-kV Autotransformer #2 at the north bus of Venus 345-kV SW by installing one 345-kV, 5,000 A breaker;

## Slide 18: Appendix B – ERCOT Recommendation (cont.)
  Loop the existing Kemp Ranch SW to Sardis SW/Soap Creek 138-kV double-circuit transmission line into the new Ironwood 138-kV SW by disconnecting the double-circuit line at structure #1/2 (Midlothian Tap) and constructing four circuits from Midlothian Tap to the new Ironwood 138-kV SW on separate structures, with normal and emergency ratings of at least 764 MVA, which will require a new ROW, approximately 2.0 miles each circuit;
Rebuild the two Kemp Ranch SW to Midlothian Tap 138-kV single-circuit transmission line sections using two separate structures, with normal and emergency ratings of at least 764 MVA, approximately 0.5 miles each circuit;
Rebuild the existing Sterrett SW to Midlothian TXI 138-kV single-circuit transmission line sections, with normal and emergency ratings of at least 764 MVA, approximately 11.8 miles;
Rebuild the existing Ennis West SW to Sterrett SW 138-kV single-circuit transmission line, with normal and emergency ratings of at least 614 MVA, approximately 21.0 miles;

## Slide 19: Appendix B – ERCOT Recommendation (cont.)
Rebuild the existing Big Brown 345-kV SW by installing twelve 345-kV, 5,000 A breakers in a breaker-and-a-half bus arrangement. Upon completion, Big Brown SW will be renamed as Pin Oak SW:
  Re-terminate the existing Big Brown SW to Jewett SW 345-kV double-circuit transmission line at the new Pin Oak 345-kV SW, which creates the new Pin Oak SW to Jewett SW 345-kV double-circuit transmission line;
  Re-terminate the existing Big Brown SW to Navarro SW 345-kV double-circuit transmission line at the new Pin Oak 345-kV SW, which creates the new Pin Oak SW – Navarro SW 345-kV double-circuit transmission line;
  Re-terminate the existing Big Brown SW to Richland Chamber SW 345-kV double-circuit transmission line at the new Pin Oak 345-kV SW, which creates the new Pin Oak SW to Richland Chambers SW 345-kV double-circuit transmission line;
Rebuild the new Jewett SW to Pin Oak SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 1,792 MVA and with a conductor rating of at least 2,987 MVA, approximately 32.8 miles;
Rebuild the existing Richland Chambers SW to Trinidad SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place with normal and emergency ratings of at least 1,792 MVA and a with conductor rating of at least 2,987 MVA, approximately 18.7 miles;

## Slide 20: Appendix B – ERCOT Recommendation (cont.)
Rebuild the existing Parker SW to Hicks SW 345-kV transmission line, with normal and emergency ratings of at least 1,912 MVA and with a conductor rating of at least 2,987 MVA, approximately 23.0 miles;
Rebuild the existing Pebble Creek SW to Shankle SW 138-kV transmission line, with normal and emergency ratings of at least 764 MVA, approximately 15.5 miles;
Rebuild the existing Mesquite East SW to Seagoville SW 138-kV transmission line, with normal and emergency ratings of at least 764 MVA, approximately 7.4 miles;
Rebuild the existing Farmersville SW to Royse SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 1,792 MVA and with a conductor rating of at least 2,987 MVA, approximately 15.3 miles;
Install one +250/-250 MVAr Grid-forming STATCOM at each of the following:
  Alba Road 345-kVSW;
  Greene Road 345-kVSW;
  Wilmer 345kV SW;

## Slide 21: Appendix B – ERCOT Recommendation (cont.)
Install 240 MVAr 345-kV capacitor banks (3-80 MVAr each):
  One at Greene Road 345-kV SW;
  Two at Alba Road 345-kV SW;
  Two at Stainback 345-kV SW;
Install 110.4 MVAr 138-kV capacitor banks (3-36.8 MVAr each) at:
  One at Greene Road 138-kVSW;
  Two at Ironwood 138-kVSW;
  Two at Pebble Creek 138-kVSW;
For terminal equipment:
  The existing 345 kV terminal equipment, ensure they meet or exceed a rating of 3000 A (1792 MVA);
  The new 345-kV terminal equipment, ensure they meet or exceed a rating of 5,000 A if the station is 5,000 A capable. Otherwise ensure the new 345-kV terminal equipment meets or exceeds a rating of 3,200 A;
  The 138-kV terminal equipment, ensure they meet or exceed a rating of 3,000 A;

## Slide 22: Appendix B – ERCOT Recommendation (cont.)
Construct a new Goat Pad 138-kV Substation:
  Install a new Goat Pad to Padera 138-kV single-circuit transmission line on double-circuit structures with only one circuits in place, with normal and emergency ratings of at least 287 MVA, approximately 2.6 miles;
  Install a new Goat Pad to Midlothian 138-kV single-circuit transmission line on double-circuit structures with only one circuits in place, with normal and emergency ratings of at least 287 MVA, approximately 3.0 miles;
  Install a new Goat Pad to Goatheard 138-kV single-circuit transmission line on double-circuit structures with only one circuits in place, with normal and emergency ratings of at least 524 MVA, approximately 0.1 miles;
Construct a new Goatheard 138-kV Substation:
  Re-terminate the existing Cedar Hill SW to Saint Paul SW 138-kV single-circuit transmission line into the new Goatheard 138-kV SW, which creates the new Goatheard SW to Cedar Hill SW and the new Goatheard SW to Saint Paul SW 138-kV single-circuit transmission line, and rebuild on double-circuit structures with only one circuits in place, with normal and emergency ratings of at least 237 MVA, approximately 0.7 miles;

## Slide 23: Appendix B – ERCOT Recommendation (cont.)
Upgrade the existing Navarro SW to the new Pin Oak (Big Brown) SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 2,987 MVA, approximately 27.6 miles;
Upgrade the existing Navarro SW to Outlaw SW 345-kV double-circuit transmission line on double-circuit structures with both one circuits in place, with normal and emergency ratings of at least 2,987 MVA, approximately 5.6 miles;
Upgrade the existing Desoto 345/138-kV SW:
  Install five 345-kV circuit breakers in a breaker-and-a-half configuration with ratings of 5,000 A;
  Install nine 138-kV circuit breakers in a breaker-and-a-half configuration with ratings of 3,200 A;
Construct a new Desoto SW to Sam SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 2,987 MVA, which will require a new ROW, approximately 56.0 miles/circuit:
  Install four 345-kV circuit breakers at the existing Desoto SW 345-kV substation with ratings of at least 5000 A;
  Install four 345-kV circuit breakers at the existing Sam SW 345-kV substation with ratings of at least 5000 A;

## Slide 24: Appendix B – ERCOT Recommendation (cont.)
Construct a new Wilmer SW to Navarro SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 2,987 MVA, which will require a new ROW, approximately 53.0 miles/circuit:
  Install three 345-kV circuit breakers at the existing Wilmer SW 345-kV substation with ratings of at least 5000 A;
  Install four 345-kV circuit breakers at the existing Navarro SW 345-kV substation with ratings of at least 5000 A;
Rebuild the existing Tri Corner 345-kV SW:
  Install twelve 345-kV circuit breakers in a breaker-and-a-half configuration with ratings of 5,000 A;
  Ensure all terminal equipment meet or exceed 5,000A;
Upgrade the existing Watermill SW to Tri Coner SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 1,912 MVA, approximately 11.5 miles/circuit:
  Ensure all terminal equipment meet or exceed 5,000A;
Upgrade the existing Tri Coner SW to Trinidad SW 345-kV double-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 1,912 MVA, approximately 40.5 miles/circuit:
  Ensure all terminal equipment meet or exceed 5,000A; and
Upgrade the existing Farmerville SW to Saltillo SW 345-kV single-circuit transmission line on double-circuit structures with both circuits in place, with normal and emergency ratings of at least 1,912 MVA, approximately 59.9 miles/circuit:
  Ensure all terminal equipment meet or exceed 3,200A.