## Slide 1
25RPG016 STEC Nueces Green Ammonia Load Interconnection Project
Prabhu Gnanam
Director, Grid Planning
Technical Advisory Committee Meeting
ERCOT Public
March 25, 2026

## Slide 2: Overview
South Texas Electric Cooperative (STEC) submitted the Ammonia Plant Load Project for Regional Planning Group (RPG) review in June 2025
    This Tier 2 STEC proposed project submission was estimated to cost $74.0 million and will require a Certificate of Convenience and Necessity (CCN)
    Address reliability issues due to proposed load addition in Nueces County in the South Weather Zone
    Based on the updated cost estimates provided by the TSPs, the project was recategorized as Tier 1 project

## Slide 3: Project Need
ERCOT’s independent review verified reliability planning criteria violations in Nueces County in the South Weather Zone due to new large load confirmed by TSP Attestation Letter (1,150 MW in 2028)
System improvement is needed to meet reliability planning criteria
Contingency Category | Voltage Violations | Thermal Violations | Unsolved Power Flow
P0: N-0 | None | None | None
P1, P2-1, P7: N-1 | None | 2** | 2**
P3: (G-1+N-1)* | None | 1** | 2**
P6-2: (X-1+N-1)* | None | 1** | 2**
*See Appendix A for list of G-1 generators and X-1 transformers tested
**Violations seen in the base case under P1 and P7 events were also seen under G-1+N-1 and/or X-1+N-1 events

## Slide 4: Comparison of Project Options
ERCOT analyzed four options and short-listed two options
Among the two short-listed options, Option 3 addresses the reliability violations, is the least expensive option, improves long-term load-serving capability, and requires the least amount of CCN miles
ERCOT recommends Option 3 as the preferred option and reclassified the project as a Tier 1 Project
STEC’s initial cost estimate did not include AEP’s increased capability requirement for the 345-kV transmission rebuild, the addition of AEP’s portion of the new Nueces Load POI substation, and the increased cost associated with recent tariff changes and have thus increased from the initial cost estimate
*Cost estimates were provided by the TSPs
 | Option 2 | Option 3
Meets ERCOT and NERC Reliability Criteria | Yes | Yes
Improves Long-Term Load-Serving Capability (~MW) | 21.8 | 633.4
Requires CCN (~miles) | Yes (49.6) | Yes (10.4)
Project Feasibility | Yes | Yes
Cost Estimate* (~$M) | 379.5 | 161.1
ISD (Year) | 2032 | 2031

## Slide 5: Tier 1 Project Requirement
Pursuant to Protocol Section 3.11.4.7 (Tier 1)
  Projects with an estimated capital cost of $100 Million or greater are Tier 1 projects
  Tier 1 projects require ERCOT Board endorsement
Pursuant to Protocol Section 3.11.4.9
  ERCOT shall present the Tier 1 project to the Technical Advisory Committee (TAC) for review and comment
  Comments from TAC shall be included in the presentation to the ERCOT Board

## Slide 6: Sub-synchronous Resonance Assessment
Pursuant to Protocol Section 3.22.1.3
  ERCOT conducted a SSR screening for Option 3 and found no adverse SSR impacts to the existing and planned generation resources at the time of this study

## Slide 7: Congestion Analysis and Sensitivity Analysis
Pursuant to Planning Guide 3.1.3
  ERCOT shall evaluate if the recommended project will have an impact on system congestion.
  ERCOT shall perform a generation sensitivity analysis and evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations
ERCOT concluded that
  Option 3 did not cause any additional congestion within the study area
  No potential future generation studied impacts the preferred option
  The load scaling did not have a material impact on the project need

## Slide 8: Dynamic Stability Analysis
ERCOT performed a dynamic stability analysis for the ERCOT-preferred option. The study utilized the Option 3 case as a starting point. The following key elements were incorporated and evaluated as part of the analysis:
  Large loads within the study area
  Critical contingencies within the study area, including P1, P7, and P6
  Additional generator dynamic models
  Option 3 (ERCOT’s preferred option)
ERCOT observed no adverse dynamic stability impacts resulting from the implementation of Option 3 (ERCOT’s preferred option)

## Slide 9: ERCOT Recommendation
Based on the review, ERCOT will recommend the Board endorse the Option 3 to address reliability issues in Nueces County in the South Weather Zone
TSPs expect to implement the upgrades by May 2031
Estimated Capital Cost: $161.1 million
  CCN filling will be required to:
    Construct the looping in of the new Nueces Load POI 345-kV substation onto the existing 345-kV transmission line from the existing Grissom substation to the existing Lon Hill substation due to approximately 5.9-mile of new right of way (ROW); and
    Construct the new 345-kV transmission line from the planned Chalcedony substation to the new Nueces Load POI substation due to approximately 4.5-mile of new ROW.

## Slide 10: ERCOT Recommendation
Construct a new Nueces Load POI 345-kV substation cutting in on the existing Reforzar to Lon Hill 345-kV transmission line;
Loop in the new Nueces Load POI onto the existing Lon Hill to Grissom 345-kV transmission line using single-circuit structures, with normal and emergency ratings of at least 1059 MVA and 1195 MVA, respectively, which will require a new ROW, approximately 5.9 miles;
Construct a new Chalcedony to Nueces Load POI 345-kV transmission line on double-circuit capable structures with one circuit in place, with normal and emergency ratings of at least 2000 MVA, which will require a new ROW, approximately 4.5 miles; and
Rebuild the existing Lon Hill to Bunsen 138-kV transmission line on double-circuit capable structures with one circuit in place where not sharing a common tower, with normal and emergency ratings of at least 400 MVA, approximately 2.6 miles.

## Slide 11: ERCOT Recommendation

## Slide 12: Appendix A – G-1 Generators and X-1 Transformers
G-1 Generators | X-1 Transformers
Papalote Creek Wind II | Lon Hill X1 345/138-kV
El Algoden Alto W U1 | Whitepoint X1 345/138-kV
Cranell Wind | Pawnee X1 345/138-kV