## Slide 1
NOGRR282 and NPRR1308 Updates
Patrick Gravois
Principal Operations Engineer
TAC Meeting
March 25, 2026

## Slide 2: NOGRR282 and NPRR1308 Timeline
ERCOT update to TAC – March 25
ROS target vote - April 2
  ERCOT responding to Data Center Coalition March 12 comments
  ERCOT plans to submit additional comments for consideration at April 2 ROS (target 3/26 filing)
PRS target vote - April 15 (NPRR 1308 only)
  Only comments received on NPRR1308 were DCC comments; no proposed revisions to definition itself
TAC provides update to BOD - April 20-21
  Part of Board Priority Revision Request Process
TAC target vote - April 29
Target June BOD vote
ROS Vote
April 2
PRS Vote
April 15
BOD Update
April 20-21
TAC Vote
April 29
BOD Vote
June 1-2
TAC Update
March 25

## Slide 3: NOGRR282 Comments Received
AEP 12/5/2025 Comments
  Discussed at DWG
  ERCOT responded on 3/11/2026
Tesla 12/18/2025 Comments
  ERCOT responded on 1/30/2026
Onward Energy 1/23/2026 Comments
  ERCOT responded on 2/16/2026
Data Center Coalition 2/9/2026 Comments
  ERCOT responded on 3/11/2026
Texas Blockchain Council 2/18/2026 Comments
Data Center Coalition 3/12/2026 Comments
  ERCOT working on response (target posting 3/26)
Schaper Energy Consulting 3/18/2026 Comments
Texas Blockchain Council 3/18/2026 Comments

## Slide 4: ERCOT Comments – 1/30/2026
ERCOT submitted comments regarding NOGRR282 on 1/30/2026 to address the following items:
  Renumber Section 2.14, Voltage Ride-Through Requirements for Large Electronic Loads, to Section 2.15 since Section 2.14 is now used for advanced grid support requirements for inverter-based Energy Storage Resources (ESRs), implemented in NOGRR272, Advanced Grid Support Requirements for Inverter-Based ESRs.
  Revise frequency and voltage ride-through requirement exemption language in paragraph (1) of Section 2.6.4 and Section 2.15.
  Respond to Tesla comments submitted on 12/18/2025. Added language to Section 2.15(6) and Section 2.15(3)(e) to explicitly allow LEL to implement load-transfer scheme to meet ride-through requirements.
  Revise the active power recovery time for post-disturbance Large Electronic Load (LEL) consumption from one second to two seconds.

## Slide 5: Onward Energy’s Comments – 1/23/2026
Onward Energy’s comments expressed concern that NOGRR282 is not clear which requirements apply when an LEL and Generation Resource are connected behind the same POI (co-located), and how ERCOT would determine which NOG requirements apply when an LEL and/or Generation Resource trip during an event
ERCOT responded on 2/16/2026
  ERCOT will be able to determine if an LEL or Generation Resource/ESR tripped (or reduced consumption/output) during a frequency or voltage disturbance event
  Telemetry is required on LELs and Generation Resources/ESRs
  ERCOT also has telemetry from POI of co-located facilities
  ERCOT may request disturbance monitoring data from TSPs, REs, and QSEs
  ERCOT could send out RFIs to aid in its analysis
  After initial investigation of the event:
    If LEL tripped or reduced consumption following system disturbance, ERCOT would verify if non-exempt LEL complied with NOG sections 2.6.4 and 2.15
    If Generation Resource/ESR tripped or reduced output following a system disturbance, ERCOT would verify if GR/ESR complied with NOG sections 2.6.2 and 2.9
  Applicability clearly defined in appropriate NOG sections, so no language revisions needed

## Slide 6: ERCOT 3/11/2026 Comments – AEP/DWG Feedback
DWG discussed NOGRR282 on 2/12/2026 and presented feedback to ROS on 3/5/2026
AEP’s 12/5/2025 comments were addressed at DWG
ERCOT submitted comments on 3/11/2026 in response:
  ERCOT and DWG agreed to increase high frequency ride-through threshold in Table A in Section 2.6.4(3) from 61.8 Hz to 63.0 Hz; as per AEP’s comments
  LEL developer feedback indicates high frequency is not a ride-through concern
  Increased high frequency threshold improves system reliability during events
Frequency (f) in (Hz) | Minimum Ride-Through Time (seconds)
f > 61.863.0 | May ride-through or trip
61.2 < f ≤ 61.863.0 | 299
58.8 ≤ f ≤ 61.2 | continuous
57.0≤ f < 58.8 | 299
f < 57.0 | May ride-through or trip
New Proposed FRT curve

## Slide 7: ERCOT 3/11/2026 Comments – AEP/DWG Feedback
DWG members wanted clarifying language for Section 2.15(3)(d)
  Paragraph defines allowable overcurrent of 125% during voltage disturbance
  ERCOT Comments included the following added sentence:
    The allowable overcurrent up to 125% shall only persist during the voltage transient with a duration not to exceed 0.5 seconds.
Additional AEP feedback not addressed in ERCOT comments
  AEP comments suggested increasing low frequency thresholds from 57.0 Hz to 58.2 Hz
    ERCOT and DWG members agreed to keep the criteria as currently written so LELs would not trip on underfrequency events unless they are performing in accordance with UFLS or Ancillary Service obligations
  AEP comments suggested additional requirement that LELs shall return to pre-disturbance consumption within 2 seconds when voltage conditions exceed “must ride-through” curve
    ERCOT decided not to include additional requirement since it could lead to the unintended consequence of LELs choosing to trip rather than riding through these conditions
    However, ERCOT agrees this should be the desired performance

## Slide 8: ERCOT Response to DCC 2/9/2026 Comments
DCC comments propose the following revisions:
  Replace Large Electronic Load with Large Load in all of NOGRR282
  Change exemption date from 11/14/2025 to 1/1/2027
  Apply VRT requirements to only 50% of the Demand at the facility
ERCOT response does not agree with these revisions
  LELs pose a more imminent risk to ERCOT System reliability than other LLs
    LELs are more sensitive to voltage disturbances than traditional LLs
    LELs are >80% of the projected Demand growth in ERCOT
    Additional requirements on other LLs may still be needed (VFDs, hydrogen, etc.)
  Many operational and approved LELs will be exempt from RT requirements
    Extending the exemption date would worsen existing reliability risk
  Applying VRT requirements to only 50% of the load would not mitigate risk
ERCOT provided additional supporting evidence in response to DCC comments
  Referenced multiple LLWG and LL workshop presentations showing need for LEL RT requirements
  ERCOT continues to examine transmission and market solutions to help mitigate risks; but maintain these solutions alone cannot mitigate risk without improved LEL RT capability

## Slide 9: DCC 3/12/2026 Comments
DCC 3/12/2026 comments provide the following suggested requirement revisions for ERCOT to consider:
  Consideration for mechanical/cooling load: Either apply VRT requirements to computational load only, 70% of the load at the facility, or possibly provide some exemptions
  Align ERCOT low frequency ride-through requirements with PRC-024: (57.0 → 57.5)
  Revise low VRT threshold to V<0.35 for 0.02 sec
  Remove reference to positive sequence voltage in VRT requirements
  Decrease overvoltage VRT threshold for 1.10 < V ≤ 1.20 from 2 sec to 0.5 sec and allow for 2% tolerance
  Allow short-duration (0.5 sec or less) post fault active power recovery for voltage conditions at POIB where 0.50 ≤ V < 0.80; instead of requiring LEL to continue consuming power
  Increase allowable overcurrent during voltage transient from 125% to 150%
  Request for allowing load-transfer schemes that coordinate with transmission events/TDSP reclosing schemes
  Change date for meeting the exemption criteria from 11/14/2025 to 6/30/2026
ERCOT plans to submit response by 3/26/2026

## Slide 10: Texas Blockchain Council and Schaper Energy Consulting Comments
TBC 2/18/2026 comments
  TBC discussed their 2/18 comments at 3/13 LLWG
  Cryptocurrency facilities can meet frequency ride-through requirements in NOGRR282 but cannot meet voltage ride-through requirements for V<0.8 pu at POIB
  Comments claim VRT solutions (BESS, UPS, etc.) are neither practical nor economical at scale
  Exploring potential pilot project with existing BESS to provide RT
TBC 3/18/2026 and Schaper Energy Consulting 3/18/2026 comments
  Under ERCOT review
  No proposed revisions to NOGRR282 language or requirements

## Slide 11: NPRR1308 Comments Received
DCC 2/9/2026 comments
  Express concern that ride-through requirements only apply to data centers and cryptocurrency mining facilities
  No proposed revisions to protocol language/ LEL definition
  ERCOT response to DCC’s 2/9/2026 comments applies to NPRR1308 comments
No additional comments/feedback received on LEL definition from comments or Working Groups

## Slide 12
Questions?