February 2026 ERCOT Monthly Operations Report

Reliability and Operations Subcommittee Meeting

April 2, 2026

Table of Contents

1.	Report Highlights	2

2.	Frequency Control	3

2.1.	Frequency Events	3

2.2.	ERCOT Contingency Reserve Deployments/Releases	4

2.3.	Responsive Reserve Deployments/Releases	4

2.4.	Load Resource Deployments	5

3.	Reliability Unit Commitment	6

4.	IRR, Wind, and Solar Generation as a Percent of Load	7

5.	Largest Net-Load Ramps	9

6.	Congestion Analysis	10

6.1.	Notable Constraints	10

6.2.	Generic Transmission Constraint Congestion	12

6.3.	Manual Overrides	12

6.4.	Congestion Costs for Calendar Year 2025	13

7.	System Events	14

7.1.	ERCOT Peak Load	14

7.2.	Load Shed Events	14

7.3.	Stability Events	15

7.4.	Notable PMU Events	15

7.5.	DC Tie Curtailment	15

7.6.	TRE/DOE Reportable Events	15

7.7.	New/Updated Constraint Management Plans	15

7.8.	New/Modified/Removed RAS	15

7.9.	New Procedures/Forms/Operating Bulletins	15

8.	Emergency Conditions	15

8.1.	OCNs	15

8.2.	Advisories	15

8.3.	Watches	16

8.4.	Emergency Notices	16

9.	Application Performance	16

9.1.	TSAT/VSAT Performance Issues	16

9.2.	Communication Issues	16

9.3.	Market System Issues	16

10.	Model Updates	17

Appendix A: Real-Time Constraints	19

# Report Highlights

The unofficial ERCOT peak load for February 2026 was 69,612 MW and occurred on 2/1/2026 during hour ending 08:00, this is 10,949 MW less than the February 2025 peak demand of 80,560 MW on 2/20/2025 during hour ending 08:00.

There were 5 frequency events.

There were 0 ERCOT Contingency Reserve Service (ECRS) events.

There were 0 Responsive Reserve Service (RRS) events.

1 Advisory due to ERCOTs VSAT and TSAT not solving in the last 30 minutes.

There were 0 Watches.

There were 0 Emergency Notices.

There were 0 HRUC commitments.

A PVGR Generation Record of 31,350 MW was set on 02/28/2026 at 15:05.

A PVGR Penetration Record of 61.64% was set on 02/07/2026 at 10:45.

A Renewable Penetration Record of 82.95% was set on 02/28/2026 at 10:32.

The following GTCs saw congestion in February:

| GTC | Days Congestion |
| --- | --- |
| Nelson Sharpe - Rio Hondo | 24 |
| Uvalde County | 24 |
| West Texas | 17 |
| South Texas Export Pawnee - Spruce | 17 |
| North Edinburg - Lobo | 17 |
| Wharton | 13 |
| South Texas Import Katoen - Lonhill | 12 |
| South Texas Export Pawnee - Tango | 12 |
| Valley Export | 11 |
| Panhandle | 10 |
| South Texas Import Pawnee - Spruce | 5 |
| McCamey | 5 |
| Kinney | 5 |
| Raymondville - Rio Hondo | 1 |
| East Texas | 1 |
| South - Far West | 1 |

# Frequency Control

## Frequency Events

The ERCOT Interconnection experienced 5 frequency events.

A summary of the frequency events is provided below. The reported frequency events meet one of the following criteria: Delta Frequency is 60 mHz or greater; the MW loss is 350 MW or greater; resource trip event triggered ECRS deployment. Frequency events that have been identified as Frequency Measurable Events (FME) for purposes of BAL-001-TRE-2 analysis are highlighted in blue. When analyzing frequency events, ERCOT evaluates PMU data according to industry standards. Events with an oscillating frequency of less than 1 Hz are inter-area, while higher frequencies indicate local events. Industry standards specify that damping ratio for inter-area oscillations should be 3.0% or greater. For the frequency event listed below, the ERCOT system met these standards and transitioned well after the disturbance. In the case of negative delta frequency, the MW Loss column could refer to load loss.

| Date and Time | Delta Frequency | Max/Min Frequency | Duration of Event | PMU Data |  | MW Loss | Load | IRR | Inertia |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | (Hz) | (Hz) |  | Oscillation Mode (Hz) | Damping Ratio |  | (MW) | % | (MW-s) |
| 2/1/2026 7:23:41 | 0.027 | 59.965 | 00:04:00 | 0.77 | 15% | 596 | 69,569 | 15% | 306,935 |
| 2/21/2026 11:59:22 | 0.053 | 59.955 | 00:02:04 | 0.82 | 11% | 469 | 49,823 | 72% | 166,992 |
| 2/24/2026 23:45:37 | 0.030 | 59.960 | 00:06:12 | 0.95 | 8% | 466 | 45,164 | 60% | 156,895 |
| 2/26/2026 6:13:31 | 0.070 | 59.938 | 00:05:25 | 0.39 | 12% | 492 | 46,835 | 49% | 187,304 |
| 2/26/2026 15:37:21 | 0.012 | 59.965 | 00:05:09 | 0.92 | 14% | 503 | 57,397 | 57% | 225,215 |

(Note: All data on this graph encompasses frequency event analysis based on BAL-001-TRE-2.)

## ERCOT Contingency Reserve Deployments/Releases

There were 0 events where ERCOT Contingency Reserve MWs were released to SCED. The events highlighted in blue were related to frequency events reported in Section 2.1 above.

| Date and Time Released to SCED | Date and Time Recalled | Duration of Event | Maximum MWs Released | Comments |
| --- | --- | --- | --- | --- |
| N/A | N/A | N/A | N/A | N/A |

## Responsive Reserve Deployments/Releases

There were no events where Responsive Reserve MWs were released to SCED.

| Date and Time Released to SCED | Date and Time Recalled | Duration of Event | Maximum MWs Released | Comments |
| --- | --- | --- | --- | --- |
| N/A | N/A | N/A | N/A | N/A |

## Load Resource Deployments

| Resource Location | # of Resources | Operating Day | Total # of Hours Committed | Total MWhs | Reason for Commitment |
| --- | --- | --- | --- | --- | --- |

There were no Load Resources events that were controlled by an Under-Frequency Relays that deployed for an emergency event.

# Reliability Unit Commitment

ERCOT reports on Reliability Unit Commitments (RUC) monthly. Commitments are reported grouped by operating day and weather zone. The total number of hours committed is the sum of the hours for all the units in the specified region. Additional information on RUC commitments can be found on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

There were 0 DRUC commitments.

There were 0 HRUC commitments.

| Resource Location | # of Resources | Operating Day | Total # of Hours Committed | Total MWhs | Reason for Commitment |
| --- | --- | --- | --- | --- | --- |
| N/A | N/A | N/A | N/A | N/A | N/A |

# IRR, Wind, and Solar Generation as a Percent of Load

The graph below shows the maximum, minimum and average aggregate solar, wind and IRR output as a percentage of total ERCOT load when evaluated as 10-minute averaged intervals, over the past 13 months. Current wind and solar generation and penetration records are listed in the footnote below. Maximum IRR penetration for February 2026 was 82.95% on 2/28/2026 interval ending 10:30 and minimum IRR penetration for February 2026 was 5.82% on 2/6/2026 interval ending 18:10.

During the hour of peak load for the month, hourly integrated wind generation was 10,274 MW and solar generation was 1,084 MW. The graph below shows the wind and solar penetration percentage during the hour of the peak load in the last 13 months.

Lastly, the graph below shows the minimum wind, solar, and IRR output during the peak load hour as a percentage of the daily peak load for every day in the month.

# Largest Net-Load Ramps

The net-load ramp is defined as the change in net-load (load minus wind and PVGR generation) during the defined time horizon. Such a variation in net-load needs to be accommodated in grid operations to ensure that the reliability of the grid is satisfactorily maintained. The largest net-load ramps over 5-minute, 10-minute, 15-minute, 30-minute, and 60-minute intervals in February 2026 were 2,379 MW, 4,431 MW, 6,479 MW, 11,451 MW, and 19,907 MW respectively. A comparison with historical values is provided in the table below.

| Month and Year | 5 min | 10 min | 15 min | 30 min | 60 min |
| --- | --- | --- | --- | --- | --- |
| February 2015 | 1,131 MW | 1,763 MW | 2,469 MW | 4,031 MW | 6,910 MW |
| February 2016 | 999 MW | 1,658 MW | 2,144 MW | 3,504 MW | 5,923 MW |
| February 2017 | 1,051 MW | 1,744 MW | 2,268 MW | 3,228 MW | 5,346 MW |
| February 2018 | 1,494 MW | 1,706 MW | 2,003 MW | 3,419 MW | 5,628 MW |
| February 2019 | 1,094 MW | 1,793 MW | 2,388 MW | 3,718 MW | 6,540 MW |
| February 2020 | 1,173 MW | 1,777 MW | 2,198 MW | 4,107 MW | 7,430 MW |
| February 2021 | 933 MW | 1,661 MW | 2,374 MW | 4,479 MW | 8,079 MW |
| February 2022 | 1,086 MW | 2,006 MW | 2,887 MW | 5,257 MW | 9,476 MW |
| February 2023 | 1,681 MW | 2,477 MW | 3,298 MW | 6,194 MW | 10,549 MW |
| February 2024 | 1,710 MW | 2,776 MW | 4,172 MW | 8,026 MW | 15,431 MW |
| February 2025 | 2,276 MW | 3,348 MW | 5,018 MW | 9,696 MW | 17,261 MW |
| February 2026 | 2,379 MW | 4,431 MW | 6,479 MW | 11,451 MW | 19,907 MW |
|  | 2/1/2026 | 2/15/2026 | 2/15/2026 | 2/5/2026 | 2/5/2026 |
|  | (IE 16:05) | (IE 17:26) | (IE 17:27) | (IE 17:27) | (IE 17:53) |
| All Months in 2015-2026 | 3,797 MW | 4,431 MW | 6,479 MW | 11,451 MW | 19,909 MW |
|  | 5/28/2025 | 2/15/2026 | 2/15/2026 | 2/5/2026 | 1/18/2026 |
|  | (IE 10:27) | (IE 17:26) | (IE 17:27) | (IE 17:27) | (IE 17:27) |

# Congestion Analysis

## Notable Constraints

Nodal protocol section 3.20 specifies that ERCOT shall identify transmission constraints that are binding in Real-Time three or more Operating Days within a calendar month. As part of this process, ERCOT reports congestion that meets this criterion to ROS. In addition, ERCOT also highlights notable constraints that have an estimated congestion rent exceeding $1,000,000 for a calendar month. These constraints are detailed in the table below, including approved transmission upgrades from TPIT that may provide some congestion relief based on ERCOT’s engineering judgement. Rows highlighted in blue indicate the congestion was affected by one or more outages. For a list of all constraints activated in SCED, please see Appendix A at the end of this report.

| Contingency Name | Overloaded Element | Contingency Name | Overloaded Element | # of Days Constraint Binding | Congestion Rent | Transmission Project |
| --- | --- | --- | --- | --- | --- | --- |
| MRNKDHM5 | 587__A | MANUAL RNKSW TO DHMSW 345&KRWSW TO DHMSW 345 DBLCKT | Argyle - Highlands Tnp 138kV | 15 | $9,426,962.89 |  |
| DBAKCED5 | HARGRO_TWINBU1_1 | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Hargrove - Twin Buttes 138kV | 14 | $9,163,694.23 |  |
| BASE CASE | WESTEX | Basecase | WESTEX GTC | 14 | $8,824,104.33 | The PUCT approved Permian Basin Relibility Plan (765-kV import paths) helps improve, but not fully exit, the GTC yet. |
| SBWDDBM5 | LPLMK_LPLNE_1 | BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Mackenzie Substation - Northeast Substation 115kV | 12 | $3,956,965.68 |  |
| DBAKCED5 | 6965__A | BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Longshore Switch - Prairieland Switch 345kV | 14 | $3,777,146.72 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034, MOD 81268) |
| STM2TMP5 | 315__A | TEMPLE PECAN CREEK to TEMPLE SWITCH LIN _A | Temple Pecan Creek - Temple Switch 345kV | 2 | $3,060,545.11 |  |
| MCATMG25 | 6945__A | MAN_SGL_CATSW-MGSES_2_345KV | Morgan Creek Ses - Cattleman Switch 345kV | 9 | $2,555,284.19 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |
| DRNS_TB5 | THWZEN71_A | Rns-Rtw & Sng-Tb 345kV | Th Wharton - Zenith 345kV | 4 | $2,535,064.33 |  |
| BASE CASE | HHGTOM_1 | Basecase | Omega - Horse Hollow Generation Tie 345kV | 12 | $2,027,136.96 |  |
| SVENFTS5 | 35055__A | FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B | Sam Switch - Venus Switch 345kV | 10 | $1,938,679.33 | Venus Switch to Sam Switch 345-kV Line Project (24RPG017, MOD 78369) |
| SCMNCPS5 | 651__B | COMANCHE SWITCH (Oncor) to COMANCHE PEAK SES LIN _A | Comanche Tap - Comanche Switch (Oncor) 138kV | 14 | $1,432,735.12 |  |
| MRGRPR25 | 6945__A | MAN_DBL_RGRSW-PRMSW+MGSES-RGRSW_345KV | Morgan Creek Ses - Cattleman Switch 345kV | 3 | $1,325,158.05 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |
| DFOAVLO5 | BRUNI_69_1 | FOWLERTON to LOBO & AVANZADA | Bruni Sub 138kV | 12 | $1,144,448.69 |  |
| BASE CASE | E_PASP | Basecase | E_PASP GTC | 14 | $1,119,831.18 | The following RPG-endorsed projects will help improve the GTC but not fully exit the GTC yet: San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| BASE CASE | NELRIO | Basecase | NELRIO GTC | 24 | $1,103,271.40 | The Lower Rio Grande Valley (LRGV) System Enhancement Project (21RPG017) will improve the NorthEd_LoboGTC to support up to 80% of total wind and solar generation capacity in the LRGV area. |
| BASE CASE | PNHNDL | Basecase | PNHNDL GTC | 7 | $1,018,786.26 |  |
| DFOAVLO5 | LASCRU_MILO1_1 | FOWLERTON to LOBO & AVANZADA | Las Cruces - Milo 138kV | 3 | $916,168.89 | AEP_TCC_Las Cruces - Milo Rebuild Tier 4 project (MOD 76076) is supposed to be in service in August 2025, but Grid Geo still reflects original line ratings. |

## Generic Transmission Constraint Congestion

| GTC | Days Congestion |
| --- | --- |
| Nelson Sharpe - Rio Hondo | 24 |
| Uvalde County | 24 |
| West Texas | 17 |
| South Texas Export Pawnee - Spruce | 17 |
| North Edinburg - Lobo | 17 |
| Wharton | 13 |
| South Texas Import Katoen - Lonhill | 12 |
| South Texas Export Pawnee - Tango | 12 |
| Valley Export | 11 |
| Panhandle | 10 |
| South Texas Import Pawnee - Spruce | 5 |
| McCamey | 5 |
| Kinney | 5 |
| Raymondville - Rio Hondo | 1 |
| East Texas | 1 |
| South - Far West | 1 |

- There was no activity on the remaining GTCs during the month.

Note: This is how many times a constraint has been activated to avoid exceeding a GTC limit, it does not imply an exceedance of the GTC occurred or that the GTC was binding.

## Manual Overrides

- None

## Congestion Costs for Calendar Year 2025

The following table represents the top twenty active constraints for the calendar year based on the estimated congestion rent attributed to the congestion. ERCOT updates this list on a monthly basis.

| Contingency | Overloaded Element | # of 5-min SCED | Estimated | Transmission |
| --- | --- | --- | --- | --- |
| MANUAL RNKSW TO DHMSW 345&KRWSW TO DHMSW 345 DBLCKT | Argyle - Highlands Tnp 138kV | 4,157 | 28,084,248.26 |  |
| DOUBLE NVARO-LEG & NVARO-OUTSW 345 KV | Big Brown Ses - Jewett 345kV | 504 | 26,003,760.95 |  |
| BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Hargrove - Twin Buttes 138kV | 3,693 | 20,139,945.01 |  |
| BAKESW-CEDACA 345kV & BAKESW-CEDACA 345kV | Longshore Switch - Prairieland Switch 345kV | 4,206 | 16,946,809.22 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034, MOD 81268) |
| STP-Elmcreek&WAP 345kV | South Texas Project - Elmcreek 345kV | 355 | 15,792,038.58 |  |
| BLACKWATER DRAW SWITCH to DOUBLE MOUNTAIN SWITCH LIN 1 | Mackenzie Substation - Northeast Substation 115kV | 3,160 | 15,620,863.74 |  |
| Basecase | WESTEX GTC | 3,866 | 14,698,785.68 | The PUCT approved Permian Basin Relibility Plan (765-kV import paths) helps improve, but not fully exit, the GTC yet. |
| Basecase | E_PASP GTC | 3,401 | 14,149,931.67 | The following RPG-endorsed projects will help improve the GTC but not fully exit the GTC yet: San Antonio South Reliability I Project (22RPG048) LRGV Transmission Improvement Project (21RPG017) San Antonio South Reliability II Project (23RPG032) |
| KENEDSW - TULETA (138) & PETTUS - BAEZ (69) | Coleto Creek - Rosata Tap 138kV | 538 | 14,029,054.48 | Coleto Creek to Kenedy SS 138 kV Transmission Project (20RPG014) approved Tier 3 project (MOD 50870) is supposed to be in service in June 2025, but Grid Geo still reflects original line ratings. |
| FOWLERTON to LOBO & AVANZADA | Lobo - Laredo Vft North 138kV | 3,509 | 10,531,926.78 |  |
| MEADOW to OASIS LIN A | Brays - H O Clarke 138kV | 1,636 | 9,520,246.85 |  |
| TEMPLE PECAN CREEK to TEMPLE SWITCH LIN _A | Temple Pecan Creek - Temple Switch 345kV | 884 | 8,797,593.04 |  |
| Basecase | PNHNDL GTC | 4,898 | 8,268,215.53 |  |
| FORT SMITH SWITCH to FORT SMITH SWITCH LIN _B | Sam Switch - Venus Switch 345kV | 1,533 | 7,682,999.19 | Venus Switch to Sam Switch 345-kV Line Project (24RPG017, MOD 78369) |
| DMTSW TO SCOSW 345 DBLCKT | Knapp - Scurry Chevron 138kV | 2,868 | 7,568,173.86 |  |
| SALSW TO KLNSW 345 DBLCKT | Temple Switch - Temple Southeast 138kV | 119 | 7,406,847.65 | Belton - Temple 138 kV Line (24RPG001) approved Tier 1 project (MOD 87709) |
| Lytton - Slaughtr & Turner 138 kV | Lytton Springs - Pilot Knob 138kV | 356 | 7,104,066.88 | AEN_26TPIT71408_PMCR_LY_PK_CKT943_Recond_3000A Tier 4 project (MOD 71408) |
| MAN_SGL_CATSW-MGSES_2_345KV | Morgan Creek Ses - Cattleman Switch 345kV | 1,952 | 6,777,900.15 | West Texas 345-kV Infrastructure Rebuild Project (23RPG034) |
| FOWLERTON to LOBO & AVANZADA | Las Cruces - Milo 138kV | 2,381 | 6,681,718.70 | Laredo VFT North to North Laredo Switch: Rebuild 138 kV Line (MOD 76076) |
| Manual dbl ckt for NEDIN-BONILLA 345kV & RIOH-PRIM138kV | Haine Drive - La Palma 138kV | 4,519 | 6,321,957.43 |  |

# System Events

## ERCOT Peak Load

The unofficial ERCOT peak load for February 2026 was 69,612 MW and occurred on 02/01/2026 during hour ending 08:00, this is 10,948 MW less than the February 2025 demand of 80,560 MW on 02/20/2025 during hour ending 08:00. Instantaneous peak for February 2026 was 70,112 MW. Actual instantaneous peak for the same month last year was 80,657 MW.

## Load Shed Events

- None.

## Stability Events

- None.

## Notable PMU Events

ERCOT analyzes PMU data for any significant system disturbances that do not fall into the Frequency Events category reported in section 2.1. The results are summarized in this section once the analysis has been completed.

There were no PMU events outside of those reported in section 2.1.

## DC Tie Curtailment

- None.

## TRE/DOE Reportable Events

AEP Submitted a DOE-417 for 2/26/2026 – Unexpected Transmission loss within its are, contrary to design, of 3 or more Bulk Electric System Facilities caused by a common disturbance.

## New/Updated Constraint Management Plans

MP_2024_06 REV5: MOD, MP_2025_10 REV1: MOD, MP_2025_12 REV2: MOD, MP_2025_13 REV2: MOD, MP_2025_17 REV3: MOD, MP_2025_21 REV1: MOD, MP_2025_27 REV1: MOD, MP_2025_31 REV2: MOD, MP_2025_32 REV2: MOD, MP_2025_16 REV3: MOD

## New/Modified/Removed RAS

- None

## New Procedures/Forms/Operating Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 2/26/2026 | Transmission and Security Desk V2 Rev 3) | 2020 |
| 2/26/2026 | Reliability Risk Desk Operating Procedure V2 Rev 1 | 2019 |
| 2/26/2026 | Resource Desk V2 Rev 2 | 2018 |
| 2/19/2026 | DC Tie V2 Rev 1 | 2017 |

# Emergency Conditions

## OCNs

- None.

## Advisories

| Date and Time | Message |
| --- | --- |
| February 12, 2026 08:29 | ERCOT is issuing an Advisory due to ERCOTs VSAT and TSAT has not solved in the last 30 minutes. |

## Watches

- None.

## Emergency Notices

- None.

# Application Performance

## TSAT/VSAT Performance Issues

| Date and Time | Message |
| --- | --- |
| February 12, 2026 08:29 | ERCOT is issuing an Advisory due to ERCOTs VSAT and TSAT has not solved in the last 30 minutes. |

## Communication Issues

- None.

## Market System Issues

- None.

# Model Updates

The Downstream Production Change (DPC) process allows ERCOT to make changes in the one-line Network Operations Model without loading a completely new model.  The purpose of this process is to allow for reliable grid operations as system conditions change between designated Network Operations Model database loads.  The DPC process is limited in scope to just those items listed below, with equipment ratings updates being the most common.  ERCOT has seen a rise in the use of the DPC process to make on-line updates to the Network Operations Model in recent years, instead of through the standard Network Operations Model Change Request process.

- Static Line ratings (Interim Update)

- Dynamic Line ratings (non-Interim Update)

- Autotransformer ratings (non-Interim Update)

- Breaker and Switch Normal status (Interim Update)

- Contingency Definitions (Interim Update)

- RAP and RAS changes or additions (Interim Update)

- Net Dependable and Reactive Capability (NDCRC) values (Interim Update)

- Impedance Updates (non-Interim)

A total of 8 DPCs were implemented in February 2026. 569 DPCs have been implemented year to date. DPCs submitted by TDSPs are mainly updates to transmission element ratings. DPCs submitted by ERCOT are mainly updates to manual contingency definitions.

| Transmission Operator | Number of DPCs |
| --- | --- |
| AEP TEXAS COMPANY (TDSP) | 1 |
| BRAZOS ELECTRIC POWER CO OP INC (TDSP) | 0 |
| BROWNSVILLE PUBLIC UTILITIES BOARD (TDSP) | 0 |
| BRYAN TEXAS UTILITIES (TDSP) | 0 |
| CENTERPOINT ENERGY HOUSTON ELECTRIC LLC (TDSP) | 0 |
| CITY OF AUSTIN DBA AUSTIN ENERGY (TDSP) | 0 |
| CITY OF COLLEGE STATION (TDSP) | 0 |
| CITY OF GARLAND (TDSP) | 0 |
| CPS ENERGY (TDSP) | 0 |
| CROSS TEXAS TRANSMISSION LLC (TSP)) | 0 |
| DENTON MUNICIPAL ELECTRIC (TDSP) | 0 |
| ELECTRIC TRANSMISSION TEXAS LLC (TDSP) | 0 |
| ERCOT | 3 |
| LCRA TRANSMISSION SERVICES CORPORATION (TDSP) | 2 |
| LONE STAR TRANSMISSION LLC (TSP) | 0 |
| ONCOR ELECTRIC DELIVERY COMPANY LLC (TDSP) | 1 |
| PEDERNALES ELECTRIC CO OP INC (TDSP) | 0 |
| RAYBURN COUNTRY CO OP DBA RAYBURN ELECTRIC (TDSP) | 0 |
| SHARYLAND UTILITIES LP (TDSP) | 0 |
| SOUTH TEXAS ELECTRIC CO OP INC (TDSP) | 1 |
| TEXAS MUNICIPAL POWER AGENCY (TDSP) | 0 |
| TEXAS-NEW MEXICO POWER CO (TDSP) | 0 |
| WIND ENERGY TRANSMISSION TEXAS LLC (TSP) | 0 |

# Appendix A: Real-Time Constraints

The following is a complete list of constraints activated in SCED. Full contingency descriptions can be found in the Standard Contingencies List located on the MIS secure site at Grid  Generation  Reliability Unit Commitment.

| Year | Month | Contingency Name | Overloaded Element | From Station | To Station | Count of Days |
| --- | --- | --- | --- | --- | --- | --- |
| 2026 | February | BASE CASE | NELRIO | n/a | n/a | 24 |
| 2026 | February | BASE CASE | UVALDE | n/a | n/a | 24 |
| 2026 | February | MHARNED5 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 22 |
| 2026 | February | SEUSWLT8 | BLASCOFE_RC_1 | BLASW | COFESSRC | 19 |
| 2026 | February | DBAKCED5 | 6965__A | LNGSW | PRLSW | 19 |
| 2026 | February | SEUSWLT8 | BLASCOFE_RC_1 | COFESSRC | BLASW | 19 |
| 2026 | February | BASE CASE | WESTEX | n/a | n/a | 17 |
| 2026 | February | BASE CASE | E_PASP | n/a | n/a | 17 |
| 2026 | February | BASE CASE | NE_LOB | n/a | n/a | 17 |
| 2026 | February | DFOWSMG5 | GEO_SIG_1 | GEOWEST | SIGMOR | 16 |
| 2026 | February | SCMNCPS5 | 651__B | CMNSW | CMNTP | 15 |
| 2026 | February | DBAKCED5 | HARGRO_TWINBU1_1 | TWINBU | HARGROVE | 15 |
| 2026 | February | MRNKDHM5 | 587__A | ARGYL | LWSVH | 15 |
| 2026 | February | DFOAVLO5 | LARDVN_LOBO2_1 | LOBO | LARDVNTH | 15 |
| 2026 | February | BASE CASE | HHGTOM_1 | HHGT | OMEGA | 14 |
| 2026 | February | SLARLOB8 | ASHERT_CATARI1_1 | CATARINA | ASHERTON | 14 |
| 2026 | February | DMTSCOS5 | 6437__F | SCRCV | KNAPP | 14 |
| 2026 | February | SLARLOB8 | ASHERT_CATARI1_1 | ASHERTON | CATARINA | 14 |
| 2026 | February | SBWDDBM5 | LPLMK_LPLNE_1 | LPLMK | LPLNE | 14 |
| 2026 | February | BASE CASE | MLB_SLR_TLINE_1 | MLB_SLR | QUASAR | 13 |
| 2026 | February | BASE CASE | WHARTN | n/a | n/a | 13 |
| 2026 | February | DFOAVLO5 | BRUNI_69_1 | BRUNI | BRUNI | 13 |
| 2026 | February | BASE CASE | I_KALO | n/a | n/a | 12 |
| 2026 | February | SBRAPIN8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 12 |
| 2026 | February | DSNG_TB5 | THWZEN71_A | ZEN | THW | 12 |
| 2026 | February | BASE CASE | E_PATA | n/a | n/a | 12 |
| 2026 | February | SCARFRI8 | ATSO_SONR1_1 | SONR | ATSO | 11 |
| 2026 | February | DELMTEX5 | BLESSING_1382 | BLESSING | BLESSING | 11 |
| 2026 | February | BASE CASE | VALEXP | n/a | n/a | 11 |
| 2026 | February | SVENFTS5 | 35055__A | SAMSW | VENSW | 10 |
| 2026 | February | SFURRAY8 | VAN_VNDB_1 | VANBLTSS | VANBLT69 | 10 |
| 2026 | February | DBIGSCH5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 10 |
| 2026 | February | BASE CASE | PNHNDL | n/a | n/a | 10 |
| 2026 | February | DSALHUT5 | 450__A | SNDSW | AUSTRO | 10 |
| 2026 | February | DFERWIR8 | 40T189_1 | FERGUS | WIRTZ | 10 |
| 2026 | February | SMA2SAP8 | MADDUX_SAPOWE1_1 | SAPOWER | MADDUX | 10 |
| 2026 | February | SSTAWIC8 | 138_IH2_COT_1 | IH20 | TNCOLIET | 10 |
| 2026 | February | SMA2SAP8 | MADDUX_SAPOWE1_1 | MADDUX | SAPOWER | 10 |
| 2026 | February | SN_SAJO5 | LASPUL_RAYMND1_1 | LASPULGA | RAYMND2 | 9 |
| 2026 | February | SBRAPIN8 | ESCOND_GANSO1_1 | ESCONDID | GANSO | 9 |
| 2026 | February | DSCOTKW5 | 6215__A | BCKSW | CGRSW | 9 |
| 2026 | February | SBRAHAM8 | ESCOND_GANSO1_1 | ESCONDID | GANSO | 9 |
| 2026 | February | SFORYEL8 | HEXT_MASONS1_1 | MASONSW | HEXT | 9 |
| 2026 | February | SFORYEL8 | HEXT_MASONS1_1 | HEXT | MASONSW | 9 |
| 2026 | February | SLARLOB8 | NLARSW_PILONC1_1 | PILONCIL | NLARSW | 9 |
| 2026 | February | SFURVAN8 | RAYBUR_FURHMAN_1 | FURHMAN | RAYBURN | 9 |
| 2026 | February | SFURVAN8 | RAYBUR_FURHMAN_1 | RAYBURN | FURHMAN | 9 |
| 2026 | February | MCATMG25 | 6945__A | MGSES | CATSW | 9 |
| 2026 | February | DRESMCL8 | I_DUPS_RESNIK1_1 | I_DUPSW | RESNIK | 9 |
| 2026 | February | DBIGKEN5 | FORTMA_YELWJC1_1 | FORTMA | YELWJCKT | 8 |
| 2026 | February | DLOFOAV5 | BRUNI_69_1 | BRUNI | BRUNI | 8 |
| 2026 | February | SASPPAI8 | ASPM_XF1L | ASPM | ASPM | 8 |
| 2026 | February | DBIGKEN5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 8 |
| 2026 | February | DSLKSOL5 | 138_FLT_FXT_1 | TNFXTAIL | FLAT_TOP | 8 |
| 2026 | February | SBAKCED5 | BAKRFLD_CEDCAN_1 | CEDACA | BAKESW | 7 |
| 2026 | February | DRILKRW5 | 109__A | EXCSW | RNKSW | 7 |
| 2026 | February | SCARFRI8 | MADDUX_SANTIA1_1 | SANTIAGO | MADDUX | 7 |
| 2026 | February | SI_DI_48 | I_DUPP_I_DUPS1_1 | I_DUPP1 | I_DUPSW | 7 |
| 2026 | February | DLOFOAV5 | ASHERT_CATARI1_1 | ASHERTON | CATARINA | 6 |
| 2026 | February | SWLTBRT8 | EUSTWLTN_RC_1 | EUSTSERC | WALTSSRC | 6 |
| 2026 | February | DBAKSOL5 | SOLSTICE_PST1 | SOLSTICE | SOLSTICE | 6 |
| 2026 | February | SHONF38 | HON_DEVI_1 | HONDOCK | DEVINESW | 6 |
| 2026 | February | DDAVGB25 | GBYLYD70_A | LYD | GBY | 6 |
| 2026 | February | SWLTBRT8 | EUSTWLTN_RC_1 | WALTSSRC | EUSTSERC | 6 |
| 2026 | February | DLOFOAV5 | NLARSW_PILONC1_1 | NLARSW | PILONCIL | 6 |
| 2026 | February | DLOFOAV5 | NLARSW_PILONC1_1 | PILONCIL | NLARSW | 6 |
| 2026 | February | DSALKLN5 | 630__B | KLNSW | HHSTH | 6 |
| 2026 | February | XFTS89 | ALPINE_BRONCO1_1 | BRONCO | ALPINE | 6 |
| 2026 | February | BASE CASE | I_PASP | n/a | n/a | 5 |
| 2026 | February | SBE2ASH8 | WCR_CARI_1 | WCRYSTS | CARIZOS | 5 |
| 2026 | February | SREAUVA8 | DOWNIES_AX1H | DOWNIES | DOWNIES | 5 |
| 2026 | February | SFORYEL8 | HEXT_YELWJC1_1 | YELWJCKT | HEXT | 5 |
| 2026 | February | BASE CASE | MCCAMY | n/a | n/a | 5 |
| 2026 | February | SFTCGAR8 | BALLINGE_FMRL | BALLINGE | BALLINGE | 5 |
| 2026 | February | DFOAVLO5 | FREER_LOBO1_1 | LOBO | FREER | 5 |
| 2026 | February | BASE CASE | KINNEY | n/a | n/a | 5 |
| 2026 | February | SMDOOAS5 | BR_HOC09_A | BR | HOC | 5 |
| 2026 | February | SORNLON8 | ORNGROV_69_1 | ORNGROV | ORNGROV | 5 |
| 2026 | February | DODEMOS5 | 6513__A | ODESA | ODNTH | 4 |
| 2026 | February | DVICDUP8 | GREENL_WEAVER1_1 | WEAVERRD | GREENLK | 4 |
| 2026 | February | SLAQLOB8 | BRUNI_69_1 | BRUNI | BRUNI | 4 |
| 2026 | February | DDILCOT8 | DILLEYSW_XF1H | DILLEYSW | DILLEYSW | 4 |
| 2026 | February | BASE CASE | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 4 |
| 2026 | February | BASE CASE | BR_HOC09_A | BR | HOC | 4 |
| 2026 | February | DELMSAN5 | HON_DEVI_1 | HONDOCK | DEVINESW | 4 |
| 2026 | February | SMCEESK8 | MKLT_TRNT1_1 | TRNT | MKLT | 4 |
| 2026 | February | DRNS_TB5 | THWZEN71_A | ZEN | THW | 4 |
| 2026 | February | DCC1_VIC | BLESSING_1382 | BLESSING | BLESSING | 4 |
| 2026 | February | MRGRMGS5 | 6945__A | MGSES | CATSW | 4 |
| 2026 | February | SENSENW8 | 943__B | ENWSW | SHKSW | 4 |
| 2026 | February | SECRDMT8 | 6215__A | BCKSW | CGRSW | 4 |
| 2026 | February | SENSENW8 | 943__B | SHKSW | ENWSW | 4 |
| 2026 | February | DSTPREF5 | BLESSING_1382 | BLESSING | BLESSING | 4 |
| 2026 | February | SGRIRAP5 | MELONC_SEADRF1_1 | SEADRFTC | MELONCRE | 4 |
| 2026 | February | DLOFOAV5 | LARDVN_LOBO2_1 | LOBO | LARDVNTH | 4 |
| 2026 | February | SBUZHMP8 | 6217__A | WLVSW | GAILS | 3 |
| 2026 | February | SSNYCGR8 | SNYDR_FMR1 | SNYDR | SNYDR | 3 |
| 2026 | February | SBRAHAM8 | GANSO_MAVERI1_1 | GANSO | MAVERICK | 3 |
| 2026 | February | DFOAVLO5 | LASCRU_MILO1_1 | LASCRUCE | MILO | 3 |
| 2026 | February | MRGRPR25 | 6945__A | MGSES | CATSW | 3 |
| 2026 | February | SGRIRAP5 | BIGTRE_V_DUPS1_1 | V_DUPSW | BIGTRE | 3 |
| 2026 | February | DSGTSCH5 | HARGRO_TWINBU1_1 | TWINBU | HARGROVE | 3 |
| 2026 | February | SBIGMO38 | HON_DEVI_1 | HONDOCK | DEVINESW | 3 |
| 2026 | February | SOXYIN28 | I_DUPP_I_DUPS1_1 | I_DUPP1 | I_DUPSW | 3 |
| 2026 | February | DMCEBUT8 | MKLT_TRNT1_1 | TRNT | MKLT | 3 |
| 2026 | February | DWAP_BI5 | BI_JN_64_A | JN | BI | 3 |
| 2026 | February | DSTEXP12 | FORMOS_JOSLIN1_1 | JOSLIN | FORMOSA | 3 |
| 2026 | February | DODEMOS5 | 6540__A | ODEHV | RTRSW | 3 |
| 2026 | February | MSSNDBG5 | 421__A | BCESW | SNDSW | 3 |
| 2026 | February | DNAVOUT5 | 50__A | JEWET | BBSES | 3 |
| 2026 | February | MHARNED5 | PANTER_WESMER1_1 | WESMER | PANTERA | 3 |
| 2026 | February | SDIMBEV8 | UVALDE_W_BATE1_1 | UVALDE | W_BATESV | 3 |
| 2026 | February | SDIMBEV8 | UVALDE_W_BATE1_1 | W_BATESV | UVALDE | 3 |
| 2026 | February | SW_BUVA8 | DOWNIES_AX1H | DOWNIES | DOWNIES | 3 |
| 2026 | February | SN_SLON5 | CELANE_KLEBER1_1 | CELANEBI | KLEBERG | 3 |
| 2026 | February | DNOESGT5 | HARGRO_TWINBU1_1 | TWINBU | HARGROVE | 3 |
| 2026 | February | SBIGOR45 | MADDUX_TREADW1_1 | TREADWEL | MADDUX | 3 |
| 2026 | February | DFOAVLO5 | NLARSW_PILONC1_1 | NLARSW | PILONCIL | 3 |
| 2026 | February | DELMSAN5 | BLESSING_1382 | BLESSING | BLESSING | 3 |
| 2026 | February | DCAGCI58 | 255T279_1 | PIPECR | MEDILA | 2 |
| 2026 | February | DELMSAN5 | SIGMOR_THREE_1_1 | SIGMOR | THREE_RI | 2 |
| 2026 | February | SSPUSLT8 | ASPM_XF1L | ASPM | ASPM | 2 |
| 2026 | February | SCOMHA38 | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 2 |
| 2026 | February | MBONMAN5 | PANTER_WESMER1_1 | WESMER | PANTERA | 2 |
| 2026 | February | BASE CASE | RANDAD_ZAPATA1_1 | RANDADO | ZAPATA | 2 |
| 2026 | February | DELMSAN5 | UVALDE_W_BATE1_1 | W_BATESV | UVALDE | 2 |
| 2026 | February | SGRSWTH8 | 100018_1_ | ORANS | ORN | 2 |
| 2026 | February | DBAKCED5 | 6950__A | MGSES | CATSW | 2 |
| 2026 | February | SBRTANT8 | EUSTWLTN_RC_1 | WALTSSRC | EUSTSERC | 2 |
| 2026 | February | BASE CASE | GALOW_MUSTNGCK_1 | MUSTNGCK | GALOW | 2 |
| 2026 | February | DBUCRGP5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 2 |
| 2026 | February | SBRAESC8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 2 |
| 2026 | February | MLONOR58 | SND_ORAN_1 | ORNGROV | SNDIEGS | 2 |
| 2026 | February | MKRWDHM5 | 109__A | EXCSW | RNKSW | 2 |
| 2026 | February | DMGSBTR5 | 6036__A | TKWSW | MGSES | 2 |
| 2026 | February | DMTSCOS5 | 6240__C | SACRC | DPCRK | 2 |
| 2026 | February | SHAYZO25 | 6T227_1 | HAYSEN | ZORN | 2 |
| 2026 | February | DELMSAN5 | BLESSI_LOLITA1_1 | LOLITA | BLESSING | 2 |
| 2026 | February | SBLACOF8 | EUSTWLTN_RC_1 | WALTSSRC | EUSTSERC | 2 |
| 2026 | February | SDUKNED8 | HEC_NEDIN2_1 | HEC | NEDIN | 2 |
| 2026 | February | SL_4RAY8 | RAYBURN_69_2 | RAYBURN | RAYBURN | 2 |
| 2026 | February | SMV_PAR8 | RIOHND_ERIOHND_1 | MV_RIOHO | RIOHONDO | 2 |
| 2026 | February | DAUSLOS5 | 190T152_1 | WINCHES | GIDEON | 2 |
| 2026 | February | SSUNRGR8 | 6240__C | SACRC | DPCRK | 2 |
| 2026 | February | DSTEXP12 | BLESSI_LOLITA1_1 | LOLITA | BLESSING | 2 |
| 2026 | February | SBROALP9 | COCS_FTST1_1 | FTST | COCS | 2 |
| 2026 | February | DCOTWR25 | FARMLAND_LONGD_1 | FARMLAND | W_LD_345 | 2 |
| 2026 | February | DTHSFBR5 | 35065__A | FVLSW | FTSSW | 2 |
| 2026 | February | DBUCRGP5 | 651__B | CMNSW | CMNTP | 2 |
| 2026 | February | DBUCRGP5 | CMNSW_MR1H | CMNSW | CMNSW | 2 |
| 2026 | February | DKG_NB_5 | MDOPHR99_A | MDO | PHR | 2 |
| 2026 | February | SORNLON8 | SND_ORAN_1 | ORNGROV | SNDIEGS | 2 |
| 2026 | February | DWPWFWP5 | STPWAP39_1 | STP | WAP | 2 |
| 2026 | February | SSGVTRC5 | 175__A | TRCNR | FORSW | 2 |
| 2026 | February | STM2TMP5 | 315__A | TMPSW | TMPCR | 2 |
| 2026 | February | MCATPRL5 | 6965__A | LNGSW | PRLSW | 2 |
| 2026 | February | DSTPSTA5 | BLESSING_1382 | BLESSING | BLESSING | 2 |
| 2026 | February | SCITWEI8 | CLARK__LON_HI1_1 | LON_HILL | CLARK_WD | 2 |
| 2026 | February | DBAKCED5 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 2 |
| 2026 | February | SN_SLON5 | LASPUL_RAYMND1_1 | LASPULGA | RAYMND2 | 2 |
| 2026 | February | SMCEABS8 | MKLT_TRNT1_1 | TRNT | MKLT | 2 |
| 2026 | February | SW_SBRN5 | 16050__B | CRTRVLLE | HILGR | 2 |
| 2026 | February | SW_SDIV5 | 16050__B | CRTRVLLE | HILGR | 2 |
| 2026 | February | SBROALP9 | COCS_FTST1_1 | COCS | FTST | 2 |
| 2026 | February | SBLACOF8 | EUSTWLTN_RC_1 | EUSTSERC | WALTSSRC | 2 |
| 2026 | February | DYELHE89 | KATEMC_MASN1_1 | MASN | KATEMCY | 2 |
| 2026 | February | DTHSFBR5 | 35045__A | SAMSW | FVLSW | 2 |
| 2026 | February | DWLDSCO5 | 15060__E | TRYSW | KOCHTAP | 1 |
| 2026 | February | DSALHUT5 | 1715__B | TMPSW | FRYSW | 1 |
| 2026 | February | DSALHUT5 | 270__A | KNBSW | TMPSW | 1 |
| 2026 | February | MSLPNWR5 | 3050__A | WTRML | LPNSW | 1 |
| 2026 | February | DTHSFBR5 | 35055__A | SAMSW | VENSW | 1 |
| 2026 | February | DVENFTS5 | 505__B | FBRSW | THSES | 1 |
| 2026 | February | DBUZLME8 | 6217__A | WLVSW | GAILS | 1 |
| 2026 | February | SCMNCPS5 | 651__C | CMNTP | SHILO | 1 |
| 2026 | February | SN_SLON5 | ALAZAN_B_DAVI1_1 | ALAZAN | B_DAVIS | 1 |
| 2026 | February | BASE CASE | BALLIN_PAINTR1_1 | BALLINGE | PAINTROC | 1 |
| 2026 | February | SEL_ARR8 | BLESSING_69A1 | BLESSING | BLESSING | 1 |
| 2026 | February | BASE CASE | DEV_NATA_1 | DEVINESW | NATALISS | 1 |
| 2026 | February | SBIGMO38 | DEV_NATA_1 | DEVINESW | NATALISS | 1 |
| 2026 | February | D_JN_BI5 | DV_TAP24_1 | DV | DV | 1 |
| 2026 | February | BASE CASE | EASTEX | n/a | n/a | 1 |
| 2026 | February | DELMSAN5 | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 1 |
| 2026 | February | SFURRAY8 | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 1 |
| 2026 | February | SRAYRI38 | HAINE__LA_PAL1_1 | LA_PALMA | HAINE_DR | 1 |
| 2026 | February | SHA2MAX8 | MAXWEL_WHITIN1_1 | MAXWELL | WHITING | 1 |
| 2026 | February | DBIGKEN5 | NAT_PRSN_1 | NATALISS | PEARSON | 1 |
| 2026 | February | SFURVAN8 | RAYBURN_69_2 | RAYBURN | RAYBURN | 1 |
| 2026 | February | BASE CASE | RAYBUR_FURHMAN_1 | FURHMAN | RAYBURN | 1 |
| 2026 | February | SBELFRY8 | SEA_AAT1 | SEA | SEA | 1 |
| 2026 | February | DDL_STF8 | STFWAP09_A | WAP | STF | 1 |
| 2026 | February | DFRIILL8 | UVALDE_W_BATE1_1 | W_BATESV | UVALDE | 1 |
| 2026 | February | MSUNESC8 | UVALDE_W_BATE1_1 | UVALDE | W_BATESV | 1 |
| 2026 | February | MHARNED5 | VERTRE_WESLAU1_1 | WESLAU | VERTREES | 1 |
| 2026 | February | STARLEO8 | 138_FTS_LNC_1 | LEONCRK | FTST | 1 |
| 2026 | February | DWLDSCO5 | 15060__A | KOCHTAP | BUZSW | 1 |
| 2026 | February | MDTMPSD5 | 1830__K | MPHTP | BEWLY | 1 |
| 2026 | February | DCPSES12 | 35065__A | FVLSW | FTSSW | 1 |
| 2026 | February | DBAKCED5 | 423T423_1 | TWINBU | REDCREEK | 1 |
| 2026 | February | MTRYBRO8 | 6217__D | KEYSB | LMESA | 1 |
| 2026 | February | DSALKLN5 | 641__A | KLNSW | STAGE | 1 |
| 2026 | February | DODEMOS5 | 6500__F | RTRSW | BTHOT | 1 |
| 2026 | February | SBWNCTL5 | 651__B | CMNSW | CMNTP | 1 |
| 2026 | February | DGRMGRS8 | 6830__B | CRDSW | OLNEY | 1 |
| 2026 | February | SSCLWF28 | 6840__B | NVKSW | ANARN | 1 |
| 2026 | February | MPRLCO25 | 6960__A | PRLSW | CONSW | 1 |
| 2026 | February | DREFSTP5 | BLESSING_1382 | BLESSING | BLESSING | 1 |
| 2026 | February | SMCEESK8 | ESKSW_TRNT1_1 | ESKSW | TRNT | 1 |
| 2026 | February | SCARFRI8 | FDR_OZNC_1 | FRIEND_R | OZNC | 1 |
| 2026 | February | SRT2WC8 | G138_17_1 | BRAZORIA | RT | 1 |
| 2026 | February | SGBYDPW5 | GBYLYD70_A | LYD | GBY | 1 |
| 2026 | February | DJCKDOW5 | JCKVL_02_A | JCK | VL | 1 |
| 2026 | February | SSILMIL8 | SILASRAY_T1 | SILASRAY | SILASRAY | 1 |
| 2026 | February | SWCAE8 | SN_STR26_A | SN | STR | 1 |
| 2026 | February | DRAZSA89 | UVALDE_W_BATE1_1 | UVALDE | W_BATESV | 1 |
| 2026 | February | BASE CASE | X5_ALAMO1_1 | OCI_ALM1 | X5 | 1 |
| 2026 | February | DBIGKEN5 | 423T423_1 | TWINBU | REDCREEK | 1 |
| 2026 | February | SSHAFRO8 | BENTSE_S_MCAL1_1 | BENTSEN | S_MCALLN | 1 |
| 2026 | February | DWPWFWP5 | BLESSING_1382 | BLESSING | BLESSING | 1 |
| 2026 | February | DBIGSCH5 | CROSSO_PALOUS1_1 | CROSSOVE | PALOUSE | 1 |
| 2026 | February | SHONF38 | DEV_NATA_1 | DEVINESW | NATALISS | 1 |
| 2026 | February | DDILPE89 | HON_DEVI_1 | HONDOCK | DEVINESW | 1 |
| 2026 | February | SBGLTWI8 | LAKENA_SAMATH1_1 | LAKENASW | SAMATHIS | 1 |
| 2026 | February | DBAKCED5 | LVOK_SANTIA1_1 | SANTIAGO | LVOK | 1 |
| 2026 | February | MANGGRI5 | MELONC_SEADRF1_1 | SEADRFTC | MELONCRE | 1 |
| 2026 | February | BASE CASE | SWEETWN3_XF31 | SWEETWN3 | SWEETWN3 | 1 |
| 2026 | February | SFURRAY8 | VND_PLCE_1 | VANBLT69 | PLCEDOS | 1 |
| 2026 | February | DTCRTHS5 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | February | DTCRTHS5 | 35055__A | SAMSW | VENSW | 1 |
| 2026 | February | MBUZEX28 | 6135__F | GUNSW | HPPOD | 1 |
| 2026 | February | DKENBA89 | COLETO_ROSATA1_1 | COLETO | ROSATA | 1 |
| 2026 | February | DELMSAN5 | F2_11_1 | KENEDSW | F2 | 1 |
| 2026 | February | SMOOPEA8 | FER_DOWNI_1 | DOWNIES | FERRISW | 1 |
| 2026 | February | DYELHE89 | HEARTL_KATEMC1_1 | HEARTLAN | KATEMCY | 1 |
| 2026 | February | DHUTLIM5 | HUTTO_MR2H | HUTTO | HUTTO | 1 |
| 2026 | February | DLOFOAV5 | LASCRU_MILO1_1 | LASCRUCE | MILO | 1 |
| 2026 | February | DBAKSOL5 | NEVILL_NORTMC_1 | NEVILLSW | NORTMC | 1 |
| 2026 | February | SPAWSAN5 | PAWNEE_XF1 | PAWNEE | PAWNEE | 1 |
| 2026 | February | DCMBCLB8 | 2270__B | ITALY | MEXTP | 1 |
| 2026 | February | DCPSES12 | 35045__A | SAMSW | FVLSW | 1 |
| 2026 | February | STHSVE65 | 35065__A | FVLSW | FTSSW | 1 |
| 2026 | February | DTRCFOR5 | 3610__G | PGTP1 | PDSES | 1 |
| 2026 | February | MDHMLWS5 | 587__A | ARGYL | LWSVH | 1 |
| 2026 | February | SFTCGAR8 | BALLINGE_FMRH | BALLINGE | BALLINGE | 1 |
| 2026 | February | SCOLBAL8 | BALLINGE_FMRL | BALLINGE | BALLINGE | 1 |
| 2026 | February | SEUSWLT8 | BRTNWLTN_RC_1 | WALTSSRC | BRTNSSRC | 1 |
| 2026 | February | SILLFTL8 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 1 |
| 2026 | February | SDOWMOO8 | DOWNIES_AX1H | DOWNIES | DOWNIES | 1 |
| 2026 | February | SW_BUVA8 | DOWNIE_READIN1_1 | DOWNIES | READING | 1 |
| 2026 | February | XGB2Y58 | GBYLYD70_A | LYD | GBY | 1 |
| 2026 | February | DYETRJU8 | HEXT_MASONS1_1 | HEXT | MASONSW | 1 |
| 2026 | February | SKBBI8 | HT_TAP24_1 | HT | HT | 1 |
| 2026 | February | BASE CASE | I_FW_S | n/a | n/a | 1 |
| 2026 | February | SLONLON8 | LON_HI_SERDEV4_1 | LON_HILL | LON_HILL | 1 |
| 2026 | February | DBAKSOL5 | NORTMC_AT2L | NORTMC | NORTMC | 1 |
| 2026 | February | SGEOORN8 | ORNGROV_69_1 | ORNGROV | ORNGROV | 1 |
| 2026 | February | DELMSAN5 | PAWNEE_SPRUCE_1 | PAWNEE | CALAVERS | 1 |
| 2026 | February | DBWN_AM5 | REDCRE_WEISS1_1 | REDCREEK | WEISS | 1 |
| 2026 | February | BASE CASE | RV_RH | n/a | n/a | 1 |
| 2026 | February | DRNS_TB5 | THWZEN98_A | ZEN | THW | 1 |
| 2026 | February | SWORBRD8 | 138_PYT_STG_1 | STAGHORN | PYOTE | 1 |
| 2026 | February | MCATMG55 | 16050__B | CRTRVLLE | HILGR | 1 |
| 2026 | February | DTCRTHS5 | 35065__A | FVLSW | FTSSW | 1 |
| 2026 | February | SRICGRS8 | 6840__B | NVKSW | ANARN | 1 |
| 2026 | February | DZORHAY5 | BERGHE_AT1H | BERGHE | BERGHE | 1 |
| 2026 | February | DWO5_EU8 | BR_HOC09_A | BR | HOC | 1 |
| 2026 | February | DELMSAN5 | DEV_NATA_1 | DEVINESW | NATALISS | 1 |
| 2026 | February | DLOFOAV5 | MINES__NLARSW1_1 | MINES_RD | NLARSW | 1 |
| 2026 | February | SBIGMO38 | NAT_PRSN_1 | NATALISS | PEARSON | 1 |
| 2026 | February | DBWNAMO5 | SAPOWE_SAST1_1 | SAPOWER | SAST | 1 |
| 2026 | February | SKBBI8 | ST_TAP25_1 | ST | ST | 1 |
| 2026 | February | BASE CASE | SUNRAY_TLINE_1 | SUN_SLR | DRYFRIO | 1 |
| 2026 | February | SBRTGRM8 | 100018_1_ | ORANS | ORN | 1 |
| 2026 | February | SBUZHMP8 | 6217__B | GAILS | KEYSB | 1 |
| 2026 | February | DELMSTP5 | BLESSING_1382 | BLESSING | BLESSING | 1 |
| 2026 | February | DELMSAN5 | COLETO_VICTOR2_1 | COLETO | VICTORIA | 1 |
| 2026 | February | SCOMHA38 | CTHR_TINSLE1_1 | CTHR | TINSLEY | 1 |
| 2026 | February | BASE CASE | EBONY_GENTIE_1 | EBNY_ESS | EBNY_ESS | 1 |
| 2026 | February | DKLNRGP5 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 1 |
| 2026 | February | SBRAPIN8 | GANSO_MAVERI1_1 | GANSO | MAVERICK | 1 |
| 2026 | February | DHICEMS5 | HCKSW_MR2L | HCKSW | HCKSW | 1 |
| 2026 | February | BASE CASE | HON_DEVI_1 | HONDOCK | DEVINESW | 1 |
| 2026 | February | MHARNED5 | LASPUL_RAYMND1_1 | LASPULGA | RAYMND2 | 1 |
| 2026 | February | DHWIND89 | MORRIS_NUECES1_1 | NUECES_B | MORRIS | 1 |
| 2026 | February | SBIGSCH5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 1 |
| 2026 | February | MBONNED5 | PANTER_WESMER1_1 | WESMER | PANTERA | 1 |
| 2026 | February | DFRYBC58 | SEA_AAT1 | SEA | SEA | 1 |
| 2026 | February | DBR_GT_8 | ST_TAP25_1 | ST | ST | 1 |
| 2026 | February | DBIGKEN5 | TREADW_YELWJC1_1 | TREADWEL | YELWJCKT | 1 |
| 2026 | February | DSLKSOL5 | 138_BRL_FLT_1 | FLAT_TOP | TNBRDRAW | 1 |
| 2026 | February | DSCOTKW5 | 6474__B | SUNSW | RGRSW | 1 |
| 2026 | February | SCOLBAL8 | BALLIN_HUMBLT1_1 | BALLINGE | HUMBLTAP | 1 |
| 2026 | February | XYEL88 | BALLIN_PAINTR1_1 | BALLINGE | PAINTROC | 1 |
| 2026 | February | SBIGV_D8 | BLESSI_PALACI1_1 | BLESSING | PALACIOS | 1 |
| 2026 | February | DFRIILL8 | CARVER_TINSLE1_1 | CARVER | TINSLEY | 1 |
| 2026 | February | SLARLOB8 | CATARI_PILONC1_1 | CATARINA | PILONCIL | 1 |
| 2026 | February | DDMTMHO5 | FARMLAND_LONGD_1 | FARMLAND | W_LD_345 | 1 |
| 2026 | February | SBIGOR45 | FORTMA_YELWJC1_1 | YELWJCKT | FORTMA | 1 |
| 2026 | February | DSTEXP12 | FURHMAN_VANDB_1 | FURHMAN | VANBLTSS | 1 |
| 2026 | February | SBIGV_D8 | GREENL_WEAVER1_1 | WEAVERRD | GREENLK | 1 |
| 2026 | February | SBRAHAM8 | HAMILT_MAVERI1_1 | HAMILTON | MAVERICK | 1 |
| 2026 | February | DBIGKEN5 | HAMILT_MAXWEL1_1 | MAXWELL | HAMILTON | 1 |
| 2026 | February | SKLELOY8 | LOYOLA_69_1 | LOYOLA | LOYOLA | 1 |
| 2026 | February | SL13LPL0 | LPLWA_LPLDB_1 | LPLDB | LPLWA | 1 |
| 2026 | February | DBAKSOL5 | NORTMC_AT1L | NORTMC | NORTMC | 1 |
| 2026 | February | SBIGTWI5 | PALOUS_WOLFCA1_1 | PALOUSE | WOLFCAMP | 1 |
| 2026 | February | SGALRIC8 | RAYBUR_FURHMAN_1 | FURHMAN | RAYBURN | 1 |
| 2026 | February | BASE CASE | ST_TAP05_1 | ST | ST | 1 |

Current Wind Generation Record: 28,550 MW on 03/03/2025 at 20:42 | Current Wind Penetration Record: 69.15% on 04/10/2022 at 01:43

Current Solar Generation Record: 31,350 MW on 02/28/2026 at 15:05 | Current Solar Penetration Record: 61.64% on 02/07/2026 at 10:45