| PGRR Number | 145 | PGRR Title | Batch Zero Process for Large Load Interconnections |
| --- | --- | --- | --- |
| Date |  | March 27, 2026 |  |

| Submitter’s Information |  |
| --- | --- |
| Name | Bharath Ravulapati |
| E-mail Address | bravulapati@crusoe.ai |
| Company | Crusoe Energy Systems LLC |
| Phone Number | 662-694-9125 |
| Cell Number |  |
| Market Segment | Not applicable |

Comments

Crusoe Energy Systems LLC (Crusoe) appreciates ERCOT’s March 17, 2026 comment filing responding to stakeholder feedback on Planning Guide Revision Request (PGRR) 145. Crusoe submits the following consolidated additional comments, incorporating our comments regarding financial commitment and timing impacts and our SSO/QSA sequencing comments, regarding the Subsynchronous Oscillation (SSO) study requirement as a prerequisite to the ERCOT Quarterly Stability Assessment (QSA) process under Section 9.6(1), Initial Energization and Continuing Operations for Large Loads, which is carried forward unchanged in the PGRR145 draft.

Section 9.6(1) of the PGRR145 draft carries forward from the prior Section 9 draft the following conditions that must be met before a Large Load may proceed to Initial Energization: (c) Completion of the requirements of Section 5.3.5, ERCOT Quarterly Stability Assessment; and (d) Completion and approval of any required Subsynchronous Oscillation (SSO) studies, SSO Mitigation plan, SSO Countermeasures, and SSO monitoring, if required. As written, this structure implies that SSO study completion is a prerequisite to — or at minimum must be completed concurrently with — the QSA in order to proceed to Initial Energization. This is inconsistent with how ERCOT treats generator interconnections under Section 6, where SSO and QSA proceed as parallel workstreams and SSO completion is not required prior to entry into the QSA process.

  - I. The Current Draft Creates an Asymmetry with Section 6 Generator Interconnections

Under Section 6 of the ERCOT Planning Guide, generator interconnection projects are subject to the QSA process under Section 5.3.5 as a prerequisite to Initial Synchronization. SSO studies required under Protocol Section 3.22.1.4 run in parallel with the interconnection study and QSA processes but are not a sequential prerequisite to QSA entry. A generator project may be included in a QSA without first completing its SSO study, so long as SSO requirements are resolved prior to energization. The PGRR 145 draft does not afford large load projects the same parallel-track treatment in Section 9.6(1). The sequential listing of SSO completion (paragraph (d)) alongside QSA (paragraph (c)) as co-equal pre-energization conditions, without clarifying their relationship, creates an ambiguity that could be read as requiring SSO completion before the QSA process may proceed. This reading would impose a sequencing burden on large loads that generators do not face and that has no technical basis.

  - II. SSO Completion Is Not Technically Required Before QSA Entry

The QSA, conducted pursuant to Section 5.3.5, evaluates system-wide dynamic and transient stability impacts of new loads and generators scheduled to energize in a given quarter. The QSA does not assess SSO risk at the individual project level — that is the function of the site-specific SSO study conducted under Protocol Section 3.22.1.4. These are independent analytical processes administered by different ERCOT functional teams. There is no technical dependency that requires SSO studies to be complete before ERCOT can include a Large Load in its system-level QSA. Requiring sequential completion of SSO before QSA entry introduces scheduling delays without any corresponding reliability benefit, particularly given that SSO countermeasures must be in place before the load is physically energized regardless of when the QSA is completed.

  - III. Proposed Revisions

Crusoe proposes the following revisions to Section 9.6(1) and, as a conforming change, to Section 9.8.2(5):

- Section 9.6(1)(c) of PGRR 145: Revise to reflect that the QSA prerequisite is submission for inclusion in the QSA process, not completion of SSO studies. The revised text should expressly state that SSO study completion is not required prior to submission for or inclusion in the QSA process. See proposed language in the “Revised Proposed Guide Language” section below.

- Section 9.6(1)(d) of PGRR 145: Retain SSO as a hard pre-energization requirement but add an express sentence clarifying that SSO completion is not a prerequisite to initiation of or inclusion in the QSA process. This preserves reliability protections while eliminating the ambiguous sequencing that the current draft creates.

- Section 9.8.2(5) of PGRR 145 (Conforming — Legacy Scoping Section): Add a sentence at the end of the existing paragraph confirming that SSO studies run concurrently with the QSA process and are not a prerequisite to QSA initiation. This reinforces the parallel-track principle at the study scoping stage and provides clear guidance to ILLEs, TSPs, and DSPs from the beginning of the interconnection process. Note: In the PGRR 145 structure, the legacy scoping provisions are renumbered to Section 9.8.2; this conforming change applies to that renumbered section.

  - IV. Conclusion

Crusoe respectfully requests that ERCOT revise Section 9.6(1)(c) and (d) of PGRR 145 to decouple SSO study completion from the QSA prerequisite for Initial Energization, consistent with the parallel-track approach ERCOT applies to generator interconnections under Section 6. The proposed revisions maintain all SSO reliability requirements by preserving SSO completion as a condition precedent to Initial Energization itself. The change solely removes the unintended sequencing implication that SSO must be completed before QSA entry, which has no technical basis and is not consistent with existing ERCOT practice. Crusoe appreciates ERCOT’s continued engagement with stakeholders and looks forward to continued collaboration as PGRR 145 advances through the stakeholder process.

――― Additional Comments: Financial Commitment and Timing ―――

Comments

Crusoe Energy Systems, LLC ("Crusoe") wishes to acknowledge and thank ERCOT staff for the continued effort and technical rigor reflected in PGRR145 and the associated workshop process. These supplemental comments are offered in the same spirit of constructive engagement as Crusoe's March 9, 2026 comments, and with the shared goal of ensuring that the Batch Zero framework operates equitably for all participants regardless of their stage of development.

These comments address a structural defect in PGRR145 that Crusoe believes has not yet been squarely resolved: the framework's dependence on PUC Project No. 58481 for its financial commitment criteria, and the resulting inequitable treatment of Batch Zero participants who have already made substantial financial commitments under prior ERCOT processes. Batch Zero is a transitional process for existing, advanced-stage loads — not a new-load intake process — and its financial framework should reflect that reality.

Crusoe proposes that PGRR145 adopt a standalone, three-tier financial commitment framework that is self-contained within the PGRR itself, independent of Project No. 58481, and calibrated to the actual development status of each category of Batch Zero participant. Under Crusoe's proposed framework, only loads that have not signed interconnection agreements and did not post necessary financial security to support the needed interconnection would be required to post new security — eliminating double payment and preserving the investment-backed status of all advanced-stage participants.

Crusoe's position: PGRR145 should establish its own financial commitment framework, self-contained within the PGRR language, that does not depend on Project No. 58481 for its operative standards. This framework should be structured in three tiers reflecting the actual development status of Batch Zero participants, as described in Comment 2 below. To the extent Project No. 58481 ultimately establishes standards that differ from those in PGRR145, ERCOT can address any alignment through a targeted revision request after Batch Zero is complete.

Timing Impact — The financial harm is only part of the picture. Large Load projects that have already cleared both legacy Section 9.4 and 9.5 requirements, with 2027 energization targets firmly in place, stand to lose six or more months of schedule if they must wait until July 10th to execute new interconnection agreements. These delays are entirely outside the control of the affected ILLEs and would impose billions of dollars in losses on data center developers who have done everything right under the existing process.

Comment on 2026 RTP References — ERCOT Should Use the Load Commissioning Plan as the Governing Demand Metric for Base Load Modeling: PGRR145 currently ties the modeling level for Base Loads (Section 9.2.1.1(2)(a)) and certain studied loads (Section 9.2.1.1(2)(b)(i)) to demand figures reported to ERCOT for the development of the 2026 Regional Transmission Plan (RTP). The 2026 RTP itself is based on PUCT Project No. 58480. Crusoe respectfully submits that the 2026 RTP is the wrong reference point for this purpose, and that ERCOT should instead use each load’s most recent Load Commissioning Plan (LCP) as the governing demand metric.

A meaningful subset of Batch Zero participants — including behind-the-meter (BTM) loads and loads approved without associated transmission upgrades — could not be included in the 2026 RTP data collection for reasons entirely outside their control. Penalizing these loads by capping their modeled demand at a zero or understated 2026 RTP figure — when their LCP accurately reflects their actual planned peak demand — would be inequitable and would understate true system needs in the Batch Zero study.

Crusoe therefore proposes that Sections 9.2.1.1(2)(a) and 9.2.1.1(2)(b)(i) be revised to replace the 2026 RTP demand reference with the demand level indicated in the most recent LCP submitted to ERCOT on or before July 24, 2026, consistent with the LCP-based approach already used in Sections 9.2.1.1(2)(b)(ii) and 9.2.1.2(2). The LCP is maintained on a rolling basis, reflects the ILLE’s actual construction and energization schedule, and represents the most current and accurate statement of each load’s demand profile. Adopting a uniform, LCP-driven modeling standard across all Batch Zero participant categories eliminates the inequity created by the RTP data gap and ensures the study reflects ground-truth load development.

# Comment 1 — PGRR145's Financial Commitment Framework Should Be Self-Contained and Independent of PUC Project No. 58481

PGRR145 currently incorporates the financial security and interconnection agreement standards from PUC Project No. 58481 by reference. As Crusoe and other stakeholders have noted, this rulemaking is not yet final. ERCOT has identified two pathways for addressing this dependency — one proceeding in parallel with the draft proposal for publication, and one awaiting the final adopted rule — but neither pathway resolves the more fundamental problem: the standards being imported from Project No. 58481 were designed for new large load interconnection requests and are not calibrated to the specific circumstances of Batch Zero participants.

Many loads in Batch Zero have already executed interconnection agreements, posted CIAC and necessary financial security, completed multiple rounds of ERCOT studies, and made capital investments in the hundreds of millions of dollars. Project No. 58481's financial standards — designed to elicit initial commitment from new market entrants — is simply the wrong tool for this population.

# Comment 2 — PGRR145 Should Adopt a Three-Tier Financial Commitment Framework That Eliminates Double Payment

The central inequity in PGRR145's current financial commitment structure is that it applies the same requirements — new financial security posting, new interconnection agreement execution, and non-refundable interconnection fees — to all loads regardless of what they have already done. This means that a load that executed a binding interconnection agreement years ago, posted CIAC, and posted financial security under its legacy LLIS process would be required to satisfy these requirements again under Section 9.7.Besides, ERCOT already added additional guardrails for the projects that are going to energize in 2027, by asking them to satisfy development criteria. This criteria will already folder out those projects that aren’t real. The financial security is double punitive which isnt necessary for those that have signed IAs and/or posted security.  This is not a policy choice — it is an oversight that the framework's broad drafting has inadvertently created.

Crusoe proposes that PGRR145 recognize three distinct tiers of Batch Zero participants and apply financial commitment requirements only where they are genuinely warranted:

| Tier | Load Category | Financial Obligation Under Proposed Framework | New IA Required? |
| --- | --- | --- | --- |
| Tier 1 Base Load | Loads that have complete and valid studies and an executed Interconnection Agreement (including all loads satisfying legacy §§ 9.9 and 9.10) | None. Fully grandfathered. Existing executed IA satisfies all Batch Zero financial commitment criteria. | No, the old agreements should be respected. |
| Tier 2 Already-Committed Studied Load | Loads with a valid LLI number that do not qualify as Base Load, but that have already executed an Interconnection Agreement with their TDSP and posted CIAC and financial security under that agreement | None. Prior CIAC posting and financial security satisfy Batch Zero financial commitment criteria. No new security posting or fee required. | No, the old agreements should be respected |
| Tier 3 LLI-Only Studied Load | Loads with a valid LLI number that qualify for Batch Zero under § 9.2.1.2, but that have NOT previously executed an IA, posted CIAC, or posted financial security under any prior ERCOT or TDSP process | Post $/MW financial security, commit to CIAC obligations, and execute Intermediate Agreement (§ 9.7.1) by July 10, 2026. Must execute full Interconnection Agreement (§ 9.7.2) at the commitment gate. | New IA required by July 10, 2026 |

## Tier 1: Base Loads — Full Grandfathering

Base Loads have already completed the interconnection process. They have been studied, approved, and in many cases are operating today or are under active construction. Their existing executed Interconnection Agreements reflect binding financial commitments — posted security, paid CIAC, and contractual obligations to TSPs — that are functionally equivalent to, and in many cases more stringent than, what Project No. 58481 proposes to require going forward.

Crusoe proposes that Section 9.2.1.1 be amended to confirm that Base Loads' existing executed Interconnection Agreements satisfy all financial commitment requirements under PGRR145, and that no additional security posting, fee payment, or re-execution of agreements is required for Batch Zero inclusion or advancement through the commitment gate.

## Tier 2: Studied Loads with Executed Agreements and Posted Security — No New Posting Required

A second category of Batch Zero participants consists of loads that do not qualify as Base Load — for example, because their studies postdate the base load cutoff -- but that have nonetheless already executed a binding Interconnection Agreement with their TDSP and posted CIAC and financial security under that agreement.

These loads have already made the financial commitment that Batch Zero's security requirements are designed to elicit. Requiring them to post additional security under Section 9.7 would result in double payment: these loads would be paying twice — once under their legacy agreement and again under PGRR145 — for the same interconnection rights.

Crusoe proposes that Section 9.2.1.2 be amended to recognize that a load with an executed Interconnection Agreement and demonstrated prior security and CIAC posting satisfies the financial commitment criteria for Batch Zero eligibility. The TDSP should be required to attest to ERCOT, by July 24, 2026, that the ILLE has executed an agreement and posted the required security under prior applicable requirements.

## Tier 3: LLI-Only Loads — New Financial Commitment Required

A third category consists of loads that have a valid LLI number and otherwise qualify for Batch Zero under Section 9.2.1.2, but that have not yet executed an Interconnection Agreement, posted CIAC, or provided financial security under any prior ERCOT or TDSP process. These loads have not yet demonstrated binding financial commitment, and it is appropriate to require them to do so as a condition of Batch Zero inclusion.

Crusoe proposes that Tier 3 loads be required to satisfy the following conditions by July 10, 2026 as a condition of eligibility for Batch Zero as studied/allocatable load:

- Execute a binding Intermediate Agreement meeting the requirements of PGRR145 Section 9.7.1;

- Post financial security at the applicable $/MW rate established in PGRR145 (consistent with Project No. 58481 draft, subject to final rule adoption);

- Commit to CIAC obligations as reflected in the Intermediate Agreement; and

- Execute a full Interconnection Agreement meeting Section 9.7.2 by the commitment gate deadline (on or before March 1, 2027) to lock in their allocated MW.

This is the only tier for which new financial requirements are appropriate and equitable. Applying these requirements only to Tier 3 loads — rather than uniformly to all Batch Zero participants — ensures that financial commitment standards serve their intended function without imposing duplicative obligations on loads that have already demonstrated commitment.

# Comment 3 — The Three-Tier Framework Resolves the "Commit Before Certainty" Problem and Protects All Categories of Participants

Multiple stakeholders — including in Crusoe's March 9 comments — have raised the concern that PGRR145 currently requires loads to make binding financial commitments before receiving confirmation of their eligibility or MW allocation, creating an "air gap" that introduces material investment risk. The three-tier framework directly resolves this problem for Tier 1 and Tier 2 loads by recognizing that their prior commitments already satisfy the eligibility standard. These loads need not make new commitments into uncertainty — their existing commitments are recognized as sufficient.

For Tier 3 loads, the commitment-before-certainty concern is addressed by ensuring that the July 10, 2026 commitment deadline is paired with sufficient pre-commitment information about study expectations and preliminary eligibility determinations. ERCOT should communicate, through the interconnecting TDSP, a preliminary indication of whether each load appears to satisfy the eligibility criteria under Section 9.2.1.2 in advance of the July 10 deadline, so that Tier 3 loads can make an informed commitment decision.

The three-tier framework also eliminates the perverse outcome — identified by numerous stakeholders — in which the most committed and advanced projects in Batch Zero bear the highest incremental cost burden. Under the current PGRR145 structure, a load that executed an IA and posted CIAC years ago is treated identically to a load with only an LLI number and no financial commitment. Under the proposed framework, the load with prior commitments is recognized and rewarded, and only the uncommitted load is required to satisfy new financial criteria.

Revised Cover Page Language

| Planning Guide Sections Requiring Revision | 2.1, Definitions 2.2, Acronyms and Abbreviations 3.1.2.1, All Projects 3.1.2, Regional Planning Group Project Submission 3.1.3, Project Evaluation 5.3.5 ERCOT Quarterly Stability Assessment 6.6.1 Modeling of Large Loads Not Co-Located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 6.6.2 Modeling of Large Loads Co-Located with an Existing Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 6.6.3 Modeling of Large Loads Co-Located with a Proposed Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 9, Large Load Additions at New or Modification of Existing Load Interconnection(s) 9.1, Introduction 9.2.1, Applicability of the Large Load Interconnection Study Process 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in Batch Zero (new) 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero (new) 9.2.1.3, Load not Included in Batch Zero (new) 9.2.1.4, Evaluation of Existing Studies for Large Loads (new) 9.2.2, Submission of Large Load Project Information and Initiation of the Large Load Interconnection Study (LLIS) 9.2.3, Modification of Large Load Project Information 9.2.4, Load Commissioning Plan 9.2.5, Required Interconnection Equipment 9.2.6, Batch Zero Financial Commitment Framework (new) 9.3, Interconnection Study Procedures for Large Loads 9.3.1, Large Load Interconnection Study (LLIS) 9.3.2, Large Load Interconnection Study Scoping Process 9.3.3, Large Load Interconnection Study Description and Methodology (delete) 9.3.4, Large Load Interconnection Study Elements (delete) 9.3.4.1, Steady-State Analysis (delete) 9.3.4.2, System Protection (Short-Circuit) Analysis (delete) 9.3.4.3, Dynamic and Transient Stability Analysis (delete) 9.4, LLIS Report and Follow-up 9.5, Interconnection Agreements and Responsibilities 9.5.1, Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility (delete) 9.5.2, Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities (delete) 9.6, Initial Energization and Continuing Operations for Large Loads 9.7, Definition of Required Commitment Criteria (new) 9.7.1, Definition of an Intermediate Agreement (new) 9.7.2, Definition of an Interconnection Agreement (new) 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand (new) 9.7.4, Non-Utilized Capacity (new) 9.7.5, Terms for Refund of Financial Security for an ILLE that Energizes (new) 9.8, Legacy Interconnection Study Procedures for Large Loads (new) 9.8.1, Legacy Large Load Interconnection Study (LLIS) (new) 9.8.2, Legacy Large Load Interconnection Study Scoping Process (new) 9.8.3, Legacy Large Load Interconnection Study Description and Methodology (new) 9.8.4, Legacy Large Load Interconnection Study Elements (new) 9.8.4.1, Legacy Steady-State Analysis (new) 9.8.4.2, Legacy System Protection (Short-Circuit) Analysis (new) 9.8.4.3, Legacy Dynamic and Transient Stability Analysis (new) 9.9, Legacy LLIS Report and Follow-up (new) 9.10, Legacy Interconnection Agreements and Responsibilities (new) 9.10.1, Legacy Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility (new) 9.10.2, Legacy Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities (new) |
| --- | --- |

Revised Proposed Guide Language

# 2.1 	DEFINITIONS

# 2.2	ACRONYMS AND ABBREVIATIONS

### 3.1.2	Regional Planning Group Project Submission

(1)	Transmission projects that are proposed for RPG Review, pursuant to Protocol Section 3.11.4.1, Project Submission, shall be submitted according to the provisions outlined in Section 3.1.2.1, All Projects.

#### 3.1.2.1	All Projects

(1)	The submittal of each transmission project (60 kV and above) for RPG Project Review, except for the Transmission Facility improvements submitted based Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan, should include the following elements:

(a)	The proposed project description including expected cost, feasible alternative(s) considered, transmission topology and Transmission Facility modeling parameter data, and all study cases used to generate results supporting the need for the project in electronic format (powerflow data should be in PTI Power System Simulator for Engineering (PSS/E) RAWD format).  Also, the submission should include accurate maps and one-line diagrams showing locations of the proposed project and feasible alternatives;

(b)	Identification of the SSWG, Dynamics Working Group (DWG), or Regional Transmission Plan powerflow cases used as a basis for the study and any associated changes that describe and allow accurate modeling of the proposed project;

(c)	Description and data for all changes made to the SSWG base cases or Regional Transmission Plan cases used to identify the need for the project, such as Resource unavailability and area peak load forecast;

(d)	A description of the reliability and/or economic problem that is being solved;

(e)	Information that supports any load values that differ from the load forecast used in the base cases identified in item (b) above, including any relevant historical load information or evidence demonstrating that a submitted load value is Substantiated Load;

(f)	A description of the Subsynchronous Resonance (SSR) impact of the proposed project to the generation Facilities in the system pursuant to Protocol Section 3.22.1, Subsynchronous Resonance Vulnerability Assessment, and potential SSR Countermeasure plan for any identified SSR vulnerability, if applicable;

(g)	Desired/needed in-service date for the project, and feasible in-service date, if different;

(h)	The phone number and email address of the single point of contact who can respond to ERCOT and RPG participant questions or requests for additional information necessary for stakeholder review; and

(i)	Analysis of rejected alternatives, including cost estimates, and other factors considered in the comparison of alternatives with the proposed project.

(2)	Both transmission and distribution solutions to performance deficiencies may be considered where applicable.

(3)	If there is any other information, not included above, that the submitting party believes is relevant to consideration of the need for any submitted project, the submitting party should include that information in the project submission.

### 3.1.3	Project Evaluation

(1)	ERCOT and the RPG shall evaluate proposed transmission projects using a variety of tools and techniques as needed to ensure that the system is able to meet applicable reliability criteria in a cost-effective manner.  For most proposed projects, except for the Transmission Facility improvements submitted based on Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan, several alternatives will be identified to meet the reliability criteria or other performance improvement objectives that the proposed project is designed to meet.  The project alternative with the expected lowest cost over the life of the project is generally recommended, subject to consideration of the expected long-term system needs in the area, including, as applicable, any evidence of Substantiated Load, and subject to consideration of the relative operational impacts of the alternatives.

(2)	In some cases, one alternative may be to dispatch the system in such a way that all reliability requirements are met, even without the proposed transmission project or any transmission alternative, resulting in a less efficient dispatch than what would be required to meet the reliability requirements if the proposed project was in place.  Consideration of the merits of this alternative relative to the proposed transmission project is more complex.  To facilitate the discussion and consideration of these alternatives, ERCOT has adopted certain definitions and practices, described in paragraph (4) of Protocol Section 3.11.2, Planning Criteria, and Sections 3.1.3.1, Definitions of Reliability-Driven and Economic-Driven Projects, and 3.1.3.2, Reliability-Driven Project Evaluation below.

(3)	In conducting an independent review of any project, ERCOT may, in its discretion, make adjustments to the planning case to ensure that the case reaches a solution.  When conducting an independent review of any project classified as Tier 1 pursuant to Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT must provide reasonable advance notice to the RPG of any proposed adjustments and an opportunity for stakeholder comment on them.

(4)	As part of its independent review of any project classified as Tier 1 pursuant to Protocol Section 3.11.4, except for the Transmission Facility improvements submitted based on Section 9.5, ERCOT shall:

(a)	Perform a generation sensitivity analysis.  The generation sensitivity analysis will evaluate the effect that proposed Generation Resources and/or ESRs in or near the study area will have on a recommended transmission project.  Generation Resources and ESRs that have signed Standard Generation Interconnection Agreements (SGIAs) but were not included in the study cases because they did not meet all of the requirements for inclusion in the cases pursuant to Section 6.9, Addition of Proposed Generation to the Planning Models, will be included in the sensitivity analysis.  ERCOT shall not consider the results of the generation sensitivity analysis in determining project need during its independent review of the project; and

(b)	Evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.  The results of this evaluation shall be included in the final recommendations in the independent review.

(5)	ERCOT’s independent review shall incorporate and consider historical load and any Substantiated Load.

#### 3.1.3.1	Definitions of Reliability-Driven and Economic-Driven Projects

(1)	Proposed transmission projects are categorized for evaluation purposes into two types:

(a)	Reliability-driven projects; and

(b)	Economic-driven projects.

(2)	The differentiation between these two types of projects is based on whether a simultaneously-feasible, security-constrained generating unit commitment and dispatch is expected to be available for all hours of the planning horizon that can resolve the system reliability issue that the proposed project is intended to resolve.  If it is not possible to simulate a dispatch of the Generation Resources and ESRs such that all reliability criteria are met without the project, and the addition of the project allows the reliability criteria to be met, then the project is classified as a reliability-driven project.  If it is possible to simulate a dispatch of the Generation Resources and ESRs in such a way that all reliability criteria are met without the project, but the project may allow the reliability criteria to be met at a lower total cost, then the project is classified as an economic-driven project.  When performing a simulation of the generating unit commitment and dispatch, only contingencies and limits that would be considered in the operations horizon shall be simulated.

5.3.5	ERCOT Quarterly Stability Assessment

(1)	ERCOT shall conduct a stability assessment every three months to assess the impact of planned large generators and Large Loads subject to the requirements of Section 9.2.1, Applicability of the Large Load Interconnection Study Process, connecting to the ERCOT System.

(a)	For large generators with planned Initial Synchronization in the period under study, the assessment shall derive the conditions to be studied with consideration given to the results of the FIS stability studies.

(b)	For new Large Loads and Load modifications subject to the requirements of Section 9.2.1, with planned Initial Energization in the period under study, the assessment shall derive the conditions to be studied from the most current Load Commissioning Plan and with consideration given to the results of the Large Load Interconnection Study (LLIS) stability studies performed according to Section 9.8.3.4, Legacy Dynamic and Transient Stability Analysis, or stability studies performed as part of the Batch Zero Interconnection Study as described in Section 9.3, Batch Zero Interconnection Study.

(c)	ERCOT may study conditions other than those identified in the FIS, LLIS, or Batch Zero Process stability studies.

(2)	Large generators that are not included in the assessment as described in this Section as result of the IE failing to meet the prerequisites by the deadlines as listed in the table below will not be eligible for Initial Synchronization during that three-month period.  Loads described in paragraph (1)(b) above that are not included in the assessment as a result of failing to meet the prerequisites by the deadlines as listed in the table below will not be eligible for Initial Energization during that three-month period.  The timeline for the quarterly stability assessment shall be in accordance with the following table:

| Generator Initial Synchronization or Large Load Initial Energization Date | Last Day for an IE, Resource Entity, or TSP to meet prerequisites as listed in paragraphs (4) and (5) below | Completion of Quarterly Stability Assessment |
| --- | --- | --- |
| Upcoming January, February, March | Prior August 1 | End of October |
| Upcoming April, May, June | Prior November 1 | End of January |
| Upcoming July, August, September | Prior February 1 | End of April |
| Upcoming October, November, December | Prior May 1 | End of July |

(3)	If the last day for an IE, Resource Entity, or TSP to meet prerequisites or if completion of the quarterly stability assessment as shown in the above table falls on a weekend or holiday, the deadline will extend to the next Business Day.

(4)	The following prerequisites shall be satisfied prior to a large generator being included in the quarterly stability assessment:

(a)	The generator has met the requirements of Section 6.9, Addition of Proposed Generation to the Planning Models.

(b)	The IE has provided all generator data in accordance with the Resource Registration Glossary, Planning Model column, including but not limited to steady state, system protection and stability models.

(i)	The IE shall submit the final dynamic data model at least 45 days prior to the quarterly stability assessment deadline described in paragraph (2) above.  If ERCOT is unable to complete its review prior to the quarterly stability assessment deadline, ERCOT shall not include the Generation Resource, ESR or Settlement Only Generator (SOG) in that quarterly stability assessment.

(ii)	Changes to the dynamic data model after the stability study is deemed complete may subject the Generation Resource, ESR, or SOG to modification of one or more FIS study elements as defined in paragraph (9) of Section 5.3.2.5, FIS Report and Follow-up.  If ERCOT and the lead TSP(s) determine that modifications to one or more FIS study elements are required, then ERCOT shall not include the Generation Resource, ESR, or SOG in a quarterly stability assessment until the revised FIS has been completed in accordance with paragraph (4)(c)(i) below.

(iii)	If an IE submitted a final dynamic data model at least 45 days prior to the quarterly stability assessment deadline but ERCOT determines that the Generation Resource, ESR, or SOG is ineligible to be included in a quarterly stability assessment pursuant to paragraphs (4)(b)(i) or (4)(b)(ii) above, ERCOT will send a notification to the IE.

(c)	The following elements must be complete:

(i)	Final FIS studies, which the TSP must have submitted via the online RIOO system at least 45 days prior to the quarterly stability assessment deadline;

(ii)	Reactive Power Study; and

(iii)	System improvements or mitigation plans that were identified in these studies as required to meet the operational standards established in the Protocols, Planning Guide, Nodal Operating Guides, and Other Binding Documents prior to synchronizing the generator.

(d)	The data used in the studies identified in paragraph (4)(c) above is consistent with data submitted by the IE as required by Section 6.9.

(5)	The following prerequisites must be satisfied prior to the inclusion of a new Large Load or Load modification subject to the requirements of Section 9.2.1 in the quarterly stability assessment:

(a)	The Large Load has met one of the following requirements:

(i)	For quarterly stability assessments with a prerequisite deadline of May 1, 2026 or earlier, the Large Load has met the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities; and

(ii)	For quarterly stability assessments with a prerequisite deadline of August 1, 2026, November 1, 2026, or February 1, 2027, the Large Load has met the requirements of paragraph (1) of Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in Batch Zero Interconnection Process; or

(iii)	For quarterly stability assessments with a prerequisite deadline of May 1, 2027 or later, the Large Load has met the requirements of paragraph (2) of Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment;

(b)	The Load Commissioning Plan has been updated to reflect the results of completed studies as required by paragraph (1) of Section 9.2.4, Load Commissioning Plan;

(c)	If applicable, the Interconnecting TSP has provided to ERCOT the dynamic load model it received from the Interconnecting Large Load Entity (ILLE) per paragraph (1) of Section 9.8.4.3, Legacy Dynamic and Transient Stability Analysis, and written affirmation that no changes to the project information have been communicated by the ILLE, per Section 9.2.3, Modification of Large Load Project Information, that would invalidate the model;

(d)	The following elements must be complete;

(i)	Reactive Power Study, if required according to Protocol Section 3.15, Voltage Support; and

(ii)	SSO Study, if required according to Protocol Section 3.22.1.4, Large Load Interconnection Assessment; and

(e)	The data used in the studies identified in paragraph (c) above is consistent with data used in the final LLIS studies approved per Section 9.9 or completed Batch Zero Interconnection Study as described in Section 9.4, as applicable.

(6)	At any time following the inclusion of a large generator or applicable Large Load in a stability assessment, but before the Initial Synchronization of the generator or Initial Energization of the Large Load, if ERCOT determines, in its sole discretion, that the generator or Large Load no longer meets the prerequisites described in paragraphs (4) or (5) above, or that an IE or ILLE has made a change to the design of the generator or Large Load that could have a material impact on ERCOT System stability, then ERCOT may refuse to allow Initial Synchronization of the generator or Initial Energization of the Large Load.  ERCOT shall include the generator or Large Load in the next quarterly stability assessment period that commences after identification of the material change or after the generator or Large Load meets the prerequisites specified in paragraphs (4) or (5) above, as applicable.  If ERCOT determines, in its sole discretion, that the change to the design of the generator or Large Load would not have a material impact on ERCOT System stability, then ERCOT may not refuse to allow Initial Synchronization of the generator or Initial Energization of the Large Load due to this change.

(7)	ERCOT shall post to the MIS Secure Area a report summarizing the results of the quarterly stability assessment within ten Business Days of completion.

### 6.6.1	Modeling of Large Loads Not Co-Located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	The Interconnecting Transmission Service Provider (TSP) shall not add a new Large Load or Load modification subject to the requirements of Section 9.2.1, Applicability of the Large Load Interconnection Study Process, to the Network Operations Model until the Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment.

### 6.6.2	Modeling of Large Loads Co-Located with an Existing Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	The addition of a new Large Load to an existing Generation Resource, ESR, or SOG, or the modification of an existing Load at the Generation Resource, ESR, or SOG, subject to the requirements of Section 9.2.1, Applicability of the Large Load Interconnection Study Process, is considered a material modification of the Resource Registration as described in paragraph (8) of Section 6.8.2, Resource Registration Process.  The Resource Entity shall update the Resource Registration data to reflect the new or increased Load.

(2)	The Resource Entity shall not update the Resource Registration data to reflect the new or increased Load until the Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment.

### 6.6.3	Modeling of Large Loads Co-Located with a Proposed Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	A new Large Load co-located with a proposed Generation Resource, ESR, or SOG shall be included in the data provided by the Interconnecting Entity (IE) or Resource Entity during the Resource Registration process.

(2)	The Large Load shall not be included in the Network Operations Model until the following requirements have been satisfied:

(a)	The Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment

; and

(b)	All applicable requirements of Section 6.9, Addition of Proposed Generation to the Planning Models, have been completed.

# 9	LARGE LOAD Interconnection or Modification

9.1	Introduction

(1)	This Section defines the requirements and processes used to facilitate new or modified Large Load interconnections with the ERCOT System. It documents the transition from a process that relied on individual Large Load interconnection studies to a new process referred to as the Batch Zero Process. The Batch Zero Process consists of a Batch Zero Interconnection Study and a Batch Zero Refinement Study.  The requirements are designed to:

(a)	Facilitate studies to identify potential system limitations and determine, to the extent feasible, facilities needed to interconnect a new Large Load to or modify an existing Large Load on the ERCOT network;

(b)	Facilitate orderly and organized Large Load interconnections, while allowing ERCOT to determine whether the interconnection of the proposed Large Load would comply with North American Electric Reliability Corporation (NERC) Reliability Standards, ERCOT Protocols, ERCOT Planning and Operating Guides, Transmission Service Provider (TSP) criteria, and any Applicable Legal Authority (ALA);

(c)	Specify the communications required between Interconnecting Large Load Entities (ILLEs), TSPs, Distribution Service Providers (DSPs), Resource Entities, Interconnecting Entities (IEs), and ERCOT;

(d)	Provide the best information on future Large Load additions for use in identifying, forecasting, and analyzing short- and long-range ERCOT capabilities, demands, and reserves; and

(e)	Provide ERCOT accurate data about a Large Load subject to the provisions detailed in Section 9.2.1, Applicability of the Batch Zero Process, to ensure that ERCOT and stakeholders have the information necessary for planning purposes.

(2)	Submission of all project data, and other communications described in this Section shall be in the manner and format prescribed by ERCOT.  ERCOT shall publicly post the format of such submissions on the ERCOT website.

(3)	ERCOT shall manage an email list that includes Transmission and/or Distribution Owner Load Interconnection to facilitate communication of confidential Large Load-related information among TDSPs and ERCOT.  Membership to this email list will be limited to ERCOT and appropriate TDSP personnel.

### 9.2.1	Applicability of the Batch Zero Process

(1)	Any request to interconnect or modify a Load Facility that meets one or more of the following criteria shall be subject to an ERCOT interconnection process:

(a)	A new Large Load;

(b)	A modification of any existing Load Facility that increases the aggregate peak Demand of the Facility by 75 MW or more; or

(c)	A modification of an existing Large Load that changes or adds a Point of Interconnection (POI) or Service Delivery Point to a different electrical bus on a different electrical circuit.

(2)	ERCOT shall not evaluate Large Load interconnection requests meeting the requirements of paragraph (1) above according to the legacy Large Load Interconnection Study (LLIS) process defined in Sections 9.8-9.10 of this Planning Guide.

(3)	ERCOT shall evaluate Large Load interconnection requests meeting the eligibility criteria in Sections 9.2.1.1 or 9.2.1.2 according to the Batch Zero Process defined in Sections 9.2-9.6.

(4)	Large Loads that do not meet the eligibility criteria in Sections 9.2.1.1 or 9.2.1.2 shall be ineligible to receive approval for Initial Energization until evaluated through a future interconnection study process.

### 9.2.1.1	Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process

(1)	A Large Load that meets one of the following requirements on or before July 10, 2026, will be modeled in the Batch Zero Process as base load according to paragraph (2) below and its Demand is not subject to further evaluation.

(a)	A Large Load that achieved Initial Energization before March 25, 2022;

(b)	A Large Load that achieved Initial Energization between March 25, 2022, and July 10, 2026;

(c)	A Large Load that met the qualification requirements for inclusion in the quarterly stability assessment or was included in an interim voltage-ride-through assessment on or before May 1, 2026, and that meets both of the following criteria:

(i)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has attested to ERCOT that the DSP or TSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance so the equipment can be installed by the requested Initial Energization date or December 31, 2026, whichever is earlier; and

(ii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence to support the attestation;

(d)	A Large Load with a requested Initial Energization date on or before December 31, 2027, that has not achieved Initial Energization as of July 10, 2026, and that meets all the following requirements:

(i)	ERCOT has determined the Large Load has a complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads;

(ii)	On or before July 24, 2026, the Interconnecting DSP has submitted to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP that the ILLE has executed an interconnection agreement that meets the requirements defined in Section 9.7.2, Definition of an Interconnection Agreement;

(iii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has attested to ERCOT that the DSP or TSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance of the requested Initial Energization date so the equipment can be installed by the ILLE’s requested Initial Energization date;

(iv)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence to support the attestation; and

(v)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested and provided evidence to the DSP or TSP that it has purchased all necessary ILLE-owned high-voltage transformers and circuit breakers and will take delivery sufficiently in advance of its requested Initial Energization date so the equipment can be installed by the ILLE’s requested Initial Energization date; or

(e)	A Large Load with a requested Initial Energization date on or after January 1, 2028 and that meets all of the following requirements:

(i)	ERCOT has determined the Large Load has a complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads; and

(ii)	On or before July 24, 2026, the Interconnecting DSP has submitted to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP that the ILLE has executed an interconnection agreement that meets the requirements defined in Section 9.7.2, Definition of an Interconnection Agreement.

(2)	ERCOT shall model Large Loads meeting the requirements of paragraph (1) above in Batch Zero as follows:

(a)	A Large Load meeting the requirements of paragraph (1)(a) shall be modeled at the Large Load’s level of peak Demand indicated in the most recent Load Commissioning Plan (LCP) provided to ERCOT on or before July 24, 2026.

(b)	A Large Load meeting the requirements of paragraph (1)(b) and (1)(c) shall be modeled at the Large Load’s level of peak Demand that is the lesser of:

(i)	The level of peak Demand indicated in the most recent Load Commissioning Plan (LCP) provided to ERCOT on or before July 24, 2026; or

(ii)	The level of peak Demand indicated in the most recent Load Commissioning Plan (LCP), if applicable, provided to ERCOT on or before July 24, 2026.

(c)	A Large Load meeting the requirements of paragraphs (1)(d) or (1)(e) shall be modeled at the level of peak Demand that is the lesser of:

(i)	The level of peak Demand that can be served reliably as indicated in the Large Load’s complete and valid interconnection studies, as described in Section 9.2.1.4, or

(ii)	The level of peak Demand specified in the Large Load’s executed interconnection agreement that meets the requirements defined in Section 9.7.2, Definition of an Interconnection Agreement.

(d)	A Large Load that qualifies for inclusion as Base Load under this Section 9.2.1.1 shall be deemed to have satisfied all financial commitment requirements applicable to Batch Zero participation, including any requirements under Sections 9.7.1 and 9.7.2, without any requirement to execute a new or amended Interconnection Agreement, post additional financial security, or pay any interconnection fee under Section 9.7.2. The Large Load’s existing executed Interconnection Agreement shall be treated as satisfying the commitment gate requirement under Section 9.4. ERCOT shall communicate Base Load classification in writing to the applicable Interconnecting DSP and Interconnecting TSP on a rolling basis.

### 9.2.1.2	Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero

(1)	A Large Load that meets one of the requirements described in this paragraph shall be included in Batch Zero as load subject to reliability assessment and allocation.

(a)	A Large Load with a requested Initial Energization date on or before December 31, 2027, that has not achieved Initial Energization as of July 10, 2026, does not meet the requirements documented in paragraphs (1)(d)(iii) through (1)(d)(v) of Section 9.2.1.1, Eligibility Criteria for Inclusion as Base Load not Subject to Additional Study in Batch Zero, and the Interconnecting DSP has submitted to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP that the ILLE has executed an intermediate agreement that meets the requirements defined in Section 9.7.1, Definition of an Intermediate Agreement; or

(b)	A Large Load with a requested Initial Energization date on or after January 1, 2028, that meets all the following requirements:

(i)	The Interconnecting DSP has submitted to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP that the ILLE has executed an intermediate agreement that meets the requirements defined in Section 9.7.1, Definition of an Intermediate Agreement; and

(ii)	ERCOT has determined the Large Load meets one of the following:

(A)	The Large Load was included in the list established in paragraph (3) of Section 9.2.1.4, Evaluation of Existing Studies for Large Loads, but was determined to have invalid existing studies according to the methodology established in paragraphs (3)(d) and (3)(e) of that Section; or

(B)	The Large Load has received ERCOT approval of a steady state or stability study as described in Section 9.8, Legacy Interconnection Study Procedures for Large Loads and Section 9.9, Legacy LLIS Report and Follow-up.

(2)	ERCOT shall model a Large Load meeting the requirements of paragraph (1) above according to the values in the most recent Load Commissioning Plan (LCP) provided by the Interconnecting TSP or Interconnecting DSP on or before July 24, 2026.  The LCP shall reflect an Initial Energization date of January 1, 2028, or later.

(3)	A Large Load that has executed a binding Interconnection Agreement with its Interconnecting TDSP, and has posted CIAC and financial security under that agreement prior to the effective date of this PGRR, shall be deemed to have satisfied the financial commitment eligibility criteria for inclusion as a Large Load to be Studied under this Section 9.2.1.2 without any requirement to execute a new Intermediate Agreement under Section 9.7.1 or post additional security. The Interconnecting TDSP shall confirm to ERCOT, by attestation submitted no later than July 24, 2026, that the applicable ILLE has executed an Interconnection Agreement and posted the required CIAC and financial security under that agreement. A Large Load that fails to satisfy the requirements of this paragraph (3) but otherwise meets the eligibility criteria of paragraph (1) must satisfy the Intermediate Agreement requirements of Section 9.7.1 by July 10, 2026 as a condition of inclusion.

### 9.2.1.3	Load not Included in Batch Zero

(1)	ERCOT shall not include in Batch Zero any Large Load that does not meet requirements described in Sections 9.2.1.1 or 9.2.1.2.

(2)	ERCOT shall not include any Large Load that otherwise meets the requirements described Sections 9.2.1.1 or 9.2.1.2 if the Interconnecting TSP or Interconnecting DSP fails to provide to ERCOT all information required by Section 9.2.2 on or before July 24, 2026.

### 9.2.1.4	Evaluation of Existing Studies for Large Loads

(1)	ERCOT shall use the methodology described in this Section to assess the completeness and validity of previous studies as prescribed in Section 9.2.1.1, Eligibility Criteria for Inclusion as Base Load not Subject to Additional Study in Batch Zero and Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero.

(2)	During its review, ERCOT may consult with the Interconnecting DSP and Interconnecting TSP.  However, ERCOT shall have sole authority to determine the completeness and validity of previous studies.

(3)	ERCOT shall consider previous studies for Large Loads that have not achieved Initial Energization by July 10, 2026, to be fully complete and valid without additional review if they meet one of the following criteria:

(a)	The Large Load was included in one or more studies submitted to the Regional Planning Group (RPG) before December 15, 2025, that Load contributed to establishing the reliability need for the RPG project, and the proposed project received RPG acceptance or ERCOT endorsement as described in Protocol Section 3.11.4.9, Regional Planning Group Acceptance and ERCOT Endorsement, on or before June 1, 2026; or

(b)	The Large Load met the requirements of Section 9.9, Legacy LLIS Report and Follow-Up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities, on or before June 1, 2026.

(4)	ERCOT will consider previous studies for Large Loads that have not achieved Initial Energization by July 10, 2026 and that do not have studies meeting the criteria in paragraph (3) above to be fully complete and valid according to the following process:

(a)	ERCOT shall identify all Large Loads that meet all of the following criteria:

(i)	The Interconnecting DSP or Interconnecting TSP has, by July 24, 2026, determined the dynamic data submitted by the ILLE per paragraph (3) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process, is not expected to adversely impact the results from the previous stability study; and

(ii)	The Large Load meets either of the following conditions:

(A)	The Large Load was included in one or more studies submitted to the Regional Planning Group (RPG) before December 15, 2025, that Load contributed to establishing the reliability need for the RPG project, and the proposed project received RPG acceptance or ERCOT endorsement as described in Protocol Section 3.11.4.9, Regional Planning Group Acceptance and ERCOT Endorsement, on or before July 10, 2026; or

(B)	The Large Load met the requirements of Section 9.9, Legacy LLIS Report and Follow-Up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities, on or before July 10, 2026.

(b)	ERCOT shall create a list of all Large Loads meeting the criteria in paragraph (4)(a)(ii) above. ERCOT shall order the list according to the date each Large Load met the applicable criteria in paragraph (4)(a)(ii). The Large Load with the oldest date shall be given first position, with subsequent loads following in order of date the criteria in paragraph (4)(a)(ii) were met.

(i)	In the event a Large Load meets both the criteria in paragraph (4)(a)(ii)(A) and (4)(a)(ii)(B) or in the event the Large Load meets the criteria in paragraph (4)(a)(ii)(A) multiple times, ERCOT shall use the date that gives the Large Load the highest position in the list.

(c)	In the event two Large Loads met the criteria documented in paragraph (4)(a)(ii) on the same date, ERCOT shall use the following methodology to determine placement on the list:

(i)	If both Large Loads were included in the same RPG study, ERCOT shall give them equal placement on the list;

(ii)	If each Large Load is from a separate RPG study, the Load with the earlier RPG study submission date will receive priority;

(iii)	If one Large Load met the criteria described in paragraph (4)(a)(ii)(A) and the other met the criteria described in paragraph (4)(a)(ii)(B), the Load meeting the criteria of paragraph (4)(a)(ii)(A) will receive priority regardless of submission date; and

(iv)	If both Large Loads met the criteria described in paragraph (4)(a)(ii)(B), the Load with the earlier submission date of a TSP study to ERCOT will receive priority;

(d)	The Large Load(s) in the first position on the list shall be considered to have valid existing studies.

(e)	ERCOT shall evaluate each subsequent Large Load on the list in the order established in paragraphs (4)(b) and (4)(c). For each Large Load or set of Large Loads evaluated, ERCOT shall consider the existing studies valid if, in ERCOT’s sole discretion, each Large Load on the list already determined to have valid existing studies is:

(i)	Located outside of the study area of the Large Load under review; or

(ii)	Located within the study area and included in the existing studies for the Large Load under review.

### 9.2.2	Submission of Large Load Information for Batch Zero Process

(1)	For any Load request meeting one or more criteria defined in paragraph (1) of Section 9.2.1, Applicability of Batch Zero Process, the following actions shall be completed prior to the initiation of the Batch Zero Interconnection Study described in Section 9.3, Batch Zero Interconnection Study.

(a)	Submission of all information, including but not limited to, data required by the Interconnecting Distribution Service Provider (DSP), the Interconnecting Transmission Service Provider (TSP), and ERCOT to perform steady state, short circuit, dynamic and transient stability analyses and any other studies the Interconnecting TSP or ERCOT deems necessary to reliably interconnect the Load;

(b)	Submission of a preliminary Load Commissioning Plan (LCP) that fully reflects the proposed project schedule; and

(c)	Written acknowledgement from the Interconnecting Large Load Entity (ILLE) of its obligations to notify the Interconnecting DSP and Interconnecting TSP of changes to the Large Load project information or to the load composition, technology, or parameters, as described in Section 9.2.3, Modification of Large Load Project Information, during the interconnection process.

[PGRR115: Insert paragraph (d) below upon system implementation of NPRR1234:] (d) Payment of the LLIS Application Fee to ERCOT as described in paragraph (3).

(2)	The Interconnecting DSP or Interconnecting TSP shall submit the information described in paragraphs (1)(a) through (1)(c) above on behalf of the ILLE on or before July 24, 2026.

(3)	By July 10, 2026, the ILLE must provide to ERCOT and the Interconnecting DSP or Interconnecting TSP dynamic data including the necessary models, parameters, and supporting documentation required for accurate representation of the Large Load. The data shall be compatible with the current version of the planning and operations model software, as described in the Dynamic Working Group Procedure Manual. If a dynamic stability study on the Large Load has previously been performed, Interconnecting DSP or Interconnecting TSP must also provide to ERCOT by July 24, 2026, a written determination as to whether the dynamic data submitted by the ILLE is expected to adversely impact the results from the previous stability study.

[PGRR115: Insert paragraph (3) below upon system implementation of NPRR1234:] (4) The ILLE shall pay to ERCOT the LLIS Application Fee, as described in the ERCOT Fee Schedule prior to the commencement of the LLIS. The interconnecting TSP, Resource Entity, or Interconnecting Entity (IE) may choose to submit this fee to ERCOT on the behalf of the ILLE. Payment of the ERCOT LLIS Application Fee shall not affect the independent responsibility of the ILLE to pay for interconnection studies conducted by the interconnecting TSP or for any Distribution Service Provider (DSP) studies.

### 9.2.3	Modification of Large Load Information

(1)	The Interconnecting DSP or Interconnecting TSP shall update any project information submitted per paragraph (1) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process, within ten Business Days of being notified by the ILLE of a material change.

(2)	The ILLE shall notify the Interconnecting DSP or Interconnecting TSP if a change to the load composition, technology, or parameters occurs after the ILLE has provided the DSP or TSP with its initial dynamic data per paragraph (3) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process. The Interconnection DSP or Interconnecting TSP shall promptly provide the updated dynamic data to ERCOT.

### 9.2.4	Load Commissioning Plan

(1)	The Load Commissioning Plan (LCP) shall be maintained and updated by the Interconnecting DSP and Interconnecting TSP and ERCOT as prescribed in Section 9 of the Planning Guide using information provided by the ILLE.  The LCP must specify the load increments and timeline by which the ILLE intends to increase peak Demand.  The LCP shall reflect the most currently available information about the Large Load and ILLE and shall be updated upon receipt of updated project information from the ILLE and as otherwise described in this Section.

(2)	Upon the completion of the Batch Zero Interconnection Study, as described in Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment, the ERCOT shall update the preliminary LCP to reflect the amount of peak Demand that can be served reliably for each year of the Batch Zero Interconnection Study scope.

(3)	Upon the execution of interconnection agreements prescribed in Section 9.7.2, Definition of an Interconnection Agreement, the Interconnecting DSP or Interconnecting TSP shall update the LCP to reflect the executed interconnection agreement.

(4)	The Interconnecting DSP or Interconnecting TSP shall continue to maintain the LCP after Initial Energization until the Large Load reaches its full requested peak Demand, updating as needed to reflect changes in the Large Load construction and timelines.

### 9.2.5	 Required Interconnection Equipment

(1)	Each Service Delivery Point for a Large Load not co-located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) interconnected at transmission voltage to the ERCOT System must have a permanent configuration consisting of one or more breakers capable of interrupting fault current to isolate the Large Load from the ERCOT System without interrupting flow on the associated transmission lines.  The breakers shall be under the remote control of the applicable Transmission Operator (TO).

(2)	Each Large Load co-located with a Generation Resource, ESR, or SOG interconnected at transmission voltage to the ERCOT System must have a permanent configuration consisting of one or more breakers capable of interrupting fault current to isolate the Large Load from the ERCOT System without isolating any of the co-located generators.  The breakers shall be remotely controllable at the direction of the applicable Qualified Scheduling Entity (QSE).

(3)	Large Loads submitted under the legacy Large Load Interconnection Study (LLIS) process described in Sections 9.8-9.10 with an initial LLIS submission date on or after June 1, 2025, and Large Loads meeting requirements, described in Sections 9.2.1.1 and 9.2.1.2, for inclusion in the Batch Zero Interconnection Study shall not have an interconnection configuration such that any category P1 or P7 event described in the North American Reliability Corporation (NERC) Reliability Standard addressing transmission planning performance requirements results in more than 1,000 MW of consequential Load loss.

(a)	All Loads co-located with a Generation Resource as described in Protocol Section 10.3.2.3, Generation Netting for ERCOT-Polled Settlement Meters, shall be subject to the requirements of this paragraph.

(4)	Large Loads submitted under the legacy Large Load Interconnection Study (LLIS) process described in Sections 9.8-9.10 with an initial LLIS submission date before June 1, 2025, shall comply with the requirements of paragraph (3) of this Section if, on or after June 1, 2025, a modification to the Large Load subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, is made.

9.2.6	Batch Zero Financial Commitment Framework

(1)	The financial commitment requirements applicable to Batch Zero participation are established in this Section 9.2.6 independently of any requirements adopted or to be adopted in PUCT Project No. 58481.  Nothing in this Section 9.2.6 shall be construed to require any Large Load to satisfy obligations under Project No. 58481 as a condition of Batch Zero eligibility or advancement. To the extent the final order in Project No. 58481 establishes standards that differ from those reflected herein, ERCOT shall address any necessary alignment through a targeted revision request following completion of the Batch Zero process.

(a)	Tier 1 — Base Load. A Large Load classified as Base Load under Section 9.2.1.1 shall have no financial commitment obligation under this Section 9.2.6. Its existing executed Interconnection Agreement shall constitute full satisfaction of all Batch Zero financial commitment criteria.

(b)	Tier 2 — Studied Load with Prior IA and Security. A Large Load eligible for inclusion under Section 9.2.1.2 that has, prior to the effective date of this PGRR, executed a binding Interconnection Agreement with its Interconnecting TDSP and posted CIAC and financial security under that agreement, shall have no additional financial commitment obligation under this Section 9.2.6. The TDSP attestation under Section 9.2.1.2(3) shall constitute full satisfaction of all Batch Zero financial commitment criteria for such load.

(c)	Tier 3 — Studied Load Without Prior IA or Security. A Large Load eligible for inclusion under Section 9.2.1.2 that has not previously executed a binding Interconnection Agreement or posted CIAC and financial security under any prior ERCOT or TDSP process must, by July 10, 2026:

(i)	Execute an Intermediate Agreement meeting the requirements of Section 9.7.1;

(ii)	Post financial security at the applicable $/MW rate; and

(iii)	Commit to CIAC obligations as reflected in the Intermediate Agreement. Such a load must execute a full Interconnection Agreement meeting Section 9.7.2 by the commitment gate deadline under Section 9.4 as a condition of retaining its MW allocation.

9.3	Batch Zero Interconnection Study

(1)	This Section establishes the procedures for conducting a Batch Zero Interconnection Study for new or modified Large Loads, as defined by Section 9.2.1, Applicability of the Batch Zero Process and Section 9.2.1.1, Inclusion Criteria for Batch Zero.

### 9.3.1	Batch Zero Process Overview and Timelines

(1)	The Batch Zero Interconnection Study consists of a singular, system-wide study covering steady-state analysis and stability screening analysis performed by ERCOT.

(2)	The Batch Zero Process shall be conducted according to the following timeline:

(a)	Interconnecting Distribution Service Providers (DSPs) and Interconnecting Transmission Service Providers (TSPs) must provide to ERCOT all information required by Section 9.2.2, Submission of Large Load Information for Batch Zero Process, on or before July 24, 2026.  ERCOT will notify each Interconnecting DSP and Interconnecting TSP of how each Large Load submitted under Section 9.2.2 is included and classified in the Batch Zero Interconnection Study according to the methodology defined in Section 9.2.1, Applicability of the Batch Zero Process, on or before August 7, 2026;

(b)	ERCOT shall provide the Batch Zero Interconnection Study report to all Interconnecting DSPs and Interconnecting TSPs or before January 29, 2027. ERCOT shall also communicate updated Load Commissioning Plans (LCPs) to Interconnecting Large Load Entities (ILLEs) reflecting Batch Zero MW allocations by this date;

(c)	Interconnecting DSPs shall provide to ERCOT a list of all Large Loads for which the ILLE has met the commitment requirements, as described in Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment, on or before March 1, 2027;

(d)	ERCOT shall complete the Batch Zero Refinement Study and provide a Batch Zero transmission plan to the Regional Planning Group (RPG), as described in Section 9.5, Batch Zero Study Refinement and Delivery of RPG Transmission Plan, on or before June 1, 2027.

(3)	The Interconnecting DSP or Interconnecting TSP must complete the short-circuit study prescribed in Section 9.5.2, System Protection (Short-Circuit) Analysis, and provide a study report to ERCOT 30 days prior to the date specified in paragraph (2)(d) above.

### 9.3.2	Batch Zero Interconnection Study Methodology

(1)	ERCOT shall establish a study scope and methodology to assess the steady state and stability impact of the Large Loads subject to assessment in accordance with paragraph (2) of Section 9.2.1.1 for years 2028 through 2032 and make them available in the Batch Zero report.

(2)	ERCOT shall post the initial Batch Zero Interconnection Study cases, the final Batch Zero Interconnection Study cases, the initial Batch Zero Refinement Study cases, and the final Batch Zero Refinement Study cases to be used in the study on the MIS Secure area once available.

(3)	For each Large Load subject to assessment in the Batch Zero Interconnection Study, ERCOT shall identify any planning criteria violations associated with the proposed addition in accordance with the study scope and shall endeavor to resolve any identified performance deficiencies by identifying Transmission Facility improvements for 2028 through 2032.  ERCOT shall consult with the applicable TSP(s) when identifying proposed Transmission Facility improvements but shall have sole authority to make the final determinations.  ERCOT shall also determine the amount of load that may be served reliably for each year within the study scope.  The amount of load that may be reliably served for 2033 will be set to the requested amount.

9.4	Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment

(1)	On or before the date specified in paragraph (2)(b) of Section 9.3.1, Batch Zero Overview and Timelines, ERCOT will provide to all Interconnecting Distribution Service Providers (DSPs) and Interconnecting Transmission Service Providers (TSPs):

(a)	A report summarizing the results of the Batch Zero Interconnection Study and proposed Transmission Facility improvements; and

(b)	An updated Load Commissioning Plan (LCP) for each Large Load that was assessed in the Batch Zero Interconnection Study that reflects the amount of peak Demand that can be served reliably for each year of the Batch Zero Interconnection Study scope; and

(c)	An estimate of the ILLE’s security requirements for each proposed Transmission Facility improvement identified in the ILLE’s LCP consistent with paragraph (1)(j) of Section 9.7.2, Definition of an Interconnection Agreement.

(2)	In order to accept the allocated MW amounts and schedule documented in the LCP, the ILLE must execute an interconnection agreement that meets the requirements in Section 9.7.2, Definition of an Interconnection Agreement.  The Interconnecting DSP must submit to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP confirming that the ILLE has executed the interconnection agreement on or before the date specified in paragraph (2)(c) of Section 9.3.1.

(3)	Any Large Load for which the Interconnecting DSP has not provided the notarized attestation mandated in paragraph (2) above by the date specified in paragraph (2)(c) of Section 9.3.1 is considered to have withdrawn from the Batch Zero Process and shall not be included in the Batch Zero Refinement Study described in Section 9.5, Batch Zero Refinement Study.  These Large Loads shall not be eligible for Initial Energization unless included in a future batch study.

(4)	Nothing in this Section shall be construed to prohibit an ILLE from negotiating and preparing an interconnection agreement described in Section 9.7.2 prior to receipt of the Batch Zero Interconnection Study results as described in paragraph (1) above.

9.5	Batch Zero Study Refinement and Delivery of Transmission Plan

(1)	The Batch Zero Refinement is an activity performed by ERCOT, in consultation with Transmission and/or Distribution Service Providers (TDSP), to update the Batch Zero Interconnection Study performed per Section 9.3, Batch Zero Study, to only include Large Loads that met the required commitment criteria per Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment. The goal of the Batch Zero Refinement Study is to determine which Transmission Facility improvements identified in the Batch Zero Interconnection Study are still needed, needed with modifications, or are no longer needed.

9.5.1	ERCOT Activities During the Batch Zero Refinement Period

(1)	After the deadline established in paragraph (2)(c) of Section 9.3.1, for the Interconnecting Distribution Service Provider (DSP) or Interconnecting Transmission Service Provider (TSP) to notify ERCOT which Large Loads included in the initial Batch Zero Interconnection Study have met the requirements for commitment, ERCOT will initiate the Batch Zero Refinement Study.

(2)	During the Batch Zero Refinement Study period ERCOT shall update its Batch Zero Interconnection Study to evaluate if the remaining Large Loads under assessment still result in planning criteria violations and if the Transmission Facility improvements for 2028-2032 identified in the Batch Zero Interconnection Study require modification.

(3)	ERCOT shall communicate with applicable TDSPs during ERCOT’s evaluation. Each TDSP shall promptly respond to all communications and provide recommendations to ERCOT as soon as practicable. Each TDSP shall provide any Transmission Facility improvement cost estimates within 15 Business Days of ERCOT’s request.

(4)	ERCOT shall prepare a final report for the Batch Zero Refinement Study described in this Section. The final report shall include a list of recommended Transmission Facility improvements, a description of the need for those Transmission Facility improvements, cost estimates for those Transmission Facility improvements, and any alternate improvements formally considered by ERCOT. ERCOT shall submit the final report for RPG Project Review by the date specified in paragraph (2)(d) of Section 9.3.1 unless the set of Transmission Facility improvements are classified as a Tier 4 project according to Nodal Protocol Section 3.11.4.3.  This final report shall serve as ERCOT’s independent review in accordance with Protocol Section 3.11.4.6 or Protocol Section 3.11.4.7, unless ERCOT decides to create an updated final report based on comments received during the RPG Project Review.

(5)	The Batch Zero Refinement Study described in this section shall not include an adjustment to the allocated MWs for any Large Loads included in the Batch Zero Interconnection Study for which the Large Load has met the required commitment criteria per Section 9.4.

9.5.2	System Protection (Short-Circuit) Analysis

(1)	The Interconnecting DSP or Interconnecting TSP shall perform a short-circuit analysis during the Batch Zero Refinement Study period.

(2)	The short-circuit study shall use the ERCOT base cases posted per paragraph (2) of Section 9.3.2, Batch Zero Interconnection Study Methodology, appropriate for the desired Initial Energization date and Load Commissioning Plan of the Load.

(3)	The Interconnecting DSP or Interconnecting TSP will determine the maximum available fault currents at the interconnection substation for determining switching device interrupting capabilities and protective relay settings.

(4)	The Interconnecting DSP or Interconnecting TSP must provide the short-circuit study report to ERCOT on or before the date prescribed in paragraph (3) of Section 9.3.1, Batch Zero Overview and Timelines.

9.6	Initial Energization and Continuing Operations for Large Loads

(1)	Each Large Load shall meet the conditions established by ERCOT before proceeding to Initial Energization.  These conditions may include, but are not limited to:

(a)	Inclusion of the Load in the Network Operations Model in accordance with Section 6.6, Modeling of Large Loads;

(b)	Verification that all required telemetry is operational and accurate;

(c)	Submission of the Large Load to ERCOT for inclusion in the ERCOT Quarterly Stability Assessment (QSA) process pursuant to Section 5.3.5, ERCOT Quarterly Stability Assessment.  Completion of any Subsynchronous Oscillation (SSO) studies required under Protocol Section 3.22.1.4, Large Load Interconnection Assessment, are not required prior to submission for or inclusion in the QSA process;

(d)	Completion and approval of any required SSO studies, SSO Mitigation plan, SSO Countermeasures, and SSO monitoring prior to Initial Energization, if required.  Completion of SSO studies, SSO Mitigation plan, SSO Countermeasures, and SSO monitoring shall not be required prior to initiation of or inclusion in the ERCOT Quarterly Stability Assessment process pursuant to Section 5.3.5; and

(e)	Submission of a current Load Commissioning Plan (LCP) meeting the requirements of Section 9.2.4, Load Commissioning Plan.

(2)	During continuing operations:

(a)	The Interconnecting DSP, Interconnecting TSP, or, if applicable, the Resource Entity shall notify ERCOT if it identifies that a Large Load has exceeded a limit on peak Demand established in the LCP.

(b)	Pursuant to Section 9.2.3, Modification of Large Load Information, if a Large Load modifies its facilities such that a previously provided dynamic load model is invalid, the Large Load shall notify and provide an updated model to the Interconnecting Distribution Service Provider (DSP) and Interconnecting Transmission Service Provider (TSP) that provides service to the Large Load.  The Interconnecting DSP or Interconnecting TSP shall subsequently provide this updated dynamic load model to ERCOT.

9.7	Definition of Required Commitment Criteria

9.7.1	Definition of an Intermediate Agreement

(1)	Except as provided in paragraph (2)(d) of Section 9.2.1.1 and paragraph (3) of Section 9.2.1.2, a Large Load that seeks inclusion in Batch Zero as a Large Load to be Studied and Allocated under Section 9.2.1.2 must, by the ILLE eligibility deadline of July 10, 2026, execute a binding Intermediate Agreement with its Interconnecting TDSP that satisfies the following requirements.

(a)	The Interconnecting Large Load Entity (ILLE) must demonstrate site control for the proposed load location through provision of one of the following property interests to the Interconnecting DSP or the Interconnecting TSP:

(i)	A signed and executed lease agreement for one or more parcels of land sufficient to accommodate the ILLE’s planned facilities at the proposed load location for a duration of at least five years from the date the ILLE is expected to reach the total non-coincident peak demand as stated in the agreement, referred to as contracted peak demand;

(ii)	A deed for one or more parcels of land sufficient to accommodate the ILLE’s planned facilities at the proposed load location; or

(iii)	A signed and executed agreement with an option to purchase or lease one or more parcels of land sufficient to accommodate the ILLE’s planned facilities at the proposed location;

(b)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE is pursuing a substantially similar interconnection request for electric service, the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request. A material change or delay includes a delay of one or more years to the Large Load’s projected date to realize its requested or contracted peak demand, a 20% or greater change in the requested or contracted peak demand, or a change in the location for the point of interconnection

(i)	An ILLE that is pursuing a substantially similar interconnection request for electric service the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request must disclose the following information to the Interconnecting DSP or the Interconnecting TSP:

(A)	The ERCOT-assigned serial number (i.e., the Large Load interconnection number) for the substantially similar interconnection request, as applicable;

(B)	The location, including the power region and, if in the ERCOT region, the load zone, of the substantially similar interconnection request;

(C)	The non-coincident peak demand of the substantially similar interconnection request;

(D)	The anticipated timing of energization of the substantially similar interconnection request; and

(E)	The Interconnecting DSP and, if different from the Interconnecting DSP, the Interconnecting TSP associated with the substantially similar interconnection request.

(ii)	An ILLE that discloses a substantially similar interconnection request under this subsection may anonymize competitively sensitive information in its disclosure to the Interconnecting DSP or the Interconnecting TSP.

(iii) 	An Interconnecting DSP and an Interconnecting TSP must not sell, share, or disclose information submitted to the Interconnecting DSP or the Interconnecting TSP under this subsection other than a disclosure to the Public Utility Commission of Texas (PUCT) or ERCOT.

(iv)	ERCOT may request and the ILLE must provide any competitively sensitive information ERCOT deems necessary to complete any analysis required as part of the interconnection process. ERCOT must treat disclosed competitively sensitive information as Protected Information under ERCOT Protocols.

(c)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and progress for site-related studies and engineering services required for Large Load development before energization (e.g., geotechnical survey, water, wastewater, or gas). The submission must be accompanied by an attestation by an officer or official with binding authority over the ILLE stating that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly;

(d)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and current progress for obtaining non-ministerial discretionary approvals from state and local regulatory authorities required for development before energization (e.g., water, air, or backup generation permits). The submission must be accompanied by an attestation by an officer or official with binding authority over the ILLE attesting that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly;

(e)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP the expected schedule, including the quarter and year, for phased energization of the contracted peak demand expressed in MW, power factor (PF), and megavolt ampere reactive (MVAr) units;

(f)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE plans to have on-site backup generating facilities. If the ILLE plans to have on site backup generating facilities, the ILLE must also disclose the following information:

(i)	The number of backup generating units;

(ii)	The nameplate capacity of each of the backup generating facilities;

(iii)	The fuel source and operational characteristics of each of the backup generating facilities, including any run hour limitations and any fuel storage limitations under the existing environmental permits; and

(iv)	How quickly each of the backup generating facilities can reach their full capacity to serve the load;

(g)	The ILLE must disclose how it plans to procure power and whether the ILLE has on-site generation that will provide power exclusively to the ILLE;

(h)	The ILLE must disclose whether it can be modeled as a Controllable Load Resource, as the term is defined in the ERCOT Protocols, in ERCOT’s Batch Zero Process;

(i)	Financial security is due at the time that the intermediate agreement is executed. The ILLE must post financial security with the Interconnecting DSP or the Interconnecting TSP in the amount of $50,000 per MW of the requested peak demand for new interconnection requests or of the incremental increase in the peak demand for expanded interconnection requests.

(i)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security:

(A)	Cash collateral;

(B)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating equivalent of BBB-/Baa3 or higher from Standard & Poor’s or Moody’s; or

(C)	A letter of credit issued by a major U.S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” by Standard & Poor’s or “A3” by Moody’s Investor Service.

(ii)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(iii)	Refund of financial security posted on a dollar per MW basis is subject to Section 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand.

(j)	An Interconnecting DSP or an Interconnecting TSP must not procure equipment or services before an ILLE posts financial security to the Interconnecting DSP or the Interconnecting TSP in an amount equal to the Interconnecting DSP and Interconnecting TSP's estimated costs for equipment with a lead time of at least six months and services necessary to interconnect the ILLE.

(i)	An ILLE may elect to amend its intermediate agreement with the Interconnecting DSP and the Interconnecting TSP to post financial security for significant equipment or services prior to executing an interconnection agreement.

(ii)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security for significant equipment or services:

- Cash collateral;

- Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating equivalent of BBB-/Baa3 or higher from Standard & Poor’s or Moody’s; or

- A letter of credit issued by a major U.S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” by Standard & Power’s or “A3” by Moody’s Investor Service.

(iii)	If the ILLE provides a corporate or parental guaranty under this subsection, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(iv) 	Refund of financial security posted for significant equipment or services is subject to Section 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand and Section 9.7.4, Terms for Refund of Financial Security for an ILLE that Energizes.

### 9.7.2	Definition of an Interconnection Agreement

(1)	An Interconnecting Large Load Entity (ILLE) must execute an interconnection agreement with the Interconnecting Distribution Service Provider (DSP) and, if different from the Interconnecting DSP, the Interconnecting Transmission Service Provider (TSP).  If the Interconnecting DSP and the Interconnecting TSP are different entities, the interconnection agreement must specifically identify each entity’s responsibilities under this Section 9.7.2, including which entity will accept financial security and contribution in aid of construction (CIAC) from the ILLE.  The interconnection agreement must meet the following requirements:

(a)	The ILLE must demonstrate site control for the load location through provision of one of the following property interests to the Interconnecting DSP or the Interconnecting TSP:

(i)	A signed and executed lease agreement for one or more parcels of land sufficient to accommodate the ILLE’s planned facilities at the proposed load location for a duration of at least five years from the date the ILLE is expected to reach the total non-coincident peak demand as stated in the agreement, referred to as contracted peak demand;

(ii)	A deed for one or more parcels of land sufficient to accommodate the ILLE’s planned facility at the proposed load location; or

(iii)	A signed and executed purchase and sales agreement;

(b)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE is pursuing a substantially similar interconnection request for electric service, the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request. A material change or delay includes a delay of one or more years to the Large Load’s projected date to realize its requested or contracted peak demand, a 20% or greater change in the requested or contracted peak demand, or a change in the location for the point of interconnection.

(i)	An ILLE that is pursuing a substantially similar interconnection request for electric service the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request must disclose the following information to the Interconnecting DSP or the Interconnecting TSP:

(A)	The ERCOT-assigned serial number (i.e., the Large Load Interconnection number) for the substantially similar interconnection request, as applicable;

(B)	The location, including the power region and, if in the ERCOT region, the load zone, of the substantially similar interconnection request;

(C)	The non-coincident peak demand of the substantially similar interconnection request;

(D)	The anticipated timing of energization of the substantially similar interconnection request; and

(E)	The Interconnecting DSP and, if different from the Interconnecting DSP, the Interconnecting TSP associated with the substantially similar interconnection request.

(ii)	An ILLE that discloses a substantially similar interconnection request under this subsection may anonymize competitively sensitive information in its disclosure to the Interconnecting DSP or the Interconnecting TSP.

(iii)	An Interconnecting DSP and an Interconnecting TSP must not sell, share, or disclose information submitted to the Interconnecting DSP or the Interconnecting TSP under this subsection other than a disclosure to the PUCT or ERCOT.

(iv)	ERCOT may request and the ILLE must provide any competitively sensitive information ERCOT deems necessary to complete any analysis required as part of the interconnection process. ERCOT must treat disclosed competitively sensitive information as Protected Information under ERCOT Protocols.

(c)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and progress for site-related studies and engineering services required for Large Load development before energization (e.g., geotechnical survey, water, wastewater, or gas). The submission must be accompanied by an attestation by an officer or official with binding authority over the ILLE stating that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly;

(d)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and current progress for obtaining non-ministerial discretionary approvals from state and local regulatory authorities required for development before energization (e.g., water, air, or backup generation permits). The submission must be accompanied by an attestation by an officer or official with binding authority over the ILLE attesting that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly;

(e)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP the expected schedule, including the quarter and year, for phased energization of the contracted peak demand expressed in MW, power factor (PF), and megavolt ampere reactive (MVAr) units;

(f)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE plans to have on-site backup generating facilities. If the ILLE plans to have on site backup generating facilities, the ILLE must also disclose the following information:

(i)	The number of backup generating units;

(ii)	The nameplate capacity of each of the backup generating facilities;

(iii) 	The fuel source and operational characteristics of each of the backup generating facilities, including any run hour limitations and any fuel storage limitations under the existing environmental permits; and

(iv)	How quickly each of the backup generating facilities can reach their full capacity to serve the load;

(g)	The ILLE must pay an interconnection fee in the amount of $50,000 per MW of contracted peak demand. The interconnection fee is non-refundable.

(i)	An Interconnecting DSP or an Interconnecting TSP must draw on any unused financial security that the ILLE posted under an intermediate agreement described in Section 9.7.1, Definition of Intermediate Agreement, to satisfy the interconnection fee.

(ii)	The interconnection fee must be paid to the Interconnecting TSP and applied by that TSP as an offset to the Interconnecting TSP’s rate base in the earlier of the Interconnecting TSP’s next interim rate proceeding or comprehensive rate proceeding.

(h)	The ILLE must post financial security for significant equipment or services not later than the date that the interconnection agreement is executed if the Interconnecting DSP or the Interconnecting TSP needs to procure significant equipment or services to interconnect the ILLE. An Interconnecting DSP and an Interconnecting TSP must not procure equipment or services before an ILLE posts financial security to the Interconnecting DSP or the Interconnecting TSP in an amount equal to the Interconnecting DSP and Interconnecting TSP’s estimated costs for equipment with a lead time of at least six months and services necessary to interconnect the ILLE.

(i)	After drawing down on financial security posted under an intermediate agreement described in Section 9.7.1, Definition of Intermediate Agreement, for payment of the interconnection fee, an Interconnecting DSP or an Interconnecting TSP must apply the balance of any unused financial security that the ILLE posted under an intermediate agreement described in Section 9.7.1, Definition of Intermediate Agreement, to satisfy the financial security for significant equipment or services under this subsection.

(ii)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security for significant equipment or services:

(A)	The cash collateral;

(B)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating equivalent of BBB-/Baa3 or higher from Standard & Poor’s or Moody’s; or

(C) 	A letter of credit issued by a major U. S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” by Standard & Poor’s or “A3” by Moody’s Investor Service.

(ii)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(iii)	Refund of financial security posted for significant equipment or services is subject to Section 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand and Section 9.7.4, Terms for Refund of Financial Security for an ILLE that Energizes.

(i)	The ILLE must pay all direct interconnection costs through CIAC, with no standard or other allowance offered to offset the ILLE’s CIAC payments.  The ILLE must pay CIAC not later than the date that the interconnection agreement is executed.  An Interconnecting DSP and Interconnecting TSP must not begin construction of facilities to interconnect an ILLE before an ILLE pays CIAC in an amount that is equal to the direct interconnection costs associated with the ILLE.

(i)	Direct interconnection costs include all costs associated with facilities built to interconnect the ILLE to the existing ERCOT system, including radial lines and substation upgrades necessary to interconnect the new ILLE. CIAC must be paid in the form of a direct cash payment.

(ii)	An Interconnecting DSP and an Interconnecting TSP must not seek to recover any large load-related direct interconnection costs, including any interconnection allowance for ILLEs, under any rates regulated by the PUCT.

(iii)	The CIAC must be trued-up to reflect the actual costs once the facilities are completed, and the ILLE may receive a credit or surcharge on their bill, as applicable, for the difference in actual costs relative to the estimate.

(j)	The ILLE must post financial security for system upgrades that are necessary to reliably serve the ILLE not later than the date that the interconnection agreement is executed.

(i)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security:

(A)	The cash collateral;

(B)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating equivalent of BBB-/Baa3 or higher from Standard & Poor’s or Moody’s; or

(C)	A letter of credit issued by a major U. S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” by Standard & Poor’s or “A3” by Moody’s Investor Service.

(ii)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(iii)	Refund of financial security posted for system upgrades is subject to Section 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand and Section 9.7.4, Terms for Refund of Financial Security for an ILLE that Energizes.

### 9.7.3	Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand

(1)	An ILLE may withdraw all or a portion of its requested peak demand or contracted peak demand for interconnection by submitting its request in writing to the Interconnecting DSP or the Interconnecting TSP.

(a)	Not later than 14 days after receipt of an ILLE’s notice to withdraw all or a portion of requested peak demand or contracted peak demand for interconnection, the Interconnecting DSP or the Interconnecting TSP must notify ERCOT via a method prescribed by ERCOT.

(b)	The Interconnecting DSP or the Interconnecting TSP must draw down on the ILLE’s financial security and apply the financial security to any outstanding amounts owed. Outstanding amounts owed include the following:

(i)	Costs incurred by the Interconnecting DSP or the Interconnecting TSP to fulfill the ILLE’s request for interconnection;

(ii)	Costs for equipment that the Interconnecting DSP or the Interconnecting TSP procured and that cannot be canceled with a full refund;

(iii)	Costs for construction that the Interconnecting DSP or the Interconnecting TSP started and that cannot be canceled with a full refund; and

(iv)	Costs for services that the Interconnecting DSP or the Interconnecting TSP initiated and that cannot be canceled with a full refund.

(c)	After applying the ILLE’s financial security to any outstanding amounts owed, the Interconnecting DSP or the Interconnecting TSP must refund 20% of the balance to the ILLE within 60 days.

(d)	After applying the financial security to any outstanding amounts owed and refunding 20% of the balance, the remaining 80% of the balance must be paid to the Interconnecting TSP and applied by that TSP as an offset to the Interconnecting TSP's rate base in the earlier of the Interconnecting TSP’s next interim rate proceeding or comprehensive rate proceeding.

(e)	CIAC is not refundable.

(f)	ERCOT must reallocate contracted peak demand that is withdrawn by an ILLE.

### 9.7.4	Terms for Refund of Financial Security for an ILLE that Energizes

(1)	An Interconnecting DSP or an Interconnecting TSP must draw down on the ILLE’s financial security and apply the financial security to any outstanding amounts owed for costs incurred by the Interconnecting DSP or the Interconnecting TSP to fulfill the ILLE’s request for interconnection of the contracted peak demand.

(a)	After applying financial security to any outstanding amounts owed, the Interconnecting DSP or the Interconnecting TSP must refund 20% of the remaining balance when the ILLE energizes and ratably as the ILLE meets the milestones identified in the ILLE’s schedule for phased energization of its contracted peak demand.

(b)	The Interconnecting DSP or the Interconnecting TSP must refund any remaining balance when the ILLE sustains operations for five years at the ILLE’s contracted peak demand.

9.8	Legacy Interconnection Study Procedures for Large Loads

(1)	This Section, previously known as Section 9.3, outlines the former procedures for conducting a Large Load Interconnection Study (LLIS) for new or modified Large Loads.  It has been replaced by the Batch Zero Process but has been retained here for reference.

### 9.8.1	Legacy Large Load Interconnection Study (LLIS)

(1)	A LLIS consists of the set of steady-state, stability, short-circuit and other relevant studies that are necessary to determine the reliability impact of a Large Load interconnection on affected Transmission Facilities and identify the Transmission Facilities that are needed to reliably interconnect the new or modified Large Load to the ERCOT System.

(2)	If an Interconnecting Entity (IE) or Resource Entity submits a large Generation Resource interconnection request, as defined in Section 5.3, Interconnection Study Procedures for Large Generators, that also includes a co-located Large Load, the Full Interconnection Study (FIS) may be used in place of a separate LLIS.  The FIS shall reflect the full requested Load amount and conform to all study requirements detailed in Sections 5.3 and 9.3, Interconnection Study Procedures for Large Loads.  For any deadlines or timelines set out in this section that conflict with the deadlines or timelines in Sections 5.2, General Provisions, and 5.3, the deadlines or timelines in Sections 5.2 and 5.3 shall govern.

(3)	During the LLIS, the interconnecting Transmission Service Provider (TSP) shall be the lead TSP unless otherwise designated by ERCOT during the study scoping process detailed in Section 9.8.2, Large Load Interconnection Study Scoping Process.

(4)	For an interconnection request involving a Large Load interconnecting at distribution voltage, the LLIS shall evaluate only the proposed Load’s transmission-level impacts, if any.  The affected Distribution Service Provider (DSP) shall provide the lead TSP with all information concerning the DSP's facilities needed to complete any required studies.

### 9.8.2	Legacy Large Load Interconnection Study Scoping Process

(1)	ERCOT will notify the interconnecting TSP after all requirements have been met.  Within ten Business Days of this notification, the lead TSP shall schedule a kick-off meeting with ERCOT and the certificated DSP to occur soon thereafter. If the proposed project is co-located with a Generation Resource, the kick-off meeting must also include the affected Resource Entity or IE.  The lead TSP shall invite the Interconnecting Large Load Entity (ILLE) to attend the kick-off meeting.  The ILLE may attend at its option.

(2)	ERCOT will notify all other TSPs of the LLIS request.  Each TSP may evaluate if it is directly affected by the interconnection request and determine if it should participate in the LLIS.  Examples of a directly affected TSP may include, but are not limited to, a TSP whose facilities are likely to experience changes in voltage or power flow because of the Load interconnection request.

(3)	Each directly affected TSP desiring to participate in the LLIS shall promptly notify the lead TSP and ERCOT and must provide a description of the expected effect of the Load interconnection on the TSP’s facilities in its notification.  The lead TSP shall include all directly affected TSP(s) in the LLIS kickoff meeting.

(4)	At the LLIS kickoff meeting, the lead TSP will present the proposed project and facilitate a general discussion of the preliminary study scope of work for the LLIS.

(5)	Any reactive studies required under Protocol Section 3.15, Voltage Support, or Subsynchronous Oscillation (SSO) studies required under Protocol Section 3.22.1.4, Large Load Interconnection Assessment, shall be scoped simultaneously with the LLIS but do not need to be included as part of the LLIS.  The Resource Entity responsible for the reactive study shall provide it to ERCOT directly.  SSO studies shall proceed concurrently with, and shall not be required to be completed prior to completion of, the ERCOT Quarterly Stability Assessment process pursuant to Section 5.3.5, ERCOT Quarterly Stability Assessment.  The Resource Entity or ILLE responsible for the SSO study shall provide it to ERCOT directly.

(6)	The lead TSP will develop a preliminary LLIS study scope within ten Business Days following the kickoff meeting.

(a)	The study scope must include all study elements required by Section 9.8.4, Large Load Interconnection Study Elements, unless ERCOT in collaboration with the TSP(s) determine that one or more studies are unnecessary.  If a study element is deemed unnecessary, the lead TSP shall provide a written technical justification for not performing the analysis in lieu of the study report.

(b)	The study scope shall specify the base cases, study assumptions, and scenarios that will be used in each LLIS element.  Any transmission facilities that will not be in service before Initial Energization of the proposed Load that may significantly impact the study results, as initially identified by the lead TSP during the project kickoff meeting, shall be documented in the study scope.  All study assumptions related to maintenance outage scenarios required under Section 4.1.1.8, Maintenance Outage Reliability Criteria, shall be explicitly identified in the study scope.

(c)	The study scope shall specify the involvement of any directly affected TSPs in the study process.  In some cases, it may be necessary for the ILLE to execute study agreements with multiple TSP(s).

(d)	The lead TSP may propose interconnection design alternatives during the scoping process.  Such alternative options shall be fully studied in all required LLIS study elements.

(7)	The lead TSP shall submit the preliminary study scope for review by ERCOT and all directly affected TSPs, including TSPs which may be directly affected due to proposed interconnection topology. Directly affected TSPs and ERCOT may provide comments on the preliminary study scope within ten Business Days of posting.

(8)	Upon closing of the comment period described in paragraph (7) above, the lead TSP shall, within ten Business Days, submit a final study scope that addresses submitted comments to the extent possible.  ERCOT in collaboration with the TSP(s) shall determine the study scope.

(9)	Within five Business Days of the lead TSP submitting the final study scope, ERCOT shall approve the final study scope or return the scope to the lead TSP with comments.  The lead TSP shall promptly address ERCOT comments and resubmit according to paragraph (8) above.

### 9.8.3	Legacy Large Load Interconnection Study Description and Methodology

(1)	The primary purpose of the LLIS is to determine whether the amount of Load being requested by the ILLE can be placed in service by the desired Initial Energization date while maintaining the reliability of the ERCOT System and ensuring compliance with all North American Reliability Corporation (NERC) Reliability Standards, Protocols, this Planning Guide, and the Operating Guides.  The LLIS will also identify any transmission improvements needed to serve the full requested Load amount, including individual load increments requested by the ILLE in the initial Load Commissioning Plan (LCP).

(2)	The LLIS consists of a series of distinct study elements.  The specific elements included in a particular LLIS will be stated in the LLIS scope.

(3)	Each proposed Large Load interconnection that requests more than one physical transmission interconnection will be studied as an individual study for each interconnection to be analyzed separately from all other such requests unless otherwise agreed by the TSP(s) in the interconnection study agreement.

(4)	The LLIS process includes developing and analyzing various computer model simulations of the existing and proposed ERCOT transmission system.  The results from these simulations will be utilized by the TSP(s) to determine the impact of the proposed interconnection.

(5)	The study shall include an analysis demonstrating the adequate reliability of any temporary interconnection configurations.

9.8.4	Legacy Large Load Interconnection Study Elements

### 9.8.4.1	Legacy Steady-State Analysis

(1)	The steady-state interconnection study base case shall be created from the most recently approved Steady State Working Group (SSWG) base case appropriate for the desired Initial Energization date of the Load.  The lead TSP shall remove from the study base case all Transmission Facilities it determines may significantly impact study results that will not be in service before Initial Energization of the proposed Load, as identified in the preliminary LLIS study scope.  The steady-state analysis shall include other relevant Large Loads and any transmission upgrades included in the LCPs for those Large Loads that have a complete LLIS per paragraph (6) of Section 9.9, LLIS Report and Follow-up, and that have met the requirements of Section 9.10, Interconnection Agreements and Responsibilities.  The lead TSP may include other transmission projects and Substantiated Load in the study base case.  All modifications to the SSWG base case made as part of the study assumptions shall be documented in the LLIS report.

(2)	The lead TSP shall perform contingency analyses as required by the NERC Reliability Standards, ERCOT Nodal Protocols, this Planning Guide, and the Operating Guides to identify any additional Facilities that may be necessary to ensure that results of the system performance conform to these standards.  The study shall identify any system limitations that would prevent the ILLE from achieving the requested load in the desired timeframe.  If the study identifies system limitations, the lead TSP shall identify potential transmission system improvements necessary to achieve the requested Load.  The results of this analysis shall be shared with TSP(s) that have Facilities identified with planning criteria violations, and those affected TSP(s) will be responsible for evaluating the impact of the Large Load and the validity of the anticipated violations.

(3)	Upon completion of the steady-state study as described in paragraph (2) above, the lead TSP shall identify any modifications to the levels of Demand and timeline specified in the ILLE’s initial LCP that are needed to account for all transmission upgrades required to support the full requested amount of Load.

### 9.8.4.2	Legacy System Protection (Short-Circuit) Analysis

(1)	The short-circuit study shall use the most recently approved System Protection Working Group (SPWG) base case appropriate for the desired Initial Energization date of the Load.  The initial transmission configuration of the study area shall correspond to the configuration used in the corresponding steady-state study to the extent practicable.

(2)	The lead TSP will determine the maximum available fault currents at the interconnection substation for determining switching device interrupting capabilities and protective relay settings.

### 9.8.4.3	Legacy Dynamic and Transient Stability Analysis

(1)	The lead TSP shall not initiate the stability study prior to receiving from the ILLE dynamic load modeling information sufficient to properly model the load in the stability studies.  The TSP shall check the dynamic load information according to the procedure specified in Section 3.4.4, Load Model Data, of the Dynamics Working Group Procedure Manual.

(2)	The stability study base case shall be created from the most recently approved Dynamics Working Group (DWG) base case appropriate for the desired Initial Energization date of the Load.  The initial transmission configuration of the study area shall be consistent with the configuration used in the corresponding steady-state study to the extent practicable.

(3)	All stability studies shall be performed in accordance with NERC Reliability Standards, Protocols, this Planning Guide, and the Operating Guides.  Transient stability studies will analyze the performance of the ERCOT System in terms of angular stability, voltage stability, and excessive frequency excursions.  Additional studies may include small signal stability or critical clearing time analyses.  Such studies should incorporate reasonable and conservative assumptions regarding impacted facility operating conditions.  ERCOT in collaboration with the TSP(s) shall determine the stability analysis to be performed.

(4)	The stability study portion of the LLIS shall document any identified instability.

(5)	If the lead TSP identifies instability (other than instability identified for extreme events) in the stability portion of the LLIS, the TSP shall investigate alternative solutions, including transmission improvements, to mitigate the instability.  The lead TSP shall identify any modifications to the levels of Demand and the timeline specified in the ILLE’s initial LCP that are needed to account for all transmission upgrades required to support the full requested amount of Load.  The TSP shall implement any mitigation measure that may be needed to address a stability risk before the Initial Energization of the Large Load in accordance with Protocol Section 3.11.4, Regional Planning Group Project Review Process.

9.9	Legacy LLIS Report and Follow-up

(1)	This Section, previously known as Section 9.4, outlines the former procedures for informing an Interconnecting Large Load Customer (ILLE) the results of its Large Load Interconnection Study (LLIS).  It has been replaced by the Batch Zero Process but has been retained here for reference.

(2)	For each of the LLIS study elements, the lead Transmission Service Provider (TSP) shall submit a preliminary study report to ERCOT and other directly affected TSPs.  The report shall include a description of the study methodology and assumptions, findings, and recommendations.  The report shall also identify any changes to the Interconnecting ILLE’s Load Commissioning Plan (LCP) to allow for transmission upgrades in accordance with the criteria in Section 9.8.4, Large Load Interconnection Study Elements.  The lead TSP may include additional information in the study report and may combine multiple LLIS study elements into a single report.

(3)	ERCOT shall review the preliminary study report within ten Business Days and provide to the lead TSP any questions, comments, and proposed revisions necessary to ensure the report complies with the requirements in Section 9.8, Interconnection Study Procedures for Large Loads.  ERCOT may extend this review period by an additional 20 Business Days and shall notify in writing the lead and directly affected TSPs of the extension.  Directly affected TSPs may also provide questions, comments, and proposed revisions during this review period.  All comments from ERCOT and directly affected TSPs shall be provided to the lead TSP in writing.

(4)	If, after considering the responses received from ERCOT and directly affected TSPs, ERCOT in collaboration with the lead TSP determines if an additional study is required, the lead TSP shall promptly perform the additional study and submit an updated preliminary study report for review as described in paragraph (2) above.

(5)	If no additional study is required as described in paragraph (4) above, the lead TSP shall prepare a final LLIS study report that incorporates all relevant feedback received in paragraph (2) above within ten Business Days.

(6)	When complete, the lead TSP shall provide the final report for the LLIS study element(s) to ERCOT and the directly affected TSPs only.

(7)	The LLIS is deemed complete when the final report has been provided for all LLIS study elements.  Within ten Business Days following the completion of the LLIS, ERCOT shall:

(a)	Determine whether system upgrades recommended to support the full requested Load amount specified in the initial LCP are sufficient based on the report in paragraph (6) above;

(b)	Grant conditional approval for the interconnection of Load in accordance with the schedule in the final LCP, as may be revised by the TSP, as the necessary transmission upgrades identified in the LCP become operational, if ERCOT has determined pursuant to paragraph (a) above that the system upgrades recommended in the LLIS are sufficient to address the reliability risks associated with the proposed load additions;

(i)	For transmission upgrades that are subject to Regional Planning Group (RPG) review as described in Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT shall grant conditional approval if it determines that a project with an equivalent impact on the ability to serve the requested Load has become operational; and

(c)	Communicate the completion of the LLIS and the resulting LCP to the lead TSP and directly affected TSPs.

(7)	The lead TSP may provide a redacted copy of the final report for each LLIS study element to the ILLE upon request.  The redacted report(s) shall conform with Protocol Section 1.3, Confidentiality.

(8)	If a material change that impacts one or more LLIS study assumptions occurs before the requirements of Section 9.10, Interconnection Agreements and Responsibilities, have been met, ERCOT or the lead TSP may require one or more LLIS study elements be updated.  ERCOT in collaboration with the lead TSP shall have discretion to determine if a change impacts any LLIS study assumptions and to require a modification of the study or a restudy be performed.  Any modification of the study report shall be treated as a preliminary study and reviewed according to paragraph (2) above.

(9)	If the requirements of Section 9.10, have not been satisfied within 180 days after the communication of the completion of the LLIS by ERCOT as described in paragraph (7) above, ERCOT may notify the lead TSP that the project is subject to cancellation.  Upon receipt of this notification, the lead TSP may submit a project status update to ERCOT that includes a request for an extension and provides an opinion on whether any of the completed LLIS elements require restudy.  If no such project status update is received within 30 days from the date the notice is issued, ERCOT may consider the project canceled.

(10)	If the Large Load has not met the requirements for Initial Energization as described in paragraph (1) of Section 9.6, Initial Energization and Continuing Operations for Large Loads, within 365 days after the Initial Energization date identified in the LLIS study report, the lead TSP shall provide an opinion to ERCOT on whether any of the completed LLIS elements require restudy.  ERCOT may require one or more LLIS study elements be updated prior to approval of Initial Energization.

9.10	Legacy Interconnection Agreements and Responsibilities

(1)	This Section, previously known as Section 9.5, outlines the former requirements an Interconnecting Large Load Entity must meet prior to Initial Energization.  It has been replaced by the Batch Zero Process but has been retained here for reference.

9.10.1	Legacy Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility

(1)	For a Large Load not co-located with a Generation Resource Facility, ERCOT shall not allow Initial Energization prior to receiving one of the following:

(a)	Confirmation from the interconnecting Transmission Service Provider (TSP) that:

(i)	All required interconnection agreements or equivalent service extension agreements with the Interconnecting Large Load Entity (ILLE) and, if applicable, directly affected TSP(s) have been executed;

(ii)	The interconnecting TSP has received written acknowledgement from the ILLE of the ILLE’s obligations to:

(A)	Notify the interconnecting TSP of changes to the Large Load project information or to the load composition, technology, or parameters, as described in Section 9.2.3, Modification of Large Load Project Information; and

(B)	Maintain Load consumption at or below the level(s) of peak Demand established in the Load Commissioning Plan (LCP);

(iii)	The interconnecting TSP has received notice to proceed with the construction of all required interconnection Facilities; and

(iv)	The interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security, applicable payments, and/or other agreements required to fund all required interconnection Facilities; or

(b)	A letter from a duly authorized person from a Municipally Owned Utility (MOU) or Electric Cooperative (EC) confirming its intent to construct and operate applicable Large Load and interconnect such Large Load to its transmission system.

9.10.2	Legacy Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities

(1)	For a Large Load co-located with a Generation Resource Facility, ERCOT shall not allow Initial Energization prior to receiving one of the following:

(a)	Confirmation from the interconnecting TSP that:

(i)	All required interconnection agreements and/or equivalent service extension or other agreements with the Resource Entity, Interconnecting Entity (IE), and ILLE have been executed;

(A)	If the required agreements include a new Standard Generation Interconnection Agreement (SGIA) or an amendment to an existing SGIA, a copy of this agreement shall be provided to ERCOT once executed, per Section 5.2.8.1, Standard Generation Interconnection Agreement for Transmission-Connected Generators; or

(B)	If no new or amended agreements are required, the interconnecting TSP shall so notify ERCOT and state affirmatively it agrees to energize the new Load per the approved LLIS studies;

(ii)	The interconnecting TSP has received written acknowledgement from either the ILLE, or the Resource Entity on behalf of the ILLE, of the obligations to:

(A)	Notify the interconnecting TSP of changes to the Large Load project information or to the load composition, technology, or parameters, as described in Section 9.2.3, Modification of Large Load Project Information; and

(B)	Maintain Load consumption at or below the level(s) of peak Demand established in the LCP; and

(iii)	The interconnecting TSP has received notice to proceed with the construction of all required interconnection Facilities; and

(iv)	The interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security required, applicable payments, and/or other agreements to fund all required interconnection Facilities; or

(b)	A letter from a duly authorized person from a MOU or EC confirming its intent to construct and operate applicable Large Load and interconnect such Large Load to its transmission system.

The amendments proposed below implement the three-tier financial commitment framework described above. The operative changes are: (1) a new provision in Section 9.2.1.1 confirming that Base Loads' existing executed Interconnection Agreements fully satisfy all Batch Zero financial commitment requirements; (2) a new provision in Section 9.2.1.2 recognizing prior CIAC and security postings as satisfying Batch Zero financial commitment criteria for Tier 2 loads; (3) a revised Section 9.7.1 clarifying that Intermediate Agreement and security requirements apply only to Tier 3 loads; and (4) a new standalone section establishing the three-tier framework explicitly and independently of Project No. 58481.

## Section 9.2.1.1 — Eligibility Criteria for Inclusion as Base Load

Proposed Addition — New § 9.2.1.1(f):

(f) A Large Load that qualifies for inclusion as Base Load under this Section 9.2.1.1 shall be deemed to have satisfied all financial commitment requirements applicable to Batch Zero participation, including any requirements under Sections 9.7.1 and 9.7.2, without any requirement to execute a new or amended Interconnection Agreement, post additional financial security, or pay any interconnection fee under Section 9.7.2. The Large Load's existing executed Interconnection Agreement shall be treated as satisfying the commitment gate requirement under Section 9.4. ERCOT shall communicate Base Load classification in writing to the applicable Interconnecting DSP and Interconnecting TSP on a rolling basis.

Basis: Base Loads have completed the interconnection process. Their existing Interconnection Agreements, posted security, and paid CIAC (as needed) reflect commitments that are equivalent to or more rigorous than what Section 9.7 seeks to establish for new participants. No policy purpose is served by requiring these loads to satisfy Section 9.7 obligations a second time. In addition, 2027 loads are being asked to show development proof which further strengthens the argument that these loads are not speculative.

## Section 9.2.1.2 — Eligibility Criteria for Inclusion as Load to be Studied

Proposed Addition — New § 9.2.1.2(3):

(3) A Large Load that has executed a binding Interconnection Agreement with its Interconnecting TDSP, and has posted CIAC and financial security under that agreement prior to the effective date of this PGRR, shall be deemed to have satisfied the financial commitment eligibility criteria for inclusion as a Large Load to be Studied under this Section 9.2.1.2 without any requirement to execute a new Intermediate Agreement under Section 9.7.1 or post additional security. The Interconnecting TDSP shall confirm to ERCOT, by attestation submitted no later than July 24, 2026, that the applicable ILLE has executed an Interconnection Agreement and posted the required CIAC and financial security under that agreement. A Large Load that fails to satisfy the requirements of this paragraph (3) but otherwise meets the eligibility criteria of paragraph (1) must satisfy the Intermediate Agreement requirements of Section 9.7.1 by July 10, 2026 as a condition of inclusion.

Basis: A load that has executed an IA and posted CIAC and security has demonstrated the financial commitment that the Intermediate Agreement requirement is designed to elicit. Requiring such a load to also execute a new Intermediate Agreement and post new security would result in double payment for the same interconnection rights. The TDSP attestation mechanism provides ERCOT with the verification it needs without requiring duplicative filings.

## Section 9.7.1 — Intermediate Agreement Requirements

Proposed Amendment — § 9.7.1(1) (revised opening clause):

(1) Except as provided in Section 9.2.1.1(f) and Section 9.2.1.2(3), a Large Load that seeks inclusion in Batch Zero as a Large Load to be Studied and Allocated under Section 9.2.1.2 must, by the ILLE eligibility deadline of July 10, 2026, execute a binding Intermediate Agreement with its Interconnecting TDSP that satisfies the following requirements: [remainder of § 9.7.1 unchanged]

Basis: The Intermediate Agreement requirement is appropriate only for Tier 3 loads — those that have not previously executed an IA or posted CIAC and security. The proposed amendment clarifies that Tier 1 and Tier 2 loads are exempt from this requirement by operation of Sections 9.2.1.1(f) and 9.2.1.2(3).

## New Section 9.2.5 — Standalone Batch Zero Financial Commitment Framework

Proposed New Section 9.2.5:

9.2.5 Batch Zero Financial Commitment Framework. The financial commitment requirements applicable to Batch Zero participation are established in this Section 9.2.5 independently of any requirements adopted or to be adopted in PUCT Project No. 58481. Nothing in this Section 9.2.5 shall be construed to require any Large Load to satisfy obligations under Project No. 58481 as a condition of Batch Zero eligibility or advancement. To the extent the final order in Project No. 58481 establishes standards that differ from those reflected herein, ERCOT shall address any necessary alignment through a targeted revision request following completion of the Batch Zero process.

- (1) Tier 1 — Base Load. A Large Load classified as Base Load under Section 9.2.1.1 shall have no financial commitment obligation under this Section 9.2.5. Its existing executed Interconnection Agreement shall constitute full satisfaction of all Batch Zero financial commitment criteria.

- (2) Tier 2 — Studied Load with Prior IA and Security. A Large Load eligible for inclusion under Section 9.2.1.2 that has, prior to the effective date of this PGRR, executed a binding Interconnection Agreement with its Interconnecting TDSP and posted CIAC and financial security under that agreement, shall have no additional financial commitment obligation under this Section 9.2.5. The TDSP attestation under Section 9.2.1.2(3) shall constitute full satisfaction of all Batch Zero financial commitment criteria for such load.

- (3) Tier 3 — Studied Load Without Prior IA or Security. A Large Load eligible for inclusion under Section 9.2.1.2 that has not previously executed a binding Interconnection Agreement or posted CIAC and financial security under any prior ERCOT or TDSP process must, by July 10, 2026: (a) execute an Intermediate Agreement meeting the requirements of Section 9.7.1; (b) post financial security at the applicable $/MW rate; and (c) commit to CIAC obligations as reflected in the Intermediate Agreement. Such a load must execute a full Interconnection Agreement meeting Section 9.7.2 by the commitment gate deadline under Section 9.4 as a condition of retaining its MW allocation.

# Summary of Requested Revisions

| Section | Issue | Requested Revision |
| --- | --- | --- |
| § 9.2.1.1 | Base Loads with executed IAs and/or posted security are not explicitly exempted from new financial commitment requirements under § 9.7 | Add new § 9.2.1.1(f): Base Loads' existing IAs fully satisfy all Batch Zero financial commitment criteria; no new security, fee, or re-execution required |
| § 9.2.1.2 | Loads with executed IAs and posted CIAC/security are treated identically to loads with no financial commitments, requiring double payment | Add new § 9.2.1.2(3): Prior IA execution and CIAC/security posting satisfies financial commitment eligibility; TDSP attestation by July 24 serves as verification |
| § 9.7.1 | Intermediate Agreement requirement applies broadly to all studied loads, including those that have already made equivalent financial commitments | Amend § 9.7.1(1) opening clause to exempt Tier 1 and Tier 2 loads; requirement applies only to Tier 3 (LLI-only) loads |
| § 9.7.2 | Interconnection Agreement and non-refundable fee requirements do not distinguish between loads with prior commitments and loads without | Conform to Tier 1/Tier 2 exemptions; Tier 3 loads must execute IA by commitment gate; non-refundable fee applies only to Tier 3 |
| New § 9.2.5 | No standalone Batch Zero financial framework exists; all requirements depend on Project No. 58481, which is not yet final | Add new § 9.2.5 establishing three-tier framework independently of Project No. 58481, with explicit statement that Batch Zero eligibility does not depend on 58481 finalization |

Respectfully submitted,

Bharath Ravulapati

Director, Grid Strategy and Execution

Crusoe Energy Systems, LLC

bravulapati@crusoe.ai

Date: March 25, 2026

PGRR145 Stakeholder Comments — Crusoe Energy Systems, LLC — March 25, 2026 | Submitted pursuant to ERCOT Nodal Protocols § 21.2 | Questions: bravulapati@crusoe.ai