## Slide 1: Large Load Interconnection Batch Study Workshop
March 30th, 2026
Workshop #6

## Slide 2: Agenda
Timeline and governance recap
Update on timeline and key workshop dates
Outline PRS/ROS/TAC pathways to June Board with key submission dates
1
Eligibility and March 4th cutoff date discussion
Understand the trade-off between investment certainty and system reliability
Review proposed Batch Zero inclusion and treatment, including how outcomes vary based on study completion timing and milestone achievement
3
Year 6 transmission
Assess alternative approaches for Year 6 MW allocation
4
5
CLR discussion
Advance discussion on CLR framework for Batch Zero
6
BYOG discussion
Vetting the Self-Limiting Facility (SLF) option
Gathering stakeholder input on key design and implementation questions
7
Q&A
Open forum for Batch Zero concerns, comments, and suggestions
2
Market Comments filed on NPRR/PGRR
Review new stakeholder comments

## Slide 3: Agenda
Timeline and governance recap
PGRR145 stakeholder feedback
Eligibility / March 4th discussion
Year 6 transmission planning
CLR discussion
BYOG discussion
Appendix

## Slide 4: Batch Zero Revision Request Timeline
Forums
Workshops and working groups
PRS (Protocols Review Subcommittee)
ROS (Reliability and Operations Subcommittee)
TAC
ERCOT Board
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Update 3/5
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
8/1 Target effective date of protocols
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
Preview structure/governing concepts of Batch Zero NPRR before filing
Confirm proposed protocol changes are ready for governance review
Endorse NPRR for advancement to TAC (contingent on technical valid.)
If accompanying PGRR filed, then ROS will be involved in review
ROS approval will be required for any PGRR(s).
Review/endorse combined NPRR/PGRR package for Board approval
Authorize implementation of Batch Zero by approval of NPRR/PGRRs
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Target Board approval date
Board Meeting 4/20
Regular PRS 4/15
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Note that TAC leadership is involved in considering options to ensure successful review and approval
Special PRS 4/22
Regular TAC 4/29
Special TAC 5/13
PRS Vote 5/6
4
Monthly LLWG updates
4/8 ERCOT files CLR/BYOG Revision Request(s)
ROS Update (special) 4/14
ROS Update (special) 4/23

## Slide 5: Revision Request Process Flow
Comments may be filed between each step of the process
Comments for NPRR1325 may be submitted using the Comments Form found here
Comments for PGRR145 may be submitted using the Comments Form found here.
NPRR Comments
PGRR Comments
Large Load Interconnection Workshops
NPRR/PGRR
Review
BOARD
PUCT
TAC
ROS
PGRR Language/IA Review
PRS
NPRR Language/IA Review

## Slide 6: Related PUCT Activities
PUC Project 58480, 16 TAC § 25.370, Large Load Forecasting Rule (Adopted & Effective March 1, 2026)
  After 2026, only Large Loads that have executed an interconnection agreement that satisfies the requirements in PUC Project 58481 will be included in the Large Load forecast. These requirements will be reflected in future revision requests.
  Establishes alternative gating criteria for Large Loads to be included in the 2026 Large Load Forecast, which is used in planning assessments until new cases are constructed in 2027 using new rule criteria.
Source: PUCT Project No. 58480 (final rule) and Project No. 58481 – Proposal for Publication of 16 TAC §25.194 (filed March 12, 2026)
XXX Changes/Clarification vs. Mar 24th Workshop
PUC Project 58481, proposed to be 16 TAC § 25.194, Large Load Interconnection Standards (Proposal for Publication published on March 12, 2026)
  Intermediate Agreement Requirements:
    Site control (updated)
    Financial Security ($50,000/MW in current PFP; subject to final rule)
    Disclosures
    Option to pay for significant equipment or services
  Interconnection Agreement Requirements:
    Site control (updated)
    Financial security
    Interconnection fee ($50,000/MW, non-refundable)
    CIAC
    Reallocation
    Withdrawal Consequences
    Refund Eligibility and Timing
  After the PUCT adopts a final rule, ERCOT will file a revision request to align Section 9.7 with the requirements in the final rule.

## Slide 7: Reminder of Scope and Priorities for Workshops
March 4 filings completed for Batch Zero: ERCOT filed the Batch Zero PGRR145 and related NPRR1325 on March 4, initiating the formal governance process and aligning with the May PRS/ROS/TAC sequence and June 1 Board target reflected in the critical path timeline
  March 17 ERCOT comments filed: ERCOT submitted follow-up comments on PGRR145 (March 17) in response to stakeholder feedback on the March 4 draft, introducing targeted refinements (e.g., safe harbor for legacy LLIS, revised deadlines, alignment with PUCT PFP)
  Workshop #5: review of 21 stakeholder comments
  Workshop #6: focus on four major themes/issues
  April 2:target for ERCOT second set of comments
  April 9 Workshop #7: discussion of ERCOT and stakeholder comments
Additional filings on target (CLR and BYOG): ERCOT is advancing targeted revision requests to clarify CLR and BYOG treatment and is currently targeting April 8 filing CLR, TBD for BYOG
Long-term Batch Process revisions: development of the enduring batch framework is out of scope for the current filing. ERCOT will incorporate lessons learned from Batch Zero to inform future revision requests and the design of a durable, repeatable batch study process

## Slide 8: Agenda
Timeline and governance recap
PGRR145 stakeholder feedback
Eligibility / March 4th discussion
Year 6 transmission planning
CLR discussion
BYOG discussion
Appendix

## Slide 9: Agenda
Timeline and governance recap
PGRR145 stakeholder feedback
Eligibility / March 4th discussion
Year 6 transmission planning
CLR discussion
BYOG discussion
Appendix

## Slide 10: Defining study validity: trade-off between certainty and system reliability
Automatic study validation – All studies approved prior to Batch Zero are valid
A
Large Load with a study approved prior to July 10
Area where grid cannot reliably supply all the approved load in all conditions
B
Automatic study validation before March 4 and coordinated study validation after, using PGRR145
Large Load with a study approved prior to March 4 deemed valid
Large Load with a study approved between March 4 and July 10 that may receive a MW amount lower than the initially approved study
Areas where grid cannot reliably supply all the approved load in all conditions are avoided
The topic receiving the most comments in PGRR145 is the proposed study validity check for studies completed after March 4, 2026
ERCOT proposed this check to ensure the base load level in Batch Zero does not exceed transmission system reliability limits

## Slide 11: Proposed Batch inclusion and treatment depend on timing of study completion and milestone achievement
March 1
Studies
Eligibility
Inclusion
Treatment
Legacy
Project has complete and valid studies as of March 4, 2026 under PGRR145 Section 9.2.1.4(3) (i.e., LLIS completed and interconnection agreement executed under PGRR115 Sections 9.4 and 9.5)
Batch Zero
If meeting Section 9.2.1.1: modeled as Base Load not subject to additional study
If meeting Section 9.2.1.2: studied and allocated based on amount of load that may be served reliably
Milestone timeline
Batch implications
2026
2027
Q1
Q2
Q3
Q4
Q1
Q2
March 4
Batch Zero
Project meets eligibility criteria under PGRR145 Sections 9.2.1.1 or 9.2.1.2 by July 10, 2026 (with DSP/TSP submission by July 24), and does not qualify under Section 9.2.1.4(3)
PGRR115 process stops on July 10, 2026
Batch Zero
Prior studies (if any) are subject to ERCOT validation and project ordering under Section 9.2.1.4
If meeting Section 9.2.1.1: modeled as Base Load not subject to additional study
If meeting Section 9.2.1.2: studied and allocated based on amount of load that may be served reliably
July 10
Batch 1
Project does not meet Batch Zero eligibility criteria under PGRR145 by July 10, 2026 (i.e., has not met required LLIS milestones under PGRR115)
Batch 1
Batch 2+
Projects not included in Batch 1 (e.g., after March 2027 cutoff)
Batch 2+
Studied and allocated in subsequent batch process; MWs determined based on amount of load that may be served reliably

## Slide 12: Proposed Batch inclusion and treatment depend on timing of study completion and milestone achievement
3/4/26
7/10/26
3/1/27
LLIS studies are deemed complete and valid*
LLIS studies may be deemed complete and valid*
* LLI projects must also meet Planning Guide Section 9.5
LLIS studies no longer accepted; if not in Batch Zero, wait for Batch 1
If not in Batch 1, wait for Batch 2
Batch Zero
Batch 1
LLIS (“PGRR115”)

## Slide 13: PGRR145 Study Validity FAQ
Q: Is March 4, 2026 a retroactive cutoff date in PGRR145 for LLIS and RPG studies to be deemed valid?
A: No. Studies that are approved for LLI projects meeting Planning Guide Section 9.5 may still be deemed valid until July 10, 2026 if no other LLI projects that impact the reliability study results (i.e., in the study area and not included in the study) achieve this status before them.
Q: How will ILLEs for LLI projects with approved studies and meeting Planning Guide Section 9.5 after March 4, 2026 know that their studies have been deemed valid?
A: Going forward, ERCOT will provide periodic updates to the interconnecting TSPs regarding LLI study validity for all LLI projects.
Q: Will the current LLIS process (“PGRR115 process”) continue for LLI projects that do not qualify to be included in Batch Zero?
A: No. As proposed in PGRR145, the PGRR115 process will cease on July 10, 2026. Going forward, all LLI projects will need to be included in a batch study as a condition for being included in a planning load forecast and for being approved to energize. If an LLI project does not qualify to be included in Batch Zero, they may be eligible for inclusion in Batch 1, pending TBD requirements.

## Slide 14: Agenda
Timeline and governance recap
PGRR145 stakeholder feedback
Eligibility / March 4th discussion
Year 6 transmission planning
CLR discussion
BYOG discussion
Appendix

## Slide 15: Two approaches to allocating future MWs: early certainty vs. alignment with transmission development
PGRR145 Approach
Alternative approach to address TSP comments
Source: ERCOT discussions
Example: 1,000 MW data center requiring full capacity by Year 6
Years 1-5
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Considerations
Provides certainty by guaranteeing full MWs by Year 6
Creates a potential step-change in MWs between Years 5 and 6, with limited time to develop required transmission
Full MW allocation is aligned with identified transmission upgrades
Requires financial commitment for partial MWs without clear visibility on timing or certainty of full MW delivery
Year 6
Full MW automatically allocated based on Batch Zero results; transmission solutions further defined in the 2027 RTP
Full MW not committed in Batch Zero; additional MWs studied and allocated through a subsequent Batch 1 process
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 1000
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
Illustrative allocation, MW
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 600
 | 400
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
TBD
Automatically set at requested peak Demand
TBD: additional MWs studied in next batch and allocated based on available capacity

## Slide 16: Agenda
Timeline and governance recap
PGRR145 stakeholder feedback
Eligibility / March 4th discussion
Year 6 transmission planning
CLR discussion
BYOG discussion
Appendix

## Slide 17: Concept Review - CLRs (Not netted with any Generation or Batteries)
Source: ERCOT discussions
Point of interconnection
Large Load registers entirely as a CLR without any type of netting with generation or storage
Load-Only CLR leverages the existing CLR framework as the simplest near-term option,1 subject to required market/system implementation items (e.g., SCED CLR Bid Curve capping enhancements) before energization
Participates as dispatchable demand and must follow SCED basepoints within its registered operating range (PC/LPC/MPC)
No assurance of service above awarded firm MW; real-time consumption may be reduced below PC based on system conditions and SCED CLR Bid Curve capping
ERCOT observes and verifies performance based on net MW at the POI and adherence to SCED dispatch instructions
Must meet existing CLR telemetry and dispatch performance requirements (subject to SCED instructions and registered operating limits)
Load may register operational capability above awarded firm MW, subject to real-time dispatch and congestion mitigation2
Illustrative example
  150 MW requested in Year 1
  ERCOT performs steady-state and stability studies and allocate phased MW (e.g., 100 MW in Years 1–2, 300 MW in Years 3-4, until transmission upgrade in Year 5)
  Operational parameters:
    PC = 0–100 MW (firm)
    LPC = 0–100 MW
    MPC = 150 MW (upper operational capability; not a planning guarantee)
    CLR quantity may be modified in later years as transmission capability increases
1. NPRR1188 later in 2026: Nodal pricing align local congestion prices. NPRR1255 mitigation methods needed (small project) | 2. Potentially subject to additional limits identified in dynamic studies
Description
Details
Load
Illustrative scheme
Chart: 
 | 100 | 100 | 300 | 300 | 1000
 | 50 | 200 | 200 | 400
50
Year 1
Year 2
Year 3
Year 4
Year 5
150
300
500
700
CLR Load
Firm Load
POTENTIALLY FEASIBLE CONFIGURATION
1A
ERCOT grid
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 18: Provisional CLRs – Structure of Revision Requests1
Will consist of a PGRR and companion NPRR
Modular structure adds to PGRR145 and NPRR1325
  Example – Section 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs) compliments Section 9.2.2 as written in PGRR145
This structure will allow the CLR Revision Requests to move forward in parallel with PGRR145 and NPRR1325 if possible, without interfering with the core Batch Zero language
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 19: Provisional CLRs – Definition1
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
New Resource Type: ‘Provisional CLR’
Same as a CLR but locked in for a period of time and has Low Power Consumption (LPC) limits defined in the Batch Zero Interconnection Study
What’s different?
P-CLR load bids can be ‘capped’ to mitigate transmission constraints identified in SCED
P-CLR bids are capped dynamically (“last-in-line/just-in-time”) in each run of SCED to a price that will just allow SCED to resolve a constraint
Submits CLR Energy Bid Curve  bid-to-buy prices between Maximum Power Consumption (MPC) and Low Power Consumption (LPC) – same as any other CLR

## Slide 20: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
ERCOT validates completion of all steps prior to granting Approval to Energize
8
QSE establishes required ICCP telemetry points
7
RE coordinates with ERCOT to establish metering and submit CLR parameters via RIOO
6
ILLE registers with ERCOT as a Resource Entity (RE) and designates a QSE
5
ERCOT studies the full load amount in the Batch Zero Refinement Study
4
ILLE submits updated Declaration to accept allocation amounts
3
ERCOT studies PCLR in Batch Zero
2
Submission of Declaration and required information to ERCOT
(by July 24)
1
Must be done before non-firm load may energize
May be done in parallel with QSA
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 21: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
1
ILLE Declaration of Intent and PCLR data submitted to ERCOT
Interconnecting Large Load Entity (ILLE) provides to the Interconnecting DSP/TSP
  A notarized Declaration of Intent to Register as a PCLR
  All additional data needed to model the PCLR in Batch Zero, including the minimum amount of load that must be firm (termed the Low Power Consumption limit)
The Interconnecting DSP/TSP provides this information to ERCOT on behalf of the ILLE on or before July 24, 2026
2
PCLR is evaluated in the Batch Zero Interconnection Study
For the steady state portion of the Batch Zero Interconnection Stuy ERCOT will assess the PCLR according to the same methodology as other included, allocated loads
  If the amount of firm load that can be reliably served in a given year of the study is greater than or equal to the requested Low Power Consumption for that year, that amount becomes the approved LPC amount and the rest of the requested load may connect as a PCLR
  If the amount of firm load that can be reliably served is less than the requested LPC, the Load receives an allocation of 0 MW for that year
ERCOT will study the full requested MW amount for determining potential transmission upgrades and in the stability screening study

## Slide 22: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
3
ILLE submits updated Declaration of Intent and accepts Batch Zero amounts
ILLE updates the Declaration of Intent to Register as a PCLR
  The update will reflect the approved LCP amounts
  The update will also reflect the date on which the Load will be eligible to de-register as a PCLR
The ILLE must also meet all the requirements documented in Section 9.4 of PGRR145
4
ERCOT studies the full load amount in the Batch Zero Refinement Study
ERCOT will study the full requested load in the Batch Zero Refinement Study for all PCLRs that met the commitment requirement
This will ensure the Transmission Plan includes the needed upgrades to allow the PCLR to be served reliably as firm load in the future

## Slide 23: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
ILLE meets all existing requirements to register as a CLR
These include, for example
Registration as a Resource Entity (RE), designation of a Qualified Scheduling Entity (QSE), and submission of the Managed Capacity Declaration form
Establishment of required metering
Submission of all required CLR parameters in RIOO
Establishment from the QSE of all required telemetry points
8
ERCOT validates completion of all steps prior before Approval to Energize
ERCOT will validate all required CLR registration and modeling steps are completed as part of the Approval to Energize process
ERCOT will not permit the PCLR to energize above the approved firm load (LPC) amounts until all required steps are completed
After energization, ERCOT will monitor to ensure the PCLR behavior is in alignment with the agreed on PCLR amounts
5-7

## Slide 24: Overview of PCLR Bid Capping Process1
After each SCED run, a list of binding transmission constraints which are approaching their max shadow price (X%)* are identified as potential list of transmission constraints to be used in the CLR Bid Capping process for the NEXT SCED run
Where the list of constraints identified for CLR bid capping process from the previous SCED run matches those active in the current SCED, any Batch CLR with a helping shift factor of Y% or greater (on a given constraint) will have its energy bid curve capped (in the Step 2** SCED run) according to the formula below
*Step 2 (in the SCED two step process) observes the limits of all constraints and uses mitigated offer caps to producing binding LMPs and Dispatch Instructions
* percentage may vary by the type of constraint (e.g IROL, GTC, basecase, contingency, voltage level)
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 25: PCLRs – Topics Still Under Internal Discussion1
Is there any study scenario that would limit the Maximum Power Consumption (MPC) of the PCLR?
Can PCLRs provide Ancillary Services?
Exact timing for CLR registration in the context of the Batch Zero process
Key parameters for PCLR bid capping process (X%, Y%)
Will Registration, RIOO, Market, or EMS system changes be needed to accommodate PCLRs?
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 26: Agenda
Timeline and governance recap
PGRR145 stakeholder feedback
Eligibility / March 4th discussion
Year 6 transmission planning
CLR discussion
BYOG discussion
Appendix

## Slide 27: BYOG Self-Limiting Facility (SLF)
Source: ERCOT discussions
Point of interconnection
Colocated Large Load and Generation operate behind a single POI under a defined net injection/ withdrawal limit enforced at the POI
Facility is structured as a PUN with a Self-Limiting Feature (SLF) (consistent with NPRR1026 framework)
The SLF ensures that net real power at the POI never exceeds the approved interconnection limit, regardless of internal load or generation configuration
Load and Generation are both registered resources
Interconnection limit applies to net MW at the POI
Requires operational coordination agreement between Load and Generator
ERCOT models the facility as a net resource at the POI, subject to the self-limiting cap
Facility must ensure net injection/withdrawal does not exceed POI cap at any time (may require breaker logic and/or reverse power relay to enforce the limit)
Transmission planning does not assume simultaneous full load and full generation at the POI:
  Either supply-side (GR/ESR) or demand-side (CLR) may participate at a given time
  Simultaneous full participation on both sides is not permitted unless structured as a Netted Network (separate construct)
The largest modeled contingency depends on internal configuration (e.g., if generators share a common step-up transformer, transformer loss may be most limiting event; if generators are electrically independent, individual G-1 may apply)
Description
Illustrative scheme
Load = 1,000 MW
Gen = 5 x 250 MW
G-1 compliant (serve 1,000 MW load) or most limiting contingency
POTENTIALLY FEASIBLE CONFIGURATION
2
Load
ERCOT grid
Gen 1
Gen 2
Gen 3
Gen 4
Gen 5
Load = 1,000 MW
Gen = 2 x 500 MW
G-1 compliant (only serve 500 MW load)
Load
ERCOT grid
Gen 1
Gen 2
Details

## Slide 28: Conceptual Batch Zero BYOG operating configurations for Large Load interconnection3
Business as Usual (BAU)
PUN+
Batch Self-Limiting Facility (SLF)
Load and generation are connected at separate POIs (shown) or behind the same POI and interact through the transmission system under existing interconnection framework
Configurations
Description
Generation and load are studied separately
Generation is only included in the LLIS if it meets PG 6.9 criteria
Load deliverability depends on transmission capability and may be constrained through the current study process
Transmission upgrades from batch study based on G-1+N-1 analysis
Details
Load is supported by dispatchable on-site generation such that G-1 ≥ load and treated as firm, with reliability managed through ERCOT operational actions
Configuration satisfies G-1 ≥ load (loss of one generator still allows remaining units to serve the load)
Load is treated as firm
No planning or administrative limit at POI
No transmission upgrades from batch study since configuration is G-1 secure
In operations:
  ERCOT may reject generator outages or require mitigation plans
  ERCOT may RUC resources1
  In real-time, mitigation plans or local load shed may be used
3. Conceptual designs still under internal review and may change | Source: ERCOT discussions
Site operates with a fixed transmission withdrawal limit determined through batch study
Generation mix may include thermal resources, renewables, and batteries
A fixed transmission withdrawal limit is established (e.g., 100 MW grid import limit) determined in the batch study
ERCOT does not coordinate RUC1 or outage management for the facility
The load and generation owners must coordinate operations to ensure grid imports never exceed the limit
The site would be equipped with a reverse power relay or equivalent protection to enforce the limit
Transmission upgrades required if identified by the batch study to meet reliability criteria2
1. RUC (Reliability Unit Commitment): ERCOT mechanism used to commit generation outside the market to maintain system reliability | 2. Based on batch study results for the generation/load mix
No admin limit
0-100 MW limit ensured by reverse power relay
~
~
~
~
~
~
~
~
~
~
~
~
~
Point of interconnection (POI)
Too many issues to resolve for
Batch Zero

## Slide 29: Key design and implementation questions
Source: ERCOT discussions
How should SLFs be modeled across Batch Study and transmission planning, especially if the processes are integrated?
How should SLFs present generation/load to ERCOT systems (COPs, outage coordination)?
Integration with planning and operations
Can reverse power above 0 MW be supported, or does it trigger RAS classification?
If classified as RAS, what are the implications for NERC compliance and control room operations?
Are there viable alternatives (e.g., reverse power relay with limits), or is zero the only feasible option?
Reverse power and compliance constraints
Should SLFs be limited to zero withdrawal (i.e., injection-only) to avoid RAS and compliance complexity?
Implications for SLF design
Should there be maximum load and generation sizes based on transmission network, e.g., can you have a 1000 MW load/gen on a 100 MW, 138-kV line?
Is the “zero withdrawal” construct acceptable from a TSP and operational perspective?
Open validation points
How should deliverability and injection limits be defined for SLF sites?

## Slide 30: Agenda
Timeline and governance recap
PGRR145 stakeholder feedback
Eligibility / March 4th discussion
Year 6 transmission planning
CLR discussion
BYOG discussion
Appendix

## Slide 31: Controllable Load Resource Rules
Key Design Considerations
  CLR is an existing resource type in ERCOT Protocols
  Similar to generators, CLRs can be dispatched down in real-time by ERCOT’s Security Constrained Economic Dispatch tool
  Some CLRs can be dispatched to zero load while others have a higher minimum load values
  ILLEs registering loads as CLRs still want the transmission system to be planned to serve the full load
  ERCOT and CLR entities need clearly defined rules to govern expectations
  NPRR1188 (expected late 2026 implementation) provides some but not all rules necessary for allowing specific consideration of CLRs in the Batch Study process
  Additional CLR Rules Needed
    Offer mitigation or similar concept to ensure high CLR offers don’t result in constraint violations in SCED optimization (SCED Step2)
    Binding commitment and exit conditions so CLRs remain as CLRs until necessary transmission upgrades are complete
    NPRR1188 does not support CLR composed of Load+Gen/Battery
  CLR Treatment in Batch Studies
    An ILLE’s designation of intent to register as CLR will be binding for the Batch Study
    A CLR will be allocated its full load request but may be required to have a minimum load amount assigned in the Batch Study process
  CLR Treatment in Other Studies
    CLRs will be modeled at their full requested load in transmission planning studies and the FAC-002 stability study
    All TSP studies must consider the full load

## Slide 32: Co-Location with Existing Generation Rules
Co-Location with existing generation
Key Design Considerations
  Senate Bill 6 rules may apply for generators existing before September 1, 2025
  The transmission system has been planned assuming the existing generation supports the system
  No specific rules aside from existing requirements in the Protocols (such as an updated Reactive Power study)

## Slide 33: Co-Location with New Generation Rules
Examples
Key Design Considerations
  New co-located generators can reduce the need for the transmission system to support a new Large Load
  There are multiple scenarios regarding how the co-located generation resource and Large Load interact with the transmission system, each requiring different rules
  In some scenarios, new rules are needed to link generation interconnection requests to LLI requests
  Scenario 1: Large Load does not consume from the grid – only from the co-located generation
    The co-located Large Load will be allocated its full load request
    Rules needed to ensure Large Load will never consume from the grid, even momentarily
    Rules needed to ensure LLI request and GINR are linked
  Scenario 2: Scenario 1 temporarily until transmission upgrades are complete
    All Scenario 1 rules apply
    A separate study is needed to determine the required transmission upgrades and rules needed to exit no-transmission-system-load status
  Scenario 3: Large Load has co-located dispatchable generation and may sometimes consume from the grid
    The co-located Large Load will be allocated their full load request except in the G-1+N-1 analysis
    Rules needed to ensure LLI request and GINR are linked
  Scenario 4: Large Load has co-located intermittent generation and/or energy storage and may sometimes consume from the grid
    No specific rules
  Not enough time in Batch Zero development for numerous scenarios; looking for feedback on priority and feasibility of scenario options (will also discuss as part of post-meeting survey).

## Slide 34: Batch Zero Overview – Two Phases
Study Inputs
Batch Zero Study
Batch Zero Refinement
ILLE Commitment Period
Transmission Plan to RPG
6 months
3 months
  Steady state study and dynamic stability screening
  Identify planning criteria violations
  Work iteratively with TSPs to determine amount of load that can be reliably served in each year and, where feasible, upgrades needed to serve full load request
Work iteratively with TSPs to
  Determine which upgrades are still needed based on ILLE commitments
  Review cost estimates and alternative upgrade options
  Develop a transmission plan to serve committed loads
Reference: Batch Zero PGRR, Sections 9.3–9.5 (Study Phase, Commitment Gate, and Refinement Phase)

## Slide 35: Batch Zero Study Scope Overview
  Study horizon: 2028–2032 (Years 1–5), load amounts not reliably served within 2028-2032 will be set equal to requested load in 2033 (Year 6)
  What ERCOT studies (per year): ERCOT builds cases from SSWG base cases and runs reliability assessment across:
    Summer peak load (high load system stress)
    Summer, no solar (sunset, net peak load)
    Fall peak (used to assess maintenance outage conditions consistent with ERCOT Planning Guide criteria)
  Reliability assessment coverage:
    Evaluate planning criteria violations triggered by adding the Batch Zero loads (across scenarios/contingencies ERCOT selects)
    Determine “reliably served MW” per load, per year (i.e., deliverable load that can be served without violating planning criteria)
    Load that cannot reliably be served in years 1-5 will be allocated in year 6 (2033).
  Generation assumptions: if additional generation is needed to serve the modeled load, ERCOT models generation additions consistent with applicable planning methodologies
  Transparency: ERCOT posts initial and final study cases (interconnection and refinement) used for Batch Zero on the MIS Secure Area once available
Scope details
Key Design Considerations
  One consistent, system-wide reliability study: ERCOT evaluates all Batch Zero-eligible Large Loads using a common set of assumptions, criteria, and cases to identify system limitations and needed upgrades
  Clear, year-by-year outcomes: for each assessed Large Load, the study determines the maximum peak MW that can be reliably served each year (2028–2033) and the transmission upgrades needed to increase service toward the requested level
Reference: Batch Zero PGRR, Sections 9.3.1–9.3.2 (Batch Zero Study and Methodology)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 36: Batch Zero Study Methodology and Study Elements
Study elements and methodology
Key Design Considerations
  Study must be repeatable and explainable: ERCOT uses transparent study inputs (posted cases), consistent criteria, and a clear link from violations to upgrades to year-by-year reliably served MW
  Actionable coordination: the process enables rapid, iterative ERCOT–TSP alignment on transmission improvements while the study is underway
  Prepare system-wide study cases (ERCOT)
    Develop annual cases for 2028–2032 from SSWG base cases
    Add Batch Zero-eligible Large Loads per the inclusion criteria and model treatment rules
    Post cases to MIS Secure once available
  System-wide reliability assessment (ERCOT)
    Study scenarios and contingencies ERCOT determines are needed to evaluate reliability impacts
    For each assessed LL, identify planning criteria violations associated with the proposed addition
    Determine the amount of peak load that can be reliably served each year
  Stability screening assessment (ERCOT)
    Perform the stability component of the Batch Zero study
    Document identified stability issues and reflect any resulting limitations in year-by-year reliably served MW
  Identify transmission improvements (ERCOT and impacted TSPs)
    Once violations are identified, ERCOT initiates communication with relevant TSPs
    TSPs provide upgrade recommendations; ERCOT and TSPs iterate through the study period until needed upgrades are identified with ERCOT retaining final determination authority
    Results translate into upgrades resolving violations/enabling higher reliably served MW over time
  Supporting prerequisites (TDSPs/TSPs, as applicable)
    Short-circuit and other relevant studies are completed by the interconnecting TDSP/TSP at least 30 days before ERCOT issues Batch Zero awards/results
    TDSPs/TSPs provide necessary model information prior to start of Batch Zero
Reference: Batch Zero PGRR, Sections 9.3.1–9.3.2 (Batch Zero Study Scope, Methodology, and Coordination)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 37: Outputs, Deliverables, and Timeline
Process and outputs
  Core timeline
    By July 10, 2026: ILLEs meet eligibility / milestone requirements
    By July 24, 2026: TSPs/DSPs submit complete project information to ERCOT
    By August 7, 2026: ERCOT confirms Batch Zero inclusion and classification of each load
    January 29, 2027: ERCOT issues the Batch Zero Study Report, provides Load Commissioning Plans (LCPs) to ILLEs (via TSPs/DSPs) and notifies TSPs of Batch Zero results
    March 1, 2027: TDSPs notify ERCOT which Large Loads have met commitment requirements
    June 1, 2027: ERCOT completes the Batch Zero Refinement Study and delivers the Batch Zero Transmission Plan to RPG
  Primary outputs
    Batch Zero Study Report (summary of reliability impacts, identified planning criteria violations, and proposed transmission upgrades)
    Load Commissioning Plan (LCP) per Large Load
      Maximum reliably served peak MW for each year (2028–2033)
        Loads not reliably served receive full requested allocation for year 2033
    Estimated security requirements and CIAC obligations required to inform ILLE commitment decisions
    Confidential TSP package: detailed upgrade list and associated Large Loads (as applicable)
  Refinement and RPG handoff
    Only Large Loads that meet commitment milestones remain in scope, loads that do not meet commitment are removed from Batch Zero
    MW allocations for Large Loads that meet commitment criteria by the deadline are not adjusted during the Refinement Study
    ERCOT re-evaluates whether previously identified upgrades are still needed/modified/no longer required
    Final Batch Zero Transmission Plan is delivered into the RPG process
  Actionable outcomes: each Large Load receives a year-by-year Load Commissioning Plan (LCP) and estimated security requirements to support commitment decisions. TSPs receive
  Clear commitment gate to planning certainty: only Large Loads that meet commitment milestones move into the Refinement Study and transmission plan delivered to RPG
Key Design Considerations
Reference: Batch Zero PGRR, Sections 9.3.1, 9.4, and 9.5 (Timeline, Outputs, and Refinement Process)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 38: Batch Zero process flow chart for studied load
Submit intermediate agreement requirements
Sign intermediate agreement and Send Batch Info to ERCOT
Build Cases and Post on MIS Secure
Perform Batch Steady State Study
Perform transmission improvement analysis
Perform Short Circuit, SSR Screening, and Facilities Studies
Post Final Cases on MIS Secure and Communicate Results
Submit interconnection agreement requirements
Sign interconnection agreement
Perform Refinement Transmission Plan Study
Provide Cost Estimates and Final Review
Submit Refinement Transmission Plan Study for RPG Review
Resolve RPG Comments and Seek BOD endorsement, when necessary
ERCOT
T(D)SP
Developer (Interconnecting Large Load Entity – ILLE)
Perform Batch Stability Screening Study
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 39: Proposed Batch Zero Timeline
1
2
3
4
5
6
7
8
9
9
Batch Refinement Study:
ERCOT: determine which transmission improvements identified in the Batch study are still required based on which loads met the commitment requirements
TSPs: provide cost estimates and refinement of transmission improvement projects and alternatives
ERCOT: final analysis of alternatives and determinization of final set of transmission improvement projects
ERCOT: prepare final report and submit to RPG
2026
2027
Aug
Sep
Oct
Nov
Jul
Dec
Feb
Mar
Apr
May
Jun
Jul
Aug
Jan
Sep
RPG Comment Period (3 weeks)
RPG Study Mode (4-weeks, if required)
TAC (August 2027)
Board (September 2027)
2026 RTP
Final Report (2 weeks)
2027 RTP
Batch Zero (Study years 2028-2032)
Stability Screening Study (14 weeks)
Steady State Analysis (15 weeks)
Developer Commitment Deadline
FAC-002 Stability
Batch Refinement Study (13 weeks)
Case Build (13 weeks)
Steady State and Stability Analyses:
ERCOT: identification of criteria violations
ERCOT and TSPs: identification of transmission improvement projects and alternatives to resolve violations
TSPs: determination of transmission improvement feasibility and schedule
TSPs: provide transmission improvement cost estimates
ERCOT: final determination of transmission improvement projects that are feasible
ERCOT: allocate MWs to loads
ERCOT: create load request to transmission improvement mapping
Reference: Batch Zero PGRR, Sections 9.3–9.5 (Study Timeline, Commitment Gate, Refinement, and RPG Delivery)

## Slide 40: Case Build
Details
Key Design Considerations
1
  Standardized ERCOT intake and deadline
  Clear eligibility and inclusion rules for Batch Zero
  Defined modeling treatment at entry
  Transparent study case development (posted to MIS Secure)
  For Batch Zero, the interconnecting TDSP submits required project information and any required attestations related to executed agreements or equipment procurement by the applicable deadlines (July 10 for ILLE milestones, July 24 for TDSP submission to ERCOT)
  ERCOT applies the Batch Zero eligibility criteria to determine which Large Loads are included and whether they are treated as base load not subject to further evaluation or load subject to reliability assessment and allocation including ERCOTs determination of whether existing interconnection studies are valid, with studies completed as of March 4, 2026, deemed valid without further review
  Projects that do not meet the criteria or fail to submit required information by the deadline are excluded from Batch Zero and evaluated in a future process
  ERCOT develops the 2028–2032 study cases using SSWG-based summer peak, summer peak net load, and fall peak cases, and posts those cases to the MIS Secure area to provide transparency into study assumptions
Reference: Batch Zero PGRR, Sections 9.2.1–9.2.2 and 9.3.2 (Eligibility Determination and Study Case Development)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 41: Steady State Analysis
Details
Key Design Considerations
2
  ERCOT performs a singular, system-wide steady-state study for all Large Loads included in Batch Zero using SSWG derived base cases appropriate for the study horizon
  ERCOT studies all scenarios and contingencies necessary to assess reliability with applicable NERC Reliability Standards, ERCOT Protocols, the Planning Guide, and Operating Guides
  As soon as violations are identified, ERCOT begins collaborative, iterative process working with TSPs to identify feasible transmission upgrades with ERCOT making final determinations to serve the Large Loads
  For each Large Load subject to assessment, ERCOT documents planning criteria violations and determines the amount of peak Demand that may be reliably served for each year of the 2028–2032 study period. The amount of load that may be reliably served for 2033 will be set to the requested amount for load not reliably served in 2028–2032
  Single, system-wide ERCOT study
  Reliability-based contingency analysis
  Identification of planning criteria violations
  Determination of reliably served MW by year
Reference: Batch Zero PGRR, Sections 9.3.1(1)–(2) (Batch Zero Overview) and 9.3.2(1), (3) (Batch Zero Study Methodology)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 42: Stability Screening Study
3
Details
Key Design Considerations
  Maintain sufficient stability margin
  Mitigation of identified instability
  Coordination with TSPs
  If stability screening criteria violation is identified, ERCOT and the applicable TSP(s) investigates mitigation measures, including transmission improvements, and identifies any required modifications to load levels or timing reflected in the Load Commissioning Plan and determines the amount of peak Demand that can be reliably served in each study year consistent with applicable planning criteria and identified violations, including stability constraints
  Updated dynamic data is evaluated based on whether it is expected to have an adverse impact on results (replacing prior “consistent with” standard)
Reference: Batch Zero PGRR, Sections 9.3.1 and 9.3.2 (Batch Zero Study and Methodology)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 43: Final Report
4
Details
Key Design Considerations
  Actionable study outcome
  Clear MW allocations by year
  Identification of required upgrades
  Security visibility
  ERCOT produces the Batch Zero Report summarizing study results and identified transmission upgrades
  For each assessed Large Load, ERCOT updates the originally provided Load Commissioning Plan reflecting the amount of peak Demand that can be reliably served each year and the upgrades required to support each level of Demand. The amount of load that may be reliably served for 2033 will be set equal to requested MW for load not achievable in earlier years
  ERCOT includes estimated security requirements in the Batch Zero Report based on TSP cost inputs; TSPs finalize financial security and CIAC obligations in the Interconnection Agreement
  Execution of the Interconnection Agreement reflecting required financial security and cost obligations is required for the ILLE to accept allocated MW amounts and schedule
Reference: Batch Zero PGRR, Sections 9.4(1)–(2), 9.5(1)–(5), and 9.7.2 (Batch Zero Report, Commitment, and Transmission Plan Delivery)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 44: Developer Commitment Deadline
5
Details
Key Design Considerations
  Clear commitment gate
  TDSP attestation as trigger
  Removal of non-committed projects
  Planning certainty before refinement
  To accept the allocated MW and schedule documented in the LCP, the ILLE must execute a binding Interconnection Agreement by the commitment deadline. The agreement must satisfy the requirements adopted in a final rule in Project No. 58481
  The interconnecting DSP must submit formal attestation to ERCOT confirming that the ILLE has executed the Interconnection Agreement by the deadline. This attestation serves as verification that the load has satisfied the commitment requirement for inclusion in the Batch Zero Refinement Study
  Large Loads that do not satisfy the commitment requirement by the deadline are deemed withdrawn from the Batch Zero process and are excluded from the Refinement Study and resulting Transmission Plan
  MW allocations for Large Loads that meet the commitment requirement by the deadline are preserved and are not adjusted during the Refinement Study once commitment requirements are met. The Refinement Study may modify recommended transmission facility improvements but does not revisit committed MW amounts
Reference: Batch Zero PGRR, Sections 9.4(2)–(3) and 9.5(5) (ILLE Commitment, Withdrawal, and MW Protection in Refinement)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 45: Batch Refinement Study
6
Details
Key Design Considerations
  Removal of non-committed loads
  Re-evaluation of identified upgrades
  Right-sizing of transmission scope
  Preparation of Transmission Plan for RPG
  Immediately following the commitment deadline, ERCOT updates the Batch Zero study to include only those Large Loads that met commitment requirements
  ERCOT evaluates whether the remaining loads continue to result in planning criteria violations and whether previously identified transmission upgrades are still needed, need modification, or are no longer required
  ERCOT works iteratively with relevant TSPs during this period and develops the final Transmission Plan to be delivered to RPG
  The Refinement Study may modify recommended transmission improvements but does not adjust MW allocations for Large Loads that met commitment criteria
  The Refinement Study results in a final report and recommended Transmission Facility improvements submitted for RPG Project Review
Reference: Batch Zero PGRR, Section 9.5(1)–(5) (Batch Zero Refinement Study and Transmission Plan Delivery)

## Slide 46: RPG Comment Period
7
update (highlight changes)
Details
Key Design Considerations
  Stakeholder review and transparency
  Time-bound comment process
  Preservation of governance pathway
  The Batch Refinement Study is submitted to the Regional Planning Group for review including recommended Transmission Facility improvements resulting from the Refinement Study
  RPG Project classification is based on the sum total of all transmission projects in the Refinement Study
  Stakeholders have an opportunity to submit comments within a defined review period. RPG review focuses on the recommended Transmission Facility improvements identified in the Refinement Study and the associated technical assumptions
  RPG review does not reopen MW allocations for committed Large Loads
Reference: Batch Zero PGRR, Sections 9.5(1)–(5) (Refinement Study and RPG Project Review)

## Slide 47: RPG Study Mode
8
Details
Key Design Considerations
  Targeted additional evaluation if necessary
  Focused response to material concerns
  If needed, ERCOT conducts a limited additional study to address specific issues raised during RPG review, any additional study is limited to recommended Transmission Facility improvements and does not reopen MW allocations for committed Large Loads
  This step is intended to provide focused technical clarification rather than a full annual RTP-level re-evaluation
  The scope of RPG Study Mode is limited to evaluation of recommended Transmission Facility improvements identified in the Refinement Study
Reference: Batch Zero PGRR, Sections 9.5(1)–(5) (Refinement Study and RPG Project Review)

## Slide 48: TAC and Board
9
Details
Key Design Considerations
  Formal governance review
  Recommendation pathway
  Final approval authority
  ERCOT endorsement of recommended projects
  Following completion of RPG review and any additional study, if applicable, the Batch Transmission Plan proceeds to TAC for review and comment in accordance with ERCOT governance procedures
  If required by the RPG process, the ERCOT Board considers and acts on the recommended Transmission Plan resulting from the Batch Zero process. Board action applies to recommended Transmission Facility improvements identified in the Refinement Study
  MW allocations for Large Loads that meet commitment criteria are not adjusted during the Refinement Study and are not part of the Transmission Plan approval considered by TAC or the ERCOT Board, if applicable
  Approval reflects ERCOT’s independent technical review, TSP coordination, and stakeholder input through the RPG process
Reference: Batch Zero PGRR, Section 9.5 (Batch Zero Refinement and Delivery of Transmission Plan) and Nodal Protocol Section 3.11.4

## Slide 49: Steady-State Batch Study process: 6-month study cadence with continuous planning integration
Year 1
Year 2
Year 3
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Jan
Feb
Mar
Apr
May
Jun
Jul
Aug
Sep
Oct
Nov
Dec
Jan
Batch refinement and transmission plan finalization​
Batch refinement and transmission plan finalization​
6-month study
6-month study
6-month study
Batch Study process going live
Batch 0
Activity
Batch 1
Batch 2
Following completion of the batch study and confirmation of commitments, ERCOT advances the resulting transmission plan through the RPG process for stakeholder review and governance approval
A new batch begins every six months, ensuring predictable decision cycles without processing gaps and building on upgrades approved in prior cycles
ILLUSTRATIVE

## Slide 50: Fundamental Principles for ERCOT's Proposed Batch Zero Criteria
Senate Bill 6 and PUC Gating Rules: Utilize the gating criteria reflected in Project No. 58481 rulemaking to determine which large loads should be confirmed firm and which should be included to be studied in Batch Zero
Pre-Transition Processes: Respect to the extent feasible already granted approvals, including approval to energize and approved studies
Large Load Near-Term Energizations: Assess development activity for large loads that declare 2026 or 2027 energization to evaluate schedule feasibility
ERCOT’s Reliability Responsibility: Ensure all Large Loads confirmed to be firm in Batch Zero have been studied to show that the load can be served reliably
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 51: Eligibility flowchart: how to assess if a load is included for Batch Zero?
1. See Batch Zero PGRR, Section 9.2.1.1(1)(a)–(b) (Eligibility Criteria for Inclusion as Base Load — Energized Loads) | 2. See Batch Zero PGRR, Sections 9.2.1.1 and 9.2.1.2 (Initial Energization date thresholds for Batch Zero eligibility) | 3. See Batch Zero PGRR, Sections 9.2.1.1(1)(c)–(e) and 9.2.1.4 (Base Load eligibility pathways and evaluation of existing studies) | 4. See Batch Zero PGRR, Section 9.2.1.1 (Eligibility criteria for inclusion as base load) | 5. See Batch Zero PGRR, Section 9.2.1.2(1) (Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero) | 6. See Batch Zero PGRR, Section 9.2.1.1 (Eligibility and modeling for base load) | 7. See Batch Zero PGRR, Sections 9.2.1.2 and 9.4 (Inclusion as studied load and MW allocation through Batch Zero results) | 8. See Batch Zero PGRR, Sections 9.2.1.3 and 9.2.2 (Load Not Included in Batch Zero)
Source: PGRR Batch Zero, March 17 2026
Has the load already achieved Initial Energization?1
Large Load request
Included in Batch Zero as a base load6
Not included in Batch Zero8
Studied in Batch Zero and will receive load allocation amounts7
Yes
Is the requested Initial Energization date on or before December 31, 2027?2
No
Does the load, by the required deadline, either: (i) qualify via QSA / interim VRT inclusion and required attestations; OR (ii) have complete and valid studies, an executed Interconnection Agreement, and required development activity?3
Yes
Has the load executed an Intermediate Agreement and met the applicable eligibility criteria for inclusion as load to be studied?5
Does the load meet the eligibility criteria for inclusion as base load (including execution of an Interconnection Agreement)?4
Yes
Yes
No
Yes
No
1
2
4
3
3
5
X
Reference tracker
No
No
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 52: Deep-dive: “Included as base load” (1/2)
If your Large Load by June 1, 2026 | Treatment in Transitional Process | MW Allocation
Is Operational or Approved to Energize | Included as base load | Loads operational before ERCOT’s interim LLI process will be allocated the MWs modeled in the 2025 RTP Loads operational after ERCOT’s interim LLI process will be allocated the lesser of: MWs modeled in the 2025 RTP less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs included in their Load Commissioning Plan, if applicable, less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs in an updated ramp schedule as provided to the DSP by June 1, 2026 Loads not yet operational will be allocated the lesser of: MWs that can be reliably served as indicated in their interconnection studies MWs included in their interconnection agreement and reflected in their financial security
MW Allocation
If your Large Load
  Achieved Initial Energization before March 25, 2022; or
  Achieved Initial Energization between March 25, 2022, and July 10, 2026
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
  Large Loads that achieved Initial Energization before March 25, 2022, shall be modeled at the level of peak Demand reported to ERCOT as part of development of the 2026 RTP
  Large Loads that achieved Initial Energization between March 25, 2022, and July 10, 2026, shall be modeled at the lesser of:
    The level of peak Demand reported to ERCOT as part of development of the 2026 RTP; or
    The level of peak Demand indicated in the most recent Load Commissioning Plan (if applicable) provided to ERCOT on or before July 24, 2026
  Large Loads meeting base load eligibility criteria that are not yet operational will be modeled at the lesser of:
    The level of peak Demand that can be served reliably as indicated in the Large Load’s complete and valid existing studies
    The level of peak Demand specified in the executed Interconnection Agreement meeting Section 9.7.2
1
Reference: Batch Zero PGRR, Section 9.2.1.1(1)(a)–(b) and 9.2.1.1(2)(a)–(c) (Eligibility and Modeling for Base Load)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 53: Deep-dive: “Included as base load” (2/2)
If your Large Load
  Has a requested Initial Energization date on or before December 31, 2027, has complete and valid interconnection studies, has executed an Interconnection Agreement by the required deadline, and has satisfied required equipment procurement and development attestations
  Has a requested Initial Energization date on or after January 1, 2028, and either (i) has complete and valid interconnection studies and (ii) executed an Interconnection Agreement by the required deadline
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
MW Allocation
  Large Loads meeting base load eligibility criteria that are not yet operational will be allocated the lesser of:
    The level of peak Demand that can be served reliably as indicated in complete and valid existing studies; or
    The level of peak Demand specified in the executed Interconnection Agreement meeting Section 9.7.2.
1
Reference: Batch Zero PGRR, Section 9.2.1.1(d)–(e) (Eligibility and Modeling for Non-Energized Base Load)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 54: Deep-dive: “Studied in Batch Zero”
If your Large Load
Treatment in Transitional Process
MW Allocation
  Has a requested Initial Energization date on or before December 31, 2027, does not meet the eligibility criteria for inclusion as base load under Section 9.2.1.1, and has executed an Intermediate Agreement meeting Section 9.7.1; or
  Has a requested Initial Energization date on or after January 1, 2028, meets the applicable study requirements (including evaluation of existing studies under Section 9.2.1.4), and has executed an Intermediate Agreement meeting Section 9.7.1 by the required eligibility deadline (ILLE deadline: July 10, 2026; TDSP/TSP notification: July 24, 2026)
  Studied in Batch Zero
  To be determined during Batch Zero study and reflected in the Load Commissioning Plan (LCP)
2
Reference: Batch Zero PGRR, Sections 9.2.1.2(1)(a)–(b) and 9.7.1 (Eligibility for Inclusion as Load to be Studied)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 55: Interconnection Studies – Treatment of complete and valid existing studies
  ERCOT has determined that the Large Load has a complete and valid set of interconnection studies (as determined through the process on the next slide) that accurately reflect current system conditions and are suitable for eligibility treatment
    Studies that met the required criteria on or before March 4, 2026 are deemed to be complete and valid without further review
  ERCOT has determined that existing studies support inclusion as studied load, subject to meeting eligibility requirements under Section 9.2.1.2
Complete and valid existing studies
3
Reference: Batch Zero PGRR, Sections 9.2.1.4 and 9.2.1.1–9.2.1.2 (Evaluation of Existing Studies and Eligibility Treatment)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 56: ERCOT sequentially evaluates legacy interconnection studies based on timing to determine eligibility for treatment as base load
Key takeaways
Step 1: Date ordered list
Step 2: Sequential Evaluation
RPG A – Loads 1&2 (Apr 15, 2026)
RPG C – Loads 1, 2, 3 (Jun 10, 2026)
LLIS – Load 2 (May 3, 2026)
LLIS – Load 1 (Apr 28, 2026)
LLIS – Load 3 (Jun 22, 2026)
RPG B – Load 1 (May 3, 2026)
LLIS – Load 4 (Jul 8, 2026)
Process for evaluating study validity for loads that qualify after March 4
RPG
LLIS
Source
Loads with a milestone date1 on or before March 4, 2026 are considered to have valid studies with no additional evaluation
ERCOT orders remaining loads sequentially by milestone date to evaluate legacy interconnection studies
  If two loads share the same date, RPG-endorsed load(s) are evaluated first (tie-breaker rule)
Milestone date depends on interconnection pathway:
  RPG loads - date of RPG endorsement
  LLIS loads - date legacy PG 9.4 and 9.5 satisfied
Earlier loads are validated first; subsequent ones remain valid only if previously validated loads are either outside the study area or included in the study
1
Source: ERCOT PGRR145, Section 9.2.1.4, Evaluation of Existing Studies for Large Loads, as modified by ERCOT March 17 comments
1. Milestone date reflects the date a load meets applicable eligibility criteria (RPG endorsement or completion of LLIS requirements, including execution of an interconnection agreement)
RPG A – Loads 1&2 (Apr 15, 2026)
RPG C – Loads 1, 2, 3 (Jun 10, 2026)
LLIS – Load 2 (May 3, 2026)
LLIS – Load 1 (Apr 28, 2026)
LLIS – Load 3 (Jun 22, 2026)
RPG B – Load 1 (May 3, 2026)
LLIS – Load 4 (Jul 8, 2026)
1
✔
✔
✔
✔
✔
LLIS – Load 2 (May 3, 2026)
✘
LLIS – Load 3 (Jun 22, 2026)
✘
3

## Slide 57: Deep-dive: “Not included in Batch Zero”
If your Large Load
Treatment in Transitional Process
MW Allocation
  Does not meet all applicable eligibility criteria in Sections 9.2.1.1 or 9.2.1.2; or
  Has studies that are sufficient for inclusion under Section 9.2.1.4 but does not meet the eligibility criteria in Section 9.2.1.2; or
  Not included in Batch Zero
  No MW allocation in Batch Zero
  May seek inclusion in a future batch process if eligibility criteria are met
4
  Fails to provide all required project information under Section 9.2.2 on or before the required submission deadline (July 10, 2026; T(D)SP notification by July 24, 2026)
Reference: Batch Zero PGRR, Sections 9.2.1.3 and 9.2.2 (Load Not Included in Batch Zero)
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 58: Demonstrated Development Activity
Large Loads with requested Initial Energization dates on or before December 31, 2027 have two paths to demonstrate development progress:
The Large Load was included in a Quarterly Stability Assessment or was included in an interim voltage-ride-through assessment on or before May 1, 2026 and the TSP/DSP has provided both of the following to ERCOT by July 24, 2026;
    Confirmation the ILLE has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence supporting the attestation; and
    An attestation the TSP/DSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance of the requested Initial Energization date so equipment can be installed by December 31, 2026
OR
The Large Load has been found to have valid studies by ERCOT according to PG 9.2.1.4 and the TSP/DSP provides all of the following on or before July 24, 2026:
    A notarized attestation that the ILLE has executed an interconnection agreement that meets the requirements defined in Section 9.7.2;
    An attestation the TSP/DSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance of the requested Initial Energization date the equipment can be installed by the ILLE’s requested Initial Energization date;
    Confirmation the ILLE has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence supporting the attestation; and
    Confirmation the ILLE has purchased all necessary ILLE-owned high-voltage transformers and circuit breakers and will take delivery sufficiently in advance so the equipment can be installed by the ILLE’s requested Initial Energization date
5
Reference: Batch Zero PGRR, Section 9.2.1.1(1)(c)–(d) (Development activity attestation / QSA or valid studies + IA pathways)
XXX Changes/ Clarification vs. Mar 10th Workshop

## Slide 59: Incorporating PUC Project 58481 into Batch Zero: Two Implementation Pathways
2026
2027
Q2
Q3
Q4
Q1
Case building
  Batch Zero Study
  Illustrative publication date of Project No. 58481
Deferred launch of Batch Zero
No need for re-alignment if adopted 58481 rule is different from published draft
Case building
Batch Zero Study
Potential re-alignment needed if adopted 58481 rule is different from published draft
Early launch of Batch Zero
Project 58481 will define readiness and financial commitment standards for Large Loads. ERCOT must determine how to align Batch Zero timing with this rulemaking
Context
  Description: embed the embed the PUCT proposal for publication (Project No. 58481) concepts directly into the PGRR language and update the PGRR with the published PFP once available
  Implications
  Enables earlier Batch Zero launch
  Uses proposed draft for intermediate agreement and interconnection agreement criteria
  Risk of misalignment if final rule differs from draft
  Description: draft PGRR to reference the final adopted 16 TAC §25.194 and begin Batch Zero a defined period (e.g., X days) after the rule becomes effective
  Implications
  Batch Zero will be aligned with final PUC rule
  May delay Batch Zero start depending on rule adoption timeline
Illustrative timeline
Option 1: Replicate the Draft 58481 PFP in the PGRR (proceed in parallel)
Option 2: Tie PGRR to Final Adopted 58481 Rule (sequential alignment)
Option
Description and implications

## Slide 60: Stakeholder feedback received to date
Source: ERCOT PGRR145 “Key Documents” section
Author
G
Date of submission
Mar 5; Mar 11; Mar 19
Mar 9; Mar 20
Mar 9; Mar 20
Mar 10
Mar 19
Mar 19
Mar 20
Mar 20
Mar 19
Mar 20
Mar 20
Schaper Energy Consulting
Reliant Energy1
Crusoe
Rose City Partners
Lancium
Skybox Datacenters
Oncor
CenterPoint Energy
IREN
Stream Datacenters2
Agentic Infrastructure1
Provident Inc.2
Mar 20
3-Waters Technical Services
Vistra
Eolic
TEBA
Satoshi Energy
Black Mountain
Sandow Lakes Energy
Emerald AI
AEP
Monarch Energy
Crow Holdings
Zero Emission Grid
Author
Date of submission
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
1. Agentic and Reliant filed comments together on Mar 20 | 2. Stream Datacenters and Provident filed comments together on Mar 20
Note: based on list of comments submitted as of 3/23

## Slide 61: Stakeholder feedback highlights: key themes across submissions
Source: ERCOT PGRR145 “Key Documents” section
Recurring feedback
Description
Treatment of advanced and legacy projects
Projects that have completed legacy LLIS processes (studies, IA execution, financial commitments, construction start) are viewed as already demonstrating firm readiness: re-assessment or reclassification at this stage raises concerns around investment certainty and financing risk
1
Timing framework and transition fairness
Current cutoff dates (e.g., March–July 2026 window) are perceived as creating inconsistent outcomes for projects with similar readiness, particularly where progress depends on ERCOT/TSP processing timelines: greater alignment between readiness and eligibility timing is sought
2
Eligibility and prioritization criteria
Preference for prioritization based on objective project maturity (studies, IA, financial commitment, construction) rather than timing metrics alone. RPG-backed projects are also viewed as valid pathways given their higher level of technical review, when combined with demonstrated readiness
3
Financial requirements and regulatory alignment
Concerns on potential duplication of financial obligations (e.g., CIAC vs. new security/fees), treatment of projects with no network upgrades, and alignment with ongoing PUCT rulemaking (Project No. 58481): request for mechanisms for crediting prior commitments and ensuring consistency with final rules
4
Process clarity, governance, and implementation
Feedback highlights the need for clearer definition of roles (ERCOT vs. TSP/DSP), standardized agreements and attestations, consistent modeling inputs, and greater transparency in study scope, assumptions, and outputs to support implementation
5
Note: based on list of comments submitted as of 3/23

## Slide 62: Stakeholder feedback concentrates on legacy project treatment and study validity in Batch Zero
Chart: 
 | 21 | 8 | 8 | 4 | 2 | 2 | 2 | 1 | 1
Comments received by section, # of comments1
Key takeaways
1. Each referenced section is counted once for each stakeholder; repeated mentions of the same section within a stakeholder’s comments are considered a single reference | Note: based on list of comments submitted as of 3/23
  Feedback is concentrated on treatment of legacy projects and prior study outcomes (Sections 9.2)
  Strong push to preserve investment-backed outcomes and avoid retroactive re-evaluation (e.g., executed IAs, completed studies, and committed capital should not be re-opened)
  Investment certainty is the central concern, particularly around re-studies, MW reallocation, and timing-based eligibility cutoffs
  Financial commitment requirements are comparatively less debated, with feedback primarily focused on implementation details (e.g., alignment with PUCT rules, avoiding duplication) rather than overall framework design
Detailed next
Main stakeholder feedback
  Eligibility and study framework (9.2)
  Cross-cutting
  Commitment criteria and agreements (9.7)
  Quarterly stability requirements (5.3)
  Energization and ongoing obligations (9.6)
  Batch study methodology (9.3)
  Ensure previously approved and mature projects are automatically recognized as Base Load (e.g., avoid re-evaluation, circular requirements, or exclusion of equivalent study pathways)
  Improve governance clarity and transparency across Batch Zero (e.g., clear roles ERCOT vs TSP/DSP, limit discretion, standardize processes, align with PUCT, enhance communication)
  Align financial requirements with PUCT and avoid duplicative obligations for legacy projects
  Consider chronological prioritization as an alternative to current allocation approach
  Align stability timelines with Batch Zero and clarify dynamic model responsibilities
  Ensure advanced projects continue without re-screening, delay, or reset
  Batch Zero refinement and transmission plan (9.5)
  Enhance TSP coordination, short circuit scope, and ensure upgrades support full load
  Load modeling and integration (6.6)
  Clarify modeling entry requirements and treatment of co-located or modified loads
  ILLE commitment and agreement execution (9.4)
  Extend commitment timelines and reduce risk from compressed agreement execution windows
Source: Batch Zero PGRR145 Stakeholder Comments

## Slide 63: Deep dive: Section 9.2 stakeholder feedback on eligibility and study validity
Chart: 
 | 16 | 11 | 4 | 3 | 2 | 1
Comments received by section, # of comments1
Main stakeholder feedback
  Study validity and ordering (9.2.1.4)
  Base load eligibility (9.2.1.1)
  Applicability framework (9.2.1)2
  Studied/allocated load (9.2.1.2)
  Commitment window (9.2.4)
  Submission requirements (9.2.2)
Key takeaways
  Section 9.2 dominates stakeholder concern, led by study validity and base load eligibility
  Protection for advanced projects is the clearest theme: stakeholders want safe harbor and no retroactive re-screening
  Eligibility is seen as too narrow and should recognize RPG, RTP, CLR/BYOG, and co-located generation pathways
  Process clarity remains a major issue, especially around timing, dynamic data, and ERCOT/TSP/DSP roles
Detailed next
  Expand safe harbor treatment for completed studies, executed agreements, financial commitment, and co-located/FIS-supported loads
  Clarify how Batch Zero applies to non-Batch projects and preserve parallel advancement pathways
  Broaden eligible pathways to include RPG-qualified, CLR/BYOG, and other substantively committed projects
  Clarify dynamic data standards and assign a consistent authority for impact determinations
  Extend the agreement-execution window and reduce pressure from compressed deadlines
1. Each referenced section is counted once for each stakeholder; repeated mentions of the same section within a stakeholder’s comments are considered a single reference | 2. Section 9.2.1 comments are cross-cutting comments addressing multiple sub-sections within 9.2.1 | Note: based on list of comments submitted as of 3/23
  Limit prior-study invalidation and use objective readiness and chronology, while recognizing valid RPG/RTP-backed projects
Source: Batch Zero PGRR145 Stakeholder Comments

## Slide 64: Study validity and re-evaluation (9.2.1.4): stakeholder feedback deep-dive
Source: Batch Zero PGRR145 (March 4) Stakeholder Comments
Protection of completed studies
Studies completed under Sections 9.4 and 9.5 should be treated as final and not subject to retroactive re-evaluation or re-determination, as this undermines investment certainty and reliance on prior approvals
Establish a safe harbor whereby completion of §§9.4 and 9.5 constitutes a complete and valid study, not subject to retroactive review under §9.2.1.4
Batch Zero should not re-order or invalidate advanced projects
Technically mature and financially committed projects should be treated as fixed base load inputs and not re-screened, re-prioritized, or displaced based on timing or interdependencies
Clarify that advanced-stage projects are preserved as base load and not subject to re-prioritization or displacement
Study validity should reflect project maturity (not timing alone)
Current proposals rely on proxies (e.g., RPG submission timing, ERCOT discretion) that do not reflect actual project maturity, risking exclusion of advanced projects
Base study validity and prioritization on completion of LLIS (or equivalent) and demonstrated commitment, rather than timing-based criteria
Main points
Description
Note: Comments reflect stakeholder feedback on both the March 4 PGRR draft and subsequent ERCOT comments issued on March 17
(Partially) Addressed by ERCOT comments on Mar 17
Stakeholder suggestion
Recognition of RPG/RTP-backed pathways
Projects supported by RPG or RTP processes are viewed as having undergone substantial technical review and should be recognized where combined with demonstrated readiness
Allow RPG/RTP-backed projects to qualify where technical review and project readiness requirements are met

## Slide 65: Base load eligibility criteria (9.2.1.1): stakeholder feedback deep-dive
Source: Batch Zero PGRR145 (March 4) Stakeholder Comments
Main points
Stakeholder suggestion
Protection of advanced projects from re-evaluation
Grant automatic Base Load classification to projects with completed studies, executed IA/FEA, and demonstrated commitment, without re-evaluation under §9.2.1.4
Recognition of equivalent study pathways (LLIS/FIS)
Allow completed FIS (incl. co-located load) to qualify as Base Load where requirements are met
Circularity and timing of attestation requirements
Description
Projects that completed LLIS (or equivalent FIS1) and demonstrated financial commitment should be treated as firm and not subject to re-evaluation or reclassification, as this undermines financing and reliance on prior approvals
FIS studies for co-located load should be explicitly recognized as equivalent to LLIS, ensuring otherwise qualified projects are not excluded from Base Load eligibility
Attestation requirements require capital commitment before Base Load status or MW allocation is confirmed, creating a circular and unworkable process
Confirm Base Load eligibility before requiring attestations or condition attestation requirements on confirmed eligibility
1. Full Interconnection Study (performed for a generation project)
Timing gap (“commit before certainty”)
Developers are required to make binding procurement and construction commitments before receiving confirmation of Base Load status, creating an “air gap” that introduces material investment risk
Align timing by confirming eligibility before requiring commitments, or remove requirements within the gap
Note: Comments reflect stakeholder feedback on both the March 4 PGRR draft and subsequent ERCOT comments issued on March 17
Eligibility should reflect demonstrated financial commitment
Financial commitment (e.g., CIAC, equipment procurement, capital deployment) is viewed as a primary indicator of project readiness and should be treated as equivalent to executed agreements for Base Load eligibility
Allow demonstrated financial commitment to qualify projects for Base Load eligibility, even where an IA has not yet been executed

## Slide 66: Frequently Asked Questions (1/3)
Source: ERCOT discussions, Feb 26th LLI Batch Study Workshop
Batch Zero process timeline and decision points
Batch Zero and planning integration
“When will the Batch Zero Study allocation be finalized and communicated?”
Allocation timing is tied to completion of the Batch Zero study phase. Under the draft PGRR145 timeline, allocation results would be issued in January 2027; final dates will be confirmed following finalization of PGRR145
“Can the 30-day commitment window be extended?”
ERCOT intends to maintain a 30-day commitment window consistent with the draft PFP in PUCT Project No. 58481. The full Batch Zero schedule, including the commitment deadline, will be published in advance
“How can Batch 1 proceed before Batch Zero Year-6 transmission solutions are fully identified and vetted?”
Under a 6-month cadence, each batch produces actionable results for Years 1–5, while Year-6 transmission solutions may continue through the RTP/RPG process. This reflects a tradeoff between speed and full transmission vetting
“What is the date for meeting commitment criteria?”
The date for meeting commitment criteria is proposed as March 1, 2027, in PGRR145 (9.3.1)
“Is it possible to include a second, post-refinement decision point for participant opt-out?”
ERCOT is designing Batch Zero with one binding commitment point. Refinement does not change the committed ramp and is not intended to increase costs; it only finalizes the transmission solution. A second opt-out would reintroduce restudy loop risk
Topic
Representative question
ERCOT answer

## Slide 67: Frequently Asked Questions (2/3)
Source: ERCOT discussions, Feb 26th LLI Batch Study Workshop
Topic
Representative question
ERCOT answer
“How are in-flight RPG projects incorporated into Batch Zero?”
Projects that have progressed through RPG and received endorsement at the start of Batch Zero will be treated consistent with established planning practices and be incorporated into Batch Zero study
“How does Batch Zero interact with the 2026 and 2027 RTP?”
Based on the current sequencing, Batch Zero will not affect the 2026 RTP because commitment occurs after the 2026 RTP modeling cycle is complete. Loads that meet commitment milestones in March 2027 may be incorporated into the 2027 RTP. Final timing alignment depends on finalization of PGRR145 and publication of the Batch Zero schedule
Batch Zero and planning integration
Transmission upgrades
“How are multi-year (Year-6) upgrades and base cases handled?”
ERCOT recognizes that Year-6 solutions may involve complex, multi-year transmission upgrades. Batch Zero establishes a committed load baseline and provides earlier clarity on required improvements. Long-duration upgrades will continue to proceed through established transmission planning processes, including RTP and RPG pathways
“If no reliable transmission solution exists within the study horizon, how will allocated MW be handled?”
Within Years 1–5, ERCOT will allocate the MW that can be reliably served based on existing system capability. Projects may receive partial allocations during this period if constraints exist. By Year 6, assumption is that RTP process will identify the transmission upgrades necessary to serve the full committed load. Accordingly, Year 6 reflects full service (100%) of the committed MW

## Slide 68: Frequently Asked Questions (3/3)
Source: ERCOT discussions, Feb 26th LLI Batch Study Workshop
Topic
Representative question
ERCOT answer
Allocation outcomes and ramp schedules
“If a project drops out, are MWs reallocated within the same batch?”
No. ERCOT is not planning to reallocate MWs within Batch Zero after commitment because it creates complexity and reopens restudy cycles. Additional MWs would generally be addressed in subsequent batches, maintaining process stability and schedule certainty
“Can ERCOT change the MW allocations after commitment?”
No. For Batch Zero after the commitment point, the MW allocation by year is locked. The refinement phase is intended to finalize only the transmission plan, not reduce MW or delay delivery years for committed MW
Financial security and cost responsibility
“Are financial obligations (including CIAC and security) locked at commitment?”
Based on the draft PFP for PUCT Project No. 58481, ERCOT is proposing that financial obligations are established and locked at the commitment point. The refinement phase may adjust transmission solution details, but it is not intended to re-price commitments or introduce post-commitment true-ups. The process is designed to provide cost certainty and avoid reopening financial obligations in subsequent planning steps
Study modeling
“How will additional generation be modeled in Batch Zero?”
ERCOT will apply the methodology established in PGRR127 when modeling additional generation in Batch Zero Study cases. The modeling approach and associated assumptions will be documented in the published case assumptions to ensure transparency and consistency
“Does Batch Zero include a low-solar scenario?”
The Batch Zero Study includes a no-solar scenario intended to reflect stressed conditions