## Slide 1: Large Load Interconnection Batch Study Workshop
April 2, 2026
ROS Update

## Slide 2: The batch study process increases outcome certainty and transparency while limiting restudy risk
…to the new batch study process
ERCOT action
Non-ERCOT action
Communication point
Dev. submits project to TSP
Single study
Single study (invalidating prior results)
Initial approval
Single study (invalidating prior results)
Initial approval
RPG, QSA
Energization
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
RPG, QSA
Energization
Batch study: ERCOT compiles applications, studies together as a batch, and allocates load
C
From the existing single study process…
A
Frequent restudies required If another project impacts the same transmission zone, all previous studies are invalidated and impacted projects which haven’t yet energized must be restudied
B
Restudy loop In the absence of capacity reservation, projects can be repeatedly pulled into restudies as new requests enter the system, delaying approvals and potentially extending timelines by years
C
Batching process Every ~6 months, all submitted requests are clustered and studied together; allocated capacity coming out of the study is “reserved” to prevent restudies
Transparent communications Along with the new batch study process, ERCOT is redesigning the study communication process to have clearly defined touchpoints and transparent information handovers
B
Source: ERCOT discussions
Dev. submits project to TSP
Dev. submits project to TSP
Single study (invalidating prior results)
Single study (invalidating prior results)
Initial approval
Initial approval
Initial approval
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
Dev. submits project to TSP
A
A
A
A

## Slide 3: Batch Zero Revision Request Timeline
Forums
Workshops and working groups
PRS (Protocols Review Subcommittee)
ROS (Reliability and Operations Subcommittee)
TAC
ERCOT Board
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Update 3/5
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
8/1 Target effective date of protocols
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
Preview structure/governing concepts of Batch Zero NPRR before filing
Confirm proposed protocol changes are ready for governance review
Endorse NPRR for advancement to TAC (contingent on technical valid.)
If accompanying PGRR filed, then ROS will be involved in review
ROS approval will be required for any PGRR(s).
Review/endorse combined NPRR/PGRR package for Board approval
Authorize implementation of Batch Zero by approval of NPRR/PGRRs
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Target Board approval date
Board Meeting 4/20
Regular PRS 4/15
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Note that TAC leadership is involved in considering options to ensure successful review and approval
Special PRS 4/22
Regular TAC 4/29
Special TAC 5/13
PRS Vote 5/6
4
Monthly LLWG updates
4/8 ERCOT files CLR/BYOG Revision Request(s)
ROS Update (special) 4/14
ROS Update (special) 4/23

## Slide 4: Reminder of Scope and Priorities for Workshops
March 4 filings completed for Batch Zero: ERCOT filed the Batch Zero PGRR145 and related NPRR1325 on March 4, initiating the formal governance process and aligning with the May PRS/ROS/TAC sequence and June 1 Board target reflected in the critical path timeline
  March 17 ERCOT comments filed: ERCOT submitted follow-up comments on PGRR145 (March 17) in response to stakeholder feedback on the March 4 draft, introducing targeted refinements (e.g., safe harbor for legacy LLIS, revised deadlines, alignment with PUCT PFP)
  Workshop #5: review of 21 stakeholder comments
  Workshop #6: focused on four major themes/issues
  April 3: Target for ERCOT second set of comments
  April 9: Workshop #7: discussion of ERCOT and stakeholder comments
Additional filings on target (CLR and BYOG): ERCOT is advancing targeted revision requests to clarify CLR and BYOG treatment and is currently targeting April 8 filing CLR, TBD for BYOG
Long-term Batch Process revisions: development of the enduring batch framework is out of scope for the current filing. ERCOT will incorporate lessons learned from Batch Zero to inform future revision requests and the design of a durable, repeatable batch study process

## Slide 5: Batch Workshop #6 Update
Timeline and governance recap
Update on timeline and key workshop dates
Outline PRS/ROS/TAC pathways to June Board with key submission dates
1
Eligibility and March 4th cutoff date discussion
Understand the trade-off between investment certainty and system reliability
Review proposed Batch Zero inclusion and treatment, including how outcomes vary based on study completion timing and milestone achievement
3
Year 6 transmission
Assess alternative approaches for Year 6 MW allocation
4
5
CLR discussion
Advance discussion on CLR framework for Batch Zero
6
BYOG discussion
Vetting the Self-Limiting Facility (SLF) option
Gathering stakeholder input on key design and implementation questions
7
Q&A
Open forum for Batch Zero concerns, comments, and suggestions
2
Market Comments filed on NPRR/PGRR
Review new stakeholder comments

## Slide 6: End- Questions? Appendix of 4 Topic Highlights

## Slide 7: Eligibility: Defining study validity: trade-off between certainty and system reliability
Automatic study validation – All studies approved prior to Batch Zero are valid
A
Large Load with a study approved prior to July 10
Area where grid cannot reliably supply all the approved load in all conditions
B
Automatic study validation before March 4 and coordinated study validation after, using PGRR145
Large Load with a study approved prior to March 4 deemed valid
Large Load with a study approved between March 4 and July 10 that may receive a MW amount lower than the initially approved study
Areas where grid cannot reliably supply all the approved load in all conditions are avoided
The topic receiving the most comments in PGRR145 is the proposed study validity check for studies completed after March 4, 2026
ERCOT proposed this check to ensure the base load level in Batch Zero does not exceed transmission system reliability limits

## Slide 8: Proposed Batch inclusion and treatment depend on timing of study completion and milestone achievement
March 1
Studies
Eligibility
Inclusion
Treatment
Legacy
Project has complete and valid studies as of March 4, 2026 under PGRR145 Section 9.2.1.4(3) (i.e., LLIS completed and interconnection agreement executed under PGRR115 Sections 9.4 and 9.5)
Batch Zero
If meeting Section 9.2.1.1: modeled as Base Load not subject to additional study
If meeting Section 9.2.1.2: studied and allocated based on amount of load that may be served reliably
Milestone timeline
Batch implications
2026
2027
Q1
Q2
Q3
Q4
Q1
Q2
March 4
Batch Zero
Project meets eligibility criteria under PGRR145 Sections 9.2.1.1 or 9.2.1.2 by July 10, 2026 (with DSP/TSP submission by July 24), and does not qualify under Section 9.2.1.4(3)
PGRR115 process stops on July 10, 2026
Batch Zero
Prior studies (if any) are subject to ERCOT validation and project ordering under Section 9.2.1.4
If meeting Section 9.2.1.1: modeled as Base Load not subject to additional study
If meeting Section 9.2.1.2: studied and allocated based on amount of load that may be served reliably
July 10
Batch 1
Project does not meet Batch Zero eligibility criteria under PGRR145 by July 10, 2026 (i.e., has not met required LLIS milestones under PGRR115)
Batch 1
Batch 2+
Projects not included in Batch 1 (e.g., after March 2027 cutoff)
Batch 2+
Studied and allocated in subsequent batch process; MWs determined based on amount of load that may be served reliably

## Slide 9: Proposed Batch inclusion and treatment depend on timing of study completion and milestone achievement
3/4/26
7/10/26
3/1/27
LLIS studies are deemed complete and valid*
LLIS studies may be deemed complete and valid*
* LLI projects must also meet Planning Guide Section 9.5
LLIS studies no longer accepted; if not in Batch Zero, wait for Batch 1
If not in Batch 1, wait for Batch 2
Batch Zero
Batch 1
LLIS (“PGRR115”)

## Slide 10: PGRR145 Study Validity FAQ
Q: Is March 4, 2026 a retroactive cutoff date in PGRR145 for LLIS and RPG studies to be deemed valid?
A: No. Studies that are approved for LLI projects meeting Planning Guide Section 9.5 may still be deemed valid until July 10, 2026 if no other LLI projects that impact the reliability study results (i.e., in the study area and not included in the study) achieve this status before them.
Q: How will ILLEs for LLI projects with approved studies and meeting Planning Guide Section 9.5 after March 4, 2026 know that their studies have been deemed valid?
A: Going forward, ERCOT will provide periodic updates to the interconnecting TSPs regarding LLI study validity for all LLI projects.
Q: Will the current LLIS process (“PGRR115 process”) continue for LLI projects that do not qualify to be included in Batch Zero?
A: No. As proposed in PGRR145, the PGRR115 process will cease on July 10, 2026. Going forward, all LLI projects will need to be included in a batch study as a condition for being included in a planning load forecast and for being approved to energize. If an LLI project does not qualify to be included in Batch Zero, they may be eligible for inclusion in Batch 1, pending TBD requirements.

## Slide 11: Two approaches to allocating future MWs: early certainty vs. alignment with transmission development
PGRR145 Approach
Alternative approach to address TSP comments
Source: ERCOT discussions
Example: 1,000 MW data center requiring full capacity by Year 6
Years 1-5
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Request studied in Batch Zero: initial MWs allocated based on system capability; transmission constraints and required upgrades identified
Considerations
Provides certainty by guaranteeing full MWs by Year 6
Creates a potential step-change in MWs between Years 5 and 6, with limited time to develop required transmission
Full MW allocation is aligned with identified transmission upgrades
Requires financial commitment for partial MWs without clear visibility on timing or certainty of full MW delivery
Year 6
Full MW automatically allocated based on Batch Zero results; transmission solutions further defined in the 2027 RTP
Full MW not committed in Batch Zero; additional MWs studied and allocated through a subsequent Batch 1 process
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 1000
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
Illustrative allocation, MW
Chart: 
 | 100 | 100 | 450 | 600 | 600 | 600
 | 400
Year 1
Year 2
Year 3
Year 4
Year 5
Year 6
TBD
Automatically set at requested peak Demand
TBD: additional MWs studied in next batch and allocated based on available capacity

## Slide 12: Concept Review - CLR
Source: ERCOT discussions
Point of interconnection
Large Load registers entirely as a CLR without any type of netting with generation or storage
Load-Only CLR leverages the existing CLR framework as the simplest near-term option,1 subject to required market/system implementation items (e.g., SCED CLR Bid Curve capping enhancements) before energization
Participates as dispatchable demand and must follow SCED basepoints within its registered operating range (PC/LPC/MPC)
No assurance of service above awarded firm MW; real-time consumption may be reduced below PC based on system conditions and SCED CLR Bid Curve capping
ERCOT observes and verifies performance based on net MW at the POI and adherence to SCED dispatch instructions
Must meet existing CLR telemetry and dispatch performance requirements (subject to SCED instructions and registered operating limits)
Load may register operational capability above awarded firm MW, subject to real-time dispatch and congestion mitigation2
Illustrative example
  150 MW requested in Year 1
  ERCOT performs steady-state and stability studies and allocate phased MW (e.g., 100 MW in Years 1–2, 300 MW in Years 3-4, until transmission upgrade in Year 5)
  Operational parameters:
    PC = 0–100 MW (firm)
    LPC = 0–100 MW
    MPC = 150 MW (upper operational capability; not a planning guarantee)
    CLR quantity may be modified in later years as transmission capability increases
1. NPRR1188 later in 2026: Nodal pricing align local congestion prices. NPRR1255 mitigation methods needed (small project) | 2. Potentially subject to additional limits identified in dynamic studies
Description
Details
Load
Illustrative scheme
Chart: 
 | 100 | 100 | 300 | 300 | 1000
 | 50 | 200 | 200 | 400
50
Year 1
Year 2
Year 3
Year 4
Year 5
150
300
500
700
CLR Load
Firm Load
POTENTIALLY FEASIBLE CONFIGURATION
ERCOT grid
XXX Changes/Clarification vs. Mar 10th Workshop

## Slide 13: Provisional CLRs – Structure of Revision Requests1
Will consist of a PGRR and companion NPRR
Modular structure adds to PGRR145 and NPRR1325
  Example – Section 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs) compliments Section 9.2.2 as written in PGRR145
This structure will allow the CLR Revision Requests to move forward in parallel with PGRR145 and NPRR1325 if possible, without interfering with the core Batch Zero language
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 14: Provisional CLRs – Definition1
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
New Resource Type: ‘Provisional CLR’
Same as a CLR but locked in for a period of time and has Low Power Consumption (LPC) limits defined in the Batch Zero Interconnection Study
What’s different?
P-CLR load bids can be ‘capped’ to mitigate transmission constraints identified in SCED
P-CLR bids are capped dynamically (“last-in-line/just-in-time”) in each run of SCED to a price that will just allow SCED to resolve a constraint
Submits CLR Energy Bid Curve  bid-to-buy prices between Maximum Power Consumption (MPC) and Low Power Consumption (LPC) – same as any other CLR

## Slide 15: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
ERCOT validates completion of all steps prior to granting Approval to Energize
8
QSE establishes required ICCP telemetry points
7
RE coordinates with ERCOT to establish metering and submit CLR parameters via RIOO
6
ILLE registers with ERCOT as a Resource Entity (RE) and designates a QSE
5
ERCOT studies the full load amount in the Batch Zero Refinement Study
4
ILLE submits updated Declaration to accept allocation amounts
3
ERCOT studies PCLR in Batch Zero
2
Submission of Declaration and required information to ERCOT
(by July 24)
1
Must be done before non-firm load may energize
May be done in parallel with QSA
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 16: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
1
ILLE Declaration of Intent and PCLR data submitted to ERCOT
Interconnecting Large Load Entity (ILLE) provides to the Interconnecting DSP/TSP
  A notarized Declaration of Intent to Register as a PCLR
  All additional data needed to model the PCLR in Batch Zero, including the minimum amount of load that must be firm (termed the Low Power Consumption limit)
The Interconnecting DSP/TSP provides this information to ERCOT on behalf of the ILLE on or before July 24, 2026
2
PCLR is evaluated in the Batch Zero Interconnection Study
For the steady state portion of the Batch Zero Interconnection Stuy ERCOT will assess the PCLR according to the same methodology as other included, allocated loads
  If the amount of firm load that can be reliably served in a given year of the study is greater than or equal to the requested Low Power Consumption for that year, that amount becomes the approved LPC amount and the rest of the requested load may connect as a PCLR
  If the amount of firm load that can be reliably served is less than the requested LPC, the Load receives an allocation of 0 MW for that year
ERCOT will study the full requested MW amount for determining potential transmission upgrades and in the stability screening study

## Slide 17: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
3
ILLE submits updated Declaration of Intent and accepts Batch Zero amounts
ILLE updates the Declaration of Intent to Register as a PCLR
  The update will reflect the approved LCP amounts
  The update will also reflect the date on which the Load will be eligible to de-register as a PCLR
The ILLE must also meet all the requirements documented in Section 9.4 of PGRR145
4
ERCOT studies the full load amount in the Batch Zero Refinement Study
ERCOT will study the full requested load in the Batch Zero Refinement Study for all PCLRs that met the commitment requirement
This will ensure the Transmission Plan includes the needed upgrades to allow the PCLR to be served reliably as firm load in the future

## Slide 18: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
1. Design and NPRR/PGRR language still under internal review and may change prior to filing
ILLE meets all existing requirements to register as a CLR
These include, for example
Registration as a Resource Entity (RE), designation of a Qualified Scheduling Entity (QSE), and submission of the Managed Capacity Declaration form
Establishment of required metering
Submission of all required CLR parameters in RIOO
Establishment from the QSE of all required telemetry points
8
ERCOT validates completion of all steps prior before Approval to Energize
ERCOT will validate all required CLR registration and modeling steps are completed as part of the Approval to Energize process
ERCOT will not permit the PCLR to energize above the approved firm load (LPC) amounts until all required steps are completed
After energization, ERCOT will monitor to ensure the PCLR behavior is in alignment with the agreed on PCLR amounts
5-7

## Slide 19: Overview of PCLR Bid Capping Process1
After each SCED run, a list of binding transmission constraints which are approaching their max shadow price (X%)* are identified as potential list of transmission constraints to be used in the CLR Bid Capping process for the NEXT SCED run
Where the list of constraints identified for CLR bid capping process from the previous SCED run matches those active in the current SCED, any Batch CLR with a helping shift factor of Y% or greater (on a given constraint) will have its energy bid curve capped (in the Step 2** SCED run) according to the formula below
*Step 2 (in the SCED two step process) observes the limits of all constraints and uses mitigated offer caps to producing binding LMPs and Dispatch Instructions
* percentage may vary by the type of constraint (e.g IROL, GTC, basecase, contingency, voltage level)
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 20: PCLRs – Topics Still Under Internal Discussion1
Is there any study scenario that would limit the Maximum Power Consumption (MPC) of the PCLR?
Can PCLRs provide Ancillary Services?
Exact timing for CLR registration in the context of the Batch Zero process
Key parameters for PCLR bid capping process (X%, Y%)
Will Registration, RIOO, Market, or EMS system changes be needed to accommodate PCLRs?
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 21: BYOG Self-Limiting Facility (SLF)
Source: ERCOT discussions
Point of interconnection
Colocated Large Load and Generation operate behind a single POI under a defined net injection/ withdrawal limit enforced at the POI
Facility is structured as a PUN with a Self-Limiting Feature (SLF) (consistent with NPRR1026 framework)
The SLF ensures that net real power at the POI never exceeds the approved interconnection limit, regardless of internal load or generation configuration
Load and Generation are both registered resources
Interconnection limit applies to net MW at the POI
Requires operational coordination agreement between Load and Generator
ERCOT models the facility as a net resource at the POI, subject to the self-limiting cap
Facility must ensure net injection/withdrawal does not exceed POI cap at any time (may require breaker logic and/or reverse power relay to enforce the limit)
Transmission planning does not assume simultaneous full load and full generation at the POI:
  Either supply-side (GR/ESR) or demand-side (CLR) may participate at a given time
  Simultaneous full participation on both sides is not permitted unless structured as a Netted Network (separate construct)
The largest modeled contingency depends on internal configuration (e.g., if generators share a common step-up transformer, transformer loss may be most limiting event; if generators are electrically independent, individual G-1 may apply)
Description
Illustrative scheme
Load = 1,000 MW
Gen = 5 x 250 MW
G-1 compliant (serve 1,000 MW load) or most limiting contingency
POTENTIALLY FEASIBLE CONFIGURATION
2
Load
ERCOT grid
Gen 1
Gen 2
Gen 3
Gen 4
Gen 5
Load = 1,000 MW
Gen = 2 x 500 MW
G-1 compliant (only serve 500 MW load)
Load
ERCOT grid
Gen 1
Gen 2
Details

## Slide 22: Conceptual Batch Zero BYOG operating configurations for Large Load interconnection3
Business as Usual (BAU)
PUN+
Batch Self-Limiting Facility (SLF)
Load and generation are connected at separate POIs (shown) or behind the same POI and interact through the transmission system under existing interconnection framework
Configurations
Description
Generation and load are studied separately
Generation is only included in the LLIS if it meets PG 6.9 criteria
Load deliverability depends on transmission capability and may be constrained through the current study process
Transmission upgrades from batch study based on G-1+N-1 analysis
Details
Load is supported by dispatchable on-site generation such that G-1 ≥ load and treated as firm, with reliability managed through ERCOT operational actions
Configuration satisfies G-1 ≥ load (loss of one generator still allows remaining units to serve the load)
Load is treated as firm
No planning or administrative limit at POI
No transmission upgrades from batch study since configuration is G-1 secure
In operations:
  ERCOT may reject generator outages or require mitigation plans
  ERCOT may RUC resources1
  In real-time, mitigation plans or local load shed may be used
3. Conceptual designs still under internal review and may change | Source: ERCOT discussions
Site operates with a fixed transmission withdrawal limit determined through batch study
Generation mix may include thermal resources, renewables, and batteries
A fixed transmission withdrawal limit is established (e.g., 100 MW grid import limit) determined in the batch study
ERCOT does not coordinate RUC1 or outage management for the facility
The load and generation owners must coordinate operations to ensure grid imports never exceed the limit
The site would be equipped with a reverse power relay or equivalent protection to enforce the limit
Transmission upgrades required if identified by the batch study to meet reliability criteria2
1. RUC (Reliability Unit Commitment): ERCOT mechanism used to commit generation outside the market to maintain system reliability | 2. Based on batch study results for the generation/load mix
No admin limit
0-100 MW limit ensured by reverse power relay
~
~
~
~
~
~
~
~
~
~
~
~
~
Point of interconnection (POI)
Too many issues to resolve for
Batch Zero

## Slide 23: Key design and implementation questions
Source: ERCOT discussions
How should SLFs be modeled across Batch Study and transmission planning, especially if the processes are integrated?
How should SLFs present generation/load to ERCOT systems (COPs, outage coordination)?
Integration with planning and operations
Can reverse power above 0 MW be supported, or does it trigger RAS classification?
If classified as RAS, what are the implications for NERC compliance and control room operations?
Are there viable alternatives (e.g., reverse power relay with limits), or is zero the only feasible option?
Reverse power and compliance constraints
Should SLFs be limited to zero withdrawal (i.e., injection-only) to avoid RAS and compliance complexity?
Implications for SLF design
Should there be maximum load and generation sizes based on transmission network, e.g., can you have a 1000 MW load/gen on a 100 MW, 138-kV line?
Is the “zero withdrawal” construct acceptable from a TSP and operational perspective?
Open validation points
How should deliverability and injection limits be defined for SLF sites?