IBRWG Update

April 2026

Chair: Julia Matevosyan, Vice-Chair: Miguel Cova Acosta

IBRWG met on March 27th (Webex).

The agenda and the presentation slides are available here

~86 people attended the meeting (at peak)

IBRWG Meeting

Advanced Grid Support Incentive Program Proposal Overview – Important to bring to ROS’s Attention

Fred Huang, ERCOT

- NOGRR 272 and PGRR 121, approved in 2025, require ESRs with an original SGIA on or after April 1, 2026, to provide advanced grid support (AGS)

- ERCOT is proposing an NPRR to create a one-time incentive IBRs, which are exempt from providing AGS under NOGRR272, to implement the AGS within 2 years of approval (includes other IBRs like wind and solar).

- Next Steps:

  - Present the concept to the IBRWG in March 2026 – done

  - ERCOT will review stakeholder feedback and submit the NPRR by Q2 2026

  - For comments or questions, please contact Shun-Hsien.Huang@ercot.com

RIOO Change Request Ride Through Suggestions

Mario de la Garza, ERCOT

- Main issue driving delays is poor-quality ride-through submittals—incomplete data, wrong scope (facility vs. resource level), and missing documentation/settings.

- Strong emphasis that compliance is at the Resource level, requiring full system representation (not just inverter/turbine capability).

- Timing of submissions is critical—ride-through packages must follow commissioning milestones (PFR, reactive tests, as-built model) to avoid rejection.

- Capability curves (FRT/VRT) must reflect full resource limitations, including protection systems and most limiting elements, with clear comparison to ERCOT requirements.

- Increasing focus on traceable validation (OEM data, settings like RoCoF/PAJ) and upcoming RIOO/tool improvements to enforce quality and reduce review timelines.

Overview of WECC 2025 IBR Events

David Grover, Curtis Hollad, WECC

- IBR disturbances continue during normally cleared faults, with widespread tripping/reduction confirming a persistent and material reliability risk. Four disturbance events from 2024 in WECC, the event report is here

- Root causes remain settings-related (non-optimized controls, firmware resets, user-level protection settings) rather than fundamental equipment limitations.

- Significant unused ride-through capability exists across the fleet, highlighting need to maximize inverter settings to equipment limits.

- Strong push for corrective actions via standards (FERC Order 901) and interconnection requirements, alongside active monitoring/enforcement (e.g., CAISO, WECC outreach).

- Key takeaway: better settings management, validation, and enforceable performance requirements are critical to reducing recurring IBR disturbance events.

NERC EMTWG Updates and Draft White Paper: Uniform EMT IBR Plant Model - Interface and Structure.

Aung Thant, NERC – was not available, we’ll have this item in March.

- NERC EMTWG is advancing EMT adoption to improve accuracy and consistency of interconnection and planning studies.

- Key focus on standardizing IBR plant models, including a draft white paper defining uniform interfaces and automated testing frameworks.

- Progress on model validation guidance, introducing quantitative performance metrics (e.g., Max Absolute Error) to align EMT models with actual equipment behavior.

- Ongoing work on model benchmarking, portability, and early verification to reduce inconsistencies across tools and study processes.

- New activity on EMT modeling for large loads (with NERC LLWG)—highly relevant to ERCOT given increasing PEIL/data center impacts.

NERC Updates

Mark Henry, TRE

- FERC Order 901 standards development progressing: key projects (model validation, system validation, uniform modeling) approved; new ride-through PRC-029 revisions targeting August 2026 filing.

- Operational & planning standards updates underway (FAC, IRO, TOP, TPL), with active drafting, industry comments, and upcoming technical conference (May 2026).

- EMT modeling standard (Project 2022-04) did not pass initial ballot, with extensive industry feedback now under review—indicates ongoing alignment challenges.

- IBR event reporting standard (EOP-004) approved, strengthening disturbance reporting and visibility of IBR performance.

- GO-2/GOP-2 registration expanding in ERCOT (32 new generators) with compliance starting May 2026—material increase in regulatory oversight of IBR fleet.

Other Industry Updates

Julia Matevosyan, ESIG

- DOE Forum for the Implementation of Reliability Standards for Transmission (i2X FIRST) – Season 2 wrapped up, monthly meetings discussing standards and implementation. Materials for Season 2 are posted here

  - Last meeting of Season 2: GFM Workshop on March 3/16, discussing GFM basics, system needs, interconnection requirements and operational projects.

- Next steps for DOE i2x

  - i2x FIRST Season 3 (IEEE2800.2 adoption, NERC Milestone 4, PRC-029 implementation, new IEEE2800 series efforts, etc.). Sign up here

  - New 2X Studies, Tools and Interconnection Consistency and Harmonization Meetings (i2X STITCH) focusing on interconnection studies and study assumptions. Sign up here.

  - New Technical Assistance Hours: one-on-one TA to interested stakeholders on the topics of standards, implementation, and conformity assessments (i.e. i2x FIRST topics). Sign up here.

- ESIG Technical Workshop in Tucson, Arizona March 16-19th, a few sessions relevant to IBRWG scope. Julia will bring more details back in April once the materials have been posted.