| PGRR Number | 145 | PGRR Title | Batch Zero Process for Large Load Interconnections |
| --- | --- | --- | --- |
| Date |  | April 4, 2026 |  |

| Submitter’s Information |  |
| --- | --- |
| Name | Agee Springer |
| E-mail Address | agee.springer@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4508 |
| Cell Number |  |
| Market Segment | Not applicable |

Comments

ERCOT appreciates the feedback on Planning Guide Revision Request (PGRR) 145 received from stakeholders. ERCOT submits these comments in response to this feedback. In the table below, ERCOT has responded to high-level summaries of individual stakeholder comments received by March 20, 2026.

In addition to any changes or additions to the proposed revisions, ERCOT has identified additional omissions or process gaps.  These changes are listed below:

- ERCOT added a new paragraph (4) to Section 9.1, Introduction, that memorializes that the Interconnecting Distribution Service Provider (DSP) may designate in writing another entity to fulfill its responsibilities under this Section.

- Additionally, ERCOT added the Permian Basin Reliability Plan Study completed by ERCOT in 2024 as a study considered to be complete and valid under proposed paragraph (3) of Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads, since this study was not a Regional Planning Group (RPG) project (and therefore does not qualify under paragraph (3)(a) of Section 9.2.1.4) but was the study used by the Public Utility Commission of Texas (PUCT) to establish the need for certain transmission projects.

- ERCOT added a sentence to paragraph (2) of Section 9.2.3, Modification of Large Load Information that requires the Interconnecting Large Load Entity (ILLE) to provide the updated dynamic data to the interconnecting DSP or interconnecting Transmission Service Provider (TSP).

- In response to stakeholder questions at a recent workshop, ERCOT agreed to present the study scope and methodology to RPG to allow an opportunity for stakeholder comments.  The addition of paragraph (2) of Section 9.3.2, Batch Zero Interconnection Study Methodology, codifies that agreement.

- ERCOT has incorporated language better defining responsibilities in Section 9.3.2 based on comments from CenterPoint.

- ERCOT has also made various corrections to typographical errors and incorrect section references throughout.

- ERCOT also made clarification revisions throughout.

| Author | Comment summary | Suggestion | ERCOT Response | Were there language changes made in ERCOT's 4/4 comments related to this comment? |
| --- | --- | --- | --- | --- |
| Oncor | Section 9.4 provides approximately 30 days between issuance of the Batch Zero Study report and the deadline for DSP attestation that Interconnection Agreements have been executed. Oncor believes 30 days may be insufficient, particularly absent a standardized Interconnection Agreement form. | Extend the 30-day commitment period to 60 days unless or until a standardized Interconnection Agreement form is developed by the PUCT. | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. ERCOT notes that after the final rule in Project No. 58481 is adopted, ERCOT will file a revision request to align with the rule, including any changes to the commitment window. Those changes should be effective before the Batch Zero commitment window opens. | No |
| AEP | Missing explicit step for energization readiness | Add Energization Request requirement to checklist | ERCOT does not believe this change is needed. Planning Guide Section 9 requires ERCOT to prescribe the manner for submitting all communications and documents. ERCOT already has a document that prescribes use of the form posted on the ERCOT website, as required by PG 9.1. Any changes to align with the Batch Zero process are more appropriately placed in this document rather than being hardcoded in the Planning Guide. This also mirrors how the Approval to Energize process for generation is handled. | No |
| Skybox Datacenters | Skybox requests that projects that have: (1) Completed required studies (2) Executed IA or FEA (3) Posted financial security and (4) Demonstrated site readiness, should continue advancing toward energization under their LCPs and should not be required to re-demonstrate eligibility or re-initiate prior milestones unless a material adverse reliability impact occurs. | Clarify in §9.6 that projects satisfying prior study and commitment milestones continue advancing toward energization without re-screening or re-demonstration of eligibility. Clarify that updates to dynamic load models required by other rulemakings do not invalidate prior studies unless they result in a material adverse reliability impact | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| AEP | Planning Guide includes rate base, CIAC, and fee treatment tied to PUCT rulemaking, creating regulatory risk | Remove or align financial provisions with PUCT 58481; avoid embedding rate base / CIAC rules in Planning Guide | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. ERCOT is open to removing the references in Section 9.7 to how TSPs should treat ILLE financial commitments for ratemaking purposes. | No |
| CenterPoint | CEHE argues that provisions governing accounting treatment, refundability, and rate base implications of financial security exceed the scope of the Planning Guide and should be addressed by the PUCT under Project 58481 | Remove all provisions related to financial accounting, refund treatment, and rate base implications from PGRR145, Defer these issues to PUCT rulemaking (Project 58481) | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Satoshi Energy | Satoshi argues that proposed $/MW financial security and fees are not cost-reflective, especially for colocated projects that require no transmission upgrades. They state that (i) intermediate-stage deposits should be fully refundable, (ii) interconnection fees should reflect actual CIAC rather than fixed $/MW, and (iii) duplicative charges create an unjustified burden and act as a “tax” on load | Make deposits fully refundable until PUCT 58481 finalized; scale fees to actual CIAC; avoid fees for no-upgrade projects; implement true-up mechanism | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| TEBA I | TEBA raises concern about embedding PUCT Project 58481 requirements into the Planning Guide before they are finalized, noting potential misalignment and governance concerns | Avoid incorporating pending PUCT rules directly into PGRR145 or ensure flexibility to align with final rulemaking | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| TEBA I | TEBA expresses concern about proposed financial security framework (e.g., 80% held for 5 years), arguing it creates excessive risk for loads and may exceed ERCOT’s authority. They emphasize need for refundability and flexibility | Improve refundability provisions, consider milestone-based exit options, and clarify treatment of guarantees; limit ERCOT role to attestation rather than enforcement | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Vistra | Vistra argues that several provisions imported from PUCT Project 58481 exceed the scope of the ERCOT Planning Guide and/or SB6. Specifically, ERCOT should not prescribe rate base treatment, cost allocation, refundability of financial security, or expand disclosure requirements beyond statutory language. These are PUCT jurisdictional matters | Remove or limit provisions related to financial security treatment, rate base offsets, and cost allocation; align disclosures strictly with SB6 (e.g., “in this state”) | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| AEP | SSO study requirement timing unclear (QSA vs energization) | Clarify that SSO study is required prior to energization, not QSA entry | ERCOT will implement this change through proposed redline edits in its April 3 comment. | Yes |
| Vistra | Vistra notes misalignment between Quarterly Stability Assessment timelines and Batch Zero energization timelines, particularly for 39.169 NMA projects, which could create unintended eligibility barriers | Align §5.3.5 timing requirements with Batch Zero and Legacy pathways to ensure 39.169 NMAs can proceed without timing conflicts | As ERCOT understands it, Vistra's suggested revisions are only necessary if large loads subject to PURA § 39.169 have two options for interconnection studies, Batch Zero or the Legacy LLIS . As addressed elsewhere, ERCOT does not agree that large loads subject to PURA § 39.169 are entitled to two paths to study for interconnection. | No |
| Sandow Lakes Energy | Sandow argues ERCOT should create a separate highest-priority category for projects tied to national interests, such as military needs, domestic manufacturing of essential goods, and health and safety-related facilities. They argue the Batch Zero framework should not fail to accommodate critical facilities whose importance goes beyond ordinary commercial queue treatment | Add a distinct priority pathway for projects identified as serving national interests, with highest-priority ERCOT review and approval treatment | Sandow Lakes Energy has not identified a statutory or rule-based rationale for ERCOT to give preferential treatment to large loads tied to undefined national interests. | No |
| IREN | IREN argues that the current framework effectively treats all loads as being at the same development stage. They contend that projected energization dates, existence of interconnection agreements, and construction stage are only part of the picture and that the absence of an objective allocation methodology could lead to arbitrary MW distribution outcomes. They propose using a “Load Request Date” metric as an objective basis for prioritization, bifurcated around March 25, 2022 (the date ERCOT implemented the Interim Large Load Interconnection Process). They argue this date is pivotal and provides a fair and administrable dividing line. | Add new section establishing a Load Request Date-based capacity allocation methodology. Aggregate loads into two groups:(1) Load Request Date on or before March 25, 2022 (“Interim Connection Date”); and (2) Load Request Date after March 25, 2022. Allocate capacity chronologically within each group, with the first group studied and allocated first before proceeding to the second group. Define “Load Request Date” as the date the Load Facility submitted a written request to its Interconnecting DSP or TSP. | ERCOT does not currently have access to this data, and respectfully disagrees that the date a customer first contacted its Interconnecting TSP/DSP serves as a reliable or realistic indicator of project maturity or seriousness. The current proposal is grounded in objective, measurable metrics of progress through the established process. It should also be noted that implementing the suggested approach would require additional study time. | No |
| TEBA I | TEBA raises concern that PGRR145 may imply ERCOT will pause or limit processing of new load interconnection requests outside Batch Zero. This creates significant investment uncertainty for projects not included in Batch Zero, as developers lack clarity on timing and process for individual studies | Clarify that ERCOT will continue processing non-Batch Zero load requests and define a clear pathway and timeline for loads outside Batch 0 | Upon approval of PGRR145, the current individual study process will no longer be in effect and Batch Zero will be the only path forward for Large Load interconnection requests. Any LLI requests that do not meet the requirements for inclusion in Batch Zero will need to wait until a later Batch study in order to be assessed and eventually interconnected. This is described in Section 9.2.1.3. As there will no longer be an individual study process, ERCOT will not be accepting TSP-performed LLIS studies once PGRR145 is effective. | No |
| Emerald AI | Projects that are ready and flexible (e.g., CLR, RTP-qualified) should be prioritized as they reduce system cost and can operate under constraints | Allow projects electing CLR and meeting RTP readiness criteria to receive Batch Zero allocation | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs in Batch Zero. | No |
| Oncor | Batch Zero eligibility relies on PUCT 58481 PFP requirements that are not yet final, creating risk of misalignment (e.g., financial security levels, refundability) if the final rule changes | True-up Batch Zero entry requirements after final PUCT rule (e.g., adjust/refund financial security) or use Intermediate Agreement (refundable security) instead of Interconnection Agreement for Base Load eligibility | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Crow Holdings | Focuses on projects that have completed legacy LLIS, executed binding interconnection agreements, and posted full financial security. Argues these projects have fully relied on ERCOT framework and should not be subject to re-evaluation, reclassification, or new agreement requirements under Batch Zero | Add new § 9.2.1.1(e) establishing automatic Base Load classification with no § 9.2.1.4 re-evaluation and no new IA requirement for projects that (i) executed IA (or equivalent) and (ii) posted required financial security by July 10, 2026 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Monarch Energy | Argues that financial commitment (CIAC, equipment procurement, LOAs) is the most accurate indicator of project readiness, not execution of an Interconnection Agreement. Current framework risks excluding advanced projects that have already deployed capital but have not yet executed a formal IA | Revise §§ 9.2.1.1 and 9.2.1.2 to recognize binding financial commitment (CIAC, long-lead procurement, LOAs) as equivalent to executed IA for Base Load eligibility | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Reliant | Reliant states that a Large Load co-located with a new Generation Resource that was included in a completed Full Interconnection Study (FIS) should be eligible for inclusion in Batch Zero as Base Load not subject to additional study. They note that under legacy Section 9.8.1(2), a Generation Resource FIS that includes a co-located Large Load may be used “in place of a separate LLIS.” Therefore, if a Generation Resource FIS that includes a co-located Large Load is complete prior to the Batch Zero eligibility deadline, that Large Load should be treated the same as Large Loads that progressed through the legacy LLIS process. Reliant’s concern is that without explicit inclusion, these loads could be excluded from Base Load status despite having completed an equivalent study process. | Revise §9.2.1.1 to explicitly allow a Large Load co-located with a new Generation Resource that was included in a completed FIS (per §5.3) to qualify as Base Load in Batch Zero, provided the FIS reflects the full requested load and meets all applicable study requirements | ERCOT wishes to reiterate comments made in recent workshops that the language in current Planning Guide Section 9.3.1(2) (renumbered to 9.8.1(2) in PGRR145) does not allow for the FIS process to completely replace the Large Load Interconnection process documented in Section 9. Rather, it is intended to prevent the TSP from having to perform duplicative studies. Accordingly, the FIS may be substituted only for the LLIS studies, and it must meet all the requirements of the LLIS studies. This includes the scoping process defined in current Section 9.3 and ERCOT review and approval of the study reports described in current 9.4. Large Load interconnection requests that utilize this provision must also meet current Section 9.5.2 of the Planning Guide in order to finalize study results. ERCOT believes the current language in PGRR145 is sufficient to include loads that utilize the FIS in place of a separate LLIS. If stakeholders believe additional clarification is needed, ERCOT is open to additional discussion to develop redlines that accurately reflect the current process. | No |
| Schaper | Schaper argues that the procurement and construction attestation requirement in § 9.2.1.1(1)(d)(iv) is circular as drafted. They explain that (1) Developers must attest to site preparation and construction progress by July 15, 2026. (2) However, under § 9.2.1.4, the applicable MW level may still be subject to ERCOT re-determination. (3) The modeled MW for Batch Zero projects is derived from the study validity determination. (4) Therefore, developers are required to commit capital before knowing whether their load will ultimately be classified as Base Load. Schaper states they are generally supportive of an attestation requirement for near-term energizations (before December 31, 2027), but only if developers receive clear notice of Base Load classification first | Modify § 9.2.1.1 to provide developers with unambiguous notice that their load has been classified as Base Load in Batch Zero prior to the attestation deadline, so that the attestation requirement is workable and not circular. | ERCOT disagrees that the site development attestation is circular. During stakeholder interviews, ERCOT repeatedly heard that even fast site development could take 18-24 months until energization. Many stakeholders also expressed belief that many in the interconnection queue are "not real loads." The attestation of sufficient site development to achieve a customer stated energization date is intended to balance the customer's desire for timely electricity service with an ERCOT and market desire to prioritize service to customers that will be ready to take that service. ERCOT has stated its intent to provide periodic status updates to the TSPs, who can update their customers, accordingly. | No |
| Lancium | Lancium notes that § 9.2.1.1(2)(b) may create inconsistencies between:(1) The Demand level reported through the 2026 RTP annual request for information; and (2) The Demand level reflected in the ILLE’s submitted Load Commissioning Plan (LCP). Lancium argues that if the objective is to model the most accurate and current Demand level, the LCP submitted by the ILLE is the more appropriate source | Modify § 9.2.1.1(2)(b) to default to the Demand level indicated in the ILLE’s LCP when it is inconsistent with the level reported through the RTP data request. | Lancium is correct that the provision in § 9.2.1.1(2)(b) is to resolve inconsistencies between an ILLE's LCP and its submission in the 2026 RTP. If the ILLE has harmonized its LCP with its 2026 RTP submission, there is no conflict. We do not agree with Lancium's proposed solution but have proposed redlines to address the inconsistency. | Yes |
| Schaper | Schaper highlights the “air gap” between March 4 and July 10, during which load customers are required to make binding procurement and construction commitments without certainty regarding study validity or firm load status prior to Batch Zero determination | Either: move the March 4 date forward or remove procurement and construction attestation requirements for projects within this gap | ERCOT has stated its intent to provide periodic status updates to the TSPs, who can update their customers, accordingly. | No |
| Oncor | Oncor notes that § 9.2.1.1 requires multiple DSP and/or TSP attestations for Base Load qualification, but does not clearly define which entity is responsible for each attestation. They also state that DSPs are not well positioned to determine what constitutes sufficient “evidence” of site preparation and construction. | Clarify in each provision whether the DSP or TSP is responsible for the required attestation. Develop ERCOT-standardized attestation forms. Remove the requirement that the ILLE provide evidence of site preparation and construction; an attestation should be sufficient. | ERCOT is currently developing an attestation form that would identify the responsible entity, as appropriate. ERCOT is continuing to consider the issue of evidence of site preparation and construction. While ERCOT is not proposing changes to the language at this time, it is open to changes in future comments. | No |
| Eolic | Eolic notes potential inconsistency between peak Demand reported through the 2026 RTP data request and the ILLE’s most recent Load Commissioning Plan (LCP). They argue that the LCP reflects the most current and project-specific information and should therefore take precedence for modeling purposes | Amend §9.2.1.1(2)(b) to specify that where RTP and LCP values differ, ERCOT shall model Demand based on the LCP | Eolic is correct that the provision in § 9.2.1.1(2)(b) is to resolve inconsistencies between an ILLE's LCP and its submission in the 2026 RTP. If the ILLE has harmonized its LCP with its 2026 RTP submission, there is no conflict. We do not agree with Eolic's proposed solution but have proposed redlines to address the inconsistency. | Yes |
| TEBA I | TEBA objects to using the “lesser of RTP vs LCP” for modeling load, arguing it may understate actual demand and penalize projects. They view the LCP as the most accurate and up-to-date representation of load | Use Load Commissioning Plan (LCP) as the primary basis for modeling load rather than taking the minimum of RTP and LCP values | TEBA is correct that the provision in § 9.2.1.1(2)(b) is to resolve inconsistencies between an ILLE's LCP and its submission in the 2026 RTP. If the ILLE has harmonized its LCP with its 2026 RTP submission, there is no conflict. We do not agree with TEBA's proposed solution but have proposed redlines to address the inconsistency. | Yes |
| TEBA I | TEBA argues that Base Load eligibility criteria for near-term projects (≤2027) are overly stringent, particularly requirements for “all necessary equipment” and full construction progress | Relax criteria to require procurement of long-lead equipment only and initiation (not completion) of site preparation | Section 9.2.1.1(d) requires attestation of purchase of high-voltage equipment (iii) and (v) and site prep sufficient to achieve the requested ISD (iv). The language does not require purchase of "all necessary equipment" and does not require the site to be fully constructed. | No |
| Monarch Energy | Current draft may implicitly require inclusion in 2026 RTP for Batch Zero eligibility, contradicting prior ERCOT guidance and penalizing projects that did not pursue RTP inclusion | Revise § 9.2.1.1(2)(b)(i) to remove any implicit requirement for RTP inclusion as a condition for Batch Zero eligibility or modeling | ERCOT acknowledges that inclusion of the Large Load in the 2026 RTP is not a requirement for inclusion in Batch Zero. ERCOT will modify § 9.2.1.1(2)(b)(i) to be applicable only if the Large Load was included in the 2026 RTP submission. ERCOT does not understand why a Large Load included in Batch Zero under § 9.2.1.1(2)(b) which is operational would not be reflected in the 2026 RTP load forecast. Similarly, ERCOT does not understand why a Large Load eligible for inclusion in Batch Zero under § 9.2.1.1(2)(c) and will energize in a matter of months would not also be reflected in the 2026 RTP load forecast. | Yes |
| Satoshi Energy | Satoshi argues that projects that completed legacy LLIS (Sections 9.9 and 9.10) have already demonstrated full commitment (executed IA, CIAC paid, construction underway) and should not be required to execute a new interconnection agreement under §9.7.2 to qualify as Base Load. Requiring a new IA is duplicative and undermines investment certainty | Add deemed-compliance provision: projects satisfying §§9.9–9.10 prior to deadline automatically qualify as Base Load without new IA | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Schaper | Schaper argues that requiring projects with existing interconnection agreements to comply with new §9.7.2 standards within a compressed timeline creates risk of non-compliance due to utility implementation constraints. Projects should not be penalized for timing-related limitations | Allow projects to demonstrate compliance using legacy §9.10 interconnection agreement standards instead of requiring immediate compliance with §9.7.2 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. ERCOT appreciates concerns about timing, but ERCOT is balancing the time needed for a stakeholder process with requests for Batch Zero to start as quickly as possible. Nothing prevents an ILLE from taking steps between now and July 10 to be ready to meet the requirements in Section 9.7.2, including obtaining site control, preparing disclosure information, determining how much additional security it may need to provide, and entering into an agreement. | No |
| Skybox Datacenters | Skybox recommends clarifying that while ERCOT intends the Interconnecting DSP to serve as the gatekeeper for attestation, the rule should accommodate situations where the DSP and TSP functions are performed by the same legal entity. The attestation should confirm general willingness and ability to serve under the applicable IA/FEA, but should not be construed as a binding commitment to specific service terms or timelines. | Clarify §§ 9.2.1.1(1)(d)(ii) and (e)(ii) to allow for circumstances where DSP and TSP are the same entity. Clarify that attestation reflects general willingness and ability to serve under the IA/FEA and is not a binding commitment to specific service terms or timelines | ERCOT agrees to make this clarification consistent with 16 TAC § 25.370(d)(3), which allows the Interconnecting DSP to designate another electric utility, municipally owned utility, or electric cooperative to submit the notarized attestation. | Yes |
| Crusoe | Crusoe argues that reassessing firmness as of July 15, 2026 for loads that have already completed legacy LLIS (Sections 9.9 and 9.10) is inappropriate and harmful. These projects have received ERCOT approval, executed interconnection agreements, posted security/CIAC, ordered long-lead equipment, and begun construction. Re-evaluating firmness mid-construction creates financing risk and operational uncertainty, particularly for 2027 and early 2028 energizations. Crusoe contends these loads are already demonstrably firm and should not be treated as speculative | Add new § 9.2.1.1(b-1) providing automatic Base Load classification for loads that satisfied §§ 9.9 and 9.10 prior to effective date of PGRR; no § 9.2.1.4 evaluation; no new § 9.7.2 agreement required | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. In addition, ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| CenterPoint | CEHE identifies gaps and inconsistencies in eligibility rules for “Load to be Studied,” particularly for projects targeting 2027 energization or those with interconnection agreements but not meeting Base Load criteria. Current rules may exclude viable near-term projects or misclassify them | Clarify linkage to §9.2.1.1(1)(d)(i) for consistency with valid study criteria, Remove January 1, 2028 restriction to allow 2027 projects into Studied Load and Allow executed interconnection agreement (9.7.2) as an alternative qualifying criterion (in addition to intermediate agreement) | ERCOT acknowledges that Large Loads under Section 9.2.1.2(1)(a) need to satisfy the eligible studies requirements in Section 9.2.1.4. The omission of such a requirement is an oversight. ERCOT agrees the January 1, 2028 restriction needs to be lifted and has made conforming changes. Any Large Load that does not qualify for inclusion in Batch Zero under Section 9.2.1.2(1)(a) may still qualify under Paragraph (1)(b). | Yes |
| Agentic Infrastructure, Reliant Energy Retail Services LLC. (“Joint Commenters”) | Joint Commenters argue that projects with an ERCOT LLI number that also met the criteria for inclusion in the 2026 RTP should be eligible for the allocated portion of Batch Zero. They contend these projects have already demonstrated material commercial and financial commitment and should be treated as substantiated load rather than excluded from the transition process. They also emphasize that aligning Batch Zero with RTP inclusion would improve transparency and provide clearer planning signals to market participants relying on ERCOT transmission planning outputs | Revise § 9.2.1.2 to include projects with an ERCOT LLI number that satisfied the criteria for inclusion in the 2026 RTP in the allocated portion of Batch Zero | ERCOT disagrees that the assignment of an LLI number and inclusion in the 2026 RTP is sufficient for inclusion in Batch Zero. One of the principal reasons for Batch Zero is to resolve the interconnection approval challenges faced by ILLEs with submitted studies. An ILLE without at least one completed and approved interconnection study is not the ILLE the Batch Zero Process is intended to serve. | No |
| Agentic Infrastructure, Reliant Energy Retail Services LLC. (“Joint Commenters”) | Joint Commenters II argue that projects with an ERCOT LLI number that elect to proceed as a Controllable Load Resource (CLR) or under a Bring Your Own Generation (BYOG) arrangement should be included in the allocated portion of Batch Zero. They argue these projects are willing to energize ahead of full network upgrades while privately bearing curtailment risk, which distinguishes them from loads seeking immediate firm network service and supports more flexible interconnection outcomes | Revise § 9.2.1.2 to include projects with an ERCOT LLI number that elect CLR or BYOG treatment through their intermediate agreement in the allocated portion of Batch Zero | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs and Large Loads proposing to locate with new generation (BYOG) in Batch Zero. | No |
| Agentic Infrastructure, Reliant Energy Retail Services LLC. (“Joint Commenters”) | Joint Commenters argue that including CLR and BYOG projects in Batch Zero would improve market efficiency and reduce ratepayer risk by allowing load to energize before full network upgrade costs are socialized. They state that these structures increase MWh served before incremental transmission capital is incurred, reduce stranded cost risk if projects abandon while waiting for firm service, and create incentives for loads to locate in areas with underutilized transmission infrastructure. In their view, Batch Zero should be designed to capture these least-cost and reliability benefits as part of the queue-clearing process | Modify Batch Zero eligibility and allocation rules to expressly accommodate CLR and BYOG projects as a policy tool to reduce stranded cost risk, improve utilization of existing transmission, and support lower-cost system expansion. | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs and Large Loads proposing to locate with new generation (BYOG) in Batch Zero. | No |
| Emerald AI | Argues that flexible loads (AI/data centers) can support grid reliability and accelerate time-to-power; Batch Zero should include CLR-enabled projects | Explicitly include Controllable Load Resource (CLR) rules in Batch Zero framework | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs and Large Loads proposing to locate with new generation (BYOG) in Batch Zero. | No |
| Crusoe | Crusoe objects to ERCOT’s proposed authority to re-evaluate the completeness and validity of previously finalized LLIS studies. They argue that once Sections 9.4 and 9.5 (now 9.9 and 9.10) were satisfied, studies were final and relied upon for major capital commitments. Retroactive review undermines investment-backed expectations and destabilizes regulatory certainty | Replace proposed § 9.2.1.4(3) with deemed-valid safe harbor: completion of §§ 9.9 and 9.10 constitutes complete and valid studies as a matter of law; no further review required or permitted | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Schaper | Schaper objects to proposed § 9.2.1.4, which would authorize ERCOT to retroactively determine the “completeness and validity” of previously finalized LLIS studies. They argue that under the current PGRR: (1) ERCOT communicates LLIS results under Section 9.4. (2) Customers satisfy Section 9.5 by executing interconnection agreements, posting security, and issuing notice to proceed. (3) Upon satisfaction of Section 9.5, the study is complete and the load is carried in future planning studies as base load. Schaper asserts that these determinations are final and not provisional. Retroactive re-evaluation would undermine reliance interests and cause irreparable financial harm to developers who committed capital under executed interconnection agreements | Substantially replace § 9.2.1.4 with a new provision establishing a safe harbor, under which completion of the study process under Sections 9.4 and 9.5 constitutes, as a matter of law, a complete and valid study finding — eliminating the proposed retroactive review entirely | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. However, ERCOT disagrees with the characterization of proposed § 9.2.1.4 as retroactive. ERCOT is using the criteria to prospectively establish eligibility in a new Batch Zero Process. | No |
| Schaper | Schaper specifically challenges proposed § 9.2.1.4(2), which vests ERCOT with “sole authority” to determine the completeness and validity of prior studies. They argue that (1) Study communications issued under current Section 9.4 are not provisional. (2) Once Section 9.5 requirements are met, the studies are final determinations. (3) Customers reasonably rely on those final determinations in executing binding agreements | Delete or substantially replace § 9.2.1.4 so that completion of Sections 9.4 and 9.5 establishes study validity and eliminates ERCOT’s authority to conduct retroactive re-determination | In its March 17 comments, ERCOT added § 9.2.1.4(3), which grants approvals under Section 9.4 and 9.5 to be valid studies. | No |
| Schaper | Schaper objects to § 9.2.1.4(3)(a)(ii)(A), which uses RPG submission-related dates as a trigger for ordering loads and possible restudy RPG submission does not constitute a completed interconnection study under Section 9.4. RPG filings may have been submitted in contravention of the Large Load interconnection rules under PGRR115. Customers who followed the binding LLIS process should not be disadvantaged relative to those relying on RPG submissions. The only appropriate ordering criterion is completion of steady-state and stability studies under Section 9.4 | Amend or substantially delete § 9.2.1.4(3)(a)(ii)(A) so that completion of the steady-state and stability study process under Section 9.4 is the ordering criterion, rather than RPG submission date | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Rose City Partners | Rose City Partners argue that under the current Planning Guide, once a developer satisfies Sections 9.4 and 9.5, they should have firm, locked-in power. Allowing ERCOT to revisit or withdraw that certainty - even after a developer has satisfied study, financial, and construction-related requirements- creates severe market disruption. Rose City frames this as a certainty issue: developers, lenders, investors, and tenants require absolute assurance before committing millions of dollars. If ERCOT can retroactively invalidate or re-evaluate completed studies, then developers cannot rely on ERCOT’s rules, and development activity will stall | Adopt new language for 9.2.1.4 that: (1) Confirms with absolute certainty that developers who satisfied §§ 9.4 and 9.5 under current rules will be treated as “firm” or “base load” in any scenario, whether a Batch Process is implemented or not. (2) Eliminates ERCOT’s ability to retroactively undermine completed LLIS approvals | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. However, ERCOT disagrees with the characterization of proposed sections as retroactive. ERCOT is using the criteria to prospectively establish eligibility in a new Batch Zero Process. | No |
| Schaper | Schaper supports narrowing the proposed §9.2.1.4 lookback to loads that achieved substantiation under §§9.4 and 9.5 immediately prior to the July 15, 2026 deadline, and proposes formal Safe Harbor language deeming such studies complete and valid. They argue that without this, substantiated projects face an extended period of classification uncertainty during active construction and long-lead procurement, contrary to ERCOT’s prior “must-study” treatment | Amend §9.2.1.4 to establish a Safe Harbor for Large Loads that satisfied §§9.4 and 9.5 on or before a defined date (e.g., June 15, 2026), deeming those studies complete and valid and classifying the loads as Base Load without further retroactive review | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Schaper | Schaper argues that proposed §9.2.1.4(3)(a)(i) could invalidate prior studies solely because updated dynamic model data differs from the model used in earlier stability studies — even where changes result from compliance with ERCOT rulemakings (e.g., NOGRR282, PGRR144). They characterize this as a compliance trap that penalizes ILLEs for improving voltage ride-through, frequency ride-through, or reactive support performance | Revise §9.2.1.4(3)(a)(i) to permit the Interconnecting DSP/TSP to determine, in reasonable engineering judgment, whether updated dynamic model data produces system performance equivalent to or more favorable than the prior study, with a presumption that improvements in ride-through or reactive support satisfy this standard (“equivalent or better” framework) | In its March 17 comments, ERCOT modified § 9.2.1.4(3)(a)(i) to allow the interconnecting TSP or interconnecting DSP to use its engineering judgment whether the updated data would result in an adverse impact from a previous stability study. | No |
| Lancium | Lancium argues that the current framework places undue weight on RPG submission dates and ERCOT endorsement, potentially excluding projects that are technically mature and financially committed. They emphasize that loads included in RPG submissions with executed interconnection agreements have already undergone substantial study and should be treated as valid | Revise §9.2.1.4 to: (i) update RPG submission cutoff date to March 4, 2026; and (ii) add a criterion recognizing loads included in RPG submissions with executed interconnection agreements as valid | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it remains opposed to changing the date by which an RPG submission must have been made from December 15, 2025 to March 4, 2026. As ERCOT has stated clearly in recent Batch Zero workshops, the choice of December 15 was not arbitrary. Rather, it is a reflection of the date Planning Guide Section 9 became effective. At that point, the only path to interconnect a Large Load became the LLIS process. Allowing loads included in RPG submissions after December 15 into Batch Zero would be contrary to the clear intent of stakeholders when they closed off RPG as an avenue for Large Load interconnections in PGRR115. Further, ERCOT does not support the classification of loads included in RPG submissions (regardless of submission date) that have not yet received RPG approval and, if applicable, ERCOT Independent Review and Board endorsement as base load in Batch Zero. Loads from submissions that have not yet been fully reviewed cannot be considered to have complete and valid studies. | No |
| Schaper | Schaper supports Skybox’s position that projects with executed IA/FEA, demonstrated financial commitment, completed studies, and site control should be treated as having satisfied Batch Zero readiness criteria and should not be re-screened, re-prioritized, or invalidated based on timing | Align with Skybox’s approach to treat advanced-stage projects as fixed base load inputs and preserve study validity based on project completeness rather than timing | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Schaper | Schaper endorses Lancium’s position that Batch Zero should function primarily as an administrative planning tool to incorporate advanced-stage load into transmission planning, rather than a mechanism to invalidate prior work performed under existing Section 9 processes | Align with Lancium’s approach to maintain Batch Zero as an administrative planning construct and avoid re-evaluation of previously completed studies | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Oncor | ERCOT’s March 17 revision validates Large Loads included in RPG projects submitted before December 15, 2025 and accepted/endorsed by March 4, 2026 without additional review. RPGs accepted/endorsed after March 4 but before July 10, 2026 would be subject to the ranking process in paragraph (4). Oncor argues there is no logical basis for distinguishing between RPGs accepted by March 4 versus those accepted by July 10, 2026, because both will have reached ERCOT acceptance/endorsement before Batch Zero begins. | Revise § 9.2.1.4 so that Large Loads addressed by RPGs submitted before December 15, 2025, and Accepted/endorsed by July 10, 2026are considered valid studies without undergoing the additional ranking/review process in paragraph (4). | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Crusoe | Crusoe disagrees with ERCOT’s use of March 4, 2026 (the original PGRR filing date) as the cutoff for automatic study validity under § 9.2.1.4(3). Crusoe argues that: A retroactive cutoff undermines the purpose of Batch Zero, which is to provide certainty. Many ILLEs targeting 2027–2028 energization have substantially completed legacy §§ 9.9 and 9.10 but are dependent on TSP/ERCOT processing timelines they do not control. Projects that narrowly missed the March 4 date are similarly situated to those that met it. | Revise § 9.2.1.4(3) to replace the March 4, 2026 cutoff date with a forward-looking cutoff of June 1, 2026 for automatic study validity. (For both RPG-based studies and Legacy LLIS corporations) | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Stream Data Centers, L.P. and Provident Inc. (“Joint Commenters”) | Joint Commenters focus on a targeted issue: the use of March 4, 2026 as the cutoff date in § 9.2.1.4(3)(a) for automatic validation of prior studies tied to RPG projects. They argue that: (1) Large load customers have spent years working with load-serving utilities under evolving study requirements. (2) Many projects were included in RPG-submitted transmission plans more than a year ago. (3) ERCOT has already expended significant effort independently reviewing these projects. (4) Contractual and financial commitments—including procurement of long lead-time equipment and revisions to energization timelines—have already been made. (5) A retroactive cutoff date risks summarily discounting these long-term efforts and commitments. | Revise § 9.2.1.4(3)(a) to replace March 4, 2026 with a prospective cutoff date, either June 3, 2026 (the day after the anticipated ERCOT Board approval of PGRR145) or June 10, 2026. | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| CenterPoint | CEHE emphasizes that ERCOT’s determination of completeness and validity of existing studies should not rely solely on ERCOT discretion. While ERCOT retains final authority, CEHE stresses that structured consultation with T/DSPs is critical to ensure informed decisions, given TSPs’ knowledge of system conditions and study assumptions | Add explicit requirement that ERCOT “shall consult with” T/DSPs when evaluating study validity, Replace or soften “sole discretion” language to reflect collaborative decision-making (while preserving ERCOT final authority) | ERCOT has modified the language to more explicitly require consultation in the spirit of the redlines offered by CenterPoint. | Yes |
| CenterPoint | CEHE raises concern that assigning T/DSPs responsibility for determining whether updated dynamic data adversely impacts prior studies could lead to inconsistent methodologies and outcomes across utilities | Assign ERCOT as the primary decision-maker for “adverse impact” determination, with TSP/DSP input; Standardize evaluation approach to ensure consistent application across the system | Because the TSP performed the previous study, ERCOT believes the TSP is better positioned to determine whether the updated data would result in an adverse impact to the prior study. | No |
| CenterPoint | CEHE highlights that the term “study area” is not defined in §9.2.1.4, creating risk of inconsistent interpretation when determining whether prior studies remain valid | Define “study area” explicitly (e.g., facilities impacted above a 3% shift factor threshold), Refine language to ensure consistent and objective application of study validity criteria | ERCOT believes that engineering judgment is needed when determining the study area and intends to use the same process as is currently used when determining the study area in current LLI studies. | No |
| Eolic | Eolic supports ERCOT’s March 17 edits and Lancium’s comments, and emphasizes that the now-final PUCT Project 58480 rule (governing Large Load inclusion in the 2026 RTP) provides a higher-quality, standardized screening framework that should be leveraged in Batch Zero. They argue that RTP inclusion under 58480 reflects significant TSP analysis and should be used as a proxy for study validity and substantiated load |  | ERCOT does not agree that the criteria for the 2026 RTP should be used to give large loads not included in (4)(a)(ii). ERCOT's concern in Section 9.2.1.4 is whether ERCOT has a study that confirms the large load can be reliably served. Meeting the requirements for inclusion in the 2026 RTP do not inform the validity of the study. | No |
| Eolic | Eolic proposes expanding §9.2.1.4 to recognize projects that combine RTP inclusion (under 58480) with either legacy interconnection progress or RPG participation. They argue this better reflects actual project maturity and avoids excluding projects that have already undergone substantial study and commitment | Add criteria to §9.2.1.4 recognizing: (i) loads with Legacy IA completed by July 10, 2026 and included in 2026 RTP; and (ii) loads included in RPG submissions (pre-March 4) and also included in the 2026 RTP | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it remains opposed to changing the date by which an RPG submission must have been made from December 15, 2025 to March 4, 2026. As ERCOT has stated clearly in recent Batch Zero workshops, the choice of December 15 was not arbitrary. Rather, it is a reflection of the date Planning Guide Section 9 became effective. At that point, the only path to interconnect a Large Load became the LLIS process. Allowing loads included in RPG submissions after December 15 into Batch Zero would be contrary to the clear intent of stakeholders when they closed off RPG as an avenue for Large Load interconnections in PGRR115. Further, ERCOT does not support the classification of loads included in RPG submissions (regardless of submission date) that have not yet received RPG approval and, if applicable, ERCOT Independent Review and Board endorsement as base load in Batch Zero. Loads from submissions that have not yet been fully reviewed cannot be considered to have complete and valid studies. | No |
| Eolic | Eolic proposes refining the ordering/tie-breaker methodology to give additional weight to projects that combine RPG inclusion with executed interconnection agreements and/or RTP inclusion under 58480. They argue this better reflects project maturity than current criteria | Modify §9.2.1.4 ordering logic to prioritize projects that combine RPG inclusion + executed IA and/or RTP inclusion under 58480 | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it remains opposed to changing the date by which an RPG submission must have been made from December 15, 2025 to March 4, 2026. As ERCOT has stated clearly in recent Batch Zero workshops, the choice of December 15 was not arbitrary. Rather, it is a reflection of the date Planning Guide Section 9 became effective. At that point, the only path to interconnect a Large Load became the LLIS process. Allowing loads included in RPG submissions after December 15 into Batch Zero would be contrary to the clear intent of stakeholders when they closed off RPG as an avenue for Large Load interconnections in PGRR115. Further, ERCOT does not support the classification of loads included in RPG submissions (regardless of submission date) that have not yet received RPG approval and, if applicable, ERCOT Independent Review and Board endorsement as base load in Batch Zero. Loads from submissions that have not yet been fully reviewed cannot be considered to have complete and valid studies. | No |
| TEBA I | TEBA argues that eligibility should not rely solely on energization dates and should incorporate loads already included in current RPG plans. RPG processes already reflect substantiated load and could accelerate interconnection timelines significantly | Add RPG-based pathway for Batch Zero inclusion or allow RPG projects to proceed independently of Batch; prioritize loads requiring minimal transmission (e.g., co-location) | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| TEBA I | TEBA opposes ERCOT’s ability to invalidate studies within the batch process (e.g., via eligible load list methodology). They argue that corrections should be handled within the batch study itself rather than through invalidation, which undermines the purpose of a collective study framework | Revise §9.2.1.4 to remove or limit study invalidation authority; ensure adjustments are handled within the batch process rather than via exclusion | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| TEBA II | TEBA argues that the proposed Batch Zero process risks delaying projects already included in submitted RPG plans until ~July 2027. They contend that existing RPG processes should continue to be used to approve transmission and associated loads in parallel, rather than forcing projects to wait for Batch Zero. TEBA emphasizes that utilities are best positioned to determine which loads are sufficiently advanced and that projects requiring minimal transmission (e.g., co-located generation) should proceed without delay. They propose that timely-approved RPG projects be included in the Batch Zero base case while continuing to advance independently to avoid stalling investment and transmission expansion | Continue approving existing RPG projects outside of Batch Zero; allow early advancement of low-transmission-impact loads; include approved RPG loads in Batch Zero base case | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it is opposed to allowing for a second pathway for Large Load interconnection outside of Batch Zero. | No |
| Satoshi Energy | Satoshi argues that limiting safe harbor to March 4, 2026 is arbitrary and undermines projects that completed the same LLIS process shortly after. They emphasize no technical distinction between studies completed before vs. after March 4 and warn that retroactive invalidation harms investment certainty | Extend automatic validity safe harbor to July 10, 2026 for projects completing §§9.9–9.10 (with dynamic data check) | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Black Mountain | Black Mountain supports ERCOT’s validity framework but argues it fails to capture projects that are technically advanced and near execution. They highlight projects targeting ≤2027 energization, with steady-state approval, studies submitted by March 24, and expected Firm status by July 10, which have effectively met the intent of “valid studies.” Excluding them based on timing (vs. readiness) risks removing viable near-term load and inefficiently using transmission | Expand safe harbor to include “near-complete” projects meeting defined readiness criteria (study completion + firming by July 10), not just those completed by March 4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Sandow Lakes Energy | Sandow argues that projects with pending studies have been left in suspense awaiting their “batch fate,” even though developers can no longer take additional steps to improve their position because timing is controlled by ERCOT and the TSP. They note that stakeholders previously proposed recognizing projects once submitted for study, rather than only after approval, as a fairer approach for developers whose outcomes depend on utility/ERCOT processing timelines rather than project readiness alone | Allow projects with load and co-located generation that have completed and submitted required study information to the TSP/ERCOT to receive priority treatment, or otherwise revise eligibility so developers are not disadvantaged solely by ERCOT/TSP processing timing | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs and Large Loads proposing to locate with new generation (BYOG) in Batch Zero. | No |
| AEP | Loads studied and submitted in RPG before Batch Zero should be eligible even without ERCOT endorsement; RPG studies are equivalent or more comprehensive than LLIS | Allow RPG-submitted loads (by July 10, 2026) into Batch Zero without requiring ERCOT endorsement | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it remains opposed to changing the date by which an RPG submission must have been made from December 15, 2025 to July 10, 2026. As ERCOT has stated clearly in recent Batch Zero workshops, the choice of December 15 was not arbitrary. Rather, it is a reflection of the date Planning Guide Section 9 became effective. At that point, the only path to interconnect a Large Load became the LLIS process. Allowing loads included in RPG submissions after December 15 into Batch Zero would be contrary to the clear intent of stakeholders when they closed off RPG as an avenue for Large Load interconnections in PGRR115. Further, ERCOT does not support the classification of loads included in RPG submissions (regardless of submission date) that have not yet received RPG approval and, if applicable, ERCOT Independent Review and Board endorsement as base load in Batch Zero. Loads from submissions that have not yet been fully reviewed cannot be considered to have complete and valid studies. | No |
| AEP | Current draft assigns DSP/TSP responsibility for determining whether dynamic data impacts prior studies | Assign ERCOT as sole decision-maker for dynamic data impact determination | Because the TSP performed the previous study, ERCOT believes the TSP is better positioned to determine whether the updated data would result in an adverse impact to the prior study. | No |
| AEP | ERCOT has “sole authority” but insufficient structured consultation with TSP/DSP | Require ERCOT to consult with DSP/TSP in study validation decisions | ERCOT has modified the language to more explicitly require consultation in the spirit of AEP's suggestion. | Yes |
| AEP | “Study area” undefined → risk of inconsistent application | Define study area using shift factor threshold (e.g., 3%) | ERCOT believes that engineering judgment is needed when determining the study area and intends to use the same process as is currently used when determining the study area in current LLI studies. | No |
| Monarch Energy | March 4 to July 10 transition creates arbitrary outcomes; projects with identical readiness may be treated differently based purely on timing | Remove or mitigate timing-based distortions in transition window; ensure projects with demonstrated commitment are treated consistently regardless of timing | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Skybox Datacenters | Skybox argues that projects with executed IA/FEA, demonstrated financial commitment, completed studies, and site control should be treated as fixed base load in Batch “0.” Batch Zero should function as an administrative planning tool and not re-screen, re-prioritize, or displace advanced-stage projects. Study validity should be based on project-specific completeness, not timing or interdependencies | Revise § 9.2.1.4 to recognize that projects meeting Section 9 readiness milestones (completed studies, executed IA/FEA, posted financial commitment, site control) are treated as fixed base load inputs in Batch “0.” Clarify that advanced-stage projects are not subject to re-prioritization or displacement | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Crusoe | Crusoe challenges the prioritization of projects based on RPG submission date (Pathway A) over completed LLIS and executed IAs (Pathway B). They argue RPG submission does not represent a completed interconnection study or binding developer commitment. Using RPG dates as a priority metric disadvantages more mature projects and was not vetted through stakeholder process | Delete RPG submission date as ordering criterion; use only completion of § 9.4 study process as priority metric; Pathway B (completed LLIS) takes priority over Pathway A (RPG submission) | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No |
| Oncor | Section 9.2.2(3) requires ILLEs to submit dynamic data by July 10, 2026. Oncor notes that it is unclear whether this requirement applies to Base Load, Load to Be Studied, or both. They also question whether updated dynamic models are expected for Base Load projects. | Clarify in writing whether § 9.2.2(3) applies to Base Load, Load to Be Studied, or both. If applicable to Base Load, clarify whether updated dynamic models are required by July 10, 2026. | ERCOT expects the ILLE to notify its interconnecting TSP of any changes to its dynamic model or data and for that information to be shared with ERCOT. That expectation for Large Loads that will be included in the Batch Zero study, regardless whether the Load will be studied as baseload or to be studied for MW allocation. | No |
| CenterPoint | CEHE notes ambiguity in sequencing and ownership of LCP updates, particularly after Batch Zero completion, and seeks to clarify roles between ERCOT and T/DSPs | Reorder §9.2.4 to reflect correct sequence of updates, Assign final LCP update responsibility to ERCOT after Batch Zero, Clarify that T/DSP role post-study is monitoring compliance, not modifying LCP | ERCOT acknowledges the potential ambiguity and has proposed redlines in Sections 9.2.4 and 9.4. | Yes |
| CenterPoint | CEHE notes that the current ~30-day window between issuance of Batch Zero results and required execution of interconnection agreements is operationally unrealistic, especially without a standardized agreement template | Extend deadline from March 1 to April 1, 2027 (~60 days), Maintain shorter timeline only if a standardized IA form is established by PUCT | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Oncor | Oncor recommends more structured TSP involvement in the Batch Zero Study process, particularly in review of scope and identification of transmission facility improvements. | Require ERCOT to post a preliminary study scope and methodology to the MIS Certified area with a five-business-day TSP review period. After consultation, provide TSPs with a formal written comment opportunity on the list of identified Transmission Facility Improvements. | ERCOT has added language requiring ERCOT to present the Batch Zero study scope to the RPG and solicit feedback from stakeholders. | Yes |
| Oncor | The current draft sets Year 6 (2033) to the ILLE’s requested amount without identifying transmission projects beyond the five-year (2028–2032) study horizon. Oncor believes this leaves necessary upgrades for full load service to be addressed later through RPG or RTP processes, creating inefficiency. | Extend the Batch Zero study horizon into a sixth year so that a comprehensive transmission plan to serve each customer’s full requested load is identified as part of the batch study. Oncor notes that additional study time would likely require only weeks, not months. | ERCOT is still considering this comment. | No |
| CenterPoint | CEHE argues that the Batch Zero study process lacks sufficient procedural structure for ERCOT–TSP coordination, particularly in defining study scope, identifying transmission upgrades, and incorporating TSP cost and feasibility input | Introduce a formal, stepwise coordination process in §9.3.2, including (1)Posting preliminary study scope/methodology for TSP review, (2) Defined TSP comment periods, (3) Formal consultation on transmission upgrades, (4) Circulation of upgrade list for TSP review and feasibility input and (5) Defined timelines for cost estimates and feedback. Support extension of study horizon to include Year 6 (2033) for full planning visibility | ERCOT has added language requiring ERCOT to present the Batch Zero study scope to the RPG and solicit feedback from stakeholders. ERCOT does not believe language formalizing ERCOT-TSP coordination would be helpful. | Yes |
| AEP | Year 6 (2033) load is set to full demand but no clear mechanism to identify/approve transmission upgrades; deferring to RTP/RPG creates uncertainty and repeats current issues | Use Batch Zero to develop a complete, actionable transmission plan covering full load (incl. Year 6), not defer to RTP/RPG | ERCOT is still considering this comment. | No |
| Zero-Emission Grid (ZEG) | Supports publication of Batch Zero cases but notes they are insufficient for full analysis without supporting data | Publish auxiliary files (incl. contingency files) alongside Batch Zero study cases in MIS | ERCOT has added a requirement to post contingency files with the study cases. | Yes |
| Oncor | Oncor raises several technical concerns: (1) An SSWG case alone is insufficient for short-circuit analysis; ERCOT must prepare a modified SPWG case. (2) Short-circuit analysis should evaluate not just the interconnecting station but also facilities impacted by proposed transmission additions. (3) Language about relay setting determination is insufficient. (4) The rule does not specify how short-circuit findings will be integrated into Refinement Study results if additional upgrades are identified. | Require ERCOT to provide an SPWG-based case suitable for short-circuit analysis. Expand scope of short-circuit study to include impacted facilities. Remove insufficient relay-setting language. Clarify how short-circuit findings will be incorporated into Refinement Study outcomes. | ERCOT is still considering this comment. | No |
| CenterPoint | CEHE identifies multiple gaps in short-circuit analysis design, including mismatch between SSWG and SPWG cases, insufficient scope (limited to interconnection point), and lack of clarity on how results feed into refinement decisions | Require ERCOT to develop SPWG-based short-circuit cases, Expand study scope to include impacted facilities beyond interconnection point, Clarify how results translate into additional upgrades in refinement study, Remove inadequate relay-setting language | ERCOT is still considering this comment. | No |
| Crusoe | Crusoe argues that Section 9.7 incorporates financial requirements from an ongoing PUCT rulemaking (Project No. 58481) that is not yet final. They contend that applying $100,000/MW interconnection fees and new security requirements to projects that already executed legacy IAs and posted security is duplicative and punitive. They also note that some projects required no network upgrades and should not be required to post upgrade security | Replace specific dollar amounts with references to PUCT Project No. 58481 final rule amounts; effective date tied to PUCT final rule adoption, not PGRR145 effective date | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| IREN | IREN believes the current Intermediate Agreement requirements include elements that are too burdensome for early-stage development. Specifically: (1) Binding options to lease or purchase should qualify as acceptable site control at this stage. (2) Requirements related to site-related studies and non-ministerial regulatory approvals are premature for an Intermediate Agreement. (3) Lack of a standardized agreement template reduces efficiency and consistency across utilities. | Revise § 9.7.1(1)(a) to allow binding lease or purchase options as valid site control. Delete §§ 9.7.1(1)(c) and (d) (site studies and regulatory approvals requirements).Add new § 9.7.1(k) requiring ERCOT to implement a standardized Intermediate Agreement template. Maintain financial security level at $50,000/MW. | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Skybox Datacenters | Skybox argues that ERCOT’s fixed $/MW interconnection fee construct should not be embedded in the Planning Guide prior to final Commission action. They recommend aligning §9.7.1 with PUCT Project No. 58481 to avoid misalignment and rework once the Commission finalizes the interconnection fee methodology | Replace fixed $/MW financial security and fee language in §9.7.1 with a reference to the amount determined by the Public Utility Commission of Texas under 16 TAC § 25.194 (as amended) | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| TEBA I | TEBA objects to requiring disclosure of power procurement strategy as part of interconnection (intermediate agreement), arguing this is unrelated to interconnection and commercially sensitive | Remove or clarify requirement to disclose power procurement plans as part of interconnection eligibility | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Crusoe | Crusoe argues that Section 9.7 incorporates financial requirements from an ongoing PUCT rulemaking (Project No. 58481) that is not yet final. They contend that applying $100,000/MW interconnection fees and new security requirements to projects that already executed legacy IAs and posted security is duplicative and punitive. They also note that some projects required no network upgrades and should not be required to post upgrade security | Replace specific dollar amounts with references to PUCT Project No. 58481 final rule amounts; effective date tied to PUCT final rule adoption, not PGRR145 effective date | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Crusoe | Duplicative security, fee, and agreement requirements for loads with executed legacy IAs, posted security, and paid CIAC; no accommodation for loads with no required upgrades | Add § 9.7.2(2) deemed compliance provision; exempt loads with no network upgrades from § 9.7.2(j) security and § 9.7.2(g) fee requirements; develop legacy agreement conversion process crediting prior payments | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| IREN | IREN believes the Interconnection Agreement requirements should better reflect long-term project realities and increase process efficiency. Specifically: (1) A five-year minimum lease term does not reflect the expected life of large load projects. (2) Site-related study and regulatory approval disclosures should be standardized to improve transparency and efficiency. (3) Lack of a standardized Interconnection Agreement template creates variability across utilities. | Revise § 9.7.2(1)(a)(i) to require a minimum lease term of 20 years. Revise §§ 9.7.2(1)(c) and (d) to require ERCOT to develop standardized lists of required site-related studies and regulatory approvals. Add new § 9.7.2(k) requiring ERCOT to implement a standardized Interconnection Agreement template. Maintain $50,000/MW interconnection fee. | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Skybox Datacenters | Skybox argues that §§ 9.7.2(1)(f) and (g) should apply prospectively only to IAs/FEAs executed after December 15, 2025. Projects that have already demonstrated financial commitment (e.g., CIAC or TDSP-determined financial security for interconnection-related costs) should be deemed to have satisfied readiness requirements under the prior framework. Skybox further emphasizes that prior financial commitments should be credited on a first-dollar basis to avoid duplicative or overlapping obligations | Apply §§ 9.7.2(1)(f) and (g) only to IAs/FEAs executed on or after December 15, 2025. Deem previously posted financial security, deposits, or CIAC reflecting TDSP-determined interconnection costs as satisfying or crediting toward § 9.7.2 requirements on a first-dollar basis | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Skybox Datacenters | Skybox argues that ERCOT’s fixed $/MW interconnection fee construct should not be embedded in the Planning Guide prior to final Commission action. They recommend aligning §9.7.2 with PUCT Project No. 58481 to avoid misalignment and rework once the Commission finalizes the interconnection fee methodology | Replace fixed $/MW financial security and fee language in §9.7.2 with a reference to the amount determined by the Public Utility Commission of Texas under 16 TAC § 25.194 (as amended) | As explained during the March 30, 2026 Batch Study Workshop, ERCOT intends to file revisions to Sections 9.7 of the Planning Guide after the PUCT issues a final rule in Project No. 58481. Doing so will allow the ILLE, Interconnecting TSP, and Interconnecting DSP to align their respective agreement and financial security with the final rule. | No |
| Skybox Datacenters | Skybox proposes clarifying that financial security requirements for significant equipment and services operate as incremental obligations rather than duplicative ones. Previously posted security, deposits, or CIAC reflecting TDSP-determined interconnection-related costs should be applied sequentially, additional financial security should only cover incremental gaps between existing commitments and actual interconnection costs. | Revise § 9.7.2(1)(h) to require sequential crediting of previously posted financial commitments before imposing additional security requirements. Limit new financial requirements to incremental amounts necessary to address identified gaps. | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No |
| Oncor | Broader ambiguity in DSP vs TSP roles across the PGRR (beyond attestations), especially for study execution, dynamic data submission, short-circuit analysis, and LCP responsibilities; historically TSP-led | (1) Clarify roles across all provisions, (2) Retain TSP as primary entity for technical studies and data submission, (3) Include DSP for notifications / customer-facing elements where appropriate | ERCOT is still considering the redline changes on this topic proposed by Oncor. | No |
| Vistra | Vistra argues that Batch Zero timelines are fundamentally incompatible with PURA §39.169 (SB6), which requires ERCOT to complete system impact studies within 120 days and PUCT action within 180 days. The Batch Zero process, combined with PUCT 58479/58481 requirements, would delay study “completion” by ~9+ months, effectively preventing 39.169 NMA projects (co-located load with existing generation) from meeting statutory timelines. They emphasize that these projects are low transmission risk and explicitly contemplated by the Legislature | Exempt or carve out 39.169 NMA projects from Batch Zero; allow them to proceed under Legacy LLIS process, with optional (not mandatory) participation in Batch; treat such projects as Base Load with no re-study or delay | PURA § 39.169 does not create an entitlement to a decision within 120 days of filing the application for the net metering study. The statute provides that the 120-day clock starts after ERCOT has everything it needs to conduct the study, and so if we move to a Batch study process, it is not unreasonable to conclude that ERCOT will need the Batch Study Process to be completed before the separate net metering study moves forward. | No |
| Vistra | Vistra further argues that 39.169 NMA projects should receive preferential treatment in Batch Zero baseline modeling given their limited number and minimal transmission impact (existing POI, self-supply / curtailment capability). Without this, they are structurally disadvantaged relative to other loads despite being more efficient for the system | Add explicit eligibility pathway for 39.169 NMA projects to be included as Base Load (with timing flexibility up to July 24, 2026 and beyond March 4 cutoff) | There is no basis in PURA § 39.169 to justify preferential treatment to large loads co-locating with existing generation resources. To the contrary, the statutory framework suggests that these arrangements warrant greater scrutiny than other large loads. Moreover, it is possible that a large load co-locating with an existing generation resource can result in the need for transmission upgrades. For example, in Docket No. 58872, the addition of a large load with an existing generation resource was not permitted its full requested MW allocation until after a transmission upgrade is completed. While ERCOT does not agree that large loads participating in a net metering arrangement with an existing generation resource are "disadvantaged," if they are, it is the consequence of co-locating with a generation resource subject to PURA section 39.169. | No |
| Vistra | Vistra highlights that PGRR145 is overly prescriptive in requiring both DSP and TSP involvement in all cases. In practice, Large Load configurations vary (e.g., netted generation, self-supply, export-only BYOG), and in some cases only a TSP relationship is relevant. The current language creates administrative inefficiency and. misalignment with real-world configurations. Note inconsistency between "TDSP" vs. "TSPs and DSPs." | Add “as applicable” flexibility throughout references to DSP/TSP roles; allow configurations where only TSP agreements are required (e.g., co-located generation, non-retail load scenarios) | ERCOT is open to the addition, but is also evaluating whether and when PGRR145 should specify the Interconnecting DSP or Interconnecting TSP. We will incorporate 'as applicable' where appropriate in a future revision request. ERCOT replaced references to "TDSP" with "Interconnecting DSP" and "Interconnecting TSP." | Yes |
| TEBA I | TEBA raises concern with multiple provisions granting ERCOT “sole discretion” (e.g., cancelling projects or determining study validity), arguing this creates unpredictability and undermines the stakeholder process | Replace “sole discretion” language with clear, objective, and transparent criteria for decision-making | ERCOT has proposed redlines in this area. | Yes |
| Satoshi Energy | Satoshi highlights uncertainty created by evolving rules (PGRR145 + PUCT 58481) and lack of clarity on project classification (Base Load vs. Studied Load). They argue developers cannot make financing and construction decisions without clear status visibility | Establish monthly ERCOT communication cadence; provide standardized checklist and pre-deadline classification guidance to ILLEs | ERCOT has stated its intent to provide periodic status updates to the TSPs, who can update their customers, accordingly. | No |
| 3-Waters Technical Services | Argues ERCOT’s planning framework relies on outdated historical weather data (2008–2023) and too short a planning horizon, leading to material underestimation of future load (esp. AI/data centers). Warns of systemic reliability risks (e.g., sympathetic tripping) that financial commitments cannot mitigate | Incorporate forward-looking climate models (e.g., CMIP6) and extend planning horizon to better capture future load and reliability risks | Broad changes to how ERCOT develops its forecasts for use in interconnection or planning studies is beyond the scope of this expedited revision request. | No |
| Sandow Lakes Energy | Sandow argues that Batch Zero does not sufficiently recognize or incentivize projects that bring co-located dispatchable generation. They contend that loads paired with new generation should receive higher priority because they better align with state goals to add new power, reduce system burden, and support faster interconnection. Sandow proposes multiple alternatives, including priority treatment for projects where co-located dispatchable generation covers a substantial share of load demand | Revise Batch Zero prioritization to give highest priority, or explicit priority status, to Large Load projects with co-located dispatchable generation, including projects where new dispatchable generation covers roughly 80–90% of the Large Load demand | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs in Batch Zero. | No |
| Emerald AI | CLR “connect-and-manage” enables load to use underutilized transmission and defer upgrades, improving cost efficiency and siting incentives | Use CLR as a policy tool to accelerate interconnection and minimize transmission expansion costs | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs in Batch Zero. | No |
| Zero-Emission Grid (ZEG) | Notes that many eligibility criteria depend on “Initial Energization” but definition may be ambiguous in practice | Provide clearer definition and guidance on “Initial Energization” for consistent interpretation | The term Initial Energization is a longstanding defined term in Section 2 of the ERCOT Nodal Protocols. | No |

Revised Cover Page Language

| Planning Guide Sections Requiring Revision | 2.1, Definitions 2.2, Acronyms and Abbreviations 3.1.2.1, All Projects 3.1.2, Regional Planning Group Project Submission 3.1.3, Project Evaluation 5.3.5 ERCOT Quarterly Stability Assessment 6.6.1 Modeling of Large Loads Not Co-Located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 6.6.2 Modeling of Large Loads Co-Located with an Existing Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 6.6.3 Modeling of Large Loads Co-Located with a Proposed Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) 9, Large Load Additions at New or Modification of Existing Load Interconnection(s) 9.1, Introduction 9.2.1, Applicability of the Large Load Interconnection Study Process 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in Batch Zero (new) 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero (new) 9.2.1.3, Load not Included in Batch Zero (new) 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads (new) 9.2.2, Submission of Large Load Project Information and Initiation of the Large Load Interconnection Study (LLIS) 9.2.3, Modification of Large Load Project Information 9.2.4, Load Commissioning Plan 9.2.5, Required Interconnection Equipment 9.3, Interconnection Study Procedures for Large Loads 9.3.1, Large Load Interconnection Study (LLIS) 9.3.2, Large Load Interconnection Study Scoping Process 9.3.3, Large Load Interconnection Study Description and Methodology (delete) 9.3.4, Large Load Interconnection Study Elements (delete) 9.3.4.1, Steady-State Analysis (delete) 9.3.4.2, System Protection (Short-Circuit) Analysis (delete) 9.3.4.3, Dynamic and Transient Stability Analysis (delete) 9.4, LLIS Report and Follow-up 9.5, Interconnection Agreements and Responsibilities 9.5.1, Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility (delete) 9.5.2, Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities (delete) 9.6, Initial Energization and Continuing Operations for Large Loads 9.7, Definition of Required Commitment Criteria (new) 9.7.1, Definition of an Intermediate Agreement (new) 9.7.2, Definition of an Interconnection Agreement (new) 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand (new) 9.7.4, Non-Utilized Capacity (new) 9.7.5, Terms for Refund of Financial Security for an ILLE that Energizes (new) 9.8, Legacy Interconnection Study Procedures for Large Loads (new) 9.8.1, Legacy Large Load Interconnection Study (LLIS) (new) 9.8.2, Legacy Large Load Interconnection Study Scoping Process (new) 9.8.3, Legacy Large Load Interconnection Study Description and Methodology (new) 9.8.4, Legacy Large Load Interconnection Study Elements (new) 9.8.4.1, Legacy Steady-State Analysis (new) 9.8.4.2, Legacy System Protection (Short-Circuit) Analysis (new) 9.8.4.3, Legacy Dynamic and Transient Stability Analysis (new) 9.9, Legacy LLIS Report and Follow-up (new) 9.10, Legacy Interconnection Agreements and Responsibilities (new) 9.10.1, Legacy Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility (new) 9.10.2, Legacy Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities (new) |
| --- | --- |

Revised Proposed Guide Language

# 2.1 	DEFINITIONS

# 2.2	ACRONYMS AND ABBREVIATIONS

### 3.1.2	Regional Planning Group Project Submission

(1)	Transmission projects that are proposed for RPG Review, pursuant to Protocol Section 3.11.4.1, Project Submission, shall be submitted according to the provisions outlined in Section 3.1.2.1, All Projects.

#### 3.1.2.1	All Projects

(1)	The submittal of each transmission project (60 kV and above) for RPG Project Review, except for the Transmission Facility improvements submitted based on Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan, should include the following elements:

(a)	The proposed project description including expected cost, feasible alternative(s) considered, transmission topology and Transmission Facility modeling parameter data, and all study cases used to generate results supporting the need for the project in electronic format (powerflow data should be in PTI Power System Simulator for Engineering (PSS/E) RAWD format).  Also, the submission should include accurate maps and one-line diagrams showing locations of the proposed project and feasible alternatives;

(b)	Identification of the SSWG, Dynamics Working Group (DWG), or Regional Transmission Plan powerflow cases used as a basis for the study and any associated changes that describe and allow accurate modeling of the proposed project;

(c)	Description and data for all changes made to the SSWG base cases or Regional Transmission Plan cases used to identify the need for the project, such as Resource unavailability and area peak load forecast;

(d)	A description of the reliability and/or economic problem that is being solved;

(e)	Information that supports any load values that differ from the load forecast used in the base cases identified in item (b) above, including any relevant historical load information or evidence demonstrating that a submitted load value is Substantiated Load;

(f)	A description of the Subsynchronous Resonance (SSR) impact of the proposed project to the generation Facilities in the system pursuant to Protocol Section 3.22.1, Subsynchronous Resonance Vulnerability Assessment, and potential SSR Countermeasure plan for any identified SSR vulnerability, if applicable;

(g)	Desired/needed in-service date for the project, and feasible in-service date, if different;

(h)	The phone number and email address of the single point of contact who can respond to ERCOT and RPG participant questions or requests for additional information necessary for stakeholder review; and

(i)	Analysis of rejected alternatives, including cost estimates, and other factors considered in the comparison of alternatives with the proposed project.

(2)	Both transmission and distribution solutions to performance deficiencies may be considered where applicable.

(3)	If there is any other information, not included above, that the submitting party believes is relevant to consideration of the need for any submitted project, the submitting party should include that information in the project submission.

### 3.1.3	Project Evaluation

(1)	ERCOT and the RPG shall evaluate proposed transmission projects using a variety of tools and techniques as needed to ensure that the system is able to meet applicable reliability criteria in a cost-effective manner.  For most proposed projects, except for the Transmission Facility improvements submitted based on Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan, several alternatives will be identified to meet the reliability criteria or other performance improvement objectives that the proposed project is designed to meet.  The project alternative with the expected lowest cost over the life of the project is generally recommended, subject to consideration of the expected long-term system needs in the area, including, as applicable, any evidence of Substantiated Load, and subject to consideration of the relative operational impacts of the alternatives.

(2)	In some cases, one alternative may be to dispatch the system in such a way that all reliability requirements are met, even without the proposed transmission project or any transmission alternative, resulting in a less efficient dispatch than what would be required to meet the reliability requirements if the proposed project was in place.  Consideration of the merits of this alternative relative to the proposed transmission project is more complex.  To facilitate the discussion and consideration of these alternatives, ERCOT has adopted certain definitions and practices, described in paragraph (4) of Protocol Section 3.11.2, Planning Criteria, and Sections 3.1.3.1, Definitions of Reliability-Driven and Economic-Driven Projects, and 3.1.3.2, Reliability-Driven Project Evaluation below.

(3)	In conducting an independent review of any project, ERCOT may, in its discretion, make adjustments to the planning case to ensure that the case reaches a solution.  When conducting an independent review of any project classified as Tier 1 pursuant to Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT must provide reasonable advance notice to the RPG of any proposed adjustments and an opportunity for stakeholder comment on them.

(4)	As part of its independent review of any project classified as Tier 1 pursuant to Protocol Section 3.11.4, except for the Transmission Facility improvements submitted based on Section 9.5, ERCOT shall:

(a)	Perform a generation sensitivity analysis.  The generation sensitivity analysis will evaluate the effect that proposed Generation Resources and/or ESRs in or near the study area will have on a recommended transmission project.  Generation Resources and ESRs that have signed Standard Generation Interconnection Agreements (SGIAs) but were not included in the study cases because they did not meet all of the requirements for inclusion in the cases pursuant to Section 6.9, Addition of Proposed Generation to the Planning Models, will be included in the sensitivity analysis.  ERCOT shall not consider the results of the generation sensitivity analysis in determining project need during its independent review of the project; and

(b)	Evaluate impacts related to the load scaling used in the study on any constraints resulting in project recommendations.  The results of this evaluation shall be included in the final recommendations in the independent review.

(5)	ERCOT’s independent review shall incorporate and consider historical load and any Substantiated Load.

#### 3.1.3.1	Definitions of Reliability-Driven and Economic-Driven Projects

(1)	Proposed transmission projects are categorized for evaluation purposes into two types:

(a)	Reliability-driven projects; and

(b)	Economic-driven projects.

(2)	The differentiation between these two types of projects is based on whether a simultaneously-feasible, security-constrained generating unit commitment and dispatch is expected to be available for all hours of the planning horizon that can resolve the system reliability issue that the proposed project is intended to resolve.  If it is not possible to simulate a dispatch of the Generation Resources and ESRs such that all reliability criteria are met without the project, and the addition of the project allows the reliability criteria to be met, then the project is classified as a reliability-driven project.  If it is possible to simulate a dispatch of the Generation Resources and ESRs in such a way that all reliability criteria are met without the project, but the project may allow the reliability criteria to be met at a lower total cost, then the project is classified as an economic-driven project.  When performing a simulation of the generating unit commitment and dispatch, only contingencies and limits that would be considered in the operations horizon shall be simulated.

5.3.5	ERCOT Quarterly Stability Assessment

(1)	ERCOT shall conduct a stability assessment every three months to assess the impact of planned large generators and Large Loads subject to the requirements of Section 9.2.1, Applicability of the Large Load Interconnection Study Process, connecting to the ERCOT System.

(a)	For large generators with planned Initial Synchronization in the period under study, the assessment shall derive the conditions to be studied with consideration given to the results of the FIS stability studies.

(b)	For new Large Loads and Load modifications subject to the requirements of Section 9.2.1, with planned Initial Energization in the period under study, the assessment shall derive the conditions to be studied from the most current Load Commissioning Plan and with consideration given to the results of the Large Load Interconnection Study (LLIS) stability studies performed according to Section 9.8.3.4, Legacy Dynamic and Transient Stability Analysis, or stability studies performed as part of the Batch Zero Interconnection Study as described in Section 9.3, Batch Zero Interconnection Study.

(c)	ERCOT may study conditions other than those identified in the FIS, LLIS, or Batch Zero Process stability studies.

(2)	Large generators that are not included in the assessment as described in this Section as result of the IE failing to meet the prerequisites by the deadlines as listed in the table below will not be eligible for Initial Synchronization during that three-month period.  Loads described in paragraph (1)(b) above that are not included in the assessment as a result of failing to meet the prerequisites by the deadlines as listed in the table below will not be eligible for Initial Energization during that three-month period.  The timeline for the quarterly stability assessment shall be in accordance with the following table:

| Generator Initial Synchronization or Large Load Initial Energization Date | Last Day for an IE, Resource Entity, or TSP to meet prerequisites as listed in paragraphs (4) and (5) below | Completion of Quarterly Stability Assessment |
| --- | --- | --- |
| Upcoming January, February, March | Prior August 1 | End of October |
| Upcoming April, May, June | Prior November 1 | End of January |
| Upcoming July, August, September | Prior February 1 | End of April |
| Upcoming October, November, December | Prior May 1 | End of July |

(3)	If the last day for an IE, Resource Entity, or TSP to meet prerequisites or if completion of the quarterly stability assessment as shown in the above table falls on a weekend or holiday, the deadline will extend to the next Business Day.

(4)	The following prerequisites shall be satisfied prior to a large generator being included in the quarterly stability assessment:

(a)	The generator has met the requirements of Section 6.9, Addition of Proposed Generation to the Planning Models.

(b)	The IE has provided all generator data in accordance with the Resource Registration Glossary, Planning Model column, including but not limited to steady state, system protection and stability models.

(i)	The IE shall submit the final dynamic data model at least 45 days prior to the quarterly stability assessment deadline described in paragraph (2) above.  If ERCOT is unable to complete its review prior to the quarterly stability assessment deadline, ERCOT shall not include the Generation Resource, ESR or Settlement Only Generator (SOG) in that quarterly stability assessment.

(ii)	Changes to the dynamic data model after the stability study is deemed complete may subject the Generation Resource, ESR, or SOG to modification of one or more FIS study elements as defined in paragraph (9) of Section 5.3.2.5, FIS Report and Follow-up.  If ERCOT and the lead TSP(s) determine that modifications to one or more FIS study elements are required, then ERCOT shall not include the Generation Resource, ESR, or SOG in a quarterly stability assessment until the revised FIS has been completed in accordance with paragraph (4)(c)(i) below.

(iii)	If an IE submitted a final dynamic data model at least 45 days prior to the quarterly stability assessment deadline but ERCOT determines that the Generation Resource, ESR, or SOG is ineligible to be included in a quarterly stability assessment pursuant to paragraphs (4)(b)(i) or (4)(b)(ii) above, ERCOT will send a notification to the IE.

(c)	The following elements must be complete:

(i)	Final FIS studies, which the TSP must have submitted via the online RIOO system at least 45 days prior to the quarterly stability assessment deadline;

(ii)	Reactive Power Study; and

(iii)	System improvements or mitigation plans that were identified in these studies as required to meet the operational standards established in the Protocols, Planning Guide, Nodal Operating Guides, and Other Binding Documents prior to synchronizing the generator.

(d)	The data used in the studies identified in paragraph (4)(c) above is consistent with data submitted by the IE as required by Section 6.9.

(5)	The following prerequisites must be satisfied prior to the inclusion of a new Large Load or Load modification subject to the requirements of Section 9.2.1 in the quarterly stability assessment:

(a)	The Large Load has met one of the following requirements:

(i)	For quarterly stability assessments with a prerequisite deadline of May 1, 2026 or earlier, the Large Load has met the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities; and

(ii)	For quarterly stability assessments with a prerequisite deadline of August 1, 2026, November 1, 2026, or February 1, 2027, the Large Load has met the requirements of paragraph (1) of Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in Batch Zero Interconnection Process; or

(iii)	For quarterly stability assessments with a prerequisite deadline of May 1, 2027 or later, the Large Load has met the requirements of paragraph (2) of Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment;

(b)	The Load Commissioning Plan has been updated to reflect the results of completed studies as required by paragraph (1) of Section 9.2.4, Load Commissioning Plan;

(c)	If applicable, the Interconnecting TSP has provided to ERCOT the dynamic load model it received from the Interconnecting Large Load Entity (ILLE) per paragraph (1) of Section 9.8.4.3, Legacy Dynamic and Transient Stability Analysis, and written affirmation that no changes to the project information have been communicated by the ILLE, per Section 9.2.3, Modification of Large Load Project Information, that would invalidate the model;

(d)	The Reactive Power Study, if required according to Protocol Section 3.15, Voltage Support, must be complete; and

(e)	The data used in the studies identified in paragraph (c) above is consistent with data used in the final LLIS studies approved per Section 9.9 or completed Batch Zero Interconnection Study as described in Section 9.4, as applicable.

(6)	At any time following the inclusion of a large generator or applicable Large Load in a stability assessment, but before the Initial Synchronization of the generator or Initial Energization of the Large Load, if ERCOT determines, in its sole discretion, that the generator or Large Load no longer meets the prerequisites described in paragraphs (4) or (5) above, or that an IE or ILLE has made a change to the design of the generator or Large Load that could have a material impact on ERCOT System stability, then ERCOT may refuse to allow Initial Synchronization of the generator or Initial Energization of the Large Load.  ERCOT shall include the generator or Large Load in the next quarterly stability assessment period that commences after identification of the material change or after the generator or Large Load meets the prerequisites specified in paragraphs (4) or (5) above, as applicable.  If ERCOT determines, in its sole discretion, that the change to the design of the generator or Large Load would not have a material impact on ERCOT System stability, then ERCOT may not refuse to allow Initial Synchronization of the generator or Initial Energization of the Large Load due to this change.

(7)	ERCOT shall post to the MIS Secure Area a report summarizing the results of the quarterly stability assessment within ten Business Days of completion.

### 6.6.1	Modeling of Large Loads Not Co-Located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	The Interconnecting Transmission Service Provider (TSP) shall not add a new Large Load or Load modification subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, to the Network Operations Model until the Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment.

### 6.6.2	Modeling of Large Loads Co-Located with an Existing Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	The addition of a new Large Load to an existing Generation Resource, ESR, or SOG, or the modification of an existing Load at the Generation Resource, ESR, or SOG, subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, is considered a material modification of the Resource Registration as described in paragraph (8) of Section 6.8.2, Resource Registration Process.  The Resource Entity shall update the Resource Registration data to reflect the new or increased Load.

(2)	The Resource Entity shall not update the Resource Registration data to reflect the new or increased Load until the Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment.

### 6.6.3	Modeling of Large Loads Co-Located with a Proposed Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG)

(1)	A new Large Load co-located with a proposed Generation Resource, ESR, or SOG shall be included in the data provided by the Interconnecting Entity (IE) or Resource Entity during the Resource Registration process.

(2)	The Large Load shall not be included in the Network Operations Model until the following requirements have been satisfied:

(a)	The Large Load has met the requirements for inclusion in the quarterly stability assessment as described in paragraph (5) of Section 5.3.5, ERCOT Quarterly Stability Assessment

; and

(b)	All applicable requirements of Section 6.9, Addition of Proposed Generation to the Planning Models, have been completed.

# 9	LARGE LOAD Interconnection or Modification

9.1	Introduction

(1)	This Section defines the requirements and processes used to facilitate new or modified Large Load interconnections with the ERCOT System. It documents the transition from a process that relied on individual Large Load interconnection studies to a new process referred to as the Batch Zero Process. The Batch Zero Process consists of a Batch Zero Interconnection Study and a Batch Zero Refinement Study.  The requirements are designed to:

(a)	Facilitate studies to identify potential system limitations and determine, to the extent feasible, facilities needed to interconnect a new Large Load to or modify an existing Large Load on the ERCOT network;

(b)	Facilitate orderly and organized Large Load interconnections, while allowing ERCOT to determine whether the interconnection of the proposed Large Load would comply with North American Electric Reliability Corporation (NERC) Reliability Standards, ERCOT Protocols, ERCOT Planning and Operating Guides, Transmission Service Provider (TSP) criteria, and any Applicable Legal Authority (ALA);

(c)	Specify the communications required between Interconnecting Large Load Entities (ILLEs), TSPs, Distribution Service Providers (DSPs), Resource Entities, Interconnecting Entities (IEs), and ERCOT;

(d)	Provide the best information on future Large Load additions for use in identifying, forecasting, and analyzing short- and long-range ERCOT capabilities, demands, and reserves; and

(e)	Provide ERCOT accurate data about a Large Load subject to the provisions detailed in Section 9.2.1, Applicability of the Batch Zero Process, to ensure that ERCOT and stakeholders have the information necessary for planning purposes.

(2)	Submission of all project data, and other communications described in this Section shall be in the manner and format prescribed by ERCOT.  ERCOT shall publicly post the format of such submissions on the ERCOT website.

(3)	ERCOT shall manage an email list that includes Transmission and/or Distribution Owner Load Interconnection to facilitate communication of confidential Large Load-related information among Interconnecting DSPs and Interconnecting TSPs and ERCOT.  Membership to this email list will be limited to ERCOT and appropriate Interconnecting DSPs’ and Interconnecting TSPs’ personnel.

(4)	Where an Interconnecting DSP must submit a notarized attestation, it may designate another electric utility, Municipally Owned Utility (MOU), or Electric Cooperative (EC) to submit the notarized attestation on the Interconnecting DSP’s behalf, provided such designation is made in writing.

### 9.2.1	Applicability of the Batch Zero Process

(1)	Any request to interconnect or modify a Load Facility that meets one or more of the following criteria shall be subject to an ERCOT interconnection process:

(a)	A new Large Load;

(b)	A modification of any existing Load Facility that increases the aggregate peak Demand of the Facility by 75 MW or more; or

(c)	A modification of an existing Large Load that changes or adds a Point of Interconnection (POI) or Service Delivery Point to a different electrical bus on a different electrical circuit.

(2)	ERCOT shall not evaluate Large Load interconnection requests meeting the requirements of paragraph (1) above according to the legacy Large Load Interconnection Study (LLIS) process defined in Sections 9.8-9.10 of this Planning Guide.

(3)	ERCOT shall evaluate Large Load interconnection requests meeting the eligibility criteria in Sections 9.2.1.1 or 9.2.1.2 according to the Batch Zero Process defined in Sections 9.2-9.6.

(4)	Large Loads that do not meet the eligibility criteria in Sections 9.2.1.1 or 9.2.1.2 shall be ineligible to receive approval for Initial Energization until evaluated through a future interconnection study process.

### 9.2.1.1	Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process

(1)	A Large Load that meets one of the following requirements on or before July 10, 2026, will be modeled in the Batch Zero Process as base load according to paragraph (2) below and its Demand is not subject to further evaluation.

(a)	A Large Load that achieved Initial Energization before March 25, 2022;

(b)	A Large Load that achieved Initial Energization between March 25, 2022, and July 10, 2026;

(c)	A Large Load that met the qualification requirements for inclusion in the quarterly stability assessment or was included in an interim voltage-ride-through assessment on or before May 1, 2026, and that meets both of the following criteria:

(i)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has attested to ERCOT that the DSP or TSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance so the equipment can be installed by the requested Initial Energization date or December 31, 2026, whichever is earlier; and

(ii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence to support the attestation;

(d)	A Large Load with a requested Initial Energization date on or before December 31, 2027, that has not achieved Initial Energization as of July 10, 2026, and that meets all the following requirements:

(i)	ERCOT has determined the Large Load has a complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads;

(ii)	On or before July 24, 2026, the Interconnecting DSP has submitted to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP that the ILLE has executed an interconnection agreement that meets the requirements defined in Section 9.7.2, Definition of an Interconnection Agreement;

(iii)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has attested to ERCOT that the DSP or TSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance of the requested Initial Energization date so the equipment can be installed by the ILLE’s requested Initial Energization date;

(iv)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested to the DSP or TSP that it has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence to support the attestation; and

(v)	On or before July 24, 2026, the Interconnecting DSP or Interconnecting TSP has informed ERCOT that the ILLE has attested and provided evidence to the DSP or TSP that it has purchased all necessary ILLE-owned high-voltage transformers and circuit breakers and will take delivery sufficiently in advance of its requested Initial Energization date so the equipment can be installed by the ILLE’s requested Initial Energization date; or

(e)	A Large Load with a requested Initial Energization date on or after January 1, 2028 and that meets all of the following requirements:

(i)	ERCOT has determined the Large Load has a complete and valid set of interconnection studies as described in Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads; and

(ii)	On or before July 24, 2026, the Interconnecting DSP has submitted to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP that the ILLE has executed an interconnection agreement that meets the requirements defined in Section 9.7.2, Definition of an Interconnection Agreement.

(2)	ERCOT shall model Large Loads meeting the requirements of paragraph (1) above in Batch Zero as follows:

(a)	A Large Load meeting the requirements of paragraph (1)(a) shall be modeled at the Large Load’s level of peak Demand reported to ERCOT in response to ERCOT’s annual request for information as part of the development of the 2026 Regional Transmission Plan (RTP).

(b)	A Large Load meeting the requirements of paragraph (1)(b) and (1)(c) shall be modeled in each year of the study at the Large Load’s level of peak Demand that is defined in one of the following documents. In the event the Large Load is represented in both documents, ERCOT shall use the document with the lower values of Demand.

(i)	The level of peak Demand reported to ERCOT in response to ERCOT’s annual request for information as part of the development of the 2026 RTP; or

(ii)	The level of peak Demand indicated in the most recent Load Commissioning Plan (LCP), if applicable, provided to ERCOT on or before July 24, 2026. The LCP provided must be consistent with the previously completed studies and existing agreements.

(c)	A Large Load meeting the requirements of paragraphs (1)(d) or (1)(e) shall be modeled in each year of the study at the level of peak Demand that is the lesser of:

(i)	The level of peak Demand that can be served reliably as indicated in the Large Load’s qualifying complete and valid interconnection studies, as described in Section 9.2.1.4, or

(ii)	The level of peak Demand specified in the Large Load’s executed interconnection agreement that meets the requirements defined in Section 9.7.2, Definition of an Interconnection Agreement.

### 9.2.1.2	Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero

(1)	A Large Load that meets one of the requirements described in this paragraph shall be included in Batch Zero as load subject to reliability assessment and allocation.

(a)	A Large Load with a requested Initial Energization date on or before December 31, 2027, that has not achieved Initial Energization as of July 10, 2026, that meets the requirements documented in paragraphs (1)(d)(i) and (1)(d)(ii) of Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, but does not meet one or more requirements documented in paragraphs (1)(d)(iii) through (1)(d)(v) of Section 9.2.1.1; or

(b)	A Large Load that meets all the following requirements:

(i)	The Interconnecting DSP has submitted to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP that the ILLE has executed an intermediate agreement that meets the requirements defined in Section 9.7.1, Definition of an Intermediate Agreement; and

(ii)	ERCOT has determined the Large Load meets one of the following:

(A)	The Large Load was included in the list established in paragraph (4) of Section 9.2.1.4, Evaluation of Existing Interconnection Studies for Large Loads, but was determined to have invalid existing studies according to the methodology established in paragraphs (4)(d) and (4)(e) of that Section; or

(B)	The Large Load has received ERCOT approval of a steady state or stability study as described in Section 9.8, Legacy Interconnection Study Procedures for Large Loads and Section 9.9, Legacy LLIS Report and Follow-up.

(2)	ERCOT shall model a Large Load meeting the requirements of paragraph (1) above according to the values in the most recent Load Commissioning Plan (LCP) provided by the Interconnecting TSP or Interconnecting DSP on or before July 24, 2026.  The LCP shall reflect an Initial Energization date of January 1, 2028, or later.

### 9.2.1.3	Load not Included in Batch Zero

(1)	ERCOT shall not include in Batch Zero any Large Load that does not meet requirements described in Sections 9.2.1.1 or 9.2.1.2.

(2)	ERCOT shall not include any Large Load that otherwise meets the requirements described in Sections 9.2.1.1 or 9.2.1.2 if the Interconnecting TSP or Interconnecting DSP fails to provide to ERCOT all information required by Section 9.2.2 on or before July 24, 2026.

### 9.2.1.4	Evaluation of Existing Interconnection Studies for Large Loads

(1)	ERCOT shall use the methodology described in this Section to assess the completeness and validity of previous studies as prescribed in Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process and Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero.

(2)	During its review, ERCOT, in consultation with the Interconnecting DSP or Interconnecting TSP, will determine the completeness and validity of previous studies.

(3)	ERCOT shall consider previous studies for Large Loads that have not achieved Initial Energization by July 10, 2026, to be fully complete and valid without additional review if they meet one of the following criteria:

(a)	The Large Load was included in one or more studies submitted to the Regional Planning Group (RPG) before December 15, 2025, that Load contributed to establishing the reliability need for the RPG project, and the proposed project received RPG acceptance or ERCOT endorsement as described in Protocol Section 3.11.4.9, Regional Planning Group Acceptance and ERCOT Endorsement, on or before March 4, 2026;

(b)	The Large Load met the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities, on or before March 4, 2026; or

(c)	The Large Load was included in the Permian Basin Reliability Plan Study completed by ERCOT in 2024 and approved by the Public Utility Commission of Texas (PUCT) in Docket No. 55718, and the Load contributed to establishing the need for the identified transmission projects.

(4)	ERCOT will consider previous studies for Large Loads that have not achieved Initial Energization by July 10, 2026, and that do not have studies meeting the criteria in paragraph (3) above to be fully complete and valid according to the following process:

(a)	ERCOT shall identify all Large Loads that meet all of the following criteria:

(i)	The Interconnecting DSP or Interconnecting TSP has, by July 24, 2026, determined the dynamic data submitted by the ILLE per paragraph (3) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process, is not expected to adversely impact the results from the previous stability study; and

(ii)	The Large Load meets either of the following conditions:

(A)	The Large Load was included in one or more studies submitted to the Regional Planning Group (RPG) before December 15, 2025, that Load contributed to establishing the reliability need for the RPG project, and the proposed project received RPG acceptance or ERCOT endorsement as described in Protocol Section 3.11.4.9, Regional Planning Group Acceptance and ERCOT Endorsement, on or before July 10, 2026; or

(B)	The Large Load met the requirements of Section 9.9, Legacy LLIS Report and Follow-up, and Section 9.10, Legacy Interconnection Agreements and Responsibilities, on or before July 10, 2026.

(b)	ERCOT shall create a list of all Large Loads meeting the criteria in paragraph (4)(a)(ii) above. ERCOT shall order the list according to the date each Large Load met the applicable criteria in paragraph (4)(a)(ii). The Large Load with the oldest date shall be given first position, with subsequent loads following in order of date the criteria in paragraph (4)(a)(ii) were met.

(i)	In the event a Large Load meets both the criteria in paragraph (4)(a)(ii)(A) and (4)(a)(ii)(B) or in the event the Large Load meets the criteria in paragraph (4)(a)(ii)(A) multiple times, ERCOT shall use the date that gives the Large Load the highest position in the list.

(c)	In the event two Large Loads met the criteria documented in paragraph (4)(a)(ii) on the same date, ERCOT shall use the following methodology to determine placement on the list:

(i)	If both Large Loads were included in the same RPG study, ERCOT shall give them equal placement on the list;

(ii)	If each Large Load is from a separate RPG study, the Load with the earlier RPG study submission date will receive priority;

(iii)	If one Large Load met the criteria described in paragraph (4)(a)(ii)(A) and the other met the criteria described in paragraph (4)(a)(ii)(B), the Load meeting the criteria of paragraph (4)(a)(ii)(A) will receive priority regardless of submission date; and

(iv)	If both Large Loads met the criteria described in paragraph (4)(a)(ii)(B), the Load with the earlier submission date of a TSP study to ERCOT will receive priority;

(d)	The Large Load(s) in the first position on the list shall be considered to have valid existing studies.

(e)	ERCOT shall evaluate each subsequent Large Load on the list in the order established in paragraphs (4)(b) and (4)(c). For each Large Load or set of Large Loads sharing equal placement under paragraph (4)(c)(i) evaluated, ERCOT shall consider the existing studies valid if, in ERCOT’s sole discretion, each Large Load on the list already determined to have valid existing studies is:

(i)	Located outside of the study area of the Large Load under review; or

(ii)	Located within the study area and included in the existing studies for the Large Load under review.

### 9.2.2	Submission of Large Load Information for Batch Zero Process

(1)	For any Load request meeting one or more criteria defined in paragraph (1) of Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, and 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, the following actions shall be completed prior to the initiation of the Batch Zero Interconnection Study described in Section 9.3, Batch Zero Interconnection Study.

(a)	Submission of all information, including but not limited to, data required by the Interconnecting Distribution Service Provider (DSP), the Interconnecting Transmission Service Provider (TSP), and ERCOT to perform steady state, short circuit, dynamic and transient stability analyses and any other studies the Interconnecting TSP or ERCOT deems necessary to reliably interconnect the Load;

(b)	Submission of a preliminary Load Commissioning Plan (LCP) that fully reflects the proposed project schedule; and

(c)	Written acknowledgement from the Interconnecting Large Load Entity (ILLE) of its obligations to notify and update the Interconnecting DSP and Interconnecting TSP of changes to the Large Load project information or to the load composition, technology, parameters, or development schedule as described in Section 9.2.3, Modification of Large Load Information, during the interconnection process.

[PGRR115: Insert paragraph (d) below upon system implementation of NPRR1234:] (d) Payment of the LLIS Application Fee to ERCOT as described in paragraph (4).

(2)	The Interconnecting DSP or Interconnecting TSP shall submit the information described in paragraphs (1)(a) through (1)(c) above on behalf of the ILLE on or before July 24, 2026.

(3)	By July 10, 2026, the ILLE must provide to ERCOT and the Interconnecting DSP or Interconnecting TSP dynamic data including the necessary models, parameters, and supporting documentation required for accurate representation of the Large Load. The data shall be compatible with the current version of the planning and operations model software, as described in the Dynamic Working Group Procedure Manual. If a dynamic stability study on the Large Load has previously been performed, Interconnecting DSP or Interconnecting TSP must also provide to ERCOT by July 24, 2026, a written determination as to whether the dynamic data submitted by the ILLE is expected to adversely impact the results from the previous stability study.

[PGRR115: Insert paragraph (3) below upon system implementation of NPRR1234:] (4) The ILLE shall pay to ERCOT the LLIS Application Fee, as described in the ERCOT Fee Schedule prior to the commencement of the LLIS. The interconnecting TSP, Resource Entity, or Interconnecting Entity (IE) may choose to submit this fee to ERCOT on the behalf of the ILLE. Payment of the ERCOT LLIS Application Fee shall not affect the independent responsibility of the ILLE to pay for interconnection studies conducted by the interconnecting TSP or for any Distribution Service Provider (DSP) studies.

### 9.2.3	Modification of Large Load Information

(1)	The Interconnecting DSP or Interconnecting TSP shall update any project information submitted per paragraph (1) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process, within ten Business Days of being notified by the ILLE of a material change.

(2)	The ILLE shall notify the Interconnecting DSP or Interconnecting TSP if a change to the load composition, technology, or parameters occurs after the ILLE has provided the DSP or TSP with its initial dynamic data per paragraph (3) of Section 9.2.2, Submission of Large Load Information for Batch Zero Process.  Upon such notification, the ILLE shall provide to the Interconnecting DSP or Interconnecting TSP updated dynamic data reflecting the change.  The Interconnecting DSP or Interconnecting TSP shall promptly provide the updated dynamic data to ERCOT.

### 9.2.4	Load Commissioning Plan

(1)	The Load Commissioning Plan (LCP) shall be maintained and updated by the Interconnecting DSP and Interconnecting TSP and ERCOT as prescribed in Section 9 of the Planning Guide using information provided by the ILLE.  The LCP must specify the load increments and timeline by which the ILLE intends to increase peak Demand.  The LCP shall reflect the most currently available information about the Large Load and ILLE and shall be updated upon receipt of updated project information from the ILLE and as otherwise described in this Section.

(2)	Upon the completion of the Batch Zero Interconnection Study, as described in Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment, ERCOT shall update the LCP to reflect the amount of peak Demand that can be served reliably for each year of the Batch Zero Interconnection Study scope.

(3)	Upon the execution of interconnection agreements prescribed in Section 9.7.2, Definition of an Interconnection Agreement, the Interconnecting DSP or Interconnecting TSP shall update the LCP to reflect the executed interconnection agreement.

(4)	The Interconnecting DSP or Interconnecting TSP shall continue to maintain the LCP after Initial Energization until the Large Load reaches its full requested peak Demand, updating as needed to reflect changes in the Large Load construction and timelines.

### 9.2.5	 Required Interconnection Equipment

(1)	Each Service Delivery Point for a Large Load not co-located with a Generation Resource, Energy Storage Resource (ESR), or Settlement Only Generator (SOG) interconnected at transmission voltage to the ERCOT System must have a permanent configuration consisting of one or more breakers capable of interrupting fault current to isolate the Large Load from the ERCOT System without interrupting flow on the associated transmission lines.  The breakers shall be under the remote control of the applicable Transmission Operator (TO).

(2)	Each Large Load co-located with a Generation Resource, ESR, or SOG interconnected at transmission voltage to the ERCOT System must have a permanent configuration consisting of one or more breakers capable of interrupting fault current to isolate the Large Load from the ERCOT System without isolating any of the co-located generators.  The breakers shall be remotely controllable at the direction of the applicable Qualified Scheduling Entity (QSE).

(3)	Large Loads submitted under the legacy Large Load Interconnection Study (LLIS) process described in Sections 9.8-9.10 with an initial LLIS submission date on or after June 1, 2025, and Large Loads meeting requirements, described in Sections 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, and 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, for inclusion in the Batch Zero Interconnection Study shall not have an interconnection configuration such that any category P1 or P7 event described in the North American Reliability Corporation (NERC) Reliability Standard addressing transmission planning performance requirements results in more than 1,000 MW of consequential Load loss.

(a)	All Loads co-located with a Generation Resource as described in Protocol Section 10.3.2.3, Generation Netting for ERCOT-Polled Settlement Meters, shall be subject to the requirements of this paragraph.

(4)	Large Loads submitted under the legacy Large Load Interconnection Study (LLIS) process described in Sections 9.8-9.10 with an initial LLIS submission date before June 1, 2025, shall comply with the requirements of paragraph (3) of this Section if, on or after June 1, 2025, a modification to the Large Load subject to the requirements of Section 9.2.1, Applicability of the Batch Zero Process, is made.

9.3	Batch Zero Interconnection Study

(1)	This Section establishes the procedures for conducting a Batch Zero Interconnection Study for new or modified Large Loads, as defined by Section 9.2.1.1, Eligibility Criteria for Inclusion of a Large Load as Base Load not Subject to Additional Study in the Batch Zero Process, and Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero.

### 9.3.1	Batch Zero Process Overview and Timelines

(1)	The Batch Zero Interconnection Study consists of a singular, system-wide study covering steady-state analysis and stability screening analysis performed by ERCOT.

(2)	The Batch Zero Process shall be conducted according to the following timeline:

(a)	Interconnecting Distribution Service Providers (DSPs) and Interconnecting Transmission Service Providers (TSPs) must provide to ERCOT all information required by Section 9.2.2, Submission of Large Load Information for Batch Zero Process, on or before July 24, 2026.  ERCOT will notify each Interconnecting DSP and Interconnecting TSP of how each Large Load submitted under Section 9.2.2 is included and classified in the Batch Zero Interconnection Study according to the methodology defined in Section 9.2.1, Applicability of the Batch Zero Process, on or before August 7, 2026;

(b)	ERCOT shall provide the Batch Zero Interconnection Study report to all Interconnecting DSPs and Interconnecting TSPs on or before January 29, 2027. ERCOT shall also communicate updated Load Commissioning Plans (LCPs) to Interconnecting Large Load Entities (ILLEs) reflecting Batch Zero MW allocations by this date;

(c)	Interconnecting DSPs shall provide to ERCOT a list of all Large Loads for which the ILLE has met the commitment requirements, as described in Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment, on or before March 1, 2027;

(d)	ERCOT shall complete the Batch Zero Refinement Study and provide a Batch Zero transmission plan to the Regional Planning Group (RPG), as described in Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan, on or before June 1, 2027.

(3)	The Interconnecting DSP or Interconnecting TSP must complete the short-circuit study prescribed in Section 9.5.2, System Protection (Short-Circuit) Analysis, and provide a study report to ERCOT 30 days prior to the date specified in paragraph (2)(d) above.

### 9.3.2	Batch Zero Interconnection Study Methodology

(1)	ERCOT shall establish a study scope and methodology to assess the steady state and stability impact of the Large Loads subject to assessment in accordance with paragraph (2) of Section 9.2.1.2, Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero, for years 2028 through 2032.

(2)	ERCOT shall present the study scope and methodology to the Regional Planning Group (RPG) and allow an opportunity for stakeholder comments.

(3)	ERCOT shall post the initial Batch Zero Interconnection Study cases and contingencies, the final Batch Zero Interconnection Study cases, the initial Batch Zero Refinement Study cases and contingencies, and the final Batch Zero Refinement Study cases to be used in the study on the MIS Secure area once available.

(4)	For each Large Load subject to assessment in the Batch Zero Interconnection Study, ERCOT shall identify any planning criteria violations associated with the proposed addition in accordance with the study scope and shall endeavor to resolve any identified performance deficiencies by identifying Transmission Facility improvements for 2028 through 2033.

(a)	ERCOT shall consult with the applicable TSP(s) when identifying proposed Transmission Facility improvements.

(b)	After consultation, and once it is available, ERCOT shall provide a list of initial Transmission Facility improvements to the applicable TSP(s) for review.

(c)	The applicable TSP(s) shall respond to ERCOT in writing with any comments to the list of initial Transmission Facility improvements, including an assessment of the construction feasibility to construct the projects, within 10 Business Days.

(d)	Each TSP shall provide any Transmission Facility improvement cost estimates within 10 Business Days of ERCOT’s request.

(e)	ERCOT shall make final determinations on the Transmission Facility improvements that will be identified in the study report.

(5)	ERCOT shall determine the amount of load that may be served reliably for each year within the study scope.

9.4	Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment

(1)	On or before the date specified in paragraph (2)(b) of Section 9.3.1, Batch Zero Process Overview and Timelines, ERCOT will provide to all Interconnecting Distribution Service Providers (DSPs) and Interconnecting Transmission Service Providers (TSPs):

(a)	A report summarizing the results of the Batch Zero Interconnection Study and proposed Transmission Facility improvements;

(b)	An updated Load Commissioning Plan (LCP) for each Large Load that was assessed in the Batch Zero Interconnection Study that reflects the amount of peak Demand that can be served reliably for each year of the Batch Zero Interconnection Study scope; and

(c)	An estimate of the ILLE’s security requirements for each proposed Transmission Facility improvement identified in the ILLE’s LCP consistent with paragraph (1)(j) of Section 9.7.2, Definition of an Interconnection Agreement.

(2)	In order to accept the allocated MW amounts and schedule documented in the LCP, the ILLE must execute an interconnection agreement that meets the requirements in Section 9.7.2, Definition of an Interconnection Agreement.  In the event the executed interconnection agreement reflect MW amounts that are lower than the values determined in paragraph (1)(b) above, the Interconnecting DSP shall update the LCP to reflect the values memorialized in the interconnection agreement.

(3)	The Interconnecting DSP must submit to ERCOT a notarized attestation sworn to by the DSP’s representative, official, officer, or other authorized person with binding authority over the DSP confirming that the ILLE has executed the interconnection agreement on or before the date specified in paragraph (2)(c) of Section 9.3.1.

(4)	Any Large Load for which the Interconnecting DSP or its designated representative has not provided the notarized attestation mandated in paragraph (2) above by the date specified in paragraph (2)(c) of Section 9.3.1 is considered to have withdrawn from the Batch Zero Process and shall not be included in the Batch Zero Refinement Study described in Section 9.5, Batch Zero Study Refinement and Delivery of Transmission Plan.  These Large Loads shall not be eligible for Initial Energization unless included in a future batch study.

(5)	Nothing in this Section shall be construed to prohibit an ILLE from negotiating and preparing an interconnection agreement described in Section 9.7.2 prior to receipt of the Batch Zero Interconnection Study results as described in paragraph (1) above.

9.5	Batch Zero Study Refinement and Delivery of Transmission Plan

(1)	The Batch Zero Refinement is an activity performed by ERCOT, in consultation with the Interconnecting DSPs and Interconnecting TSPs, to update the Batch Zero Interconnection Study performed per Section 9.3, Batch Zero Interconnection Study, to only include Large Loads that met the required commitment criteria per Section 9.4, Batch Zero Report and Interconnecting Large Load Entity (ILLE) Commitment. The goal of the Batch Zero Refinement Study is to determine which Transmission Facility improvements identified in the Batch Zero Interconnection Study are still needed, needed with modifications, or are no longer needed.

9.5.1	ERCOT Activities During the Batch Zero Refinement Period

(1)	After the deadline established in paragraph (2)(c) of Section 9.3.1, Batch Zero Process Overview and Timelines, for the Interconnecting Distribution Service Provider (DSP) or Interconnecting Transmission Service Provider (TSP) to notify ERCOT which Large Loads included in the initial Batch Zero Interconnection Study have met the requirements for commitment, ERCOT will initiate the Batch Zero Refinement Study.

(2)	During the Batch Zero Refinement Study period ERCOT shall update its Batch Zero Interconnection Study to evaluate if the remaining Large Loads under assessment still result in planning criteria violations and if the Transmission Facility improvements for 2028-2032 identified in the Batch Zero Interconnection Study require modification.

(3)	ERCOT shall communicate with applicable Interconnecting DSPs and Interconnecting TSPs during ERCOT’s evaluation. Each Interconnecting DSP and Interconnecting TSP shall promptly respond to all communications and provide recommendations to ERCOT as soon as practicable. Each Interconnecting DSP and Interconnecting TSP shall provide any Transmission Facility improvement cost estimates within 15 Business Days of ERCOT’s request.

(4)	ERCOT shall prepare a final report for the Batch Zero Refinement Study described in this Section. The final report shall include a list of recommended Transmission Facility improvements, a description of the need for those Transmission Facility improvements, cost estimates for those Transmission Facility improvements, and any alternate improvements formally considered by ERCOT.

(5)	ERCOT shall submit the final report for RPG Project Review by the date specified in paragraph (2)(d) of Section 9.3.1 unless the set of Transmission Facility improvements are classified as a Tier 4 project according to Nodal Protocol Section 3.11.4.3.  This final report shall serve as ERCOT’s independent review in accordance with Protocol Section 3.11.4.6 or Protocol Section 3.11.4.7, unless ERCOT decides to create an updated final report based on comments received during the RPG Project Review.

(6)	The Batch Zero Refinement Study described in this section shall not include an adjustment to the allocated MWs for any Large Loads included in the Batch Zero Interconnection Study for which the Large Load has met the required commitment criteria per Section 9.4.

9.5.2	System Protection (Short-Circuit) Analysis

(1)	The Interconnecting DSP or Interconnecting TSP shall perform a short-circuit analysis during the Batch Zero Refinement Study period.

(2)	The short-circuit study shall use the ERCOT base cases posted per paragraph (2) of Section 9.3.2, Batch Zero Interconnection Study Methodology, appropriate for the desired Initial Energization date and Load Commissioning Plan of the Load.

(3)	The Interconnecting DSP or Interconnecting TSP will determine the maximum available fault currents at the interconnection substation for determining switching device interrupting capabilities and protective relay settings.

(4)	The Interconnecting DSP or Interconnecting TSP must provide the short-circuit study report to ERCOT on or before the date prescribed in paragraph (3) of Section 9.3.1, Batch Zero Process Overview and Timelines.

9.6	Initial Energization and Continuing Operations for Large Loads

(1)	Each Large Load shall meet the conditions established by ERCOT before proceeding to Initial Energization.  These conditions may include, but are not limited to:

(a)	Inclusion of the Load in the Network Operations Model in accordance with Section 6.6, Modeling of Large Loads;

(b)	Verification that all required telemetry is operational and accurate;

(c)	Completion of the requirements of Section 5.3.5, ERCOT Quarterly Stability Assessment;

(d)	Completion and approval of any required Subsynchronous Oscillation (SSO) studies, SSO Mitigation plan, SSO Countermeasures, and SSO monitoring, if required; and

(e)	Submission of a current Load Commissioning Plan (LCP) meeting the requirements of Section 9.2.4, Load Commissioning Plan.

(2)	During continuing operations:

(a)	The Interconnecting DSP, Interconnecting TSP, or, if applicable, the Resource Entity shall notify ERCOT if it identifies that a Large Load has exceeded a limit on peak Demand established in the LCP.

(b)	Pursuant to Section 9.2.3, Modification of Large Load Information, if an ILLE modifies its facilities such that a previously provided dynamic load model is invalid, the Large Load shall notify and provide an updated model to the Interconnecting Distribution Service Provider (DSP) and Interconnecting Transmission Service Provider (TSP) that provides service to the Large Load.  The Interconnecting DSP or Interconnecting TSP shall subsequently provide this updated dynamic load model to ERCOT.

9.7	Definition of Required Commitment Criteria

9.7.1	Definition of an Intermediate Agreement

(1)	An ILLE must execute an intermediate agreement with the Interconnecting Distribution Service Provider (DSP) and, if different from the Interconnecting DSP, the Interconnecting Transmission Service Provider (TSP).  If the Interconnecting DSP and the Interconnecting TSP are different entities, the intermediate agreement must specifically identify each entity’s responsibilities under this Section 9.7.1, including which entity will accept financial security from the ILLE.  An intermediate agreement must meet the following requirements:

(a)	The Interconnecting Large Load Entity (ILLE) must demonstrate site control for the proposed load location through provision of one of the following property interests to the Interconnecting DSP or the Interconnecting TSP:

(i)	A signed and executed lease agreement for one or more parcels of land sufficient to accommodate the ILLE’s planned facilities at the proposed load location for a duration of at least five years from the date the ILLE is expected to reach the total non-coincident peak demand as stated in the agreement, referred to as contracted peak demand;

(ii)	A deed for one or more parcels of land sufficient to accommodate the ILLE’s planned facilities at the proposed load location; or

(iii)	A signed and executed agreement with an option to purchase or lease one or more parcels of land sufficient to accommodate the ILLE’s planned facilities at the proposed location;

(b)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE is pursuing a substantially similar interconnection request for electric service, the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request. A material change or delay includes a delay of one or more years to the Large Load’s projected date to realize its requested or contracted peak demand, a 20% or greater change in the requested or contracted peak demand, or a change in the location for the point of interconnection.

(i)	An ILLE that is pursuing a substantially similar interconnection request for electric service the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request must disclose the following information to the Interconnecting DSP or the Interconnecting TSP:

(A)	The ERCOT-assigned serial number (i.e., the Large Load interconnection number) for the substantially similar interconnection request, as applicable;

(B)	The location, including the power region and, if in the ERCOT region, the load zone, of the substantially similar interconnection request;

(C)	The non-coincident peak demand of the substantially similar interconnection request;

(D)	The anticipated timing of energization of the substantially similar interconnection request; and

(E)	The Interconnecting DSP and, if different from the Interconnecting DSP, the Interconnecting TSP associated with the substantially similar interconnection request.

(ii)	An ILLE that discloses a substantially similar interconnection request under this subsection may anonymize competitively sensitive information in its disclosure to the Interconnecting DSP or the Interconnecting TSP.

(iii) 	An Interconnecting DSP and an Interconnecting TSP must not sell, share, or disclose information submitted to the Interconnecting DSP or the Interconnecting TSP under this subsection other than a disclosure to the Public Utility Commission of Texas (PUCT) or ERCOT.

(iv)	ERCOT may request and the ILLE must provide any competitively sensitive information ERCOT deems necessary to complete any analysis required as part of the interconnection process. ERCOT must treat disclosed competitively sensitive information as Protected Information under ERCOT Protocols.

(c)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and progress for site-related studies and engineering services required for Large Load development before energization (e.g., geotechnical survey, water, wastewater, or gas). The submission must be accompanied by an attestation by an officer or official with binding authority over the ILLE stating that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly;

(d)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and current progress for obtaining non-ministerial discretionary approvals from state and local regulatory authorities required for development before energization (e.g., water, air, or backup generation permits). The submission must be accompanied by an attestation by an officer or official with binding authority over the ILLE attesting that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly;

(e)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP the expected schedule, including the quarter and year, for phased energization of the contracted peak demand expressed in MW, power factor (PF), and megavolt ampere reactive (MVAr) units;

(f)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE plans to have on-site backup generating facilities. If the ILLE plans to have on site backup generating facilities, the ILLE must also disclose the following information:

(i)	The number of backup generating units;

(ii)	The nameplate capacity of each of the backup generating facilities;

(iii)	The fuel source and operational characteristics of each of the backup generating facilities, including any run hour limitations and any fuel storage limitations under the existing environmental permits; and

(iv)	How quickly each of the backup generating facilities can reach their full capacity to serve the load;

(g)	The ILLE must disclose how it plans to procure power and whether the ILLE has on-site generation that will provide power exclusively to the ILLE;

(h)	The ILLE must disclose whether it can be modeled as a Controllable Load Resource, as the term is defined in the ERCOT Protocols, in ERCOT’s Batch Zero Process;

(i)	Financial security is due at the time that the intermediate agreement is executed. The ILLE must post financial security with the Interconnecting DSP or the Interconnecting TSP in the amount of $50,000 per MW of the requested peak demand for new interconnection requests or of the incremental increase in the peak demand for expanded interconnection requests.

(i)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security:

(A)	Cash collateral;

(B)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating equivalent of BBB-/Baa3 or higher from Standard & Poor’s or Moody’s; or

(C)	A letter of credit issued by a major U.S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” by Standard & Poor’s or “A3” by Moody’s Investor Service.

(ii)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(iii)	Refund of financial security posted on a dollar per MW basis is subject to Section 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand.

(j)	An Interconnecting DSP or an Interconnecting TSP must not procure equipment or services before an ILLE posts financial security to the Interconnecting DSP or the Interconnecting TSP in an amount equal to the Interconnecting DSP and Interconnecting TSP’s estimated costs for equipment with a lead time of at least six months and services necessary to interconnect the ILLE.

(i)	An ILLE may elect to amend its intermediate agreement with the Interconnecting DSP and the Interconnecting TSP to post financial security for significant equipment or services prior to executing an interconnection agreement.

(ii)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security for significant equipment or services:

- Cash collateral;

- Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating equivalent of BBB-/Baa3 or higher from Standard & Poor’s or Moody’s; or

- A letter of credit issued by a major U.S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” by Standard & Poor’s or “A3” by Moody’s Investor Service.

(iii)	If the ILLE provides a corporate or parental guaranty under this subsection, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(iv) 	Refund of financial security posted for significant equipment or services is subject to Section 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand and Section 9.7.4, Terms for Refund of Financial Security for an ILLE that Energizes.

### 9.7.2	Definition of an Interconnection Agreement

(1)	An Interconnecting Large Load Entity (ILLE) must execute an interconnection agreement with the Interconnecting Distribution Service Provider (DSP) and, if different from the Interconnecting DSP, the Interconnecting Transmission Service Provider (TSP).  If the Interconnecting DSP and the Interconnecting TSP are different entities, the interconnection agreement must specifically identify each entity’s responsibilities under this Section 9.7.2, including which entity will accept financial security and contribution in aid of construction (CIAC) from the ILLE.  The interconnection agreement must meet the following requirements:

(a)	The ILLE must demonstrate site control for the load location through provision of one of the following property interests to the Interconnecting DSP or the Interconnecting TSP:

(i)	A signed and executed lease agreement for one or more parcels of land sufficient to accommodate the ILLE’s planned facilities at the proposed load location for a duration of at least five years from the date the ILLE is expected to reach the total non-coincident peak demand as stated in the agreement, referred to as contracted peak demand;

(ii)	A deed for one or more parcels of land sufficient to accommodate the ILLE’s planned facility at the proposed load location; or

(iii)	A signed and executed purchase and sales agreement;

(b)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE is pursuing a substantially similar interconnection request for electric service, the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request. A material change or delay includes a delay of one or more years to the Large Load’s projected date to realize its requested or contracted peak demand, a 20% or greater change in the requested or contracted peak demand, or a change in the location for the point of interconnection.

(i)	An ILLE that is pursuing a substantially similar interconnection request for electric service the approval of which would result in the ILLE materially changing, delaying, or withdrawing the interconnection request must disclose the following information to the Interconnecting DSP or the Interconnecting TSP:

(A)	The ERCOT-assigned serial number (i.e., the Large Load Interconnection number) for the substantially similar interconnection request, as applicable;

(B)	The location, including the power region and, if in the ERCOT region, the load zone, of the substantially similar interconnection request;

(C)	The non-coincident peak demand of the substantially similar interconnection request;

(D)	The anticipated timing of energization of the substantially similar interconnection request; and

(E)	The Interconnecting DSP and, if different from the Interconnecting DSP, the Interconnecting TSP associated with the substantially similar interconnection request.

(ii)	An ILLE that discloses a substantially similar interconnection request under this subsection may anonymize competitively sensitive information in its disclosure to the Interconnecting DSP or the Interconnecting TSP.

(iii)	An Interconnecting DSP and an Interconnecting TSP must not sell, share, or disclose information submitted to the Interconnecting DSP or the Interconnecting TSP under this subsection other than a disclosure to the PUCT or ERCOT.

(iv)	ERCOT may request and the ILLE must provide any competitively sensitive information ERCOT deems necessary to complete any analysis required as part of the interconnection process. ERCOT must treat disclosed competitively sensitive information as Protected Information under ERCOT Protocols.

(c)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and progress for site-related studies and engineering services required for Large Load development before energization (e.g., geotechnical survey, water, wastewater, or gas). The submission must be accompanied by an attestation by an officer or official with binding authority over the ILLE stating that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly;

(d)	The ILLE must submit to the Interconnecting DSP or the Interconnecting TSP the ILLE’s plans, expected timing, and current progress for obtaining non-ministerial discretionary approvals from state and local regulatory authorities required for development before energization (e.g., water, air, or backup generation permits). The submission must be accompanied by an attestation by an officer or official with binding authority over the ILLE attesting that the information contained in the submission is complete and accurate at the time the attestation is signed. The ILLE must provide updates or progress reports to the Interconnecting DSP or the Interconnecting TSP when requested, but no more frequently than quarterly;

(e)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP the expected schedule, including the quarter and year, for phased energization of the contracted peak demand expressed in MW, power factor (PF), and megavolt ampere reactive (MVAr) units;

(f)	The ILLE must disclose to the Interconnecting DSP or the Interconnecting TSP whether the ILLE plans to have on-site backup generating facilities. If the ILLE plans to have on site backup generating facilities, the ILLE must also disclose the following information:

(i)	The number of backup generating units;

(ii)	The nameplate capacity of each of the backup generating facilities;

(iii) 	The fuel source and operational characteristics of each of the backup generating facilities, including any run hour limitations and any fuel storage limitations under the existing environmental permits; and

(iv)	How quickly each of the backup generating facilities can reach their full capacity to serve the load;

(g)	The ILLE must pay an interconnection fee in the amount of $50,000 per MW of contracted peak demand. The interconnection fee is non-refundable.

(i)	An Interconnecting DSP or an Interconnecting TSP must draw on any unused financial security that the ILLE posted under an intermediate agreement described in Section 9.7.1, Definition of an Intermediate Agreement, to satisfy the interconnection fee.

(ii)	The interconnection fee must be paid to the Interconnecting TSP and applied by that TSP as an offset to the Interconnecting TSP’s rate base in the earlier of the Interconnecting TSP’s next interim rate proceeding or comprehensive rate proceeding.

(h)	The ILLE must post financial security for significant equipment or services not later than the date that the interconnection agreement is executed if the Interconnecting DSP or the Interconnecting TSP needs to procure significant equipment or services to interconnect the ILLE. An Interconnecting DSP and an Interconnecting TSP must not procure equipment or services before an ILLE posts financial security to the Interconnecting DSP or the Interconnecting TSP in an amount equal to the Interconnecting DSP and Interconnecting TSP’s estimated costs for equipment with a lead time of at least six months and services necessary to interconnect the ILLE.

(i)	After drawing down on financial security posted under an intermediate agreement described in Section 9.7.1, Definition of an Intermediate Agreement, for payment of the interconnection fee, an Interconnecting DSP or an Interconnecting TSP must apply the balance of any unused financial security that the ILLE posted under an intermediate agreement described in Section 9.7.1 to satisfy the financial security for significant equipment or services under this subsection.

(ii)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security for significant equipment or services:

(A)	The cash collateral;

(B)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating equivalent of BBB-/Baa3 or higher from Standard & Poor’s or Moody’s; or

(C) 	A letter of credit issued by a major U. S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” by Standard & Poor’s or “A3” by Moody’s Investor Service.

(iii)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(iv)	Refund of financial security posted for significant equipment or services is subject to Section 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand and Section 9.7.4, Terms for Refund of Financial Security for an ILLE that Energizes.

(i)	The ILLE must pay all direct interconnection costs through CIAC, with no standard or other allowance offered to offset the ILLE’s CIAC payments.  The ILLE must pay CIAC not later than the date that the interconnection agreement is executed.  An Interconnecting DSP and Interconnecting TSP must not begin construction of facilities to interconnect an ILLE before an ILLE pays CIAC in an amount that is equal to the direct interconnection costs associated with the ILLE.

(i)	Direct interconnection costs include all costs associated with facilities built to interconnect the ILLE to the existing ERCOT system, including radial lines and substation upgrades necessary to interconnect the new ILLE. CIAC must be paid in the form of a direct cash payment.

(ii)	An Interconnecting DSP and an Interconnecting TSP must not seek to recover any large load-related direct interconnection costs, including any interconnection allowance for ILLEs, under any rates regulated by the PUCT.

(iii)	The CIAC must be trued-up to reflect the actual costs once the facilities are completed, and the ILLE may receive a credit or surcharge on their bill, as applicable, for the difference in actual costs relative to the estimate.

(j)	The ILLE must post financial security for system upgrades that are necessary to reliably serve the ILLE not later than the date that the interconnection agreement is executed.

(i)	The Interconnecting DSP or the Interconnecting TSP may accept the following forms of financial security:

(A)	The cash collateral;

(B)	Corporate or parental guaranty, only if the corporation or parent corporation has a credit rating equivalent of BBB-/Baa3 or higher from Standard & Poor’s or Moody’s; or

(C)	A letter of credit issued by a major U. S. commercial bank, or a U.S. branch office of a major foreign commercial bank, with a credit rating of at least “A-” by Standard & Poor’s or “A3” by Moody’s Investor Service.

(ii)	If the ILLE provides a corporate or parental guaranty, the Interconnecting DSP or the Interconnecting TSP may require the submission of financial records or statements to determine the ILLE’s financial stability.

(iii)	Refund of financial security posted for system upgrades is subject to Section 9.7.3, Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand and Section 9.7.4, Terms for Refund of Financial Security for an ILLE that Energizes.

### 9.7.3	Withdrawal of All or a Portion of Requested Peak Demand or Contracted Peak Demand

(1)	An ILLE may withdraw all or a portion of its requested peak demand or contracted peak demand for interconnection by submitting its request in writing to the Interconnecting DSP or the Interconnecting TSP.

(a)	Not later than 14 days after receipt of an ILLE’s notice to withdraw all or a portion of requested peak demand or contracted peak demand for interconnection, the Interconnecting DSP or the Interconnecting TSP must notify ERCOT via a method prescribed by ERCOT.

(b)	The Interconnecting DSP or the Interconnecting TSP must draw down on the ILLE’s financial security and apply the financial security to any outstanding amounts owed. Outstanding amounts owed include the following:

(i)	Costs incurred by the Interconnecting DSP or the Interconnecting TSP to fulfill the ILLE’s request for interconnection;

(ii)	Costs for equipment that the Interconnecting DSP or the Interconnecting TSP procured and that cannot be canceled with a full refund;

(iii)	Costs for construction that the Interconnecting DSP or the Interconnecting TSP started and that cannot be canceled with a full refund; and

(iv)	Costs for services that the Interconnecting DSP or the Interconnecting TSP initiated and that cannot be canceled with a full refund.

(c)	After applying the ILLE’s financial security to any outstanding amounts owed, the Interconnecting DSP or the Interconnecting TSP must refund 20% of the balance to the ILLE within 60 days.

(d)	After applying the financial security to any outstanding amounts owed and refunding 20% of the balance, the remaining 80% of the balance must be paid to the Interconnecting TSP and applied by that TSP as an offset to the Interconnecting TSP's rate base in the earlier of the Interconnecting TSP’s next interim rate proceeding or comprehensive rate proceeding.

(e)	CIAC is not refundable.

(f)	ERCOT must reallocate contracted peak demand that is withdrawn by an ILLE.

### 9.7.4	Terms for Refund of Financial Security for an ILLE that Energizes

(1)	An Interconnecting DSP or an Interconnecting TSP must draw down on the ILLE’s financial security and apply the financial security to any outstanding amounts owed for costs incurred by the Interconnecting DSP or the Interconnecting TSP to fulfill the ILLE’s request for interconnection of the contracted peak demand.

(a)	After applying financial security to any outstanding amounts owed, the Interconnecting DSP or the Interconnecting TSP must refund 20% of the remaining balance when the ILLE energizes and ratably as the ILLE meets the milestones identified in the ILLE’s schedule for phased energization of its contracted peak demand.

(b)	The Interconnecting DSP or the Interconnecting TSP must refund any remaining balance when the ILLE sustains operations for five years at the ILLE’s contracted peak demand.

9.8	Legacy Interconnection Study Procedures for Large Loads

(1)	This Section, previously known as Section 9.3, outlines the former procedures for conducting a Large Load Interconnection Study (LLIS) for new or modified Large Loads.  It has been replaced by the Batch Zero Process but has been retained here for reference.

### 9.8.1	Legacy Large Load Interconnection Study (LLIS)

(1)	A LLIS consists of the set of steady-state, stability, short-circuit and other relevant studies that are necessary to determine the reliability impact of a Large Load interconnection on affected Transmission Facilities and identify the Transmission Facilities that are needed to reliably interconnect the new or modified Large Load to the ERCOT System.

(2)	If an Interconnecting Entity (IE) or Resource Entity submits a large Generation Resource interconnection request, as defined in Section 5.3, Interconnection Study Procedures for Large Generators, that also includes a co-located Large Load, the Full Interconnection Study (FIS) may be used in place of a separate LLIS.  The FIS shall reflect the full requested Load amount and conform to all study requirements detailed in Sections 5.3 and 9.8, Legacy Interconnection Study Procedures for Large Loads.  For any deadlines or timelines set out in this section that conflict with the deadlines or timelines in Sections 5.2, General Provisions, and 5.3, the deadlines or timelines in Sections 5.2 and 5.3 shall govern.

(3)	During the LLIS, the interconnecting Transmission Service Provider (TSP) shall be the lead TSP unless otherwise designated by ERCOT during the study scoping process detailed in Section 9.8.2, Large Load Interconnection Study Scoping Process.

(4)	For an interconnection request involving a Large Load interconnecting at distribution voltage, the LLIS shall evaluate only the proposed Load’s transmission-level impacts, if any.  The affected Distribution Service Provider (DSP) shall provide the lead TSP with all information concerning the DSP's facilities needed to complete any required studies.

### 9.8.2	Legacy Large Load Interconnection Study Scoping Process

(1)	ERCOT will notify the interconnecting TSP after all requirements have been met.  Within ten Business Days of this notification, the lead TSP shall schedule a kick-off meeting with ERCOT and the certificated DSP to occur soon thereafter. If the proposed project is co-located with a Generation Resource, the kick-off meeting must also include the affected Resource Entity or IE.  The lead TSP shall invite the Interconnecting Large Load Entity (ILLE) to attend the kick-off meeting.  The ILLE may attend at its option.

(2)	ERCOT will notify all other TSPs of the LLIS request.  Each TSP may evaluate if it is directly affected by the interconnection request and determine if it should participate in the LLIS.  Examples of a directly affected TSP may include, but are not limited to, a TSP whose facilities are likely to experience changes in voltage or power flow because of the Load interconnection request.

(3)	Each directly affected TSP desiring to participate in the LLIS shall promptly notify the lead TSP and ERCOT and must provide a description of the expected effect of the Load interconnection on the TSP’s facilities in its notification.  The lead TSP shall include all directly affected TSP(s) in the LLIS kickoff meeting.

(4)	At the LLIS kickoff meeting, the lead TSP will present the proposed project and facilitate a general discussion of the preliminary study scope of work for the LLIS.

(5)	Any reactive studies required under Protocol Section 3.15, Voltage Support, or Subsynchronous Oscillation (SSO) studies required under Protocol Section 3.22.1.4, Large Load Interconnection Assessment, shall be scoped simultaneously with the LLIS but do not need to be included as part of the LLIS.  The Resource Entity responsible for the reactive study shall provide it to ERCOT directly.

(6)	The lead TSP will develop a preliminary LLIS study scope within ten Business Days following the kickoff meeting.

(a)	The study scope must include all study elements required by Section 9.8.4, Legacy Large Load Interconnection Study Elements, unless ERCOT in collaboration with the TSP(s) determine that one or more studies are unnecessary.  If a study element is deemed unnecessary, the lead TSP shall provide a written technical justification for not performing the analysis in lieu of the study report.

(b)	The study scope shall specify the base cases, study assumptions, and scenarios that will be used in each LLIS element.  Any transmission facilities that will not be in service before Initial Energization of the proposed Load that may significantly impact the study results, as initially identified by the lead TSP during the project kickoff meeting, shall be documented in the study scope.  All study assumptions related to maintenance outage scenarios required under Section 4.1.1.8, Maintenance Outage Reliability Criteria, shall be explicitly identified in the study scope.

(c)	The study scope shall specify the involvement of any directly affected TSPs in the study process.  In some cases, it may be necessary for the ILLE to execute study agreements with multiple TSP(s).

(d)	The lead TSP may propose interconnection design alternatives during the scoping process.  Such alternative options shall be fully studied in all required LLIS study elements.

(7)	The lead TSP shall submit the preliminary study scope for review by ERCOT and all directly affected TSPs, including TSPs which may be directly affected due to proposed interconnection topology. Directly affected TSPs and ERCOT may provide comments on the preliminary study scope within ten Business Days of posting.

(8)	Upon closing of the comment period described in paragraph (7) above, the lead TSP shall, within ten Business Days, submit a final study scope that addresses submitted comments to the extent possible.  ERCOT in collaboration with the TSP(s) shall determine the study scope.

(9)	Within five Business Days of the lead TSP submitting the final study scope, ERCOT shall approve the final study scope or return the scope to the lead TSP with comments.  The lead TSP shall promptly address ERCOT comments and resubmit according to paragraph (8) above.

### 9.8.3	Legacy Large Load Interconnection Study Description and Methodology

(1)	The primary purpose of the LLIS is to determine whether the amount of Load being requested by the ILLE can be placed in service by the desired Initial Energization date while maintaining the reliability of the ERCOT System and ensuring compliance with all North American Reliability Corporation (NERC) Reliability Standards, Protocols, this Planning Guide, and the Operating Guides.  The LLIS will also identify any transmission improvements needed to serve the full requested Load amount, including individual load increments requested by the ILLE in the initial Load Commissioning Plan (LCP).

(2)	The LLIS consists of a series of distinct study elements.  The specific elements included in a particular LLIS will be stated in the LLIS scope.

(3)	Each proposed Large Load interconnection that requests more than one physical transmission interconnection will be studied as an individual study for each interconnection to be analyzed separately from all other such requests unless otherwise agreed by the TSP(s) in the interconnection study agreement.

(4)	The LLIS process includes developing and analyzing various computer model simulations of the existing and proposed ERCOT transmission system.  The results from these simulations will be utilized by the TSP(s) to determine the impact of the proposed interconnection.

(5)	The study shall include an analysis demonstrating the adequate reliability of any temporary interconnection configurations.

9.8.4	Legacy Large Load Interconnection Study Elements

### 9.8.4.1	Legacy Steady-State Analysis

(1)	The steady-state interconnection study base case shall be created from the most recently approved Steady State Working Group (SSWG) base case appropriate for the desired Initial Energization date of the Load.  The lead TSP shall remove from the study base case all Transmission Facilities it determines may significantly impact study results that will not be in service before Initial Energization of the proposed Load, as identified in the preliminary LLIS study scope.  The steady-state analysis shall include other relevant Large Loads and any transmission upgrades included in the LCPs for those Large Loads that have a complete LLIS per paragraph (7) of Section 9.9, Legacy LLIS Report and Follow-up, and that have met the requirements of Section 9.10, Legacy Interconnection Agreements and Responsibilities.  The lead TSP may include other transmission projects and Substantiated Load in the study base case.  All modifications to the SSWG base case made as part of the study assumptions shall be documented in the LLIS report.

(2)	The lead TSP shall perform contingency analyses as required by the NERC Reliability Standards, ERCOT Nodal Protocols, this Planning Guide, and the Operating Guides to identify any additional Facilities that may be necessary to ensure that results of the system performance conform to these standards.  The study shall identify any system limitations that would prevent the ILLE from achieving the requested load in the desired timeframe.  If the study identifies system limitations, the lead TSP shall identify potential transmission system improvements necessary to achieve the requested Load.  The results of this analysis shall be shared with TSP(s) that have Facilities identified with planning criteria violations, and those affected TSP(s) will be responsible for evaluating the impact of the Large Load and the validity of the anticipated violations.

(3)	Upon completion of the steady-state study as described in paragraph (2) above, the lead TSP shall identify any modifications to the levels of Demand and timeline specified in the ILLE’s initial LCP that are needed to account for all transmission upgrades required to support the full requested amount of Load.

### 9.8.4.2	Legacy System Protection (Short-Circuit) Analysis

(1)	The short-circuit study shall use the most recently approved System Protection Working Group (SPWG) base case appropriate for the desired Initial Energization date of the Load.  The initial transmission configuration of the study area shall correspond to the configuration used in the corresponding steady-state study to the extent practicable.

(2)	The lead TSP will determine the maximum available fault currents at the interconnection substation for determining switching device interrupting capabilities and protective relay settings.

### 9.8.4.3	Legacy Dynamic and Transient Stability Analysis

(1)	The lead TSP shall not initiate the stability study prior to receiving from the ILLE dynamic load modeling information sufficient to properly model the load in the stability studies.  The TSP shall check the dynamic load information according to the procedure specified in Section 3.4.4, Load Model Data, of the Dynamics Working Group Procedure Manual.

(2)	The stability study base case shall be created from the most recently approved Dynamics Working Group (DWG) base case appropriate for the desired Initial Energization date of the Load.  The initial transmission configuration of the study area shall be consistent with the configuration used in the corresponding steady-state study to the extent practicable.

(3)	All stability studies shall be performed in accordance with NERC Reliability Standards, Protocols, this Planning Guide, and the Operating Guides.  Transient stability studies will analyze the performance of the ERCOT System in terms of angular stability, voltage stability, and excessive frequency excursions.  Additional studies may include small signal stability or critical clearing time analyses.  Such studies should incorporate reasonable and conservative assumptions regarding impacted facility operating conditions.  ERCOT in collaboration with the TSP(s) shall determine the stability analysis to be performed.

(4)	The stability study portion of the LLIS shall document any identified instability.

(5)	If the lead TSP identifies instability (other than instability identified for extreme events) in the stability portion of the LLIS, the TSP shall investigate alternative solutions, including transmission improvements, to mitigate the instability.  The lead TSP shall identify any modifications to the levels of Demand and the timeline specified in the ILLE’s initial LCP that are needed to account for all transmission upgrades required to support the full requested amount of Load.  The TSP shall implement any mitigation measure that may be needed to address a stability risk before the Initial Energization of the Large Load in accordance with Protocol Section 3.11.4, Regional Planning Group Project Review Process.

9.9	Legacy LLIS Report and Follow-up

(1)	This Section, previously known as Section 9.4, outlines the former procedures for informing an Interconnecting Large Load Entity (ILLE) the results of its Large Load Interconnection Study (LLIS).  It has been replaced by the Batch Zero Process but has been retained here for reference.

(2)	For each of the LLIS study elements, the lead Transmission Service Provider (TSP) shall submit a preliminary study report to ERCOT and other directly affected TSPs.  The report shall include a description of the study methodology and assumptions, findings, and recommendations.  The report shall also identify any changes to the Interconnecting ILLE’s Load Commissioning Plan (LCP) to allow for transmission upgrades in accordance with the criteria in Section 9.8.4, Large Load Interconnection Study Elements.  The lead TSP may include additional information in the study report and may combine multiple LLIS study elements into a single report.

(3)	ERCOT shall review the preliminary study report within ten Business Days and provide to the lead TSP any questions, comments, and proposed revisions necessary to ensure the report complies with the requirements in Section 9.8, Legacy Interconnection Study Procedures for Large Loads.  ERCOT may extend this review period by an additional 20 Business Days and shall notify in writing the lead and directly affected TSPs of the extension.  Directly affected TSPs may also provide questions, comments, and proposed revisions during this review period.  All comments from ERCOT and directly affected TSPs shall be provided to the lead TSP in writing.

(4)	If, after considering the responses received from ERCOT and directly affected TSPs, ERCOT in collaboration with the lead TSP determines if an additional study is required, the lead TSP shall promptly perform the additional study and submit an updated preliminary study report for review as described in paragraph (2) above.

(5)	If no additional study is required as described in paragraph (4) above, the lead TSP shall prepare a final LLIS study report that incorporates all relevant feedback received in paragraph (2) above within ten Business Days.

(6)	When complete, the lead TSP shall provide the final report for the LLIS study element(s) to ERCOT and the directly affected TSPs only.

(7)	The LLIS is deemed complete when the final report has been provided for all LLIS study elements.  Within ten Business Days following the completion of the LLIS, ERCOT shall:

(a)	Determine whether system upgrades recommended to support the full requested Load amount specified in the initial LCP are sufficient based on the report in paragraph (6) above;

(b)	Grant conditional approval for the interconnection of Load in accordance with the schedule in the final LCP, as may be revised by the TSP, as the necessary transmission upgrades identified in the LCP become operational, if ERCOT has determined pursuant to paragraph (a) above that the system upgrades recommended in the LLIS are sufficient to address the reliability risks associated with the proposed load additions;

(i)	For transmission upgrades that are subject to Regional Planning Group (RPG) review as described in Protocol Section 3.11.4, Regional Planning Group Project Review Process, ERCOT shall grant conditional approval if it determines that a project with an equivalent impact on the ability to serve the requested Load has become operational; and

(c)	Communicate the completion of the LLIS and the resulting LCP to the lead TSP and directly affected TSPs.

(8)	The lead TSP may provide a redacted copy of the final report for each LLIS study element to the ILLE upon request.  The redacted report(s) shall conform with Protocol Section 1.3, Confidentiality.

(9)	If a material change that impacts one or more LLIS study assumptions occurs before the requirements of Section 9.10, Legacy Interconnection Agreements and Responsibilities, have been met, ERCOT or the lead TSP may require one or more LLIS study elements be updated.  ERCOT in collaboration with the lead TSP shall have discretion to determine if a change impacts any LLIS study assumptions and to require a modification of the study or a restudy be performed.  Any modification of the study report shall be treated as a preliminary study and reviewed according to paragraph (2) above.

(10)	If the requirements of Section 9.10, have not been satisfied within 180 days after the communication of the completion of the LLIS by ERCOT as described in paragraph (7) above, ERCOT may notify the lead TSP that the project is subject to cancellation.  Upon receipt of this notification, the lead TSP may submit a project status update to ERCOT that includes a request for an extension and provides an opinion on whether any of the completed LLIS elements require restudy.  If no such project status update is received within 30 days from the date the notice is issued, ERCOT may consider the project canceled.

(11)	If the Large Load has not met the requirements for Initial Energization as described in paragraph (1) of Section 9.6, Initial Energization and Continuing Operations for Large Loads, within 365 days after the Initial Energization date identified in the LLIS study report, the lead TSP shall provide an opinion to ERCOT on whether any of the completed LLIS elements require restudy.  ERCOT may require one or more LLIS study elements be updated prior to approval of Initial Energization.

9.10	Legacy Interconnection Agreements and Responsibilities

(1)	This Section, previously known as Section 9.5, outlines the former requirements an Interconnecting Large Load Entity must meet prior to Initial Energization.  It has been replaced by the Batch Zero Process but has been retained here for reference.

9.10.1	Legacy Interconnection Agreement for Large Loads not Co-Located with a Generation Resource Facility

(1)	For a Large Load not co-located with a Generation Resource Facility, ERCOT shall not allow Initial Energization prior to receiving one of the following:

(a)	Confirmation from the interconnecting Transmission Service Provider (TSP) that:

(i)	All required interconnection agreements or equivalent service extension agreements with the Interconnecting Large Load Entity (ILLE) and, if applicable, directly affected TSP(s) have been executed;

(ii)	The interconnecting TSP has received written acknowledgement from the ILLE of the ILLE’s obligations to:

(A)	Notify the interconnecting TSP of changes to the Large Load project information or to the load composition, technology, or parameters, as described in Section 9.2.3, Modification of Large Load Information; and

(B)	Maintain Load consumption at or below the level(s) of peak Demand established in the Load Commissioning Plan (LCP);

(iii)	The interconnecting TSP has received notice to proceed with the construction of all required interconnection Facilities; and

(iv)	The interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security, applicable payments, and/or other agreements required to fund all required interconnection Facilities; or

(b)	A letter from a duly authorized person from a Municipally Owned Utility (MOU) or Electric Cooperative (EC) confirming its intent to construct and operate applicable Large Load and interconnect such Large Load to its transmission system.

9.10.2	Legacy Interconnection Agreement for Large Loads Co-Located with One or More Generation Resource Facilities

(1)	For a Large Load co-located with a Generation Resource Facility, ERCOT shall not allow Initial Energization prior to receiving one of the following:

(a)	Confirmation from the interconnecting TSP that:

(i)	All required interconnection agreements and/or equivalent service extension or other agreements with the Resource Entity, Interconnecting Entity (IE), and ILLE have been executed;

(A)	If the required agreements include a new Standard Generation Interconnection Agreement (SGIA) or an amendment to an existing SGIA, a copy of this agreement shall be provided to ERCOT once executed, per Section 5.2.8.1, Standard Generation Interconnection Agreement for Transmission-Connected Generators; or

(B)	If no new or amended agreements are required, the interconnecting TSP shall so notify ERCOT and state affirmatively it agrees to energize the new Load per the approved LLIS studies;

(ii)	The interconnecting TSP has received written acknowledgement from either the ILLE, or the Resource Entity on behalf of the ILLE, of the obligations to:

(A)	Notify the interconnecting TSP of changes to the Large Load project information or to the load composition, technology, or parameters, as described in Section 9.2.3, Modification of Large Load Information; and

(B)	Maintain Load consumption at or below the level(s) of peak Demand established in the LCP; and

(iii)	The interconnecting TSP has received notice to proceed with the construction of all required interconnection Facilities; and

(iv)	The interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security required, applicable payments, and/or other agreements to fund all required interconnection Facilities; or

(b)	A letter from a duly authorized person from a MOU or EC confirming its intent to construct and operate applicable Large Load and interconnect such Large Load to its transmission system.