| NOGRR Number | 282 | NOGRR Title | Board Priority - Large Electronic Load Ride-Through Requirements |
| --- | --- | --- | --- |
| Date of Decision |  | April 2, 2026 |  |
| Action |  | Recommended Approval |  |
| Timeline |  | Urgent – On 12/8/25, the Board designated Nodal Operating Guide Revision Request (NOGRR) 282 a Board Priority Revision Request. |  |
| Estimated Impacts |  | Cost/Budgetary: Annual Recurring Operations and Maintenance (O&M) Staffing Cost: $600K – $750K Project Duration: No project required |  |
| Proposed Effective Date |  | The first of the month following Public Utility Commission of Texas (PUCT) approval |  |
| Priority and Rank Assigned |  | Not applicable |  |
| Nodal Operating Guide Sections Requiring Revision |  | 2.6.4, Frequency Ride-Through Requirements for Large Electronic Loads (new) 2.15, Voltage Ride-Through Requirements for Large Electronic Loads (new) |  |
| Related Documents Requiring Revision/Related Revision Requests |  | Nodal Protocol Revision Request (NPRR) 1308, Board Priority - Related to NOGRR282, Large Electronic Load Ride-Through Requirements |  |
| Revision Description |  | This NOGRR establishes frequency and voltage ride-through requirements for Large Electronic Loads. |  |
| Reason for Revision |  | Strategic Plan Objective 1 – Be an industry leader for grid reliability and resilience Strategic Plan Objective 2 - Enhance the ERCOT region’s economic competitiveness with respect to trends in wholesale power rates and retail electricity prices to consumers Strategic Plan Objective 3 - Advance ERCOT, Inc. as an independent leading industry expert and an employer of choice by fostering innovation, investing in our people, and emphasizing the importance of our mission General system and/or process improvement(s) Regulatory requirements ERCOT Board/PUCT Directive (please select ONLY ONE – if more than one apply, please select the ONE that is most relevant) |  |
| Justification of Reason for Revision and Market Impacts |  | The frequency and voltage ride-through requirements in this NOGRR are necessary to ensure Large Electronic Loads do not present a reliability risk to the system by tripping when frequency and voltage excursions within a specified range occur. ERCOT has identified many events since October 2022 that included Load loss from one or more LELs during a typical voltage disturbance in which system protection operated as designed. As LELs increase on the ERCOT System, similar events would be expected to increase in magnitude and frequency, leading to frequency instability and other reliability problems absent frequency and voltage ride-through requirements. ERCOT has also identified ride-through risks associated with other Large Loads and intends to submit a NOGRR to address those risks. ERCOT anticipates that the requirements for those Large Loads could differ from those proposed in this NOGRR based on differences in the technology of the loads, just as ERCOT’s ride-through requirements for different generating technologies differ from one technology to another. |  |
| ROS Decision |  | On 12/4/25, ROS voted unanimously to table NOGRR282 and refer the issue to the Dynamics Working Group (DWG) and System Protection Working Group (SPWG). All Market Segments participated in the vote. On 4/2/26, ROS voted to recommend approval of NOGRR282 as amended by the 3/27/26 ERCOT comments as revised by ROS and to forward to TAC NOGRR282 and the 11/14/25 Impact Analysis. There was one opposing vote from the Consumer (Galaxy Power) Market Segment and eight abstentions from the Consumer (Sierra Club), Cooperative (GSEC), Independent Generator (2) (Southern Power, Vistra), Independent Power Marketer (IPM) (2) (Tenaska, Morgan Stanley), and Independent Retail Electric Provider (IREP) (2) (Demand Control 2, Chariot Energy) Market Segments. All Market Segments participated in the vote. |  |
| Summary of ROS Discussion |  | On 12/4/25, ERCOT Staff provided an overview of NOGRR282 and noted preliminary discussions at the Large Load Working Group (LLWG). Participants requested additional review by DWG and SPWG. On 4/2/26, ERCOT Staff presented a summary of the numerous sets of formal comments filed for NOGRR282 and ERCOT’s responses. Opponents expressed concerns about the viability of the proposed requirements, the availability of technology to meet the requirements, and ERCOT’s authority to impose such requirements. |  |

| Opinions |  |
| --- | --- |
| Credit Review | Not applicable |
| Independent Market Monitor Opinion | To be determined |
| ERCOT Opinion | To be determined |
| ERCOT Market Impact Statement | To be determined |

| Sponsor |  |
| --- | --- |
| Name | Patrick Gravois |
| E-mail Address | patrick.gravois@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4695 |
| Cell Number |  |
| Market Segment | Not applicable |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Cory Phillips |
| E-Mail Address | cory.phillips@ercot.com |
| Phone Number | 512-248-6464 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| AEP 120525 | Proposed additional redlines shifting the frequency thresholds within Section 2.6.4 and adding an exception to allow for UPS battery charge decreases within a set percentage |
| Tesla 121825 | Proposed additional redlines detailing exceptions for certain frequency deviations |
| Onward Energy 012326 | Raised discussion topics related to NOGRR245, Inverter-Based Resource (IBR) Ride-Through Requirements, and how ride-through requirements will apply to co-located facilities and Large Electronic Loads (LELs) |
| ERCOT 013026 | Provided additional redlines to the 12/18/25 Tesla comments based on prior comments and stakeholder feedback |
| Data Center Coalition 020926 | Proposed additional redlines to the 1/30/26 ERCOT comments replacing uses of “Large Electronic Load (LEL)” with the broader term “Large Load” and replacing the proposed cut-off date of “November 14, 2025” with “January 1, 2027” |
| ERCOT 021626 | Provided responses to the 1/23/26 Onward Energy comments |
| Texas Blockchain Council 021826 | Raised discussion topics related to the applicability and feasibility of the proposed ride-through requirements |
| ERCOT 031126 | Proposed additional redlines to the 1/30/26 ERCOT comments based on prior comments and stakeholder feedback |
| Data Center Coalition 031226 | Proposed additional redlines to the 3/11/26 ERCOT comments including modifying the proposed frequency and voltage thresholds; replacing the proposed cut-off date of “November 14, 2025” with “June 30, 2026”; and providing additional exception language |
| Schaper Energy Consulting 031826 | Expressed support for the 3/12/26 Data Center Coalition comments |
| Texas Blockchain Council 031826 | Raised discussion topics and high-level direction for suggested revisions |
| TIEC 032526 | Opined that ERCOT lacks authority to impose standards on retail customers and proposed additional redlines to the 3/11/26 ERCOT comments replacing customer requirements with language describing ERCOT’s ability to request information from Transmission and/or Distribution Service Providers (TDSPs) |
| ERCOT 032726 | Proposed additional redlines to the 3/12/26 Data Center Coalition comments |
| Google 033126 | Expressed support for the 3/12/26 Data Center Coalition comments |
| Intersect Power 040126 | Raised discussion topics and high-level direction for suggested revisions |
| Texas Blockchain Council 040126 | Opposed NOGRR282 and questioned ERCOT’s authority to impose such requirements on end-use customers |

Market Rules Notes

None

Proposed Guide Language Revision

## 2.6.4	Frequency Ride-Through Requirements for Large Electronic Loads

(1)	A Customer that proposes to interconnect or maintains an interconnection of a Large Electronic Load (LEL) with the ERCOT System shall ensure the LEL complies with the frequency ride-through requirements of this section, unless the Customer can demonstrate that:

(a)	The LEL was operational and consuming power from the ERCOT System or received written approval to energize from ERCOT on or before November 14, 2025; or

(b)	If the LEL is not co-located with a Generation Resource Facility, all required interconnection agreements or equivalent service extension agreements between the Interconnecting Large Load Entity (ILLE) and the applicable TDSP were executed on or before November 14, 2025; or

(c)	If the LEL is co-located with a Generation Resource Facility, all required interconnection agreements and/or equivalent service extension or other agreements with the Resource Entity, Interconnecting Entity, and ILLE were executed on or before November 14, 2025.

(d)	For an LEL meeting the conditions in paragraph (b) or (c) above, the interconnecting TSP received notice to proceed with the construction of all required interconnection Facilities and the interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security, applicable payments, and/or other agreements required to fund all required interconnection Facilities, and either of the following additional criteria below were met;

(i)	Its Large Load Interconnection Study (LLIS), as part of the interim Large Load Interconnection process, has been completed and approved by ERCOT on or before November 14, 2025; or

(ii)	Both of the following conditions have been met:

(A)	ERCOT received a written attestation from the Authorized Representative of the interconnecting TDSP before December 31, 2026, stating that the LEL was not required to be in the interim Large Load Interconnection process and that the LEL is expected to be energized between November 14, 2025, and December 31, 2026, and ERCOT provided written approval of the exemption; and

(B)	The LEL achieved Initial Energization by December 31, 2026.

(2)	An LEL that meets the exemption criteria of paragraph (1) above but makes a modification after November 14, 2025, that meets the criteria in paragraph (1)(b) of Planning Guide Section 9.2.1, Applicability of the Large Load Interconnection Study Process, shall not be exempt from the frequency ride-through requirements.

(3)	An LEL shall ride through frequency disturbances of the magnitude and duration specified in Table A below, as measured at the LEL’s Service Delivery Point, or if the LEL is co-located with a Generation Resource or Energy Storage Resource, at the Point of Interconnection Bus (POIB) of that Resource.  An LEL is not required to ride-through if it is either performing in accordance with its interconnecting TDSP’s Under-Frequency Load Shed (UFLS) program or providing an Ancillary Service that would require the LEL to trip or reduce consumption due to a frequency disturbance.

Table A

| Frequency (f) in (Hz) | Minimum Ride-Through Time (seconds) |
| --- | --- |
| f > 63.0 | May ride-through or trip |
| 61.2 < f ≤ 63.0 | 299 |
| 58.8 ≤ f ≤ 61.2 | continuous |
| 57.5 ≤ f < 58.8 | 299 |
| f < 57.5 | May ride-through or trip |

(4)	Nothing in paragraph (3) above shall be interpreted to require an LEL to trip or transfer load to backup generation for frequency conditions beyond those for which ride-through is required.

(5)	If an LEL is consuming electric current from the grid at the time of the frequency disturbance, the LEL shall continue to consume electric current from the grid during frequency deviations requiring ride-through.  In addition, an LEL should continue to consume active power within 10% of the pre-disturbance level during frequency deviations requiring ride-through.

(6)	For frequency deviations outside the continuous operating range specified in Table A of paragraph (3) above, an LEL may implement an internal load-transfer or control-stabilization scheme such that the LEL facility returns to at least 90% of its pre-disturbance consumption level within two seconds, as measured from the LEL’s Service Delivery Point or POIB.

(a)	For LELs composed of multiple internal devices, one load-transfer or control action per disturbance event per individual device shall be permitted.

(7)	If protection systems are installed and activated to trip the LEL, they shall enable the LEL to ride-through frequency conditions beyond those defined in paragraph (3) above to the maximum level the equipment allows, unless the protection systems are set to respond to an UFLS event or Ancillary Service obligation.

(8)	If frequency protection schemes are installed and activated to trip an LEL, they shall use filtered quantities or add sufficient time delays to prevent misoperations while providing the desired equipment protection.  Protection schemes shall not trip an LEL based on an instantaneous frequency measurement.

(9)	If ERCOT determines that an LEL has failed to ride through a frequency disturbance in accordance with any requirement in Section 2.6.4:

(a)	The interconnecting TDSP shall provide available information to ERCOT to assist with ERCOT’s event analysis;

(b)	The Customer representing the LEL shall:

(i)	Investigate and determine the root cause of the frequency ride-through failure and report the results of the investigation to ERCOT within 90 days of ERCOT’s request;

(ii)	Develop a plan to ensure the LEL can meet the applicable ride-through performance requirements and submit the plan to ERCOT within 90 days of completion of (i) above; and

(iii)	Implement the plan upon ERCOT approval within 180 days of (ii) above unless ERCOT approves a longer timeline.

(c)	Notwithstanding the requirements of paragraph (b) above, if ERCOT determines that the operation of an LEL following a failure to comply with the requirements of Section 2.6.4 poses an imminent risk to local or system reliability, ERCOT may require the LEL to disconnect from the ERCOT System and remain disconnected until the Customer representing the LEL has demonstrated to ERCOT’s satisfaction that the LEL can comply with the ride-through performance requirements of this Section.

## 2.15	Voltage Ride-Through Requirements for Large Electronic Loads

(1)	A Customer that proposes to interconnect or maintains an interconnection of a Large Electronic Load (LEL) with the ERCOT System shall ensure the LEL complies with the voltage ride-through requirements of this section, unless the Customer can demonstrate that:

(a)	The LEL was operational and consuming power from the ERCOT System or received written approval to energize from ERCOT on or before November 14, 2025; or

(b)	If the LEL is not co-located with a Generation Resource Facility, all required interconnection agreements or equivalent service extension agreements between the Interconnecting Large Load Entity (ILLE) and the applicable TDSP were executed on or before November 14, 2025.

(c)	If the LEL is co-located with a Generation Resource Facility, all required interconnection agreements and/or equivalent service extension or other agreements with the Resource Entity, Interconnecting Entity, and ILLE were executed on or before November 14, 2025.

(d)	For an LEL meeting the conditions in paragraph (b) or (c), the interconnecting TSP received notice to proceed with the construction of all required interconnection Facilities and the interconnecting TSP and, if applicable, directly affected TSP(s) have received the financial security, applicable payments, and/or other agreements required to fund all required interconnection Facilities, and either of the following additional criteria below were met;

(i)	Its Large Load Interconnection Study, as part of the interim Large Load Interconnection process, has been completed and approved by ERCOT on or before November 14, 2025; or

(ii)	Both of the following conditions have been met:

- ERCOT received a written attestation from the Authorized Representative of the interconnecting TDSP before December 31, 2026, stating that the LEL was not required to be in the interim Large Load Interconnection process and the LEL is expected to be energized between November 14, 2025, and December 31, 2026, and ERCOT provided written approval of the exemption; and

(B)	The LEL achieved Initial Energization by December 31, 2026.

(2)	An LEL that meets the exemption criteria in paragraph (1) above but makes a modification after November 14, 2025, that meets the criteria in Planning Guide Section 9.2.1 paragraph (1)(b), shall not be exempt from the voltage ride-through requirements.

(3)	An LEL interconnecting with the ERCOT System shall ride through the root-mean-square voltage conditions of the magnitude and duration specified in Table A below, as measured at the LEL’s Service Delivery Point, or if the LEL is co-located with a Generation Resource or Energy Storage Resource, at the Point of Interconnection Bus (POIB) of that Resource.  An LEL shall remain connected to the Transmission Grid during voltage conditions requiring ride-through.  Additional LEL performance requirements for voltage conditions requiring ride-through are listed below.  Cooling or mechanical load at the LEL facility may ride through or trip when voltage conditions are below 0.35 p.u. for any duration.

Table A

| Root-Mean-Square Voltage (p.u. of nominal) | Minimum Ride-Through Time (seconds) |
| --- | --- |
| V > 1.20 | May ride-through or trip |
| 1.10 < V ≤ 1.20 | 1.0 |
| 0.90 ≤ V ≤ 1.10 | Continuous |
| 0.80 ≤ V < 0.90 | 2.0 |
| 0.50 ≤ V < 0.80 | 0.5 |
| 0.35 ≤ V < 0.50 | 0.25 |
| V < 0.35 | 0.15 |

(a)	When voltage at the Service Delivery Point or, if the LEL co-located with a Generation Resource or Energy Storage Resource, at the POIB, remains within the continuous operating range in Table A during a disturbance or exceeds 1.1 per unit and remains below 1.2 per unit for less than 1.0 seconds for an overvoltage condition, the LEL shall continue consuming active power from the grid at the pre-disturbance level during the disturbance.

(b)	When voltage at the Service Delivery Point or POIB falls below 0.9 per unit but remains above 0.8 per unit and then returns to above 0.9 per unit within 2 seconds, the LEL shall continue consuming active power from the grid during the low voltage condition. In such cases, the LEL may reduce its active power consumption proportional to the voltage drop but shall return to 90% of its pre-disturbance consumption level from the grid within two seconds of voltage at the Service Delivery Point or POIB returning to above 0.9 per unit.

(c)	For any voltage condition at the Service Delivery Point or POIB that an LEL is required to ride-through and involves a voltage condition below 0.8 per unit, the LEL may decrease active power consumption from the grid but shall return to at least 90% of its pre-disturbance consumption level from the grid within two seconds of voltage at the Service Delivery Point or POIB returning to above 0.90 per unit.  For purposes of determining compliance with this requirement, if any cooling load at an LEL facility were to trip for voltage conditions below 0.35 p.u. at the Service Delivery Point or POIB, the amount of pre-disturbance cooling load would be subtracted from the total pre-disturbance consumption.  This adjustment applies to the remaining requirements of this Section.  Additional performance requirements for the allowable reduction of consumption in active power when voltage drops below 0.8 per unit are defined as follows:

(i)	For any LEL that satisfies the requirements in Planning Guide Section 9.5, Interconnection Agreements and Responsibilities, after November 14, 2025 but on or before January 1, 2028, if the LEL needs to temporarily reduce active power consumption from the grid to allow the facility to ride through the voltage disturbance in accordance with the performance requirements defined in paragraph (c) above, that reduction in active power shall be proportional to the voltage drop for any voltage between 0.8 and 0.5 per unit at the Service Delivery Point or POIB, if capable.  The LEL may reduce active power consumption as much as needed for voltage drops below 0.5 per unit.  If the LEL equipment is not capable of the performance described above, then the LEL may reduce active power consumption as much as necessary to remain connected to the grid but shall return to pre-disturbance consumption as defined in paragraph (c) above.

(ii)	For any LEL that satisfies the requirements in Planning Guide Section 9.5 after January 1, 2028, the LEL shall continue consuming active power from the grid when the voltage at the Service Delivery Point or POIB is between 0.8 and 0.5 per unit but may temporarily reduce active power consumption from the grid proportional to the voltage drop.  An LEL that cannot continue consuming active power as described in the previous sentence may implement a load-transfer scheme in accordance with paragraph (e) below.  When the voltage at the Service Delivery Point or POIB is below 0.5 per unit, the LEL may reduce active power consumption as needed to allow the facility to ride through the voltage disturbance in accordance with the performance requirements defined in paragraph (c) above.

(d)	When a voltage disturbance causes the voltage at the Service Delivery Point or POIB to drop below the continuous operating range in Table A of paragraph (3) above, an LEL shall not consume electric current during the disturbance at a level that exceeds  150% of its maximum electric current consumption during normal operations.  The allowable overcurrent up to  150% shall only persist during the voltage transient with a duration not to exceed 0.5 seconds.

(e)	For undervoltage deviationsbelow 0.8 p.u. at the LEL’s Service Delivery Point or POIB, an LEL may implement a load-transfer or control stabilization scheme such that the LEL facility begins returning to the grid within 0.25 seconds of voltage at the Service Delivery Point or POIB returning to above 0.9 p.u., and shall return to at least 90% of its pre-disturbance consumption level within 0.5 seconds of voltage returning to above 0.9 p.u., as measured from the LEL’s Service Delivery Point or POIB.

(i)	For LELs composed of multiple internal devices, one load-transfer or control action per disturbance event per individual device shall be permitted.

(f)	Notwithstanding the foregoing requirements of this section, before January 1, 2028, an LEL may trip or transfer load for any voltage condition at the Service Delivery Point or POIB above 1.08 p.u. that persists for 5 seconds or greater if needed to protect voltage-sensitive equipment.

(4)	Nothing in paragraph (3) above shall be interpreted to require an LEL to trip or transfer load to backup generation for voltage conditions beyond those for which ride-through is required.

(5)	If installed and activated to trip or transfer the LEL, all protection systems (including but not limited to protection for over-/under-voltage) shall enable the LEL to ride-through voltage conditions beyond those defined in paragraph (3) above to the maximum level the equipment allows.

(6)	If instantaneous over-current or over-voltage protection systems are installed and activated to trip or transfer the LEL, they shall use filtered quantities or time delays to prevent misoperation while providing the desired equipment protection.  Any alternating current instantaneous over-voltage protection that could disrupt the LEL power consumption shall use a measurement window of at least one cycle of fundamental frequency.

(7)	An LEL shall not implement a load trip or transfer scheme that disconnects or transfers load to backup generation due solely to a certain number of voltage sags or swells within a certain period of time if the LEL is required under paragraph (3) above to ride through each such condition.  If such a load trip or transfer scheme must be activated due to limitations of the equipment, the LEL must be capable of remaining connected to the system for a minimum of six voltage sags or swells within a 90-second period.

(8)	If ERCOT determines that an LEL has failed to ride through a voltage disturbance in accordance with any requirement in this Section 2.15:

(a)	The interconnecting TDSP shall provide available information to ERCOT to assist with ERCOT’s event analysis;

(b)	The Customer representing the LEL shall:

(i)	Investigate and determine the root cause of the voltage ride-through failure and report the results of the investigation to ERCOT within 90 days of ERCOT’s request;

(ii)	Develop a plan to ensure the LEL can meet the applicable ride-through performance requirements and submit the plan to ERCOT within 90 days of completion of (i) above; and

(iii)	Implement the plan upon ERCOT approval within 180 days of (ii) above unless ERCOT approves a longer timeline.

(c)	Notwithstanding the requirements of paragraph (b) above, if ERCOT determines that the operation of an LEL following a failure to comply with the requirements of Section 2.15 poses an imminent risk to local or system reliability, ERCOT may require the LEL to disconnect from the ERCOT System and remain disconnected until the Customer representing the LEL has demonstrated to ERCOT’s satisfaction that the LEL can comply with the ride-through performance requirements of this Section.