## PGRR145 Comments and Responses
Author | Date | Source | Macro-topic | Comment summary | Type | Suggestion | PGRR145 section reference (detailed) | ERCOT Response | Were there language changes made in ERCOT's 4/3 comments related to this comment?
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Timeline Feasibility / Agreement Execution | Section 9.4 provides approximately 30 days between issuance of the Batch Zero Study report and the deadline for DSP attestation that Interconnection Agreements have been executed. Oncor believes 30 days may be insufficient, particularly absent a standardized Interconnection Agreement form. | Change request | Extend the 30-day commitment period to 60 days unless or until a standardized Interconnection Agreement form is developed by the PUCT. | 9.4 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. ERCOT notes that after the final rule in Project No. 58481 is adopted, ERCOT will file a revision request to align with the rule, including any changes to the commitment window. Those changes should be effective before the Batch Zero commitment window opens. | No
AEP | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-26-AEP-Comments-032026.docx | Process transparency / energization | Missing explicit step for energization readiness | Change request | Add Energization Request requirement to checklist | 9.6 | ERCOT does not believe this change is needed. Planning Guide Section 9 requires ERCOT to prescribe the manner for submitting all communications and documents. ERCOT already has a document that prescribes use of the form posted on the ERCOT website, as required by PG 9.1. Any changes to align with the Batch Zero process are more appropriately placed in this document rather than being hardcoded in the Planning Guide. This also mirrors how the Approval to Energize process for generation is handled. | No
Skybox Datacenters | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-10-Skybox-Datacenters-Comments-031926.docx | Project Advancement / Non-Reset Principle | Skybox requests that projects that have: (1) Completed required studies (2) Executed IA or FEA (3) Posted financial security and (4) Demonstrated site readiness, should continue advancing toward energization under their LCPs and should not be required to re-demonstrate eligibility or re-initiate prior milestones unless a material adverse reliability impact occurs. | Change request | Clarify in §9.6 that projects satisfying prior study and commitment milestones continue advancing toward energization without re-screening or re-demonstration of eligibility. Clarify that updates to dynamic load models required by other rulemakings do not invalidate prior studies unless they result in a material adverse reliability impact | 9.6 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
AEP | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-26-AEP-Comments-032026.docx | Financial framework / regulatory scope | Planning Guide includes rate base, CIAC, and fee treatment tied to PUCT rulemaking, creating regulatory risk | Change request | Remove or align financial provisions with PUCT 58481; avoid embedding rate base / CIAC rules in Planning Guide | 9.7 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. ERCOT is open to removing the references in Section 9.7 to how TSPs should treat ILLE financial commitments for ratemaking purposes. | No
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Financial Security / Regulatory Scope | CEHE argues that provisions governing accounting treatment, refundability, and rate base implications of financial security exceed the scope of the Planning Guide and should be addressed by the PUCT under Project 58481 | Change request | Remove all provisions related to financial accounting, refund treatment, and rate base implications from PGRR145, Defer these issues to PUCT rulemaking (Project 58481) | 9.7 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Satoshi Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-21-Satoshi-Energy-Comments-032026.docx | Financial requirements / cost causation | Satoshi argues that proposed $/MW financial security and fees are not cost-reflective, especially for colocated projects that require no transmission upgrades. They state that (i) intermediate-stage deposits should be fully refundable, (ii) interconnection fees should reflect actual CIAC rather than fixed $/MW, and (iii) duplicative charges create an unjustified burden and act as a “tax” on load | Change request | Make deposits fully refundable until PUCT 58481 finalized; scale fees to actual CIAC; avoid fees for no-upgrade projects; implement true-up mechanism | 9.7 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Regulatory alignment / PUCT dependency | TEBA raises concern about embedding PUCT Project 58481 requirements into the Planning Guide before they are finalized, noting potential misalignment and governance concerns | Change request | Avoid incorporating pending PUCT rules directly into PGRR145 or ensure flexibility to align with final rulemaking | 9.7 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Financial security / refundability | TEBA expresses concern about proposed financial security framework (e.g., 80% held for 5 years), arguing it creates excessive risk for loads and may exceed ERCOT’s authority. They emphasize need for refundability and flexibility | Change request | Improve refundability provisions, consider milestone-based exit options, and clarify treatment of guarantees; limit ERCOT role to attestation rather than enforcement | 9.7 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Vistra | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-18-Vistra-Comments-032026.docx | Regulatory scope / PUCT vs ERCOT authority | Vistra argues that several provisions imported from PUCT Project 58481 exceed the scope of the ERCOT Planning Guide and/or SB6. Specifically, ERCOT should not prescribe rate base treatment, cost allocation, refundability of financial security, or expand disclosure requirements beyond statutory language. These are PUCT jurisdictional matters | Change request | Remove or limit provisions related to financial security treatment, rate base offsets, and cost allocation; align disclosures strictly with SB6 (e.g., “in this state”) | 9.7 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
AEP | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-26-AEP-Comments-032026.docx | Process / operational clarity | SSO study requirement timing unclear (QSA vs energization) | Change request | Clarify that SSO study is required prior to energization, not QSA entry | 5.3.5 | ERCOT will implement this change through proposed redline edits in its April 3 comment. | Yes
Vistra | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-18-Vistra-Comments-032026.docx | Timeline coordination / operational alignment | Vistra notes misalignment between Quarterly Stability Assessment timelines and Batch Zero energization timelines, particularly for 39.169 NMA projects, which could create unintended eligibility barriers | Change request | Align §5.3.5 timing requirements with Batch Zero and Legacy pathways to ensure 39.169 NMAs can proceed without timing conflicts | 5.3.5 | As ERCOT understands it, Vistra's suggested revisions are only necessary if large loads subject to PURA § 39.169 have two options for interconnection studies, Batch Zero or the Legacy LLIS . As addressed elsewhere, ERCOT does not agree that large loads subject to PURA § 39.169 are entitled to two paths to study for interconnection. | No
Sandow Lakes Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-24-Sandow-Comments-032026.docx | Special priority category / national interest projects | Sandow argues ERCOT should create a separate highest-priority category for projects tied to national interests, such as military needs, domestic manufacturing of essential goods, and health and safety-related facilities. They argue the Batch Zero framework should not fail to accommodate critical facilities whose importance goes beyond ordinary commercial queue treatment | Change request | Add a distinct priority pathway for projects identified as serving national interests, with highest-priority ERCOT review and approval treatment | 6.6.3 | Sandow Lakes Energy has not identified a statutory or rule-based rationale for ERCOT to give preferential treatment to large loads tied to undefined national interests. | No
IREN | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-12-IREN-Comments-031926.docx | Capacity Allocation / Queue Rationalization / Objective Prioritization | IREN argues that the current framework effectively treats all loads as being at the same development stage. They contend that projected energization dates, existence of interconnection agreements, and construction stage are only part of the picture and that the absence of an objective allocation methodology could lead to arbitrary MW distribution outcomes. They propose using a “Load Request Date” metric as an objective basis for prioritization, bifurcated around March 25, 2022 (the date ERCOT implemented the Interim Large Load Interconnection Process). They argue this date is pivotal and provides a fair and administrable dividing line. | Change request | Add new section establishing a Load Request Date-based capacity allocation methodology. Aggregate loads into two groups:(1) Load Request Date on or before March 25, 2022 (“Interim Connection Date”); and (2) Load Request Date after March 25, 2022. Allocate capacity chronologically within each group, with the first group studied and allocated first before proceeding to the second group. Define “Load Request Date” as the date the Load Facility submitted a written request to its Interconnecting DSP or TSP. | 9.2.1 | ERCOT does not currently have access to this data, and respectfully disagrees that the date a customer first contacted its Interconnecting TSP/DSP serves as a reliable or realistic indicator of project maturity or seriousness. The current proposal is grounded in objective, measurable metrics of progress through the established process. It should also be noted that implementing the suggested approach would require additional study time. | No
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Process continuity / treatment of non-Batch loads | TEBA raises concern that PGRR145 may imply ERCOT will pause or limit processing of new load interconnection requests outside Batch Zero. This creates significant investment uncertainty for projects not included in Batch Zero, as developers lack clarity on timing and process for individual studies | Change request | Clarify that ERCOT will continue processing non-Batch Zero load requests and define a clear pathway and timeline for loads outside Batch 0 | 9.2.1 | Upon approval of PGRR145, the current individual study process will no longer be in effect and Batch Zero will be the only path forward for Large Load interconnection requests. Any LLI requests that do not meet the requirements for inclusion in Batch Zero will need to wait until a later Batch study in order to be assessed and eventually interconnected. This is described in Section 9.2.1.3. As there will no longer be an individual study process, ERCOT will not be accepting TSP-performed LLIS studies once PGRR145 is effective. | No
Emerald AI | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-25-Emerald-AI-Comments-032026.docx | Eligibility / allocation philosophy | Projects that are ready and flexible (e.g., CLR, RTP-qualified) should be prioritized as they reduce system cost and can operate under constraints | Change request | Allow projects electing CLR and meeting RTP readiness criteria to receive Batch Zero allocation | 9.2.1 | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs in Batch Zero. | No
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Regulatory Alignment / PUCT PFP Dependency | Batch Zero eligibility relies on PUCT 58481 PFP requirements that are not yet final, creating risk of misalignment (e.g., financial security levels, refundability) if the final rule changes | Change request | True-up Batch Zero entry requirements after final PUCT rule (e.g., adjust/refund financial security) or use Intermediate Agreement (refundable security) instead of Interconnection Agreement for Base Load eligibility | 9.2.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Crow Holdings | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-28-Crow-Holdings-Comments-032026.docx | Base load eligibility / safe harbor for fully committed projects | Focuses on projects that have completed legacy LLIS, executed binding interconnection agreements, and posted full financial security. Argues these projects have fully relied on ERCOT framework and should not be subject to re-evaluation, reclassification, or new agreement requirements under Batch Zero | Change request | Add new § 9.2.1.1(e) establishing automatic Base Load classification with no § 9.2.1.4 re-evaluation and no new IA requirement for projects that (i) executed IA (or equivalent) and (ii) posted required financial security by July 10, 2026 | 9.2.1.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Monarch Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-27-Monarch-Energy-Comments-032026.docx | Base load eligibility / financial commitment | Argues that financial commitment (CIAC, equipment procurement, LOAs) is the most accurate indicator of project readiness, not execution of an Interconnection Agreement. Current framework risks excluding advanced projects that have already deployed capital but have not yet executed a formal IA | Change request | Revise §§ 9.2.1.1 and 9.2.1.2 to recognize binding financial commitment (CIAC, long-lead procurement, LOAs) as equivalent to executed IA for Base Load eligibility | 9.2.1.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Reliant | 2026-03-09 | https://www.ercot.com/files/docs/2026/03/09/145PGRR-04-Reliant-Energy-Comments-030926.docx | Base load eligibility | Reliant states that a Large Load co-located with a new Generation Resource that was included in a completed Full Interconnection Study (FIS) should be eligible for inclusion in Batch Zero as Base Load not subject to additional study. They note that under legacy Section 9.8.1(2), a Generation Resource FIS that includes a co-located Large Load may be used “in place of a separate LLIS.” Therefore, if a Generation Resource FIS that includes a co-located Large Load is complete prior to the Batch Zero eligibility deadline, that Large Load should be treated the same as Large Loads that progressed through the legacy LLIS process. Reliant’s concern is that without explicit inclusion, these loads could be excluded from Base Load status despite having completed an equivalent study process. | Change request | Revise §9.2.1.1 to explicitly allow a Large Load co-located with a new Generation Resource that was included in a completed FIS (per §5.3) to qualify as Base Load in Batch Zero, provided the FIS reflects the full requested load and meets all applicable study requirements | 9.2.1.1 | ERCOT wishes to reiterate comments made in recent workshops that the language in current Planning Guide Section 9.3.1(2) (renumbered to 9.8.1(2) in PGRR145) does not allow for the FIS process to completely replace the Large Load Interconnection process documented in Section 9. Rather, it is intended to prevent the TSP from having to perform duplicative studies. Accordingly, the FIS may be substituted only for the LLIS studies, and it must meet all the requirements of the LLIS studies. This includes the scoping process defined in current Section 9.3 and ERCOT review and approval of the study reports described in current 9.4. Large Load interconnection requests that utilize this provision must also meet current Section 9.5.2 of the Planning Guide in order to finalize study results. ERCOT believes the current language in PGRR145 is sufficient to include loads that utilize the FIS in place of a separate LLIS. If stakeholders believe additional clarification is needed, ERCOT is open to additional discussion to develop redlines that accurately reflect the current process. | No
Schaper | 2026-03-05 | https://www.ercot.com/files/docs/2026/03/05/145PGRR-03-Schaper-Energy-Consulting-Comments-030526.docx | Construction and procurement attestation requirement | Schaper argues that the procurement and construction attestation requirement in § 9.2.1.1(1)(d)(iv) is circular as drafted. They explain that (1) Developers must attest to site preparation and construction progress by July 15, 2026. (2) However, under § 9.2.1.4, the applicable MW level may still be subject to ERCOT re-determination. (3) The modeled MW for Batch Zero projects is derived from the study validity determination. (4) Therefore, developers are required to commit capital before knowing whether their load will ultimately be classified as Base Load. Schaper states they are generally supportive of an attestation requirement for near-term energizations (before December 31, 2027), but only if developers receive clear notice of Base Load classification first | Change request | Modify § 9.2.1.1 to provide developers with unambiguous notice that their load has been classified as Base Load in Batch Zero prior to the attestation deadline, so that the attestation requirement is workable and not circular. | 9.2.1.1 | ERCOT disagrees that the site development attestation is circular. During stakeholder interviews, ERCOT repeatedly heard that even fast site development could take 18-24 months until energization. Many stakeholders also expressed belief that many in the interconnection queue are "not real loads." The attestation of sufficient site development to achieve a customer stated energization date is intended to balance the customer's desire for timely electricity service with an ERCOT and market desire to prioritize service to customers that will be ready to take that service. ERCOT has stated its intent to provide periodic status updates to the TSPs, who can update their customers, accordingly. | No
Lancium | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-09-Lancium-Comments-031926.docx | Modeling Accuracy / Data Source Hierarchy | Lancium notes that § 9.2.1.1(2)(b) may create inconsistencies between:(1) The Demand level reported through the 2026 RTP annual request for information; and (2) The Demand level reflected in the ILLE’s submitted Load Commissioning Plan (LCP). Lancium argues that if the objective is to model the most accurate and current Demand level, the LCP submitted by the ILLE is the more appropriate source | Change request | Modify § 9.2.1.1(2)(b) to default to the Demand level indicated in the ILLE’s LCP when it is inconsistent with the level reported through the RTP data request. | 9.2.1.1 | Lancium is correct that the provision in § 9.2.1.1(2)(b) is to resolve inconsistencies between an ILLE's LCP and its submission in the 2026 RTP. If the ILLE has harmonized its LCP with its 2026 RTP submission, there is no conflict. We do not agree with Lancium's proposed solution but have proposed redlines to address the inconsistency. | Yes
Schaper | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-11-Schaper-Energy-Consulting-Comments-031926.docx | Timeline / Eligibility Gap (“Air Gap”) | Schaper highlights the “air gap” between March 4 and July 10, during which load customers are required to make binding procurement and construction commitments without certainty regarding study validity or firm load status prior to Batch Zero determination | Change request | Either: move the March 4 date forward or remove procurement and construction attestation requirements for projects within this gap | 9.2.1.1 | ERCOT has stated its intent to provide periodic status updates to the TSPs, who can update their customers, accordingly. | No
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Attestation Clarity / Role Definition / Administrative Workability | Oncor notes that § 9.2.1.1 requires multiple DSP and/or TSP attestations for Base Load qualification, but does not clearly define which entity is responsible for each attestation. They also state that DSPs are not well positioned to determine what constitutes sufficient “evidence” of site preparation and construction. | Change request | Clarify in each provision whether the DSP or TSP is responsible for the required attestation. Develop ERCOT-standardized attestation forms. Remove the requirement that the ILLE provide evidence of site preparation and construction; an attestation should be sufficient. | 9.2.1.1 | ERCOT is currently developing an attestation form that would identify the responsible entity, as appropriate. ERCOT is continuing to consider the issue of evidence of site preparation and construction. While ERCOT is not proposing changes to the language at this time, it is open to changes in future comments. | No
Eolic | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-19-Eolic-Comments-032026.docx | Modeling consistency / Demand source hierarchy | Eolic notes potential inconsistency between peak Demand reported through the 2026 RTP data request and the ILLE’s most recent Load Commissioning Plan (LCP). They argue that the LCP reflects the most current and project-specific information and should therefore take precedence for modeling purposes | Change request | Amend §9.2.1.1(2)(b) to specify that where RTP and LCP values differ, ERCOT shall model Demand based on the LCP | 9.2.1.1 | Eolic is correct that the provision in § 9.2.1.1(2)(b) is to resolve inconsistencies between an ILLE's LCP and its submission in the 2026 RTP. If the ILLE has harmonized its LCP with its 2026 RTP submission, there is no conflict. We do not agree with Eolic's proposed solution but have proposed redlines to address the inconsistency. | Yes
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Modeling approach / Demand source | TEBA objects to using the “lesser of RTP vs LCP” for modeling load, arguing it may understate actual demand and penalize projects. They view the LCP as the most accurate and up-to-date representation of load | Change request | Use Load Commissioning Plan (LCP) as the primary basis for modeling load rather than taking the minimum of RTP and LCP values | 9.2.1.1 | TEBA is correct that the provision in § 9.2.1.1(2)(b) is to resolve inconsistencies between an ILLE's LCP and its submission in the 2026 RTP. If the ILLE has harmonized its LCP with its 2026 RTP submission, there is no conflict. We do not agree with TEBA's proposed solution but have proposed redlines to address the inconsistency. | Yes
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Eligibility criteria / attestation requirements | TEBA argues that Base Load eligibility criteria for near-term projects (≤2027) are overly stringent, particularly requirements for “all necessary equipment” and full construction progress | Change request | Relax criteria to require procurement of long-lead equipment only and initiation (not completion) of site preparation | 9.2.1.1 | Section 9.2.1.1(d) requires attestation of purchase of high-voltage equipment (iii) and (v) and site prep sufficient to achieve the requested ISD (iv). The language does not require purchase of "all necessary equipment" and does not require the site to be fully constructed. | No
Monarch Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-27-Monarch-Energy-Comments-032026.docx | RTP alignment / eligibility | Current draft may implicitly require inclusion in 2026 RTP for Batch Zero eligibility, contradicting prior ERCOT guidance and penalizing projects that did not pursue RTP inclusion | Change request | Revise § 9.2.1.1(2)(b)(i) to remove any implicit requirement for RTP inclusion as a condition for Batch Zero eligibility or modeling | 9.2.1.1 | ERCOT acknowledges that inclusion of the Large Load in the 2026 RTP is not a requirement for inclusion in Batch Zero. ERCOT will modify § 9.2.1.1(2)(b)(i) to be applicable only if the Large Load was included in the 2026 RTP submission. ERCOT does not understand why a Large Load included in Batch Zero under § 9.2.1.1(2)(b) which is operational would not be reflected in the 2026 RTP load forecast. Similarly, ERCOT does not understand why a Large Load eligible for inclusion in Batch Zero under § 9.2.1.1(2)(c) and will energize in a matter of months would not also be reflected in the 2026 RTP load forecast. | Yes
Satoshi Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-21-Satoshi-Energy-Comments-032026.docx | Legacy IA / base load eligibility | Satoshi argues that projects that completed legacy LLIS (Sections 9.9 and 9.10) have already demonstrated full commitment (executed IA, CIAC paid, construction underway) and should not be required to execute a new interconnection agreement under §9.7.2 to qualify as Base Load. Requiring a new IA is duplicative and undermines investment certainty | Change request | Add deemed-compliance provision: projects satisfying §§9.9–9.10 prior to deadline automatically qualify as Base Load without new IA | 9.2.1.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Schaper | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-11-Schaper-Energy-Consulting-Comments-031926.docx | Transition / Legacy Agreement Treatment | Schaper argues that requiring projects with existing interconnection agreements to comply with new §9.7.2 standards within a compressed timeline creates risk of non-compliance due to utility implementation constraints. Projects should not be penalized for timing-related limitations | Change request | Allow projects to demonstrate compliance using legacy §9.10 interconnection agreement standards instead of requiring immediate compliance with §9.7.2 | 9.2.1.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. ERCOT appreciates concerns about timing, but ERCOT is balancing the time needed for a stakeholder process with requests for Batch Zero to start as quickly as possible. Nothing prevents an ILLE from taking steps between now and July 10 to be ready to meet the requirements in Section 9.7.2, including obtaining site control, preparing disclosure information, determining how much additional security it may need to provide, and entering into an agreement. | No
Skybox Datacenters | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-10-Skybox-Datacenters-Comments-031926.docx | Attestation Process / DSP–TSP Functional Overlap | Skybox recommends clarifying that while ERCOT intends the Interconnecting DSP to serve as the gatekeeper for attestation, the rule should accommodate situations where the DSP and TSP functions are performed by the same legal entity. The attestation should confirm general willingness and ability to serve under the applicable IA/FEA, but should not be construed as a binding commitment to specific service terms or timelines. | Change request | Clarify §§ 9.2.1.1(1)(d)(ii) and (e)(ii) to allow for circumstances where DSP and TSP are the same entity. Clarify that attestation reflects general willingness and ability to serve under the IA/FEA and is not a binding commitment to specific service terms or timelines | 9.2.1.1 | ERCOT agrees to make this clarification consistent with 16 TAC § 25.370(d)(3), which allows the Interconnecting DSP to designate another electric utility, municipally owned utility, or electric cooperative to submit the notarized attestation. | Yes
Crusoe | 2026-03-09 | https://www.ercot.com/files/docs/2026/03/09/145PGRR-05-Crusoe-Comments-030926.docx | Date for re-assessing approved LLIS loads | Crusoe argues that reassessing firmness as of July 15, 2026 for loads that have already completed legacy LLIS (Sections 9.9 and 9.10) is inappropriate and harmful. These projects have received ERCOT approval, executed interconnection agreements, posted security/CIAC, ordered long-lead equipment, and begun construction. Re-evaluating firmness mid-construction creates financing risk and operational uncertainty, particularly for 2027 and early 2028 energizations. Crusoe contends these loads are already demonstrably firm and should not be treated as speculative | Change request | Add new § 9.2.1.1(b-1) providing automatic Base Load classification for loads that satisfied §§ 9.9 and 9.10 prior to effective date of PGRR; no § 9.2.1.4 evaluation; no new § 9.7.2 agreement required | 9.2.1.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. In addition, ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Eligibility Criteria / Studied Load Pathways | CEHE identifies gaps and inconsistencies in eligibility rules for “Load to be Studied,” particularly for projects targeting 2027 energization or those with interconnection agreements but not meeting Base Load criteria. Current rules may exclude viable near-term projects or misclassify them | Change request | Clarify linkage to §9.2.1.1(1)(d)(i) for consistency with valid study criteria, Remove January 1, 2028 restriction to allow 2027 projects into Studied Load and Allow executed interconnection agreement (9.7.2) as an alternative qualifying criterion (in addition to intermediate agreement) | 9.2.1.2 | ERCOT acknowledges that Large Loads under Section 9.2.1.2(1)(a) need to satisfy the eligible studies requirements in Section 9.2.1.4. The omission of such a requirement is an oversight. ERCOT agrees the January 1, 2028 restriction needs to be lifted and has made conforming changes. Any Large Load that does not qualify for inclusion in Batch Zero under Section 9.2.1.2(1)(a) may still qualify under Paragraph (1)(b). | Yes
Agentic Infrastructure, Reliant Energy Retail Services LLC. (“Joint Commenters”) | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-17-Joint-Commenters-II-Comments-032026.docx | Batch Zero eligibility / RTP inclusion | Joint Commenters argue that projects with an ERCOT LLI number that also met the criteria for inclusion in the 2026 RTP should be eligible for the allocated portion of Batch Zero. They contend these projects have already demonstrated material commercial and financial commitment and should be treated as substantiated load rather than excluded from the transition process. They also emphasize that aligning Batch Zero with RTP inclusion would improve transparency and provide clearer planning signals to market participants relying on ERCOT transmission planning outputs | Change request | Revise § 9.2.1.2 to include projects with an ERCOT LLI number that satisfied the criteria for inclusion in the 2026 RTP in the allocated portion of Batch Zero | 9.2.1.2 | ERCOT disagrees that the assignment of an LLI number and inclusion in the 2026 RTP is sufficient for inclusion in Batch Zero. One of the principal reasons for Batch Zero is to resolve the interconnection approval challenges faced by ILLEs with submitted studies. An ILLE without at least one completed and approved interconnection study is not the ILLE the Batch Zero Process is intended to serve. | No
Agentic Infrastructure, Reliant Energy Retail Services LLC. (“Joint Commenters”) | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-17-Joint-Commenters-II-Comments-032026.docx | CLR / BYOG treatment / allocated load eligibility | Joint Commenters II argue that projects with an ERCOT LLI number that elect to proceed as a Controllable Load Resource (CLR) or under a Bring Your Own Generation (BYOG) arrangement should be included in the allocated portion of Batch Zero. They argue these projects are willing to energize ahead of full network upgrades while privately bearing curtailment risk, which distinguishes them from loads seeking immediate firm network service and supports more flexible interconnection outcomes | Change request | Revise § 9.2.1.2 to include projects with an ERCOT LLI number that elect CLR or BYOG treatment through their intermediate agreement in the allocated portion of Batch Zero | 9.2.1.2 | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs and Large Loads proposing to locate with new generation (BYOG) in Batch Zero. | No
Agentic Infrastructure, Reliant Energy Retail Services LLC. (“Joint Commenters”) | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-17-Joint-Commenters-II-Comments-032026.docx | Market efficiency / ratepayer protection / siting incentives | Joint Commenters argue that including CLR and BYOG projects in Batch Zero would improve market efficiency and reduce ratepayer risk by allowing load to energize before full network upgrade costs are socialized. They state that these structures increase MWh served before incremental transmission capital is incurred, reduce stranded cost risk if projects abandon while waiting for firm service, and create incentives for loads to locate in areas with underutilized transmission infrastructure. In their view, Batch Zero should be designed to capture these least-cost and reliability benefits as part of the queue-clearing process | Change request | Modify Batch Zero eligibility and allocation rules to expressly accommodate CLR and BYOG projects as a policy tool to reduce stranded cost risk, improve utilization of existing transmission, and support lower-cost system expansion. | 9.2.1.2 | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs and Large Loads proposing to locate with new generation (BYOG) in Batch Zero. | No
Emerald AI | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-25-Emerald-AI-Comments-032026.docx | CLR / flexibility integration | Argues that flexible loads (AI/data centers) can support grid reliability and accelerate time-to-power; Batch Zero should include CLR-enabled projects | Change request | Explicitly include Controllable Load Resource (CLR) rules in Batch Zero framework | 9.2.1.2 | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs and Large Loads proposing to locate with new generation (BYOG) in Batch Zero. | No
Crusoe | 2026-03-09 | https://www.ercot.com/files/docs/2026/03/09/145PGRR-05-Crusoe-Comments-030926.docx | Re-evaluation of previously finalized LLIS studies | Crusoe objects to ERCOT’s proposed authority to re-evaluate the completeness and validity of previously finalized LLIS studies. They argue that once Sections 9.4 and 9.5 (now 9.9 and 9.10) were satisfied, studies were final and relied upon for major capital commitments. Retroactive review undermines investment-backed expectations and destabilizes regulatory certainty | Change request | Replace proposed § 9.2.1.4(3) with deemed-valid safe harbor: completion of §§ 9.9 and 9.10 constitutes complete and valid studies as a matter of law; no further review required or permitted | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Schaper | 2026-03-05 | https://www.ercot.com/files/docs/2026/03/05/145PGRR-03-Schaper-Energy-Consulting-Comments-030526.docx | Re-evaluation of previously finalized LLIS studies | Schaper objects to proposed § 9.2.1.4, which would authorize ERCOT to retroactively determine the “completeness and validity” of previously finalized LLIS studies. They argue that under the current PGRR: (1) ERCOT communicates LLIS results under Section 9.4. (2) Customers satisfy Section 9.5 by executing interconnection agreements, posting security, and issuing notice to proceed. (3) Upon satisfaction of Section 9.5, the study is complete and the load is carried in future planning studies as base load. Schaper asserts that these determinations are final and not provisional. Retroactive re-evaluation would undermine reliance interests and cause irreparable financial harm to developers who committed capital under executed interconnection agreements | Change request | Substantially replace § 9.2.1.4 with a new provision establishing a safe harbor, under which completion of the study process under Sections 9.4 and 9.5 constitutes, as a matter of law, a complete and valid study finding — eliminating the proposed retroactive review entirely | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. However, ERCOT disagrees with the characterization of proposed § 9.2.1.4 as retroactive. ERCOT is using the criteria to prospectively establish eligibility in a new Batch Zero Process. | No
Schaper | 2026-03-05 | https://www.ercot.com/files/docs/2026/03/05/145PGRR-03-Schaper-Energy-Consulting-Comments-030526.docx | Governance/Scope of ERCOT authority | Schaper specifically challenges proposed § 9.2.1.4(2), which vests ERCOT with “sole authority” to determine the completeness and validity of prior studies. They argue that (1) Study communications issued under current Section 9.4 are not provisional. (2) Once Section 9.5 requirements are met, the studies are final determinations. (3) Customers reasonably rely on those final determinations in executing binding agreements | Change request | Delete or substantially replace § 9.2.1.4 so that completion of Sections 9.4 and 9.5 establishes study validity and eliminates ERCOT’s authority to conduct retroactive re-determination | 9.2.1.4 | In its March 17 comments, ERCOT added § 9.2.1.4(3), which grants approvals under Section 9.4 and 9.5 to be valid studies. | No
Schaper | 2026-03-05 | https://www.ercot.com/files/docs/2026/03/05/145PGRR-03-Schaper-Energy-Consulting-Comments-030526.docx | Load prioritization methodology | Schaper objects to § 9.2.1.4(3)(a)(ii)(A), which uses RPG submission-related dates as a trigger for ordering loads and possible restudy RPG submission does not constitute a completed interconnection study under Section 9.4. RPG filings may have been submitted in contravention of the Large Load interconnection rules under PGRR115. Customers who followed the binding LLIS process should not be disadvantaged relative to those relying on RPG submissions. The only appropriate ordering criterion is completion of steady-state and stability studies under Section 9.4 | Change request | Amend or substantially delete § 9.2.1.4(3)(a)(ii)(A) so that completion of the steady-state and stability study process under Section 9.4 is the ordering criterion, rather than RPG submission date | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Rose City Partners | 2026-03-10 | https://www.ercot.com/files/docs/2026/03/10/145PGRR-06-Rose-City-Partners-Comments-031026.docx | Re-evaluation of previously finalized LLIS studies | Rose City Partners argue that under the current Planning Guide, once a developer satisfies Sections 9.4 and 9.5, they should have firm, locked-in power. Allowing ERCOT to revisit or withdraw that certainty - even after a developer has satisfied study, financial, and construction-related requirements- creates severe market disruption. Rose City frames this as a certainty issue: developers, lenders, investors, and tenants require absolute assurance before committing millions of dollars. If ERCOT can retroactively invalidate or re-evaluate completed studies, then developers cannot rely on ERCOT’s rules, and development activity will stall | Change request | Adopt new language for 9.2.1.4 that: (1) Confirms with absolute certainty that developers who satisfied §§ 9.4 and 9.5 under current rules will be treated as “firm” or “base load” in any scenario, whether a Batch Process is implemented or not. (2) Eliminates ERCOT’s ability to retroactively undermine completed LLIS approvals | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. However, ERCOT disagrees with the characterization of proposed sections as retroactive. ERCOT is using the criteria to prospectively establish eligibility in a new Batch Zero Process. | No
Schaper | 2026-03-11 | https://www.ercot.com/files/docs/2026/03/11/145PGRR-07-Schaper-Energy-Consulting-Comments-031126.docx | Safe harbor timing / narrowed lookback window | Schaper supports narrowing the proposed §9.2.1.4 lookback to loads that achieved substantiation under §§9.4 and 9.5 immediately prior to the July 15, 2026 deadline, and proposes formal Safe Harbor language deeming such studies complete and valid. They argue that without this, substantiated projects face an extended period of classification uncertainty during active construction and long-lead procurement, contrary to ERCOT’s prior “must-study” treatment | Change request | Amend §9.2.1.4 to establish a Safe Harbor for Large Loads that satisfied §§9.4 and 9.5 on or before a defined date (e.g., June 15, 2026), deeming those studies complete and valid and classifying the loads as Base Load without further retroactive review | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Schaper | 2026-03-11 | https://www.ercot.com/files/docs/2026/03/11/145PGRR-07-Schaper-Energy-Consulting-Comments-031126.docx | Dynamic Model Validity – “Equivalent or Better” Standard | Schaper argues that proposed §9.2.1.4(3)(a)(i) could invalidate prior studies solely because updated dynamic model data differs from the model used in earlier stability studies — even where changes result from compliance with ERCOT rulemakings (e.g., NOGRR282, PGRR144). They characterize this as a compliance trap that penalizes ILLEs for improving voltage ride-through, frequency ride-through, or reactive support performance | Change request | Revise §9.2.1.4(3)(a)(i) to permit the Interconnecting DSP/TSP to determine, in reasonable engineering judgment, whether updated dynamic model data produces system performance equivalent to or more favorable than the prior study, with a presumption that improvements in ride-through or reactive support satisfy this standard (“equivalent or better” framework) | 9.2.1.4 | In its March 17 comments, ERCOT modified § 9.2.1.4(3)(a)(i) to allow the interconnecting TSP or interconnecting DSP to use its engineering judgment whether the updated data would result in an adverse impact from a previous stability study. | No
Lancium | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-09-Lancium-Comments-031926.docx | Study Validity / Eligibility Criteria | Lancium argues that the current framework places undue weight on RPG submission dates and ERCOT endorsement, potentially excluding projects that are technically mature and financially committed. They emphasize that loads included in RPG submissions with executed interconnection agreements have already undergone substantial study and should be treated as valid | Change request | Revise §9.2.1.4 to: (i) update RPG submission cutoff date to March 4, 2026; and (ii) add a criterion recognizing loads included in RPG submissions with executed interconnection agreements as valid | 9.2.1.4 | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it remains opposed to changing the date by which an RPG submission must have been made from December 15, 2025 to March 4, 2026. As ERCOT has stated clearly in recent Batch Zero workshops, the choice of December 15 was not arbitrary. Rather, it is a reflection of the date Planning Guide Section 9 became effective. At that point, the only path to interconnect a Large Load became the LLIS process. Allowing loads included in RPG submissions after December 15 into Batch Zero would be contrary to the clear intent of stakeholders when they closed off RPG as an avenue for Large Load interconnections in PGRR115. Further, ERCOT does not support the classification of loads included in RPG submissions (regardless of submission date) that have not yet received RPG approval and, if applicable, ERCOT Independent Review and Board endorsement as base load in Batch Zero. Loads from submissions that have not yet been fully reviewed cannot be considered to have complete and valid studies. | No
Schaper | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-11-Schaper-Energy-Consulting-Comments-031926.docx | Study Validity / Base Load Certainty | Schaper supports Skybox’s position that projects with executed IA/FEA, demonstrated financial commitment, completed studies, and site control should be treated as having satisfied Batch Zero readiness criteria and should not be re-screened, re-prioritized, or invalidated based on timing | Change request | Align with Skybox’s approach to treat advanced-stage projects as fixed base load inputs and preserve study validity based on project completeness rather than timing | 9.2.1.4 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Schaper | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-11-Schaper-Energy-Consulting-Comments-031926.docx | Process Design / Administrative Function | Schaper endorses Lancium’s position that Batch Zero should function primarily as an administrative planning tool to incorporate advanced-stage load into transmission planning, rather than a mechanism to invalidate prior work performed under existing Section 9 processes | Change request | Align with Lancium’s approach to maintain Batch Zero as an administrative planning construct and avoid re-evaluation of previously completed studies | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Existing Study Validity / RPG Acceptance Dates | ERCOT’s March 17 revision validates Large Loads included in RPG projects submitted before December 15, 2025 and accepted/endorsed by March 4, 2026 without additional review. RPGs accepted/endorsed after March 4 but before July 10, 2026 would be subject to the ranking process in paragraph (4). Oncor argues there is no logical basis for distinguishing between RPGs accepted by March 4 versus those accepted by July 10, 2026, because both will have reached ERCOT acceptance/endorsement before Batch Zero begins. | Change request | Revise § 9.2.1.4 so that Large Loads addressed by RPGs submitted before December 15, 2025, and Accepted/endorsed by July 10, 2026are considered valid studies without undergoing the additional ranking/review process in paragraph (4). | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Crusoe | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-14-Crusoe-Comments-032026.docx | Study Validity / Retroactivity / Investment Certainty | Crusoe disagrees with ERCOT’s use of March 4, 2026 (the original PGRR filing date) as the cutoff for automatic study validity under § 9.2.1.4(3). Crusoe argues that: A retroactive cutoff undermines the purpose of Batch Zero, which is to provide certainty. Many ILLEs targeting 2027–2028 energization have substantially completed legacy §§ 9.9 and 9.10 but are dependent on TSP/ERCOT processing timelines they do not control. Projects that narrowly missed the March 4 date are similarly situated to those that met it. | Change request | Revise § 9.2.1.4(3) to replace the March 4, 2026 cutoff date with a forward-looking cutoff of June 1, 2026 for automatic study validity. (For both RPG-based studies and Legacy LLIS corporations) | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Stream Data Centers, L.P. and Provident Inc. (“Joint Commenters”) | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-15-Joint-Commenters-Comments-032026.docx | Study Validity / Retroactive Cutoff | Joint Commenters focus on a targeted issue: the use of March 4, 2026 as the cutoff date in § 9.2.1.4(3)(a) for automatic validation of prior studies tied to RPG projects. They argue that: (1) Large load customers have spent years working with load-serving utilities under evolving study requirements. (2) Many projects were included in RPG-submitted transmission plans more than a year ago. (3) ERCOT has already expended significant effort independently reviewing these projects. (4) Contractual and financial commitments—including procurement of long lead-time equipment and revisions to energization timelines—have already been made. (5) A retroactive cutoff date risks summarily discounting these long-term efforts and commitments. | Change request | Revise § 9.2.1.4(3)(a) to replace March 4, 2026 with a prospective cutoff date, either June 3, 2026 (the day after the anticipated ERCOT Board approval of PGRR145) or June 10, 2026. | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Collaboration / ERCOT–TSP Coordination | CEHE emphasizes that ERCOT’s determination of completeness and validity of existing studies should not rely solely on ERCOT discretion. While ERCOT retains final authority, CEHE stresses that structured consultation with T/DSPs is critical to ensure informed decisions, given TSPs’ knowledge of system conditions and study assumptions | Change request | Add explicit requirement that ERCOT “shall consult with” T/DSPs when evaluating study validity, Replace or soften “sole discretion” language to reflect collaborative decision-making (while preserving ERCOT final authority) | 9.2.1.4 | ERCOT has modified the language to more explicitly require consultation in the spirit of the redlines offered by CenterPoint. | Yes
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Dynamic Data / Modeling Responsibility | CEHE raises concern that assigning T/DSPs responsibility for determining whether updated dynamic data adversely impacts prior studies could lead to inconsistent methodologies and outcomes across utilities | Change request | Assign ERCOT as the primary decision-maker for “adverse impact” determination, with TSP/DSP input; Standardize evaluation approach to ensure consistent application across the system | 9.2.1.4 | Because the TSP performed the previous study, ERCOT believes the TSP is better positioned to determine whether the updated data would result in an adverse impact to the prior study. | No
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Study Area Definition / Evaluation Criteria | CEHE highlights that the term “study area” is not defined in §9.2.1.4, creating risk of inconsistent interpretation when determining whether prior studies remain valid | Change request | Define “study area” explicitly (e.g., facilities impacted above a 3% shift factor threshold), Refine language to ensure consistent and objective application of study validity criteria | 9.2.1.4 | ERCOT believes that engineering judgment is needed when determining the study area and intends to use the same process as is currently used when determining the study area in current LLI studies. | No
Eolic | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-19-Eolic-Comments-032026.docx | Study validity / RTP alignment (PUCT 58480) | Eolic supports ERCOT’s March 17 edits and Lancium’s comments, and emphasizes that the now-final PUCT Project 58480 rule (governing Large Load inclusion in the 2026 RTP) provides a higher-quality, standardized screening framework that should be leveraged in Batch Zero. They argue that RTP inclusion under 58480 reflects significant TSP analysis and should be used as a proxy for study validity and substantiated load | Endorsement |  | 9.2.1.4 | ERCOT does not agree that the criteria for the 2026 RTP should be used to give large loads not included in (4)(a)(ii). ERCOT's concern in Section 9.2.1.4 is whether ERCOT has a study that confirms the large load can be reliably served. Meeting the requirements for inclusion in the 2026 RTP do not inform the validity of the study. | No
Eolic | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-19-Eolic-Comments-032026.docx | Study validity / RTP + legacy alignment | Eolic proposes expanding §9.2.1.4 to recognize projects that combine RTP inclusion (under 58480) with either legacy interconnection progress or RPG participation. They argue this better reflects actual project maturity and avoids excluding projects that have already undergone substantial study and commitment | Change request | Add criteria to §9.2.1.4 recognizing: (i) loads with Legacy IA completed by July 10, 2026 and included in 2026 RTP; and (ii) loads included in RPG submissions (pre-March 4) and also included in the 2026 RTP | 9.2.1.4 | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it remains opposed to changing the date by which an RPG submission must have been made from December 15, 2025 to March 4, 2026. As ERCOT has stated clearly in recent Batch Zero workshops, the choice of December 15 was not arbitrary. Rather, it is a reflection of the date Planning Guide Section 9 became effective. At that point, the only path to interconnect a Large Load became the LLIS process. Allowing loads included in RPG submissions after December 15 into Batch Zero would be contrary to the clear intent of stakeholders when they closed off RPG as an avenue for Large Load interconnections in PGRR115. Further, ERCOT does not support the classification of loads included in RPG submissions (regardless of submission date) that have not yet received RPG approval and, if applicable, ERCOT Independent Review and Board endorsement as base load in Batch Zero. Loads from submissions that have not yet been fully reviewed cannot be considered to have complete and valid studies. | No
Eolic | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-19-Eolic-Comments-032026.docx | Study validity / ordering methodology refinement | Eolic proposes refining the ordering/tie-breaker methodology to give additional weight to projects that combine RPG inclusion with executed interconnection agreements and/or RTP inclusion under 58480. They argue this better reflects project maturity than current criteria | Change request | Modify §9.2.1.4 ordering logic to prioritize projects that combine RPG inclusion + executed IA and/or RTP inclusion under 58480 | 9.2.1.4 | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it remains opposed to changing the date by which an RPG submission must have been made from December 15, 2025 to March 4, 2026. As ERCOT has stated clearly in recent Batch Zero workshops, the choice of December 15 was not arbitrary. Rather, it is a reflection of the date Planning Guide Section 9 became effective. At that point, the only path to interconnect a Large Load became the LLIS process. Allowing loads included in RPG submissions after December 15 into Batch Zero would be contrary to the clear intent of stakeholders when they closed off RPG as an avenue for Large Load interconnections in PGRR115. Further, ERCOT does not support the classification of loads included in RPG submissions (regardless of submission date) that have not yet received RPG approval and, if applicable, ERCOT Independent Review and Board endorsement as base load in Batch Zero. Loads from submissions that have not yet been fully reviewed cannot be considered to have complete and valid studies. | No
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Eligibility / RPG integration | TEBA argues that eligibility should not rely solely on energization dates and should incorporate loads already included in current RPG plans. RPG processes already reflect substantiated load and could accelerate interconnection timelines significantly | Change request | Add RPG-based pathway for Batch Zero inclusion or allow RPG projects to proceed independently of Batch; prioritize loads requiring minimal transmission (e.g., co-location) | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Study validity / process integrity | TEBA opposes ERCOT’s ability to invalidate studies within the batch process (e.g., via eligible load list methodology). They argue that corrections should be handled within the batch study itself rather than through invalidation, which undermines the purpose of a collective study framework | Change request | Revise §9.2.1.4 to remove or limit study invalidation authority; ensure adjustments are handled within the batch process rather than via exclusion | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
TEBA II | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20b-TEBA-Comments-032026.docx | RPG integration / process acceleration | TEBA argues that the proposed Batch Zero process risks delaying projects already included in submitted RPG plans until ~July 2027. They contend that existing RPG processes should continue to be used to approve transmission and associated loads in parallel, rather than forcing projects to wait for Batch Zero. TEBA emphasizes that utilities are best positioned to determine which loads are sufficiently advanced and that projects requiring minimal transmission (e.g., co-located generation) should proceed without delay. They propose that timely-approved RPG projects be included in the Batch Zero base case while continuing to advance independently to avoid stalling investment and transmission expansion | Change request | Continue approving existing RPG projects outside of Batch Zero; allow early advancement of low-transmission-impact loads; include approved RPG loads in Batch Zero base case | 9.2.1.4 | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it is opposed to allowing for a second pathway for Large Load interconnection outside of Batch Zero. | No
Satoshi Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-21-Satoshi-Energy-Comments-032026.docx | Study validity / cutoff date | Satoshi argues that limiting safe harbor to March 4, 2026 is arbitrary and undermines projects that completed the same LLIS process shortly after. They emphasize no technical distinction between studies completed before vs. after March 4 and warn that retroactive invalidation harms investment certainty | Change request | Extend automatic validity safe harbor to July 10, 2026 for projects completing §§9.9–9.10 (with dynamic data check) | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Black Mountain | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-22-Black-Mountain-Comments-032026.docx | Study validity / safe harbor expansion | Black Mountain supports ERCOT’s validity framework but argues it fails to capture projects that are technically advanced and near execution. They highlight projects targeting ≤2027 energization, with steady-state approval, studies submitted by March 24, and expected Firm status by July 10, which have effectively met the intent of “valid studies.” Excluding them based on timing (vs. readiness) risks removing viable near-term load and inefficiently using transmission | Change request | Expand safe harbor to include “near-complete” projects meeting defined readiness criteria (study completion + firming by July 10), not just those completed by March 4 | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Sandow Lakes Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-24-Sandow-Comments-032026.docx | Study timing / fairness to pending projects | Sandow argues that projects with pending studies have been left in suspense awaiting their “batch fate,” even though developers can no longer take additional steps to improve their position because timing is controlled by ERCOT and the TSP. They note that stakeholders previously proposed recognizing projects once submitted for study, rather than only after approval, as a fairer approach for developers whose outcomes depend on utility/ERCOT processing timelines rather than project readiness alone | Change request | Allow projects with load and co-located generation that have completed and submitted required study information to the TSP/ERCOT to receive priority treatment, or otherwise revise eligibility so developers are not disadvantaged solely by ERCOT/TSP processing timing | 9.2.1.4 | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs and Large Loads proposing to locate with new generation (BYOG) in Batch Zero. | No
AEP | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-26-AEP-Comments-032026.docx | Eligibility / RPG integration | Loads studied and submitted in RPG before Batch Zero should be eligible even without ERCOT endorsement; RPG studies are equivalent or more comprehensive than LLIS | Change request | Allow RPG-submitted loads (by July 10, 2026) into Batch Zero without requiring ERCOT endorsement | 9.2.1.4 | While ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4, it remains opposed to changing the date by which an RPG submission must have been made from December 15, 2025 to July 10, 2026. As ERCOT has stated clearly in recent Batch Zero workshops, the choice of December 15 was not arbitrary. Rather, it is a reflection of the date Planning Guide Section 9 became effective. At that point, the only path to interconnect a Large Load became the LLIS process. Allowing loads included in RPG submissions after December 15 into Batch Zero would be contrary to the clear intent of stakeholders when they closed off RPG as an avenue for Large Load interconnections in PGRR115. Further, ERCOT does not support the classification of loads included in RPG submissions (regardless of submission date) that have not yet received RPG approval and, if applicable, ERCOT Independent Review and Board endorsement as base load in Batch Zero. Loads from submissions that have not yet been fully reviewed cannot be considered to have complete and valid studies. | No
AEP | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-26-AEP-Comments-032026.docx | Dynamic data governance | Current draft assigns DSP/TSP responsibility for determining whether dynamic data impacts prior studies | Change request | Assign ERCOT as sole decision-maker for dynamic data impact determination | 9.2.1.4 | Because the TSP performed the previous study, ERCOT believes the TSP is better positioned to determine whether the updated data would result in an adverse impact to the prior study. | No
AEP | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-26-AEP-Comments-032026.docx | Governance / collaboration | ERCOT has “sole authority” but insufficient structured consultation with TSP/DSP | Change request | Require ERCOT to consult with DSP/TSP in study validation decisions | 9.2.1.4 | ERCOT has modified the language to more explicitly require consultation in the spirit of AEP's suggestion. | Yes
AEP | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-26-AEP-Comments-032026.docx | Methodology clarity / study area | “Study area” undefined → risk of inconsistent application | Change request | Define study area using shift factor threshold (e.g., 3%) | 9.2.1.4 | ERCOT believes that engineering judgment is needed when determining the study area and intends to use the same process as is currently used when determining the study area in current LLI studies. | No
Monarch Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-27-Monarch-Energy-Comments-032026.docx | Transition timing / fairness | March 4 to July 10 transition creates arbitrary outcomes; projects with identical readiness may be treated differently based purely on timing | Change request | Remove or mitigate timing-based distortions in transition window; ensure projects with demonstrated commitment are treated consistently regardless of timing | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Skybox Datacenters | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-10-Skybox-Datacenters-Comments-031926.docx | Study Validity / Base Load Certainty | Skybox argues that projects with executed IA/FEA, demonstrated financial commitment, completed studies, and site control should be treated as fixed base load in Batch “0.” Batch Zero should function as an administrative planning tool and not re-screen, re-prioritize, or displace advanced-stage projects. Study validity should be based on project-specific completeness, not timing or interdependencies | Change request | Revise § 9.2.1.4 to recognize that projects meeting Section 9 readiness milestones (completed studies, executed IA/FEA, posted financial commitment, site control) are treated as fixed base load inputs in Batch “0.” Clarify that advanced-stage projects are not subject to re-prioritization or displacement | 9.2.1.4 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Crusoe | 2026-03-09 | https://www.ercot.com/files/docs/2026/03/09/145PGRR-05-Crusoe-Comments-030926.docx | Load prioritization methodology | Crusoe challenges the prioritization of projects based on RPG submission date (Pathway A) over completed LLIS and executed IAs (Pathway B). They argue RPG submission does not represent a completed interconnection study or binding developer commitment. Using RPG dates as a priority metric disadvantages more mature projects and was not vetted through stakeholder process | Change request | Delete RPG submission date as ordering criterion; use only completion of § 9.4 study process as priority metric; Pathway B (completed LLIS) takes priority over Pathway A (RPG submission) | 9.2.1.4 | ERCOT continues to evaluate proposed changes to the Batch Zero eligibility criteria and deadlines described in Sections 9.2.1.1 through 9.2.1.4. These will be addressed in future comments. | No
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Applicability Clarity / Dynamic Model Updates | Section 9.2.2(3) requires ILLEs to submit dynamic data by July 10, 2026. Oncor notes that it is unclear whether this requirement applies to Base Load, Load to Be Studied, or both. They also question whether updated dynamic models are expected for Base Load projects. | Change request | Clarify in writing whether § 9.2.2(3) applies to Base Load, Load to Be Studied, or both. If applicable to Base Load, clarify whether updated dynamic models are required by July 10, 2026. | 9.2.2 | ERCOT expects the ILLE to notify its interconnecting TSP of any changes to its dynamic model or data and for that information to be shared with ERCOT. That expectation for Large Loads that will be included in the Batch Zero study, regardless whether the Load will be studied as baseload or to be studied for MW allocation. | No
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Load Commissioning Plan / Ownership & Sequencing | CEHE notes ambiguity in sequencing and ownership of LCP updates, particularly after Batch Zero completion, and seeks to clarify roles between ERCOT and T/DSPs | Change request | Reorder §9.2.4 to reflect correct sequence of updates, Assign final LCP update responsibility to ERCOT after Batch Zero, Clarify that T/DSP role post-study is monitoring compliance, not modifying LCP | 9.2.4 | ERCOT acknowledges the potential ambiguity and has proposed redlines in Sections 9.2.4 and 9.4. | Yes
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Timeline Feasibility / Agreement Execution | CEHE notes that the current ~30-day window between issuance of Batch Zero results and required execution of interconnection agreements is operationally unrealistic, especially without a standardized agreement template | Change request | Extend deadline from March 1 to April 1, 2027 (~60 days), Maintain shorter timeline only if a standardized IA form is established by PUCT | 9.3.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Study Transparency / TSP Participation | Oncor recommends more structured TSP involvement in the Batch Zero Study process, particularly in review of scope and identification of transmission facility improvements. | Change request | Require ERCOT to post a preliminary study scope and methodology to the MIS Certified area with a five-business-day TSP review period. After consultation, provide TSPs with a formal written comment opportunity on the list of identified Transmission Facility Improvements. | 9.3.2 | ERCOT has added language requiring ERCOT to present the Batch Zero study scope to the RPG and solicit feedback from stakeholders. | Yes
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Study Horizon / Comprehensive Transmission Planning | The current draft sets Year 6 (2033) to the ILLE’s requested amount without identifying transmission projects beyond the five-year (2028–2032) study horizon. Oncor believes this leaves necessary upgrades for full load service to be addressed later through RPG or RTP processes, creating inefficiency. | Change request | Extend the Batch Zero study horizon into a sixth year so that a comprehensive transmission plan to serve each customer’s full requested load is identified as part of the batch study. Oncor notes that additional study time would likely require only weeks, not months. | 9.3.2 | ERCOT is still considering this comment. | No
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Study Governance / TSP Involvement | CEHE argues that the Batch Zero study process lacks sufficient procedural structure for ERCOT–TSP coordination, particularly in defining study scope, identifying transmission upgrades, and incorporating TSP cost and feasibility input | Change request | Introduce a formal, stepwise coordination process in §9.3.2, including (1)Posting preliminary study scope/methodology for TSP review, (2) Defined TSP comment periods, (3) Formal consultation on transmission upgrades, (4) Circulation of upgrade list for TSP review and feasibility input and (5) Defined timelines for cost estimates and feedback. Support extension of study horizon to include Year 6 (2033) for full planning visibility | 9.3.2 | ERCOT has added language requiring ERCOT to present the Batch Zero study scope to the RPG and solicit feedback from stakeholders. ERCOT does not believe language formalizing ERCOT-TSP coordination would be helpful. | Yes
AEP | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-26-AEP-Comments-032026.docx | Study horizon / transmission planning | Year 6 (2033) load is set to full demand but no clear mechanism to identify/approve transmission upgrades; deferring to RTP/RPG creates uncertainty and repeats current issues | Change request | Use Batch Zero to develop a complete, actionable transmission plan covering full load (incl. Year 6), not defer to RTP/RPG | 9.3.2 | ERCOT is still considering this comment. | No
Zero-Emission Grid (ZEG) | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-29-ZEG-Comments-032026.docx | Transparency of study inputs | Supports publication of Batch Zero cases but notes they are insufficient for full analysis without supporting data | Change request | Publish auxiliary files (incl. contingency files) alongside Batch Zero study cases in MIS | 9.3.2 | ERCOT has added a requirement to post contingency files with the study cases. | Yes
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Technical Modeling / Study Integration | Oncor raises several technical concerns: (1) An SSWG case alone is insufficient for short-circuit analysis; ERCOT must prepare a modified SPWG case. (2) Short-circuit analysis should evaluate not just the interconnecting station but also facilities impacted by proposed transmission additions. (3) Language about relay setting determination is insufficient. (4) The rule does not specify how short-circuit findings will be integrated into Refinement Study results if additional upgrades are identified. | Change request | Require ERCOT to provide an SPWG-based case suitable for short-circuit analysis. Expand scope of short-circuit study to include impacted facilities. Remove insufficient relay-setting language. Clarify how short-circuit findings will be incorporated into Refinement Study outcomes. | 9.5.2 | ERCOT is still considering this comment. | No
CenterPoint | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-16-CenterPoint-Energy-Comments-032026.docx | Short-Circuit Analysis / Study Inputs | CEHE identifies multiple gaps in short-circuit analysis design, including mismatch between SSWG and SPWG cases, insufficient scope (limited to interconnection point), and lack of clarity on how results feed into refinement decisions | Change request | Require ERCOT to develop SPWG-based short-circuit cases, Expand study scope to include impacted facilities beyond interconnection point, Clarify how results translate into additional upgrades in refinement study, Remove inadequate relay-setting language | 9.5.2 | ERCOT is still considering this comment. | No
Crusoe | 2026-03-09 | https://www.ercot.com/files/docs/2026/03/09/145PGRR-05-Crusoe-Comments-030926.docx | Financial security and interconnection agreement requirements | Crusoe argues that Section 9.7 incorporates financial requirements from an ongoing PUCT rulemaking (Project No. 58481) that is not yet final. They contend that applying $100,000/MW interconnection fees and new security requirements to projects that already executed legacy IAs and posted security is duplicative and punitive. They also note that some projects required no network upgrades and should not be required to post upgrade security | Change request | Replace specific dollar amounts with references to PUCT Project No. 58481 final rule amounts; effective date tied to PUCT final rule adoption, not PGRR145 effective date | 9.7.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
IREN | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-12-IREN-Comments-031926.docx | Intermediate Agreement Requirements / Early-Stage Standards | IREN believes the current Intermediate Agreement requirements include elements that are too burdensome for early-stage development. Specifically: (1) Binding options to lease or purchase should qualify as acceptable site control at this stage. (2) Requirements related to site-related studies and non-ministerial regulatory approvals are premature for an Intermediate Agreement. (3) Lack of a standardized agreement template reduces efficiency and consistency across utilities. | Change request | Revise § 9.7.1(1)(a) to allow binding lease or purchase options as valid site control. Delete §§ 9.7.1(1)(c) and (d) (site studies and regulatory approvals requirements).Add new § 9.7.1(k) requiring ERCOT to implement a standardized Intermediate Agreement template. Maintain financial security level at $50,000/MW. | 9.7.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Skybox Datacenters | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-10-Skybox-Datacenters-Comments-031926.docx | Interconnection Fee / Regulatory Alignment (PUCT 58481) | Skybox argues that ERCOT’s fixed $/MW interconnection fee construct should not be embedded in the Planning Guide prior to final Commission action. They recommend aligning §9.7.1 with PUCT Project No. 58481 to avoid misalignment and rework once the Commission finalizes the interconnection fee methodology | Change request | Replace fixed $/MW financial security and fee language in §9.7.1 with a reference to the amount determined by the Public Utility Commission of Texas under 16 TAC § 25.194 (as amended) | 9.7.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Commercial requirements / scope of interconnection | TEBA objects to requiring disclosure of power procurement strategy as part of interconnection (intermediate agreement), arguing this is unrelated to interconnection and commercially sensitive | Change request | Remove or clarify requirement to disclose power procurement plans as part of interconnection eligibility | 9.7.1 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Crusoe | 2026-03-09 | https://www.ercot.com/files/docs/2026/03/09/145PGRR-05-Crusoe-Comments-030926.docx | Financial security and interconnection agreement requirements | Crusoe argues that Section 9.7 incorporates financial requirements from an ongoing PUCT rulemaking (Project No. 58481) that is not yet final. They contend that applying $100,000/MW interconnection fees and new security requirements to projects that already executed legacy IAs and posted security is duplicative and punitive. They also note that some projects required no network upgrades and should not be required to post upgrade security | Change request | Replace specific dollar amounts with references to PUCT Project No. 58481 final rule amounts; effective date tied to PUCT final rule adoption, not PGRR145 effective date | 9.7.2 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Crusoe | 2026-03-09 | https://www.ercot.com/files/docs/2026/03/09/145PGRR-05-Crusoe-Comments-030926.docx | Financial security and interconnection agreement requirements | Duplicative security, fee, and agreement requirements for loads with executed legacy IAs, posted security, and paid CIAC; no accommodation for loads with no required upgrades | Change request | Add § 9.7.2(2) deemed compliance provision; exempt loads with no network upgrades from § 9.7.2(j) security and § 9.7.2(g) fee requirements; develop legacy agreement conversion process crediting prior payments | 9.7.2 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
IREN | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-12-IREN-Comments-031926.docx | Interconnection Agreement Standards / Lease Duration / Standardization | IREN believes the Interconnection Agreement requirements should better reflect long-term project realities and increase process efficiency. Specifically: (1) A five-year minimum lease term does not reflect the expected life of large load projects. (2) Site-related study and regulatory approval disclosures should be standardized to improve transparency and efficiency. (3) Lack of a standardized Interconnection Agreement template creates variability across utilities. | Change request | Revise § 9.7.2(1)(a)(i) to require a minimum lease term of 20 years. Revise §§ 9.7.2(1)(c) and (d) to require ERCOT to develop standardized lists of required site-related studies and regulatory approvals. Add new § 9.7.2(k) requiring ERCOT to implement a standardized Interconnection Agreement template. Maintain $50,000/MW interconnection fee. | 9.7.2 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Skybox Datacenters | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-10-Skybox-Datacenters-Comments-031926.docx | Prospective Application / Avoid Duplicative Obligations | Skybox argues that §§ 9.7.2(1)(f) and (g) should apply prospectively only to IAs/FEAs executed after December 15, 2025. Projects that have already demonstrated financial commitment (e.g., CIAC or TDSP-determined financial security for interconnection-related costs) should be deemed to have satisfied readiness requirements under the prior framework. Skybox further emphasizes that prior financial commitments should be credited on a first-dollar basis to avoid duplicative or overlapping obligations | Change request | Apply §§ 9.7.2(1)(f) and (g) only to IAs/FEAs executed on or after December 15, 2025. Deem previously posted financial security, deposits, or CIAC reflecting TDSP-determined interconnection costs as satisfying or crediting toward § 9.7.2 requirements on a first-dollar basis | 9.7.2 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Skybox Datacenters | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-10-Skybox-Datacenters-Comments-031926.docx | Interconnection Fee / Regulatory Alignment (PUCT 58481) | Skybox argues that ERCOT’s fixed $/MW interconnection fee construct should not be embedded in the Planning Guide prior to final Commission action. They recommend aligning §9.7.2 with PUCT Project No. 58481 to avoid misalignment and rework once the Commission finalizes the interconnection fee methodology | Change request | Replace fixed $/MW financial security and fee language in §9.7.2 with a reference to the amount determined by the Public Utility Commission of Texas under 16 TAC § 25.194 (as amended) | 9.7.2 | As explained during the March 30, 2026 Batch Study Workshop, ERCOT intends to file revisions to Sections 9.7 of the Planning Guide after the PUCT issues a final rule in Project No. 58481. Doing so will allow the ILLE, Interconnecting TSP, and Interconnecting DSP to align their respective agreement and financial security with the final rule. | No
Skybox Datacenters | 2026-03-19 | https://www.ercot.com/files/docs/2026/03/19/145PGRR-10-Skybox-Datacenters-Comments-031926.docx | Incremental Financial Security / Sequential Application | Skybox proposes clarifying that financial security requirements for significant equipment and services operate as incremental obligations rather than duplicative ones. Previously posted security, deposits, or CIAC reflecting TDSP-determined interconnection-related costs should be applied sequentially, additional financial security should only cover incremental gaps between existing commitments and actual interconnection costs. | Change request | Revise § 9.7.2(1)(h) to require sequential crediting of previously posted financial commitments before imposing additional security requirements. Limit new financial requirements to incremental amounts necessary to address identified gaps. | 9.7.2 | Currently, ERCOT intends to retain as eligibility criteria for Batch Zero the proposed large load interconnection standards in the Public Utility Commission of Texas’s (PUCT) Proposal for Publication (PFP) in Project No. 58481 (58481 PFP) and is not offering at this time redline revisions to Sections 9.2 or 9.7. However, at the April 2, 2026 Open Meeting, PUCT Commissioners indicated that they plan to offer guidance on the eligibility criteria for Batch Zero loads. ERCOT will review any guidance from the Commissioners and submit additional comments on Sections 9.2 and 9.7, as necessary, following the April 17, 2026 Open Meeting. ERCOT encourages stakeholders interested in the eligibility criteria to file comments in Project No. 58481 in advance of the April 17, 2026 Open Meeting. | No
Oncor | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-13-Oncor-Comments-032026.docx | Role Clarity / TSP vs DSP Responsibilities (Governance) | Broader ambiguity in DSP vs TSP roles across the PGRR (beyond attestations), especially for study execution, dynamic data submission, short-circuit analysis, and LCP responsibilities; historically TSP-led | Change request | (1) Clarify roles across all provisions, (2) Retain TSP as primary entity for technical studies and data submission, (3) Include DSP for notifications / customer-facing elements where appropriate | Cross-cutting | ERCOT is still considering the redline changes on this topic proposed by Oncor. | No
Vistra | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-18-Vistra-Comments-032026.docx | SB6 alignment / 39.169 NMA treatment | Vistra argues that Batch Zero timelines are fundamentally incompatible with PURA §39.169 (SB6), which requires ERCOT to complete system impact studies within 120 days and PUCT action within 180 days. The Batch Zero process, combined with PUCT 58479/58481 requirements, would delay study “completion” by ~9+ months, effectively preventing 39.169 NMA projects (co-located load with existing generation) from meeting statutory timelines. They emphasize that these projects are low transmission risk and explicitly contemplated by the Legislature | Change request | Exempt or carve out 39.169 NMA projects from Batch Zero; allow them to proceed under Legacy LLIS process, with optional (not mandatory) participation in Batch; treat such projects as Base Load with no re-study or delay | Cross-cutting | PURA § 39.169 does not create an entitlement to a decision within 120 days of filing the application for the net metering study. The statute provides that the 120-day clock starts after ERCOT has everything it needs to conduct the study, and so if we move to a Batch study process, it is not unreasonable to conclude that ERCOT will need the Batch Study Process to be completed before the separate net metering study moves forward. | No
Vistra | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-18-Vistra-Comments-032026.docx | Eligibility / Base load treatment for NMAs | Vistra further argues that 39.169 NMA projects should receive preferential treatment in Batch Zero baseline modeling given their limited number and minimal transmission impact (existing POI, self-supply / curtailment capability). Without this, they are structurally disadvantaged relative to other loads despite being more efficient for the system | Change request | Add explicit eligibility pathway for 39.169 NMA projects to be included as Base Load (with timing flexibility up to July 24, 2026 and beyond March 4 cutoff) | Cross-cutting | There is no basis in PURA § 39.169 to justify preferential treatment to large loads co-locating with existing generation resources. To the contrary, the statutory framework suggests that these arrangements warrant greater scrutiny than other large loads. Moreover, it is possible that a large load co-locating with an existing generation resource can result in the need for transmission upgrades. For example, in Docket No. 58872, the addition of a large load with an existing generation resource was not permitted its full requested MW allocation until after a transmission upgrade is completed. While ERCOT does not agree that large loads participating in a net metering arrangement with an existing generation resource are "disadvantaged," if they are, it is the consequence of co-locating with a generation resource subject to PURA section 39.169. | No
Vistra | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-18-Vistra-Comments-032026.docx | Process design / Flexibility across configurations | Vistra highlights that PGRR145 is overly prescriptive in requiring both DSP and TSP involvement in all cases. In practice, Large Load configurations vary (e.g., netted generation, self-supply, export-only BYOG), and in some cases only a TSP relationship is relevant. The current language creates administrative inefficiency and. misalignment with real-world configurations. Note inconsistency between "TDSP" vs. "TSPs and DSPs." | Change request | Add “as applicable” flexibility throughout references to DSP/TSP roles; allow configurations where only TSP agreements are required (e.g., co-located generation, non-retail load scenarios) | Cross-cutting | ERCOT is open to the addition, but is also evaluating whether and when PGRR145 should specify the Interconnecting DSP or Interconnecting TSP. We will incorporate 'as applicable' where appropriate in a future revision request. ERCOT replaced references to "TDSP" with "Interconnecting DSP" and "Interconnecting TSP." | Yes
TEBA I | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-20a-TEBA-Comments-032026.docx | Governance / discretion vs transparency | TEBA raises concern with multiple provisions granting ERCOT “sole discretion” (e.g., cancelling projects or determining study validity), arguing this creates unpredictability and undermines the stakeholder process | Change request | Replace “sole discretion” language with clear, objective, and transparent criteria for decision-making | Cross-cutting | ERCOT has proposed redlines in this area. | Yes
Satoshi Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-21-Satoshi-Energy-Comments-032026.docx | Process transparency / developer certainty | Satoshi highlights uncertainty created by evolving rules (PGRR145 + PUCT 58481) and lack of clarity on project classification (Base Load vs. Studied Load). They argue developers cannot make financing and construction decisions without clear status visibility | Change request | Establish monthly ERCOT communication cadence; provide standardized checklist and pre-deadline classification guidance to ILLEs | Cross-cutting | ERCOT has stated its intent to provide periodic status updates to the TSPs, who can update their customers, accordingly. | No
3-Waters Technical Services | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-23-3-Waters-Technical-Services-Comments-032026.docx | Load forecasting / reliability risk | Argues ERCOT’s planning framework relies on outdated historical weather data (2008–2023) and too short a planning horizon, leading to material underestimation of future load (esp. AI/data centers). Warns of systemic reliability risks (e.g., sympathetic tripping) that financial commitments cannot mitigate | Change request | Incorporate forward-looking climate models (e.g., CMIP6) and extend planning horizon to better capture future load and reliability risks | Cross-cutting | Broad changes to how ERCOT develops its forecasts for use in interconnection or planning studies is beyond the scope of this expedited revision request. | No
Sandow Lakes Energy | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-24-Sandow-Comments-032026.docx | Prioritization / co-located generation | Sandow argues that Batch Zero does not sufficiently recognize or incentivize projects that bring co-located dispatchable generation. They contend that loads paired with new generation should receive higher priority because they better align with state goals to add new power, reduce system burden, and support faster interconnection. Sandow proposes multiple alternatives, including priority treatment for projects where co-located dispatchable generation covers a substantial share of load demand | Change request | Revise Batch Zero prioritization to give highest priority, or explicit priority status, to Large Load projects with co-located dispatchable generation, including projects where new dispatchable generation covers roughly 80–90% of the Large Load demand | Cross-cutting | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs in Batch Zero. | No
Emerald AI | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-25-Emerald-AI-Comments-032026.docx | System efficiency / cost / siting | CLR “connect-and-manage” enables load to use underutilized transmission and defer upgrades, improving cost efficiency and siting incentives | Change request | Use CLR as a policy tool to accelerate interconnection and minimize transmission expansion costs | Cross-cutting | ERCOT is currently drafting Revision Requests that would establish rules related to the inclusion of CLRs in Batch Zero. | No
Zero-Emission Grid (ZEG) | 2026-03-20 | https://www.ercot.com/files/docs/2026/03/20/145PGRR-29-ZEG-Comments-032026.docx | Definition clarity / eligibility criteria | Notes that many eligibility criteria depend on “Initial Energization” but definition may be ambiguous in practice | Change request | Provide clearer definition and guidance on “Initial Energization” for consistent interpretation | Cross-cutting | The term Initial Energization is a longstanding defined term in Section 2 of the ERCOT Nodal Protocols. | No