## Slide 1
Intra-Hour IRR Forecast Accuracy Updates
(March 2026)
WMWG
Operations Analysis
April 08, 2026

## Slide 2: Current GTBD Parameters
GTBD Component Tuning events:
  None
K1 | 0.00
K2 | 0.00
K3 | 1.00
K4 | 0.20
K5 | 0.50
K6 | 1.00
K7 | 1.00
K8 | 1.00
Integral ACE Cap | 350.00
PWRR Cap | 30.00
PSRR Cap | 40.00*
PDCTRR Cap | 20.00
*PSRR day-time threshold
Notes: 3/12/18 – Integral ACE Time Constant Changed from 60 min to 45 min
5/17/18 – K4 Changed from 0.3 to 0.2 and K5 Changed from 0.4 to 0.5
12/4/18 – 10:05 AM – K6 Changed from 0 to 0.5
2/12/19 – 2:15 PM – K6 changed from 0.5 to 1.0
3/12/19 – 2:10 PM – PWRR Threshold from 10 to 15 MW/min
3/19/19 – 2:15 PM – PWRR Threshold from 15 to 20 MW/min
4/01/19 – 10:00 AM – K5 changed from 0.5 to 0.4 and Max. Integral ACE Feedback changed from 250 to 150
4/24/19 – 1:15 PM – Max. Integral ACE Feedback changed from 150 to 160. PWRR Threshold changed from 20 to 25.
5/22/19 – 1:10 PM – K5 changed from 0.4 to 0.5, Max Integral ACE feedback changed from 160 to 200, PWRR Threshold changed from 25 to 30
6/17/20 – 10 AM - PWRR Calculation method changed from Direct to Interpolated
9/1/20 – 11 AM - Max Integral ACE Feedback changed from 200 to 250
9/3/20 – 3 PM - Max Integral ACE Feedback changed from 250 to 300
9/4/20 – 3 PM - Max Integral ACE Feedback changed from 300 to 250
6/1/21 – 10:00 AM – K8 Changed from 0 to 0.5, PSRR Threshold changed to 10
6/2/21 – 10:00 AM – PSRR Threshold changed from 10 to 20
6/3/21 – 10:00 AM – K8 Changed from 0.5 to 0.75
6/4/21 – 10:00 AM – K8 Changed from 0.75 to 1
9/2/21 – 10:00 AM – PSRR Threshold changed from 20 to 30
7/21/22 – Integral ACE Cap Changed from 250 to 350
7/21/22 – K5 changed from 0.5 to 1
7/22/22 – K5 changed from 1 to 0.5
6/12/23 - PSRR dynamic threshold enabled. The Max PSSR started at 80 MW/min for sunrise and sunset hours
6/15/23 – The Max PSRR threshold increased to 100 MW/min for sunrise and sunset hours
10/26/23- Integral ACE Cap Changed from 350 to 250
05/30/24 – Max Integral ACE Feedback changed from 250 to 300
05/31/24 - Max Integral ACE Feedback changed from 300 to 350
10/31/24– K5 changed to 0.5 to 1 to correct the time error
11/1/24 - K5 changed from 1 to 0.75
11/5/24 – K5 changed from 0.75 to 0.5
11/18/24 – K5 changed from 0.5 to 0.75
11/22/24 – K5 changed from 0.75 to 0.5
3/5/25 – K5 changed from 0.5 to 0.75
3/6/25 – K5 changed from 0.75 to 1
3/7/25 – Max Ace Integral Feedback changed from 350 MW to 400 MW
3/7/25 – PSRR Dynamic Threshold for sunrise and sunset changed from 180 MW/Min to 225 MW/Min
3/11/25 – Max Ace Integral Feedback changed from 400 MW to 350 MW
3/12/25 – K5 changed from 1 to 0.5
6/6/25 – K5 changed from 0.5 to 0.75
6/13/25 – K5 changed from 0.75 to 0.5
7/14/25 – K5 changed from 0.5 to 0.75
7/18/25 – K5 changed from 0.75 to 0.5
7/24/25 – Enabled PWRR direct method in GTBD calculation
12/10/25 – PSRR Dynamic Threshold for sunrise and sunset changed from 225 MW/Min to 280 MW/Min
01/05/26 – PSRR Dynamic Threshold for sunrise changed from 280 MW/min to 180 MW/Min
02/03/26 - PSRR Dynamic Threshold for sunrise changed from 180 MW/min to 280 MW/Min

## Slide 3: Predicted Wind Ramp Rate (PWRR) Error
Performance Metric | Persistence Ramp* | SCED PWRR
Monthly MAE (MW per 5 minutes) | 123 | 85
Monthly MAE when 5-Min. Wind Ramp > 100 MW | 206 | 124
* Persistence Ramp assumes a 0 MW wind ramp

## Slide 4: Predicted Solar Ramp Rate (PSRR) Error
Performance Metric | Persistence Ramp* | SCED PSRR | PSRR, IHPPF | PSRR, STPPF
Monthly MAE (MW per 5 minutes) | 444 | 207 | 200 | 223
Monthly MAE when 5-Min. Solar Ramp > 100 MW | 586 | 254 | 246 | 262
* Persistence Ramp assumes a 0 MW solar ramp