## Slide 1
Large Load Interconnection Batch Study for Special ROS
April 14, 2026
Version 2

## Slide 2: Agenda
Timeline and governance recap
Update on timeline and key workshop dates
Outline PRS/ROS/TAC pathways to June Board with key submission dates
1
6
3
CLR discussion
Review revision language for CLR
BYOG discussion
Further discussion of BYOG approach
Advance discussion on BYOG framework for Batch Zero
5
Market Comments filed on NPRR/PGRR
Review stakeholder comments received
2
Batch Zero Concepts
Detailed review of Batch Zero Concepts
4
Summary of ERCOT Comments
Review updated ERCOT comments to PGRR145 filed on April 4
Review ERCOT responses to stakeholder comments1

## Slide 3: Agenda
Timeline and governance recap
Batch Zero Concepts
Summary of ERCOT Comments
Stakeholder feedback
CLR discussion
BYOG discussion

## Slide 4: Batch Zero Revision Request Timeline
Forums
ROS (Reliability and Operations Subcommittee)
2026
Q1
Q2
Q3
Feb
Mar
Apr
May
Jun
Jul
Workshop #2 Feb 12
Workshop #4 Mar 10
Workshop #5 Mar 24
Workshop #6 Mar 30
PRS Update 3/11
ROS Vote 5/7
Board Vote 6/1
3/4 ERCOT files Batch Zero Revision Request(s)
7/10 Target effective date of protocols
Consideration of Batch Zero NPRR 1325 and PGRR 145
LLWG Feb 19
Workshop #3 Feb 26
TAC Vote 5/19-20
Target Board approval date
Board Meeting 4/20
ROS Update 4/2
Monthly TAC updates
Workshop #7 Apr 9
Special PRS 4/22
Regular TAC 4/29
Special TAC 5/13
PRS Vote 5/6
Monthly LLWG updates
4/9 ERCOT files draft comments to the PGRR for CLR, followed by NPRRs for both CLR and BYOG (TBD)
ROS Update (special) 4/14
ROS Update 3/5
ROS Update (special) 4/23
PRS (Protocols Review Subcommittee)
Workshops and working groups
TAC
ERCOT Board
Objective
Align stakeholders on direction/scope following Commission decision
Define the scope, boundaries, and intended role of Batch Zero
File NPRR 1325 for Workshops and PRS review
Endorse NPRR 1325 for advancement to TAC
File PGRR 145 for Workshops and ROS review
Endorse PGRR 145 for advancement to TAC
Review/endorse combined NPRR/PGRR package for Board approval
Close outstanding design and drafting issues, incorporate vetted stakeholder feedback, and finalize Revision Request language for committee approval
Preview structure/governing concepts of Batch Zero PGRR before filing
Note that TAC leadership is involved in considering options to ensure successful review and approval
Source: ERCOT discussions
Regular PRS 4/15
ERCOT is considering focus of next week’s
ROS 4/14 and PRS 4/15 as educational
and for highlighting key issues.

## Slide 5: Revision Request Process Flow
Comments may be filed between each step of the process
Comments for NPRR1325 may be submitted using the Comments Form found here
Comments for PGRR145 may be submitted using the Comments Form found here.
Submit to RevisionRequest@ercot.com
NPRR Comments
PGRR Comments
Large Load Interconnection Workshops
NPRR/PGRR
Review
BOARD
PUCT
TAC
ROS
PGRR Language/IA Review
PRS
NPRR Language/IA Review

## Slide 6: CLR and BYOG frameworks are being integrated into Batch Zero filing, forming a first comprehensive design with further refinement over time
PCLR comments
PCLR comments
PCLR comments
BYOG comments
PCLR comments
BYOG comments
March 4: ERCOT files PGRR145 and NPRR1325
March 17 and April 4: targeted ERCOT comments to incorporate stakeholder feedback
Establishes foundational framework for Batch Zero execution and LLI processing
April 13: PCLR introduced as modular enhancement via comments to PGRR145 / NPRR1325
Enables early shaping of controllable load pathway without delaying core filing
April (TBD): BYOG introduced as modular enhancement via comments to PGRR145 / NPRR1325
Enables integration of generation-backed load pathway without delaying core filing
Path of PGRR145 and NPRR1325 towards governance approval
Key takeaways
Modular approach enables speed without locking design: core framework advanced while PCLR and BYOG are developed in parallel
Convergence toward June Board: PGRR145/NPRR1325, PCLR, and BYOG converge into a complete, minimum viable package for decision-making
Minimum viable, not final design: PCLR and BYOG are introduced as initial concepts, with further refinement expected post June Board
Source: ERCOT discussion
1
2
3
Core Batch Zero framework established
PCLR framework integration
BYOG framework integration
Detailed next
PGRR145
PGRR145
PGRR145
NPRR1325
NPRR1325
NPRR1325

## Slide 7: PCLR introduces a flexible pathway within Batch Zero, requiring targeted updates across PGRR sections
PGRR145 reference section
Section 9.2 – Applicability, Eligibility, and Submission Requirements
Section 9.3 – Batch Zero Interconnection Study Methodology
Section 9.4 – Batch Zero Results and Commitment Requirements
Section 9.5 – Refinement Study and Transmission Planning
Section 9.6 – Energization and Operational Requirements
How PCLRs impact/integrate PGRR145 sections
Expand applicability to include PCLR as a distinct pathway, alongside Base Load and Studied Load
Introduce LPC-based modeling and enhanced data requirements for controllable load evaluation
Update LCP to reflect flexible load ranges (LPC to max) and non-linear energization profiles
Model PCLRs at LPC for reliability, decoupling operational and requested demand
Apply binary allocation logic: approve full load if LPC is supportable, otherwise allocate zero
Enable conditional approval of full demand, contingent on operational controllability
Introduce dual commitment structure, requiring interconnection agreement plus PCLR operational commitment
Require signed LPC commitments and notarized forms
Link study results to binding operational constraints and qualification requirements
Plan transmission for full requested load, despite near-term operation at LPC levels
Decouple planning horizon (full load) from operational reality (constrained load)
Allow staged energization, with initial operation capped at LPC until full qualification
Enforce dispatchability and LPC limits, requiring ERCOT approval before exceeding initial thresholds
Source: PGRR145- 38- 4/4/2026 ERCOT Comments; PGRR145 PCLR Comments

## Slide 8: PCLR enables dispatchable, price-responsive load, requiring targeted NPRR updates across pricing, dispatch, and commitment layers
Source: NPRR1325 (March 4, 2026); NPRR1325 Revised Protocol Language (PCLR comments)
NPRR1325 reference section
Section 2 – Definitions, acronyms and abbreviations
How PCLRs impact/integrate NPRR1325 sections
Introduce PCLR as a new controllable load construct, extending CLR into planning/operations
Define eligibility, LPC constraints, and operational limitations
Establish standardized terminology to enable consistent integration across Protocols
Section 3.2.5 – Publication of resource and load information
Publish CLR/PCLR energy bid curves and dispatch behavior
Include PCLR-adjusted bids, reflecting constraint-driven modifications
Provide visibility into real-time demand response to congestion
Section 4.4.9.4 – Mitigated offer cap/floor
Extend mitigation framework to incorporate PCLR participation alongside generation/ESRs
Align traditional offer caps with demand-side bid controls to ensure mitigation treatment
Ensure consistent price formation across supply and flexible demand resources
Section 6.5.7.3 – Security Constrained Economic Dispatch (SCED)
Integrate PCLRs into SCED as dispatchable, price-responsive load resources
Apply Adjusted Bid Caps within the two-step SCED process
Use Energy Bid Curves (instead of static load) to represent flexible demand
Enable real-time congestion management via demand response while maintaining reliability
Section 23 (Form W) – PCLR registration and commitment
Establish formal PCLR registration mechanism (Part A election, Part B commitment)
Require LPC commitments by year, tied to study outcomes
Enforce notarized forms and binding operational obligations
Link planning outcomes to dispatch compliance and ongoing qualification requirements
Section 4.4.9.4.4 – Adjusted Bid Caps (ABC)
Introduce dynamic bid capping for PCLRs based on constraint shadow prices
Use shift factors to determine each PCLR’s contribution to congestion
Enable targeted demand response while preventing over-response and price distortion
New section introduced

## Slide 9: Related PUCT Activities
PUC Project 58480, 16 TAC § 25.370, Large Load Forecasting Rule (Adopted & Effective March 1, 2026)
  After 2026, only Large Loads that have executed an interconnection agreement that satisfies the requirements in PUC Project 58481 will be included in the Large Load forecast. These requirements will be reflected in future revision requests.
  Establishes alternative gating criteria for Large Loads to be included in the 2026 Large Load Forecast, which is used in planning assessments until new cases are constructed in 2027 using new rule criteria.
Source: PUCT Project No. 58480 (final rule) and Project No. 58481 – Proposal for Publication of 16 TAC §25.194 (filed March 12, 2026)
PUC Project 58481, proposed to be 16 TAC § 25.194, Large Load Interconnection Standards (Proposal for Publication published on March 12, 2026)
  Intermediate Agreement Requirements:
    Site control (updated)
    Financial Security ($50,000/MW in current PFP; subject to final rule)
    Disclosures
    Option to pay for significant equipment or services
  Interconnection Agreement Requirements:
    Site control (updated)
    Financial security
    Interconnection fee ($50,000/MW, non-refundable)
    CIAC
    Reallocation
    Withdrawal Consequences
    Refund Eligibility and Timing
  After the PUCT adopts a final rule, ERCOT will file a revision request to align Section 9.7 with the requirements in the final rule.

## Slide 10: Reminder of Scope and Priorities for Workshops
March 4 filings completed for Batch Zero: ERCOT filed the Batch Zero PGRR145 and related NPRR1325 on March 4, initiating the formal governance process and aligning with the May PRS/ROS/TAC sequence and June 1 Board target reflected in the critical path timeline
  March 17 ERCOT comments filed
  April 4 ERCOT comments filed: ERCOT submitted comments on PGRR145 responding to stakeholder feedback received by March 20, incorporating targeted clarifications and refinements (e.g., study scope governance, consultation requirements, modeling updates, alignment with PUCT PFP)
ERCOT will be filing CLR and BYOG design as comments to PGRR145 and NPRR1325. As such Batch Zero comments approved by stakeholders can be specific comments that do or do not include CLR and/or BYOG design elements. ERCOT Market Rules will help manage these versions.
  CLR Status: ERCOT draft revisions review today (April 9) ahead of comment filing next week
  BYOG Status: Concepts in progress, targeting filing comments for PRS 4/22 and ROS 4/23
Long-term Batch Process revisions: out of scope for the current filing but soon after June 1. ERCOT will incorporate lessons learned from Batch Zero to inform future revision requests and the design of a durable, repeatable batch study process

## Slide 11: Agenda
Batch Zero Concepts
Summary of ERCOT Comments
Stakeholder feedback
CLR discussion
BYOG discussion
Batch Zero Concepts
Timeline and Governance Recap

## Slide 12: Batch Zero Overview – Two Phases
Study Inputs
Batch Zero Study
Batch Zero Refinement
ILLE Commitment Period
Transmission Plan to RPG
~6 months
~3 months
  Steady state study and dynamic stability screening
  Identify planning criteria violations
  Present study scope and methodology to RPG for stakeholder input
  Work iteratively with TSPs to determine amount of load that can be reliably served in each year and, where feasible, upgrades needed to serve full load request
Work iteratively with TSPs to
  Refine and update required transmission upgrades based on committed loads
  Review cost estimates and alternative upgrade options
  Develop a transmission plan to serve committed loads

## Slide 13: Batch Zero Study Scope Overview
  Study horizon: 2028–2032 (Years 1–5), load amounts not reliably served within 2028-2032 will be set equal to requested load in 2033 (Year 6)
  What ERCOT studies (per year): ERCOT builds cases from SSWG base cases and runs reliability assessment across:
    Summer peak load (high load system stress)
    Summer, no solar (sunset, net peak load)
    Fall peak (used to assess maintenance outage conditions consistent with ERCOT Planning Guide criteria)
  Reliability assessment coverage:
    Evaluate planning criteria violations triggered by adding the Batch Zero loads (across scenarios/contingencies ERCOT selects)
    Determine “reliably served MW” per load, per year (i.e., deliverable load that can be served without violating planning criteria)
    Load that cannot be reliably served in years 1-5 will be allocated in year 6 (2033)
  Generation assumptions: if additional generation is needed to serve the modeled load, ERCOT models generation additions consistent with applicable planning methodologies
  Transparency: ERCOT posts study cases and contingencies (interconnection and refinement) used for Batch Zero on the MIS Secure Area once available
Scope details
Key Design Considerations
  One consistent, system-wide reliability study: ERCOT evaluates all Batch Zero-eligible Large Loads using a common set of assumptions, criteria, and cases to identify system limitations and needed upgrades
  Clear, year-by-year outcomes: for each assessed Large Load, the study determines the maximum peak MW that can be reliably served each year (2028–2033) and the transmission upgrades needed to increase service toward the requested level
  Stakeholder input on methodology: ERCOT presents study scope and approach to RPG for comment prior to execution

## Slide 14: Batch Zero Study Methodology and Study Elements
Study elements and methodology
Key Design Considerations
  Study must be repeatable and explainable: ERCOT uses transparent study inputs (posted cases), consistent criteria, and a clear link from violations to upgrades to year-by-year reliably served MW
  Actionable coordination: the process enables rapid, iterative ERCOT–TSP alignment on transmission improvements while the study is underway
  Prepare system-wide study cases (ERCOT)
    Develop annual cases for 2028–2032 from SSWG base cases
    Add Batch Zero-eligible Large Loads per the inclusion criteria and model treatment rules
    Post cases to MIS Secure once available
  System-wide reliability assessment (ERCOT)
    Study scenarios and contingencies ERCOT determines are needed to evaluate reliability impacts
    For each assessed LL, identify planning criteria violations associated with the proposed addition
    Determine the amount of peak load that can be reliably served each year
  Stability screening assessment (ERCOT)
    Perform the stability component of the Batch Zero study
    Document identified stability issues and reflect any resulting limitations in year-by-year reliably served MW
  Identify transmission improvements (ERCOT and impacted TSPs)
    Once violations are identified, ERCOT initiates communication with relevant TSPs
    TSPs provide upgrade recommendations; ERCOT and TSPs iterate through the study period until needed upgrades are identified with ERCOT retaining final determination authority
    Results translate into upgrades resolving violations/enabling higher reliably served MW over time
  Supporting prerequisites (TDSPs/TSPs, as applicable)
    Short-circuit and other relevant studies are completed by the interconnecting TDSP/TSP at least 30 days before ERCOT completes the Batch Zero study and issues results
    TDSPs/TSPs provide necessary model information prior to start of Batch Zero

## Slide 15: Outputs, Deliverables, and Timeline
Process and outputs
  Core timeline
    By July 10, 2026: ILLEs meet eligibility / milestone requirements
    By July 24, 2026: TSPs/DSPs submit complete project information to ERCOT
    By August 7, 2026: ERCOT confirms Batch Zero inclusion and classification of each load
    January 29, 2027: ERCOT issues the Batch Zero Study Report, provides Load Commissioning Plans (LCPs) to ILLEs (via TSPs/DSPs) and notifies TSPs of Batch Zero results
    March 1, 2027: TDSPs notify ERCOT which Large Loads have met commitment requirements
    June 1, 2027: ERCOT completes the Batch Zero Refinement Study and delivers the Batch Zero Transmission Plan to RPG
  Primary outputs
    Batch Zero Study Report (summary of reliability impacts, identified planning criteria violations, and proposed transmission upgrades)
    Load Commissioning Plan (LCP) per Large Load
      Maximum reliably served peak MW for each year (2028–2033)
        Loads not reliably served receive full requested allocation for year 2033
    Estimated security requirements and CIAC obligations required to inform ILLE commitment decisions
    Confidential TSP package: detailed upgrade list and associated Large Loads (as applicable)
  Refinement and RPG handoff
    Only Large Loads that meet commitment milestones remain in scope, loads that do not meet commitment are removed from Batch Zero
    MW allocations for Large Loads that meet commitment criteria by the deadline are not adjusted during the Refinement Study
    ERCOT re-evaluates whether previously identified upgrades are still needed/modified/no longer required
    Final Batch Zero Transmission Plan is delivered into the RPG process
  Actionable outcomes: each Large Load receives a year-by-year Load Commissioning Plan (LCP) and estimated security requirements to support commitment decisions. TSPs receive
  Clear commitment gate to planning certainty: only Large Loads that meet commitment milestones move into the Refinement Study and transmission plan delivered to RPG
Key Design Considerations

## Slide 16: Batch Zero process flow chart for studied load
Submit intermediate agreement requirements
Sign intermediate agreement and Send Batch Info to ERCOT
Build Cases and Post on MIS Secure
Perform Batch Steady State Study
Perform transmission improvement analysis
Perform supporting studies (as applicable, including refinement phase)
Post cases and results on MIS Secure and Communicate Results
Submit interconnection agreement requirements
Sign interconnection agreement
Perform Refinement Transmission Plan Study
Provide Cost Estimates and supporting inputs
Submit Refinement Transmission Plan Study for RPG Review
Resolve RPG Comments and Seek BOD endorsement, when necessary
ERCOT
T(D)SP
Developer (Interconnecting Large Load Entity – ILLE)
Perform Batch Stability Screening Study

## Slide 17: Proposed Batch Zero Timeline
1
2
3
4
5
6
7
8
9
9
2026
2027
Aug
Sep
Oct
Nov
Jul
Dec
Feb
Mar
Apr
May
Jun
Jul
Aug
Jan
Sep
RPG Comment Period (3 weeks)
RPG Study Mode (4-weeks, if required)
TAC (August 2027)
Board (September 2027)
2026 RTP
Final Report (2 weeks)
2027 RTP
Batch Zero (Study years 2028-2032)
Stability Screening Study (14 weeks)
Steady State Analysis (15 weeks)
Developer Commitment Deadline
FAC-002 Stability
Batch Refinement Study (13 weeks)
Case Build (13 weeks)
Batch Refinement Study:
ERCOT: determine which transmission improvements identified in the Batch study are still required based on which loads met the commitment requirements
TSPs: provide cost estimates and refinement of transmission improvement projects and alternatives
ERCOT: refine and confirm transmission improvements for RPG submission
ERCOT: prepare final report and submit to RPG
Steady State and Stability Analyses:
ERCOT: identification of criteria violations
ERCOT and TSPs: identification of transmission improvement projects and alternatives to resolve violations
TSPs: determination of transmission improvement feasibility and schedule
TSPs: provide transmission improvement cost estimates
ERCOT: determine transmission improvements for study purposes
ERCOT: determine reliably served MW for each load
ERCOT: create load request to transmission improvement mapping

## Slide 18: Case Build
1
Details
Key Design Considerations
  Standardized ERCOT intake and deadline
  Clear eligibility and inclusion rules for Batch Zero
  Defined modeling treatment at entry
  Transparent study case development (posted to MIS Secure)
  For Batch Zero, the interconnecting TDSP submits required project information and any required attestations related to executed agreements or equipment procurement by the applicable deadlines (July 10 for ILLE milestones, July 24 for TDSP submission to ERCOT)
  ERCOT applies the Batch Zero eligibility criteria to determine which Large Loads are included and whether they are treated as base load not subject to further evaluation or load subject to reliability assessment and allocation including ERCOTs determination of whether existing interconnection studies are valid, with certain studies deemed valid without further review under Section 9.2.1.4(3) (e.g., legacy LLIS completed by March 4, 2026 and qualifying RPG-endorsed projects)
  Projects that do not meet the criteria or fail to submit required information by the deadline are excluded from Batch Zero and evaluated in a future process
  ERCOT develops the 2028–2032 study cases using SSWG-based summer peak, summer peak net load, and fall peak cases, and posts those cases to the MIS Secure area to provide transparency into study assumptions

## Slide 19
Details
Key Design Considerations
  ERCOT performs a singular, system-wide steady-state study for all Large Loads included in Batch Zero using SSWG derived base cases appropriate for the study horizon
  ERCOT studies all scenarios and contingencies necessary to assess reliability with applicable NERC Reliability Standards, ERCOT Protocols, the Planning Guide, and Operating Guides
  As soon as violations are identified, ERCOT begins collaborative, iterative process working with TSPs to identify feasible transmission upgrades with ERCOT making final determinations to serve the Large Loads
  For each Large Load subject to assessment, ERCOT documents planning criteria violations and determines the amount of peak Demand that may be reliably served for each year of the 2028–2032 study period. The amount of load that may be reliably served for 2033 will be set to the requested amount for load not reliably served in 2028–2032
  Single, system-wide ERCOT study
  Reliability-based contingency analysis
  Identification of planning criteria violations
  Determination of reliably served MW by year
Steady State Analysis
2

## Slide 20
Details
Key Design Considerations
  Maintain sufficient stability margin
  Mitigation of identified instability
  Coordination with TSPs
  If stability screening criteria violation is identified, ERCOT and the applicable TSP(s) investigates mitigation measures, including transmission improvements, and identifies any required modifications to load levels or timing reflected in the Load Commissioning Plan and determines the amount of peak Demand that can be reliably served in each study year consistent with applicable planning criteria and identified violations, including stability constraints
  Updated dynamic data is evaluated based on whether it is expected to have an adverse impact on results (replacing prior “consistent with” standard)
Stability Screening Study
3

## Slide 21
Details
Key Design Considerations
  Actionable study outcome
  Clear MW allocations by year
  Identification of required upgrades
  Security visibility
  ERCOT produces the Batch Zero Report summarizing study results and identified transmission upgrades
  For each assessed Large Load, ERCOT updates the originally provided Load Commissioning Plan reflecting the amount of peak Demand that can be reliably served each year and the upgrades required to support each level of Demand. The amount of load that may be reliably served for 2033 will be set equal to requested MW for load not achievable in earlier years
  ERCOT includes estimated security requirements in the Batch Zero Report based on TSP cost inputs; TSPs finalize financial security and CIAC obligations in the Interconnection Agreement
  Execution of the Interconnection Agreement reflecting required financial security and cost obligations is required for the ILLE to accept allocated MW amounts and schedule
Final Report
4

## Slide 22
Details
Key Design Considerations
  Clear commitment gate
  TDSP attestation as trigger
  Removal of non-committed projects
  Planning certainty before refinement
  To accept the allocated MW and schedule documented in the LCP, the ILLE must execute a binding Interconnection Agreement by the commitment deadline. The agreement must satisfy the requirements defined in Section 9.7.2 (aligned with PUCT Project No. 58481)
  The interconnecting DSP must submit formal attestation to ERCOT confirming that the ILLE has executed the Interconnection Agreement by the deadline. This attestation serves as verification that the load has satisfied the commitment requirement for inclusion in the Batch Zero Refinement Study
  Large Loads that do not satisfy the commitment requirement by the deadline are deemed withdrawn from the Batch Zero process and are excluded from the Refinement Study and resulting Transmission Plan
  MW allocations for Large Loads that meet the commitment requirement by the deadline are preserved and are not adjusted during the Refinement Study once commitment requirements are met. The Refinement Study may modify recommended transmission facility improvements but does not revisit committed MW amounts
Developer Commitment Deadline
5

## Slide 23
Details
Key Design Considerations
  Removal of non-committed loads
  Re-evaluation of identified upgrades
  Right-sizing of transmission scope
  Preparation of Transmission Plan for RPG
  Immediately following the commitment deadline, ERCOT updates the Batch Zero study to include only those Large Loads that met commitment requirements
  ERCOT evaluates whether the remaining loads continue to result in planning criteria violations and whether previously identified transmission upgrades are still needed, need modification, or are no longer required
  ERCOT works iteratively with relevant TSPs during this period and develops the final Transmission Plan to be delivered to RPG
  The Refinement Study may modify recommended transmission improvements but does not adjust MW allocations for Large Loads that met commitment criteria
  The Refinement Study results in a final report and recommended Transmission Facility improvements submitted for RPG Project Review
Batch Refinement Study
6

## Slide 24
update (highlight changes)
Details
Key Design Considerations
  Stakeholder review and transparency
  Time-bound comment process
  Preservation of governance pathway
  The Batch Refinement Study is submitted to the Regional Planning Group for review including recommended Transmission Facility improvements resulting from the Refinement Study
  RPG Project classification is based on the sum total of all transmission projects in the Refinement Study
  Stakeholders have an opportunity to submit comments within a defined review period. RPG review focuses on the recommended Transmission Facility improvements identified in the Refinement Study and the associated technical assumptions
  RPG review does not reopen MW allocations for committed Large Loads
RPG Comment Period
7

## Slide 25
Details
Key Design Considerations
  Targeted additional evaluation if necessary
  Focused response to material concerns
  If needed, ERCOT may perform targeted additional analysis to address issues raised during RPG review, any additional study is limited to recommended Transmission Facility improvements and does not reopen MW allocations for committed Large Loads
  This step is intended to provide focused technical clarification rather than a full annual RTP-level re-evaluation
  The scope of additional analysis during RPG review is limited to evaluation of recommended Transmission Facility improvements identified in the Refinement Study
RPG Study Mode
8

## Slide 26
Details
Key Design Considerations
  Formal governance review
  Recommendation pathway
  Final approval authority
  ERCOT independent review and approval of recommended projects
  Following completion of RPG review and any additional study, if applicable, the Batch Transmission Plan proceeds to TAC for review and comment in accordance with ERCOT governance procedures
  If required under ERCOT governance procedures, the ERCOT Board considers and acts on the recommended Transmission Plan resulting from the Batch Zero process. Board action applies to recommended Transmission Facility improvements identified in the Refinement Study
  MW allocations for Large Loads that meet commitment criteria are not adjusted during the Refinement Study and are not part of the Transmission Plan approval considered by TAC or the ERCOT Board, if applicable
  Approval reflects ERCOT’s independent technical review, TSP coordination, and stakeholder input through the RPG process
TAC and Board
9

## Slide 27: Fundamental Principles for ERCOT's Proposed Batch Zero Criteria
Senate Bill 6 and PUC Gating Rules: Utilize (and align with) the gating criteria reflected in Project No. 58481 rulemaking (subject to final PUCT direction) to determine which large loads should be confirmed firm and which should be included to be studied in Batch Zero
Pre-Transition Processes: Respect to the extent feasible already granted approvals, including approval to energize and approved studies
Large Load Near-Term Energizations: Assess development activity for large loads that declare 2026 or 2027 energization to evaluate schedule feasibility
ERCOT’s Reliability Responsibility: Ensure all Large Loads confirmed to be firm in Batch Zero have been studied to show that the load can be served reliably
XXX Changes/Clarification vs. Mar 30th Workshop
ERCOT–TSP Coordination: Incorporate structured consultation with Transmission Service Providers in study validation and transmission planning decisions

## Slide 28: Eligibility flowchart: how to assess if a load is included for Batch Zero?
1. See Batch Zero PGRR, Section 9.2.1.1(1)(a)–(b) (Eligibility Criteria for Inclusion as Base Load — Energized Loads) | 2. See Batch Zero PGRR, Sections 9.2.1.1 and 9.2.1.2 (Initial Energization date thresholds for Batch Zero eligibility) | 3. See Batch Zero PGRR, Sections 9.2.1.1(1)(c)–(e) and 9.2.1.4 (Base Load eligibility pathways and evaluation of existing studies) | 4. See Batch Zero PGRR, Section 9.2.1.1 (Eligibility criteria for inclusion as base load) | 5. See Batch Zero PGRR, Section 9.2.1.2(1) (Eligibility Criteria for Inclusion as Load to be Studied and Allocated in Batch Zero) | 6. See Batch Zero PGRR, Section 9.2.1.1 (Eligibility and modeling for base load) | 7. See Batch Zero PGRR, Sections 9.2.1.2 and 9.4 (Inclusion as studied load and MW allocation through Batch Zero results) | 8. See Batch Zero PGRR, Sections 9.2.1.3 and 9.2.2 (Load Not Included in Batch Zero)
Has the load already achieved Initial Energization?1
Large Load request
Included in Batch Zero as a base load6
Not included in Batch Zero8
Studied in Batch Zero and will receive load allocation amounts7
Yes
Is the requested Initial Energization date on or before December 31, 2027?2
No
Does the load, by the required deadline, either: (i) qualify via QSA / interim VRT inclusion and required attestations; OR (ii) have complete and valid studies, an executed Interconnection Agreement, and required development activity?3
Yes
Has the load executed an Intermediate Agreement and met the applicable eligibility criteria for inclusion as load to be studied?5
Does the load meet the eligibility criteria for inclusion as base load (including execution of an Interconnection Agreement)?4
Yes
Yes
No
Yes
No
1
2
4
3
3
5
X
Reference tracker
No
No

## Slide 29: Deep-dive: “Included as base load” (1/2)
If your Large Load by June 1, 2026 | Treatment in Transitional Process | MW Allocation
Is Operational or Approved to Energize | Included as base load | Loads operational before ERCOT’s interim LLI process will be allocated the MWs modeled in the 2025 RTP Loads operational after ERCOT’s interim LLI process will be allocated the lesser of: MWs modeled in the 2025 RTP less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs included in their Load Commissioning Plan, if applicable, less the difference between: The planned MW by December 1, 2025, and the maximum consumed by June 1, 2026 MWs in an updated ramp schedule as provided to the DSP by June 1, 2026 Loads not yet operational will be allocated the lesser of: MWs that can be reliably served as indicated in their interconnection studies MWs included in their interconnection agreement and reflected in their financial security
MW Allocation
If your Large Load
  Achieved Initial Energization before March 25, 2022; or
  Achieved Initial Energization between March 25, 2022, and July 10, 2026
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
  Large Loads that achieved Initial Energization before March 25, 2022, shall be modeled at the level of peak Demand reported to ERCOT as part of development of the 2026 RTP
  Large Loads that achieved Initial Energization between March 25, 2022, and July 10, 2026, shall be modeled at the lesser of:
    The level of peak Demand reported to ERCOT as part of development of the 2026 RTP; or
    The level of peak Demand indicated in the most recent Load Commissioning Plan (if applicable) provided to ERCOT on or before July 24, 2026
  Large Loads meeting base load eligibility criteria that are not yet operational will be modeled at the lesser of:
    The level of peak Demand that can be served reliably as indicated in the Large Load’s complete and valid existing studies
    The level of peak Demand specified in the executed Interconnection Agreement meeting Section 9.7.2
1

## Slide 30: Deep-dive: “Included as base load” (2/2)
If your Large Load
  Has a requested Initial Energization date on or before December 31, 2027, has interconnection studies determined by ERCOT to be complete and valid, has executed an Interconnection Agreement by the required deadline, and has satisfied required equipment procurement and development attestations
  Has a requested Initial Energization date on or after January 1, 2028, and either (i) has complete and valid interconnection studies and (ii) executed an Interconnection Agreement by the required deadline
Treatment in Transitional Process
  Included as base load and not subject to further reliability assessment
MW Allocation
  Large Loads meeting base load eligibility criteria that are not yet operational will be modeled at the lesser of:
    The level of peak Demand that can be served reliably as indicated in complete and valid existing studies; or
    The level of peak Demand specified in the executed Interconnection Agreement meeting Section 9.7.2.
1

## Slide 31
If your Large Load
Treatment in Transitional Process
MW Allocation
  Has a requested Initial Energization date on or before December 31, 2027, does not meet the eligibility criteria for inclusion as base load under Section 9.2.1.1, and has executed an Intermediate Agreement meeting Section 9.7.1; or
  Has a requested Initial Energization date on or after January 1, 2028, meets the applicable study requirements (including evaluation of existing studies under Section 9.2.1.4), and has executed an Intermediate Agreement meeting Section 9.7.1 by the required eligibility deadline (ILLE deadline: July 10, 2026; TDSP/TSP notification: July 24, 2026)
  Studied in Batch Zero
  To be determined during Batch Zero study and reflected in the Load Commissioning Plan (LCP)
Deep-dive: “Studied in Batch Zero”
2

## Slide 32
  ERCOT has determined that the Large Load has a complete and valid set of interconnection studies (as determined through the process on the next slide) that accurately reflect current system conditions and are suitable for eligibility treatment
    Studies that met the required criteria on or before March 4, 2026 are deemed to be complete and valid without further review under Section 9.2.1.4(3)
  ERCOT has determined that existing studies support inclusion as studied load, subject to meeting eligibility requirements under Section 9.2.1.2
  Loads included in the 2024 Permian Basin Reliability Plan Study are treated as complete and valid consistent with the criteria in Section 9.2.1.4(3)
Complete and valid existing studies
Interconnection Studies – Treatment of complete and valid existing studies
3

## Slide 33
Key takeaways
Step 1: Date ordered list
Step 2: Sequential Evaluation
RPG A – Loads 1&2 (Apr 15, 2026)
RPG C – Loads 1, 2, 3 (Jun 10, 2026)
LLIS – Load 2 (May 3, 2026)
LLIS – Load 1 (Apr 28, 2026)
LLIS – Load 3 (Jun 22, 2026)
RPG B – Load 1 (May 3, 2026)
LLIS – Load 4 (Jul 8, 2026)
Process for evaluating study validity for loads that qualify after March 4
Loads with a milestone date1 on or before March 4, 2026 that meet the criteria in Section 9.2.1.4(3) are considered to have valid studies with no additional evaluation
ERCOT orders remaining loads sequentially by milestone date to evaluate legacy interconnection studies
  If two loads share the same date, ERCOT applies pathway-based tie-breakers (e.g., RPG-based loads prioritized over LLIS, then submission timing)
Milestone date depends on interconnection pathway:
  RPG loads - date of RPG endorsement
  LLIS loads - date legacy PG 9.4 and 9.5 satisfied
Earlier loads are validated first; subsequent ones remain valid only if previously validated loads are either outside the study area or included in the study
1
Reference: Batch Zero PGRR145 (April 4, 2026), Section 9.2.1.4 (Evaluation of Existing Studies for Large Loads)
1. Milestone date reflects the date a load meets applicable eligibility criteria (RPG endorsement or completion of LLIS requirements, including execution of an interconnection agreement)
RPG A – Loads 1&2 (Apr 15, 2026)
RPG C – Loads 1, 2, 3 (Jun 10, 2026)
LLIS – Load 2 (May 3, 2026)
LLIS – Load 1 (Apr 28, 2026)
LLIS – Load 3 (Jun 22, 2026)
RPG B – Load 1 (May 3, 2026)
LLIS – Load 4 (Jul 8, 2026)
1
✔
✔
✔
✔
✔
LLIS – Load 2 (May 3, 2026)
✘
LLIS – Load 3 (Jun 22, 2026)
✘
RPG
LLIS
Source
ERCOT sequentially evaluates legacy interconnection studies based on timing to determine eligibility for treatment as base load
3

## Slide 34
If your Large Load
Treatment in Transitional Process
MW Allocation
  Does not meet all applicable eligibility criteria in Sections 9.2.1.1 or 9.2.1.2; or
  Has studies that are sufficient for inclusion under Section 9.2.1.4 but does not meet the eligibility criteria in Section 9.2.1.2; or
  Not included in Batch Zero
  No MW allocation in Batch Zero
  May seek inclusion in a future batch process if eligibility criteria are met
  Fails to provide all required project information under Section 9.2.2 on or before the required submission deadline (July 10, 2026; T(D)SP notification by July 24, 2026)
Deep-dive: “Not included in Batch Zero”
4

## Slide 35
Large Loads with requested Initial Energization dates on or before December 31, 2027 have two paths to demonstrate development progress:
The Large Load was included in a Quarterly Stability Assessment or was included in an interim voltage-ride-through assessment on or before May 1, 2026 and the TSP/DSP has provided both of the following to ERCOT by July 24, 2026;
    Confirmation the ILLE has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence supporting the attestation; and
    An attestation the TSP/DSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance of the requested Initial Energization date so equipment can be installed by December 31, 2026
OR
The Large Load has been found to have valid studies by ERCOT according to PG 9.2.1.4 and the TSP/DSP provides all of the following on or before July 24, 2026:
    A notarized attestation that the ILLE has executed an interconnection agreement that meets the requirements defined in Section 9.7.2;
    An attestation the TSP/DSP has purchased all necessary high-voltage transformers and circuit breakers needed to serve the Load and will take delivery sufficiently in advance of the requested Initial Energization date the equipment can be installed by the ILLE’s requested Initial Energization date;
    Confirmation the ILLE has begun site preparation and construction sufficient to meet its requested Initial Energization date and provided evidence supporting the attestation; and
    Confirmation the ILLE has purchased all necessary ILLE-owned high-voltage transformers and circuit breakers and will take delivery sufficiently in advance so the equipment can be installed by the ILLE’s requested Initial Energization date
Demonstrated Development Activity
5

## Slide 36: Agenda
Batch Zero Concepts
Summary of ERCOT Comments
CLR discussion
BYOG discussion
Timeline and Governance Recap
Stakeholder Feedback

## Slide 37: Stakeholder feedback through March 20
Source: ERCOT PGRR145 “Key Documents” section
Author
G
Date of submission
Mar 5; Mar 11; Mar 19
Mar 9; Mar 20
Mar 9; Mar 20
Mar 10
Mar 19
Mar 19
Mar 20
Mar 20
Mar 19
Mar 20
Mar 20
Schaper Energy Consulting
Reliant Energy1
Crusoe
Rose City Partners
Lancium
Skybox Datacenters
Oncor
CenterPoint Energy
IREN
Stream Datacenters2
Agentic Infrastructure1
Provident Inc.2
Mar 20
3-Waters Technical Services
Vistra
Eolic
TEBA
Satoshi Energy
Black Mountain
Sandow Lakes Energy
Emerald AI
AEP
Monarch Energy
Crow Holdings
Zero Emission Grid
Author
Date of submission
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
Mar 20
1. Agentic and Reliant filed comments together on Mar 20 | 2. Stream Datacenters and Provident filed comments together on Mar 20
Note: based on list of comments submitted as of 3/23

## Slide 38: Comments Filed after Workshop up to March 30, 2026
Speaker
Company
Andrew Schaper
Shannon Caraway
Lee Bratcher
Adam Taylor
Blake Holt, Sandeep Borkar
Harsh Naik
Jim Lee
Ned Bonskowski, Monica Jha

## Slide 39: Agenda
Batch Zero Concepts
Summary of ERCOT Comments
CLR discussion
BYOG discussion
Timeline and Governance Recap
Summary of ERCOT Feedback
Stakeholder Feedback

## Slide 40: Key updates in April 4 PGRR145 ERCOT comments
Incremental clarifications and gap fixes to Planning Guide language: added targeted provisions (e.g., DSP delegation flexibility, explicit dynamic data submission responsibility, clarification of roles and processes) to address identified omissions and improve operability
Expanded definition of valid studies: explicitly recognized additional studies (e.g., Permian Basin Reliability Plan) as eligible for “complete and valid” status, broadening the safe harbor scope
Strengthened governance and stakeholder engagement in study process: codified requirement to present Batch Zero study scope and methodology to RPG and incorporate stakeholder feedback
Refined roles and responsibilities across entities (ERCOT / TSP / DSP): clarified responsibilities in key sections (e.g., study coordination, data submission, attestations), including incorporation of stakeholder feedback
Improved internal consistency and process clarity: addressed inconsistencies (e.g., LCP vs RTP alignment, sequencing of updates, removal of unintended eligibility constraints) and corrected structural gaps in eligibility logic
Enhanced coordination requirements in study execution: introduced more explicit consultation steps with TSPs in identifying transmission upgrades and study outputs
General drafting clean-up and clarifications: incorporated typographical fixes, corrected references, and clarified language throughout the document
Year 6 (2033) allocation remains under development. ERCOT is actively reassessing the approach and will provide more explicit guidance in future comments

## Slide 41: Key updates in April 4 PGRR145 ERCOT comments
Link to PGRR145 Comments from ERCOT April 4
  Includes matrix of ERCOT responses to every comment (sample below)
ERCOT plans next round of comments April 22 (after PUCT 4/17 meeting)
ERCOT has filed responses to stakeholder comments submitted on or before March 20, 2026; additional responses may follow to address subsequent comments

## Slide 42: Agenda
Batch Zero Concepts
Summary of ERCOT Comments
CLR discussion
BYOG discussion
Timeline and Governance Recap
CLR Discussion
Stakeholder Feedback

## Slide 43: Provisional CLRs – Definition1
New Resource Type: ‘Provisional CLR’
Same as a CLR but locked in for a period of time and has Low Power Consumption (LPC) limits defined in the Batch Zero Interconnection Study
What’s different?
PCLR load bids can be ‘capped’ to mitigate transmission constraints identified in SCED
PCLR bids are capped dynamically (“last-in-line/just-in-time”) in each run of SCED to a price that will just allow SCED to resolve a constraint
Submits CLR Energy Bid Curve  bid-to-buy prices between Low Power Consumption (LPC) and Maximum Power Consumption (MPC) – same as any other CLR
PCLRs are not eligible to provide Ancillary Services
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 44: Provisional CLRs – Structure of Revision Requests1
Will consist of a comments to existing PGRR145 and companion NPRR1325
Modular structure adds to PGRR145 and NPRR1325
  Example – Section 9.2.2.1, Additional Information Required for Provisional Controllable Load Resources (PCLRs) compliments Section 9.2.2 as written in PGRR145
This structure will allow the PCLR concepts to move forward in parallel with PGRR145 and NPRR1325 if possible, without interfering with the core Batch Zero language
Language related to PCLR approval to energize and PCLR bid capping in SCED is intended to remain grey-boxed until implementation of NPRR1188 and until system changes for the bid capping are in place
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 45: PCLR Language – Foundational Concepts1
Allocation in Batch Zero
Registration Requirements
Ensure Real-Time Dispatch
Load is assessed through the Batch Zero process in the same manner as load requesting firm service for steady state and at full consumption for stability
The level of firm load that can be reliably served becomes the maximum Low Power Consumption (LPC) value for the PCLR in real-time (instead of a hard limit)
The remaining requested load amount is approved contingent on qualification as a PCLR
Intention to register as a PCLR must be declared prior to the start of Batch Zero
Once allocated in Batch Zero, the load must register and qualify as PCLR before it may consume above initial limits
Load must remain registered as a PCLR until an exit date identified in Batch Zero
Obligation to remain a PCLR transfers to subsequent owners of the Large Load
Like traditional CLRs, PCLRs must follow SCED basepoints when consuming energy2
Dynamic bid capping logic is added to ensure the PCLR will be dispatched rather than allowing the constraint to violate
1. Design and NPRR/PGRR language still under internal review and may change prior to filing | 2. On implementation of NPRR1188

## Slide 46: Provisional Controllable Load Resources (PCLRs) in Batch Zero1
ERCOT validates completion of all steps prior to granting Approval to Energize
8
QSE establishes required ICCP telemetry points
7
RE coordinates with ERCOT to establish metering and submit CLR parameters via RIOO
6
ILLE registers with ERCOT as a Resource Entity (RE) and designates a QSE
5
ERCOT studies the full load amount in the Batch Zero Refinement Study
4
ILLE submits updated Declaration to accept allocation amounts
3
ERCOT studies PCLR in Batch Zero
2
Submission of Declaration and required information to ERCOT
(by July 24)
1
Must be done before non-firm load may energize
May be done in parallel with QSA
1. Design and NPRR/PGRR language still under internal review and may change prior to filing

## Slide 47: Provision CLR (PCLR) – Dynamic Bid Capping Process
PUBLIC
1
SCED₋₁ (Previous Run)
After each SCED run, generate a fresh list of transmission constraints whose Shadow Price ≥ 90% of Max Shadow Price:
Constraint₁₂₃
Constraint₂₃₄
Constraint₃₄₅
Constraint₄₅₆
⚡ Shadow price threshold triggered
Match
2
SCEDcurrent (Before Step 2)
Compare the matching list against all active constraints in the current SCED run:
Constraint₂₃₄
Constraint₄₅₆
Constraint₆₇₈
Constraint₇₈₉
✔ 2 constraints match — evaluate PCLRs
Cap
3
SCED Step 2 (Bid Capped)
−0.02
Shift Factor Rule
Only PCLRs with a Shift Factor ≤ −0.02 on a matching constraint are eligible for bid capping
CAP
Bid Cap Applied
The PCLR's Energy Bid Curve is capped at the Adjusted Bid Cap (ABC) value before Step 2 executes
✓
Adjusted Bid Cap Formula:
ABC = Step 1 System Lambda − max ( MaxShadowPrice × ShiftFactor ) − $0.01 / MWh
Only applied where PCLR Shift Factor ≤ −0.02 | Constraint must appear in prior-run trigger list | No standard market mitigation applies to Energy Bid Curves

## Slide 48: Agenda
Batch Zero Concepts
Summary of ERCOT Comments
CLR discussion
BYOG discussion
Timeline and Governance Recap
BYOG Discussion
Stakeholder Feedback

## Slide 49: BYOG Objectives: Allocation, Coordination, and Operating Agreement
Allocation in Batch
Load and Generator Coordination
Operating Agreement
Load is assessed through the Batch Study process in consideration of co-location with generation
Load from the grid may be limited or zero, but higher load levels may be approved when considering co-located generation
Entity(ies) are responsible for self-limiting operations of the site to adhere to limits: load and generation must be coordinated to ensure compliance under all conditions
ERCOT Operations engaged on details of operational solutions to ensure reliable grid performance
Load and Generator enter into an operating agreement defined in protocols
The agreement defines obligations for self-limiting behavior, including load reduction upon generation loss

## Slide 50: Conceptual Batch Zero BYOG operating configurations for Large Load interconnection3
Batch Self-Limiting Facility (SLF)
Source: ERCOT discussions
Site operates with a fixed transmission withdrawal limit determined through the Batch Study
Generation mix may include thermal resources, renewables, and batteries
A fixed transmission withdrawal limit is established at the POI
Load and generation owners must coordinate operations to ensure grid imports never exceed the limit
The site would be equipped with a reverse power relay or equivalent protection to enforce the limit
Transmission upgrades may be required, as identified by the batch study, to meet reliability criteria2
1. RUC (Reliability Unit Commitment): ERCOT mechanism used to commit generation outside the market to maintain system reliability | 2. Based on batch study results for the generation/load mix | 3. Conceptual designs still under internal review and may change
Point of interconnection (POI)
MW limit ensured by reverse power relay
~
~
~
ERCOT considering range of operations
Connected island (Operating range net 0): operates effectively at net 0, with only auxiliary load for generation
Net Generation site (Operating Range from 0 to Gen): operates from 0 to full generation output for SCED dispatch not consumed by local load
Batch Load to Net Gen site (Operating Range from Batch Load to Gen): Operates from batch-limited load (grid import) up to full generation output for SCED dispatch not consumed by local load
1
2
3

## Slide 51: Up to date BYOG concept scales from islanded to grid-interactive with increasing complexity
Details
Proposed framework
  ERCOT still reviewing SLF options1
  Fully islanded configuration where generation equals load with no grid interaction
  Allows generation to export while load remains restricted to zero consumption from the grid
  Batch-allocated load with co-located generation under a contractual “self-limiting” arrangement
Generation follows the standard interconnection process and is dispatchable, with export subject to SCED
Load is studied in the batch process and limited to the approved import level at the POI; import limits always apply, regardless of co-located generation availability or status
An operating agreement requires load to automatically and immediately reduce consumption upon generation loss or outage
Batch assumes generation for planning but allocates capacity as if generation is unavailable, enforcing self-limiting behavior
Enables load to operate above traditional G-1 limits by shifting contingency response from the grid to the load (via curtailment)
ERCOT is already having numerous meeting with Operations, Gen Interconnection, Planning, Markets, and Compliance teams to find a Batch Zero solution
Goal for revision language in 2 more weeks (PRS 4/22 and ROS 4/23)
Still potential for Batch Zero, but June 1 approval remains challenging
1. All options rely on reverse power relays to enforce strict import limits and protect the grid
Source: ERCOT discussions
Next
Steps

## Slide 52: APPENDIX

## Slide 53: Concept Review – Provisional CLR
Source: ERCOT discussions
Point of interconnection
Large Load registers entirely as a CLR, with no associated/ synchronized generation or storage commonly metered with the CLR at the POI.
Load-Only CLR leverages the existing CLR framework as the simplest near-term option,1 subject to required market/system implementation items (e.g., SCED CLR Bid Curve capping enhancements) before energization
Participates as dispatchable demand and must follow SCED basepoints within its registered operating range (PC/LPC/MPC)
No assurance of service above awarded firm MW; real-time consumption may be reduced below PC based on system conditions and SCED CLR Bid Curve capping
Must meet existing CLR telemetry and dispatch performance requirements (subject to SCED instructions and registered operating limits)
Load may register operational capability above awarded firm MW, subject to real-time dispatch and congestion mitigation2
Illustrative example
  150 MW requested in Year 1
  ERCOT performs steady-state and stability studies and allocate phased MW (e.g., 100 MW in Years 1–2, 300 MW in Years 3-4, until transmission upgrade in Year 5)
  Operational parameters:
    PC = 0–100 MW (firm)
    LPC = 0–100 MW
    MPC = 150 MW (upper operational capability; not a planning guarantee)
    CLR quantity may be modified in later years as transmission capability increases
1. NPRR1188 later in 2026: Nodal pricing align local congestion prices. NPRR1255 mitigation methods needed (small project) | 2. Potentially subject to additional limits identified in dynamic studies
Description
Details
Load
Illustrative scheme
Chart: 
 | 100 | 100 | 300 | 300 | 1000
 | 50 | 200 | 200 | 400
50
Year 1
Year 2
Year 3
Year 4
Year 5
150
300
500
700
CLR Load
Firm Load
POTENTIALLY FEASIBLE CONFIGURATION
1
ERCOT grid
XXX Changes/Clarification vs. Mar 10th Workshop